## Instructions
Custom Express: Transformer Early Replacement Calculator
v1.0 6/27/2024
Instructions:
This section provides the instructions for using the Transformers Savings Tool to screen, conduct metering, calculate savings, and generate project documentation for transformer replacement projects.
STEP 1— Project Data tab.
Complete general project information in blue cells on the Project Data tab.
STEP 2—ECM Data tab.
Complete the inventory of existing transformers on the ECM Data tab by listing the inventory of up to 50 existing transformers and the related parameters of this equipment as shown in the sections highlighted in blue. - Only include transformers sizes from 15 to 500 kVA - Only include replacement of existing pre-TP1/pre-2000 transformers - Single phase transformers and specialty transformers are not allowed - A custom savings calculation is required for other transformer applications
STEP 3—Efficiency Tables tab
The Efficiency Tables tab provides information about the how the savings are dervied using baseline and proposed transformer parameters in the "Transformer Loss Data" section. In the "Transformer Efficiency Specifications" section, confirm whether the proposed transformers meet the TP-1 efficiency standard.
STEP 4—Pre-Install Photos
The Pre-Install Photos tab peovides information on how to upload photos of preexisting tranfsromers. When uploading please include photos of the transformers' nameplates and serial numbers.
STEP 5—Savings Summary tab
On the Summary tab, review project costs and view the estimated project savings. The measure life for all transformer projects is 30 years. Submit the new transformer cut sheet(s) (highlighting the KVA and no load watts information), the Mass Save custom project application, and this savings calculator to the electric Program Sponsor as noted in the Project Information section of the Project Information tab. All energy savings cacluations are required to be reviewed by the appropriate Program Sponsor prior to the customer receipt of an incentive offer.
STEP 6—Minimum Requirements Data (MRD) tab(s)
The Minimum Requirements tab provides information the project will need to deliver the energy savings projected. The project should be reviewed for this information prior to close.

## Project Data
Custom Express: Transformer Early Replacement Calculator
v1.0 6/27/2024
Facility Information
Facility Name:
Street Address:
City:
Zip Code:
State:
Customer Information
Company Name:
Contact Person:
Phone Number:
Email Address:
Vendor Information
Company Name:
Street Address:
City:
Zip Code:
State:
Contact Person:
Phone Number:
Email Address:
PROJECT DESCRIPTION AND NOTES

## ECM Data
Custom Express: Transformer Early Replacement Calculator
Instructions: - Only include transformers sizes from 15 to 500 kVA - Only include replacement of existing pre-TP1/pre-2000 transformers - Single phase transformers and specialty transformers are not allowed - A custom savings calculation is required for other transformer applications
Line No. | Transformer Identification |  |  |  | Equipment Operation |  |  | Existing Transformers |  |  | Replacement Transformers |  |  |  |  | Energy |  |  | Peak | Project Costs |  |  |  | Minimum Eff
| Transformer | Building | Location | Transformer | Hours | Days | Average | Rated | No Load | Year | Manufacturer | Model | Rated | No Load | Replace? | Baseline | Proposed | Savings | Demand | Materials | Labor | Total | Comments
| Tag | Name | or Room ID No | Designation/ ID | per | per | Load | kVA | Losses | Manufactured |  | No. | kVA | Losses | 1 = Yes | Losses | Losses | per Year | Reduction |  |  |  |  | NLL | Check
| No. |  |  | (if any) | Day | Year | % |  | (Watts) |  |  |  |  | (Watts) | 0 = No | kWh | kWh | (kWh) | (kW) |  |  |  |  | Watts | %
Example: | T-001 | Murphy Bldg | 14th Fl Elec Rm | LT01 | 24 | 365 | 40% | 30 | 453.4887 | 1976 | REX | BA30H-M/Z3 | 30 | 75 | 1 | 3972.5606 | 657 | 3315.5606 | 0.37849 | 1000 | 1000 | 2000
Project Totals: | [14 empty] | 0 |  |  |  |  | 5000 | 5000 | 10000
1 | [19 empty] | 1000 | 1000 | 2000 |  |  | #VALUE!
2 | [19 empty] | 1000 | 1000 | 2000 |  |  | #VALUE!
3 | [19 empty] | 1000 | 1000 | 2000 |  |  | #VALUE!
4 | [19 empty] | 1000 | 1000 | 2000 |  |  | #VALUE!
5 | [19 empty] | 1000 | 1000 | 2000 |  |  | #VALUE!
6 | [24 empty] | #VALUE!
7 | [24 empty] | #VALUE!
8 | [24 empty] | #VALUE!
9 | [24 empty] | #VALUE!
10 | [24 empty] | #VALUE!
11 | [24 empty] | #VALUE!
12 | [24 empty] | #VALUE!
13 | [24 empty] | #VALUE!
14 | [24 empty] | #VALUE!
15 | [24 empty] | #VALUE!
16 | [24 empty] | #VALUE!
17 | [24 empty] | #VALUE!
18 | [24 empty] | #VALUE!
19 | [24 empty] | #VALUE!
20 | [24 empty] | #VALUE!
21 | [24 empty] | #VALUE!
22 | [24 empty] | #VALUE!
23 | [24 empty] | #VALUE!
24 | [24 empty] | #VALUE!
25 | [24 empty] | #VALUE!
26 | [24 empty] | #VALUE!
27 | [24 empty] | #VALUE!
28 | [24 empty] | #VALUE!
29 | [24 empty] | #VALUE!
30 | [24 empty] | #VALUE!
31 | [24 empty] | #VALUE!
32 | [24 empty] | #VALUE!
33 | [24 empty] | #VALUE!
34 | [24 empty] | #VALUE!
35 | [24 empty] | #VALUE!
36 | [24 empty] | #VALUE!
37 | [24 empty] | #VALUE!
38 | [24 empty] | #VALUE!
39 | [24 empty] | #VALUE!
40 | [24 empty] | #VALUE!
41 | [24 empty] | #VALUE!
42 | [24 empty] | #VALUE!
43 | [24 empty] | #VALUE!
44 | [24 empty] | #VALUE!
45 | [24 empty] | #VALUE!
46 | [24 empty] | #VALUE!
47 | [24 empty] | #VALUE!
48 | [24 empty] | #VALUE!
49 | [24 empty] | #VALUE!
50 | [24 empty] | #VALUE!
[13 empty] | Project Totals: |  | 0 | 0 | 0 | 0 | 0 | 5000 | 5000 | 10000 |  | 0 | #DIV/0!
Note on I11: Guidance: Default value is 10% - only update this field if based on metering data.
Note on P11: Guidance: No load losses should be entered by the vendor per the cutsheet. No load losses can differ based on manufacturer and is also dependent on whether the transformer has an aluminium or copper core
Note on P13: Guidance: No load losses should be entered by the vendor per the cutsheet. No load losses can differ based on manufacturer and is also dependent on whether the transformer has an aluminium or copper core

## Efficiency Tables
Transformer Loss Data
This sheet contains transformer loss specifications for both proposed (Powersmiths K-7) and baseline (pre-TP-1) options
Proposed case efficiency is based on losses from Powersmiths K-7 cutsheets for varying sizes and %load conditions. The values were used to create regressions that calculate losses for different transformer sizes and part-load conditions.
Baseline efficiency is based on Powersmiths metering data. This tool calculates baseline losses and part-load conditions using two datasets:
1- No load losses were compiled by Powersmiths base on 1,000+ low-load (<5%) measurements
2- part-load losses are based on a curve shape provided by Powersmiths for 75 kVA transformers - it is assumed that the same curve shape (%load vs %loss) relationship applies to other transformer sizes
Baseline load losses are calculated based on #1 and #2. Powersmiths could not provide a similar table, citing intellectual property concerns, so it was necessary to create a calculation using a sample of part-load measurements and no-load losses for additional sizes.
After adding functionality to include part load losses, it was observed that these curve shapes do not result in significantly different savings than using NLL only for applications under 20% load. The calculator was revised to use NLL only.
Transformer Efficiency Specifications
Curves created excluding 75% and 100% to improve regression accuracy (r-squared) in the most common %load region (50-100% load is atypical)
Proposed Case Efficiency - Load Losses
Powersmiths K7 Linear Load Losses (watts) | [12 empty] | Powersmiths E-Saver-80R
Size | Percent Load | [11 empty] | Aluminum, K-7, 130C Rise |  |  |  |  | Proposed Polynomial Coefficients Table
kVA | 0% | 16.7% | 25% | 35% | 50% | 75% | 100% | [5 empty] | kVA | No Load Losses (W) | Full Load Losses (W) | Coil Losses (W) |  | Size kVA | A | B | C
15 | 35 | 50 | 69 | 104 | 181 | 396 | 775 | [5 empty] | 15 | 35 | 775 | 740 |  | 15 | 620.92 | 19.334 | 35.215
30 | 57 | 84 | 118 | 176 | 310 | 680 | 1332 | [5 empty] | 30 | 57 | 1332 | 1275 |  | 30 | 1058.1 | 25.619 | 57.535
45 | 78 | 113 | 156 | 234 | 406 | 883 | 1725 | [5 empty] | 45 | 78 | 1725 | 1647 |  | 45 | 1371.6 | 31.912 | 78.51
75 | 111 | 164 | 230 | 348 | 611 | 1341 | 2537 | [5 empty] | 75 | 111 | 2537 | 2426 |  | 75 | 2095.8 | 51.472 | 111.82
112.5 | 164 | 232 | 316 | 467 | 801 | 1719 | 3313 | [5 empty] | 112.5 | 165 | 3231 | 3066 |  | 112.5 | 2659.6 | 59.951 | 164.97
150 | 203 | 284 | 386 | 567 | 969 | 2068 | 3945 | [5 empty] | 150 | 203 | 3945 | 3742 |  | 150 | 3202.6 | 74.035 | 204.07
225 | 319 | 406 | 515 | 709 | 1140 | 2315 | 4317 | [5 empty] | 225 | 319 | 4317 | 3998 |  | 225 | 3433.1 | 79.869 | 320.21
300 | 384.1818 | 495.4545 | 635.2727 | 883.2727 | 1433.4545 | 2923.7273 | 5435.7273 | [5 empty] | 300 | 371 | 6229 | 5858 |  | 300 | 4379.9 | -97.8 | 385.63
500 | 558 | 734 | 956 | 1348 | 2216 | 4547 | 8419 | [5 empty] | 500 | 558 | 8419 | 7861 |  | 500 | 6904.6 | 145.62 | 560.09 | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c
This performance data is from Powersmiths cutsheets takeoffs | [21 empty] | a | 620.92 | a | 1058.1 | a | 1371.6 | a | 2095.8 | a | 2659.6 | a | 3202.6 | a | 3433.1 | a | 4379.9 | a | 6904.6
[22 empty] | b | 19.334 | b | 25.619 | b | 31.912 | b | 51.472 | b | 59.951 | b | 74.035 | b | 79.869 | b | -97.8 | b | 145.62
Baseline Efficiency Curve (redundant to next table) | [12 empty] | Baseline Efficiency Curve (2022) | [8 empty] | c | 35.215 | c | 57.535 | c | 78.51 | c | 111.82 | c | 164.97 | c | 204.07 | c | 320.21 | c | 385.63 | c | 560.09
Baseline/Pre-TP-1 Linear Load Losses | [8 empty] | Measured Baseline Losses | [8 empty] | Baseline Polynomial Coefficients Table
kVA | 0% | 16.7% | 25% | 35% | 50% | 75% | 100% |  | kVA | No. of Data Points | Average % Loading | Minimum % Loading of Sample | Maximum % Loading of Sample | Losses at Avg % Load (W) | Minimum Losses of Sample (W) | Maximum Losses of Sample (W) | Coil Losses (W) | Size kVA | A | B | C
15 | 297.3204 | 317.4852 | 348.0182 | 402.8941 | 522.276 | 820.0935 | 1241.471 |  | 15 | 59 | 2.3% | 0.1% | 4.9% | 297 | 123 | 832 | 867 | 15 | 988.48 | -44.328 | 297.32
30 | 453.4887 | 484.2452 | 530.8157 | 614.5153 | 796.6027 | 1250.8497 | 1893.5567 |  | 30 | 241 | 2.5% | 0.1% | 5% | 453 | 205 | 1154 | 994 | 30 | 1507.7 | -67.612 | 453.49
45 | 653.7044 | 698.0399 | 765.1714 | 885.8245 | 1148.3037 | 1803.1013 | 2729.5641 |  | 45 | 293 | 2.5% | 0.1% | 5% | 653 | 260 | 1577 | 1560 | 45 | 2173.3 | -97.463 | 653.7
75 | 856.9234 | 915.0416 | 1003.0424 | 1161.2033 | 1505.2802 | 2363.6366 | 3578.1116 |  | 75 | 394 | 2.5% | 0.1% | 5% | 856 | 450 | 2434 | 2479 | 75 | 2848.9 | -127.76 | 856.92
112.5 | 1164.2545 | 1243.2166 | 1362.7785 | 1577.6629 | 2045.1412 | 3211.3427 | 4861.383 |  | 112.5 | 199 | 2.4% | 0.1% | 4.9% | 1163 | 477 | 3341 | 3071 | 112.5 | 3870.7 | -173.58 | 1164.3
150 | 1510.6278 | 1613.0816 | 1768.2139 | 2047.0278 | 2653.5839 | 4166.7378 | 6307.6757 |  | 150 | 161 | 2.5% | 0.1% | 4.9% | 1509 | 580 | 4510 | 4026 | 150 | 5022.3 | -225.22 | 1510.6
225 | 1818.96 | 1942.3255 | 2129.1216 | 2464.8439 | 3195.2034 | 5017.2052 | 7595.1271 |  | 225 | 139 | 2.6% | 0.1% | 4.9% | 1817 | 721 | 3214 | 6218 | 225 | 6047.4 | -271.19 | 1819
300 | 2439.6288 | 2605.0893 | 2855.6244 | 3305.9024 | 4285.4764 | 6729.185 | 10186.75 |  | 300 | 40 | 2.7% | 0.1% | 5% | 2437 | 1107 | 3518 | 6049 | 300 | 8110.9 | -363.73 | 2439.6
500 | 3512.7852 | 3751.0293 | 4111.771 | 4760.1196 | 6170.5937 | 9689.2532 | 14667.7496 |  | 500 | 14 | 3% | 0.2% | 4.9% | 3509 | 2085 | 5074 | 8330 | 500 | 11697 | -523.73 | 3512.8
Source: Validated data from Powersmiths International Corp. database of field measurements as of August 17, 2022
this data is used to estimate the missing 300KVA losses | [21 empty] | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c |  | y=a*x^2-b*x+c
225 | 319 | 406 | 515 | 709 | 1140 | 2315 | 4317 |  | Notes: | [12 empty] | a | 988.48 | a | 1507.7 | a | 2173.3 | a | 2848.9 | a | 3870.7 | a | 5022.3 | a | 6047.4 | a | 8110.9 | a | 11697
500 | 558 | 734 | 956 | 1348 | 2216 | 4547 | 8419 |  | 1. On-Site measurements of existing transformers collected using the Cyberhawk EP-300 Portable Meter. | [12 empty] | b | -44.328 | b | -67.612 | b | -97.463 | b | -127.76 | b | -173.58 | b | -225.22 | b | -271.19 | b | -363.73 | b | -523.73
[9 empty] | With the unique capability to simultaneously measure up to three 3-phase ports, the Cyberhawk Portable Meter | [12 empty] | c | 297.32 | c | 453.49 | c | 653.7 | c | 856.92 | c | 1164.3 | c | 1510.6 | c | 1819 | c | 2439.6 | c | 3512.8
can be used to quantify losses and efficiency of transformers with near revenue class accuracy.
2. Due to the small quantity of data points for 500 kVA transformers, each project will be required to
measure the 500 kVA transformers, provided they are safe to open and measure.
Baseline Efficiency Curve Shapes
this data is used to estiamte losses at part load conditions (only the NLL were measured for baseline pre TP-1 transformers)
Watts Takeoffs
% load | % load^2 | Watts | % of NLL |  | Curve | Curve
0 | 0 | 855 | 100% |  | Fit (% NLL) | Fit
0.03 | 0.0009 | 856 | 100.1% |  | 3.3282 | 2845.621
0.15 | 0.0225 | 900 | 105.3% |  | -0.14925 | -127.6117
0.21 | 0.0441 | 955 | 111.7% |  | 1.0011 | 855.9223
Powersmiths 75 kVA Pre-TP-1 Measurement Takeoffs | [9 empty] | Powersmiths 75 kVA Pre-TP-1 Measurement Summary
% | Efficiency Takeoffs
Load | Eff | % Loss | Load (W) | Loss (W)
3% | 62% | 38% | 2250 | 855
5% | 76.5% | 23.5% | 3750 | 881.25
7% | 83% | 17% | 5250 | 892.5
9% | 87% | 13% | 6750 | 877.5
11% | 89% | 11% | 8250 | 907.5
13% | 91% | 9% | 9750 | 877.5
15% | 92% | 8% | 11250 | 900
17% | 93% | 7% | 12750 | 892.5
19% | 93.5% | 6.5% | 14250 | 926.25
21% | 94% | 6% | 15750 | 945
30% | 96% | 4% | 22500 | 900
40% | 96.5% | 3.5% | 30000 | 1050
50% | 96.6% | 3.4% | 37500 | 1275
60% | 96.8% | 3.2% | 45000 | 1440
70% | 96.8% | 3.2% | 52500 | 1680
80% | 96.6% | 3.4% | 60000 | 2040
90% | 96.2% | 3.8% | 67500 | 2565
100% | 95.8% | 4.2% | 75000 | 3150
|  |  | 75 | kVA
Comparison of Efficiency and Wattage Takeoffs
75 kVA Baseline
% | Efficiency Takeoffs |  |  |  | Watts Takeoffs |  | Curve Fit |  | Diff
Load | Eff | % Loss | Load (W) | Loss (W) | Loss (W) | Eff | Loss (W) | Eff | %
3% | 62% | 38% | 11580 | 4400.4 | 856 | 92.61% | 854.655 | 92.62% | 0.1571%
5% | 76.5% | 23.5% | 19300 | 4535.5 |  |  | 856.6558 | 95.56%
7% | 83% | 17% | 27020 | 4593.4 |  |  | 860.933 | 96.81%
9% | 87% | 13% | 34740 | 4516.2 |  |  | 867.4868 | 97.5%
11% | 89% | 11% | 42460 | 4670.6 |  |  | 876.317 | 97.94%
13% | 91% | 9% | 50180 | 4516.2 |  |  | 887.4238 | 98.23%
15% | 92% | 8% | 57900 | 4632 | 900 | 98.45% | 900.807 | 98.44% | -0.08967%
17% | 93% | 7% | 65620 | 4593.4 |  |  | 916.4667 | 98.6%
19% | 93.5% | 6.5% | 73340 | 4767.1 |  |  | 934.403 | 98.73%
21% | 94% | 6% | 81060 | 4863.6 | 955 | 98.82% | 954.6157 | 98.82% | 0.04024%
This table was created to check that the two takeoff methodologies provide a consistent result
Report Tables - these tables are used in the Appendix B section of the word document
kVA | Pre-TP-1 NLL | Proposed NLL | P NLL | Proposed NLL | Annual kWh | [7 empty] | Expected Annual Savings, kWh | Expected Annual Savings, kWh
| Watts | Watts | kWh | kWh | Savings | [5 empty] | Original Size (kVA) | New Size (kVA) | (TP-1) | (NEMA Premium®)
15 | 297.3204 | 35 | 2604.5265 | 306.6 | 2297.9265 | [5 empty] | 15 | N/A | N/A | N/A
30 | 453.4887 | 57 | 3972.5606 | 499.32 | 3027 | [5 empty] | 30 | 15 | 800 | 1300
45 | 653.7044 | 78 | 5726.4505 | 683.28 | 4274 | [5 empty] | 45 | 30 | 900 | 1600
75 | 856.9234 | 111 | 7506.6487 | 972.36 | 6563 | [5 empty] | 75 | 45 | 1500 | 2400
112.5 | 1164.2545 | 164 | 10198.8697 | 1436.64 | 8791 | [5 empty] | 112.5 | 75 | 1800 | 3100
150 | 1510.6278 | 203 | 13233.0992 | 1778.28 | 10553 | [5 empty] | 150 | 112.5 | 1500 | 3100
225 | 1818.96 | 319 | 15934.0896 | 2794.44 | 11975 | [5 empty] | 225 | 150 | 2300 | 4300
500 | 2439.6288 | 558 | 21371.1482 | 4888.08 | 9626 | [5 empty] | 300 | 225 | 3100 | 5500
[11 empty] | 500 | 300 | 5500 | 8900
[11 empty] | 750 | 500 | 6000 | 10900
[11 empty] | 1000 | 750 | 7300 | 13300

## Pre-Install Photos
Pre-Installation / Existing Transformer Photos
Instructions to add photos of existing transformer nameplate(s): |  | Transformer 1 | Transformer 2 | Transformer 3
Please upload photos of the transformer nameplate(s) and serial numbers |  | Click Here | Click Here | Click Here
1. Select a blue box to the right.
2. Click on the "Insert" menu at the top of the -----> left of the menu in the Excel workbook ribbon.
3. Under the "Text" group click on "Object." ----->
4. Select "Create From File" tab.
5. Select "Browse" button to find photo file location & select photo. |  | Description/Location | Description/Location | Description/Location
6. Check the box to "Display as icon" | ------>
7. Click on "OK" so photo icon shows on spreadsheet. |  | Transformer 4 | Transformer 5 | Transformer 6
8. Enter description/location below photo. |  | Click Here | Click Here | Click Here
|  | Description/Location | Description/Location | Description/Location
|  | Transformer 7 | Transformer 8 | Transformer 9
|  | Click Here | Click Here | Click Here
|  | Description/Location | Description/Location | Description/Location
|  | Transformer 10 | Transformer 11 | Transformer 12
|  | Click Here | Click Here | Click Here
|  | Description/Location | Description/Location | Description/Location
|  | Transformer 13 | Transformer 14 | Transformer 15
|  | Click Here | Click Here | Click Here
|  | Description/Location | Description/Location | Description/Location
|  | Transformer 16 | Transformer 17 | Transformer 18
|  | Click Here | Click Here | Click Here
|  | Description/Location | Description/Location | Description/Location

## Savings Summary
Custom Express: Transformer Early Replacement Calculator
Cell Color Key
Required Input
Calculated Result
Table Header/Guidance
OVERALL PROJECT SAVINGS SUMMARY:
Total Labor Cost ($):
Total Material Cost ($):
Total Proposed Cost ($): | 0
Value of Federal/State Tax Credits ($): | 0
Energy Savings (kWh): | 0
% Summer On Peak: | 15.75%
% Summer Off Peak: | 17.69%
% Winter On Peak: | 29.68%
% Winter Off Peak: | 36.87%
Summer Peak (kW): | 0
Winter Peak (kW): | 0
Measure Life (years): | 30

## MRD
Customer |  | 0
Facility |  | 0
Document: |  | Transformer Replacement Minimum Requirement Document (MRD)
This document specifies the agreed upon minimum equipment specifications and operational requirements of the proposed system. These requirements shall address the criteria necessary to be met to achieve the demand and energy savings estimated in the engineering analysis for this project. (Use additional sheets if necessary.)
Yes/No checkboxes are intended to be used during post-installation inspections to record site findings.
EQUIPMENT DESCRIPTION: Provide a list of equipment or materials installed as part of this project. Include mfr, model, HP, kW, efficiency ratings, etc.
| Project Intent | [5 empty] | Comment
| N/A indicates an evaluated transformer is not included in the replacement scope | [5 empty] | Ref No.
| 1. | Replaced the listed existing transformers with new units having the listed kVA and no-load ratings.
|  | Building | Location | Existing | Replacement
|  | Name | or Room ID | Rated | Rated | No Load
|  |  |  | kVA | kVA | Watts
Yes □ No □
Refer to Page 2 MRD for projects with more than 10 transformers
SEQUENCES OF OPERATION: Provide a description of equipment operating sequences, setpoints, operating schedules, balancing requirements (flow, velocity, head, etc.) or any other required operating parameters. Describe requirements separately.
Yes □ No □ | 2. | Removal of pre-retrofit transformers
DOCUMENTATION: List written documentation required to train, verify, operate, or maintain the equipment being installed or controlled. This may include specification sheets, test reports, construction drawings, etc.
Yes □ No □ | 3. | Provide pictures of installation and cut sheets documenting the NLL losses for each transformer
Yes □ No □ | 4. | Provide documentation of project costs such as transformer purchase costs, labor costs, and incidental costs.
The preapproved incentive is subject to the Companies' Post-Installation inspection of final specifications, drawings and operation of the proposed equipment. In the event the proposed system is altered from the above description, notify the Company of the change prior to the equipment purchase and installation as the change in design and operation may impact the incentive.
|  | Pre-Installation |  | Post-Installation
|  | Signature | Date | Signature |  |  | Date
Customer
Tech Rep

## MRD-Overflow
Customer |  | 0
Facility |  | 0
Document: |  | Transformer Replacement Minimum Requirements Document (MRD)
EQUIPMENT DESCRIPTION - PAGE 2 Appendix: For projects with more than 10 transformers.
| Project Intent | [5 empty] | Comment
| N/A indicates an evaluated transformer is not included in the replacement scope | [5 empty] | Ref No.
| 1. | Replaced the listed existing transformers with new units having the listed kVA and no-load ratings (Page 2).
|  | Building | Location | Existing | Replacement
|  | Name | or Room ID | Rated | Rated | No Load
|  |  |  | kVA | kVA | Watts
Yes □ No □
#VALUE!

## Versions (hidden)
Version History
Version | Date | Note
v1.0 | 2024-01-01 | Updated Formatting and Added Instructions.
v2.3 | 2023-07-28 | Revised MRDs to show actual NLL instead of select vendor data.
v2.2 | 2023-05-23 | First vendor version - corrected calculation where No Load Losses Watts and Peak Demand Reduction kW (columns J and T) do not populate properly. The formulas are not extended to the bottom of the page.
v2.1 | 2023-05-17 | Calculation corrections.