## Read Me
Mass Save Heat Pump Qualified Products List (HPQPL) | [7 empty] | Data pulled | 2025-12-11
IMPORTANT NOTICE
1. AHRI has replaced the "Heating Capacity (H1Full) - Single or High Stage (47F), btuh" field with the "Heating Capacity (47F), btuh (Appendix M1)" field. This data update has resulted in systems that once qualified to no longer qualify. These systems will be eligible for a rebate if installed on or before March 31, 2026, but will no longer be eligible for a rebate beginning April 1, 2026. These systems are marked with "4/1/2026" in column B “Date No Longer Eligible”. 2. The industry is moving away from R410A refrigerants to A2L refrigerants, like R-454B and R-32, to comply with the EPA’s transition rule. Key terms to understand the transition: System: A grouping of HVAC components, otherwise known as split systems (ex: IDUs paired with ODUs). Product: A self-contained unit, otherwise known as a packaged heat pump (ex: evaporator coil, condenser, and compressor all located in one cabinet). As of January 1, 2026, the EPA ruling prohibits the installation of new residential and light commercial heat pump Systems with GWPs >700. Systems using R410 refrigerants have been removed from the Heat Pump Qualified Product List. For more information on the A2L transition, view the “Introduction to A2L Refrigerants” course on the Mass Save Heating and Cooling Learning Center. Please note, new residential and light commercial heat pump variable refrigerant flow Systems that are 65,000 BTU/h or greater can be installed prior to January 1, 2027. To clarify this on the Mass Save Heat Pump Qualified Product List (HPQPL), the “Commercial Air Source VRF” tab, column B “Date No Longer Eligible”, all rows will read “1/1/2027.” Additionally, self-contained heat pump Products with GWPs >700 that are fully assembled and charged at the factory can be installed prior to January 1, 2028. R410A Products are marked with a "1/1/2028" in column B “Date No Longer Eligible”.
Installation Type | Equipment Type | Equipment Capacity1 |  | Efficiency Ratings
|  | Tons | Btu/Hr | EER2 | IEER3 | COP4 @ 47°F | COP4 @ 17°F
Residential and Commercial | Air Source Heat Pumps (ASHP) | < 5.4 | < 65,000 | See ASHPs < 5.4 Tons table below
Commercial |  | ≥ 5.4 and < 11.33 | ≥ 65,000 and < 135,000 | 11.1 | 15.4 | 3.5 | 2.25
|  | ≥ 11.33 and < 20 | ≥ 135,000 and < 240,000 | 10.7 | 14.6 | 3.4 | 2.05
|  | ≥ 20 and ≤ 150 | ≥ 240,000 and ≤ 1,800,000 | 9.6 | 13 | 3.3 | 2.05
Residential | Air to Water Heat Pumps (AWHP) | See AWHP criteria listed below
Residential | Ground Source Heat Pumps (GSHP) | ENERGY STAR Certified (see tab)
Commercial | Ground Source Heat Pumps - Closed Loop (GSHP-C), GLHP | ≤ 150 | ≤ 1,800,000 | 17.1 | --- | 3.6 | ---
| Ground Source Heat Pumps - Open Loop (GSHP-O), GWHP | ≤ 150 | ≤ 1,800,000 | 21.1 | --- | 4.1 | ---
1 Btu / Hr based on AHRI rated cooling capacity @ 95°F; Tons are calculated as Btu / Hr divided by 12,000 Btu / Hr 2 Energy Efficiency Ratio 3 Integrated Energy Efficiency Ratio 4 Coefficient of Performance
Equipment Type | Equipment Capacity1 |  | Efficiency Ratings
| Tons | Btu/Hr | EER² (1230-2021) Listed "Active" | EER² (1230-2014) | IEER3 | COP4 @ 47°F | COP4 @ 17°F
Air Source Variable Refriegerant Flow Heat Pumps (VRF) | ≥ 5.4 and < 11.33 | ≥ 65,000 and < 135,000 | 10.3 | 11.1 | 18.9 | 3.4 | 2.25
| ≥ 11.33 and < 20 | ≥ 135,000 and < 240,000 | 9.9 | 10.7 | 18 | 3.25 | 2.07
| ≥ 20 and ≤ 150 | ≥ 240,000 and ≤ 1,800,000 | 9.1 | 9.6 | 16.4 | 3.25 | 2.07
1 Btu / Hr based on AHRI rated cooling capacity @ 95°F; Tons are calculated as Btu / Hr divided by 12,000 Btu / Hr 2 Energy Efficiency Ratio 3 Integrated Energy Efficiency Ratio 4 Coefficient of Performance
Air Source Heat Pumps (ASHPs) < 5.4 Tons
Equipment |  |  | Efficiency Ratings 1
|  |  | HSPF2 2 | SEER2 3 | HCR4 @5°F | COP5 @5°F
Ductless | Mini-Split | Single-Zone | 8.5 | 15.2 | 70% | 1.75
Ductless | Mini-Split | Multi-Zone
Ducted | Mini-Split | Single-Zone | 8.1 | 15.2 | 70% | 1.75
Ducted | Mini-Split | Multi-Zone
Ducted | Central | --
Single Packaged Roof Top Units (Commercial Only) |  |  | 7.2 | 15.2 | 10.6 EER2⁶
Ducted | High Velocity | -- | 7 | 12.5 | 70% | 1.5
1 Aligns with ENERGY STAR 6.1 Cold-Climate Specification, except Ducted High Velocity Heat Pumps 2 Heating Season Performance Factor 3 Seasonal Energy Efficiency Ratio 4 Heating Capacity Ratio, calculated as heating capacity at the specified temperature divided by heating capacity @ 47°F 5 Coefficient of Performance 6 Energy Efficiency Ratio
The Data Fields below are sourced directly from the AHRI Directory of Cerified Product Performance
AHRI Directory
Air Source Heat Pumps < 5.4 Tons |  |  | Air Source Heat Pumps > 5.4 Tons |  | VRF Heat Pumps |  |  | Ground Source Heat Pumps
AHRI Certified Reference Number |  |  | AHRI Certified Reference Number |  | AHRI Certified Reference Number |  |  | AHRI Certified Reference Number
Brand Name |  |  | Brand Name |  | Brand Name |  |  | Brand Name
AHRI Type |  |  | AHRI Type |  | AHRI Type |  |  | AHRI Type
Indoor Type |  |  | Outdoor Unit Model Number |  | Indoor Type |  |  | Program Type
Outdoor Unit Model Number |  |  | Indoor Unit Model Number |  | System Model Number |  |  | Outdoor Unit Model Number
Indoor Unit Model Number(s) |  |  | Cooling Capacity (95F) |  | Module Model Number 1 |  |  | Indoor Unit Model Number(s)
Furnace Model Number |  |  | EER (95F) |  | Module Model Number 2 |  |  | Full Load GLHP Cooling Capacity (Btuh)
Cooling Capacity (AFull) - Single or High Stage (95F), btuh |  |  | IEER |  | Module Model Number 3 |  |  | Full Load GLHP Cooling EER (Btuh/watt)
SEER2 |  |  | COP at 47°F |  | Cooling Capacity (95F) |  |  | Full Load GLHP Heating COP
EER2 (AFull) - Single or High Stage (95F) |  |  | Heating Capacity at 47°F |  | EER (95F) |  |  | Full Load GLHP Heating Capacity (Btuh)
HSPF2 (Region IV) |  |  | Heating Capacity at 17°F |  | IEER
Heating Capacity (H1Full) - Single or High Stage (47F), btuh |  |  | COP at 17°F |  | High COP (47F)
Heating Capacity at 5°F as calculated by M1 |  |  |  |  | High Heating Capacity (47F)
Heating COP at 5°F as calculated by M1 |  |  |  |  | Low Heating Capacity (17F)
Heating Capacity at 17°F as calculated by M1 |  |  |  |  | Low COP (17F)
Equipment Category | AHRI Types
Ducted | ·HRCU-A-CB = Split System: Heat Pump with Remote Outdoor Unit-Air-Source ·HRCU-A-C =Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source (Ducted) ·HSP-A = Single-Package Heat Pump Air-Source ·HMSV-A-CB = Multi-Split Heat Pump (Ducted, Mixed) ·HMSR-A-CB = Multi-Split Heat Recovery Heat Pump (Ducted, Mixed)
Ductless | ·HRCU-A-CB-O =Mini-Split Heat Pump, with Remote Outdoor Unit Air-Source, Free Delivery ·HMSV-A-CB-O = Multi-Split Heat Pump, Free Delivery (Non-ducted) ·HMSR-A-CB-O = Multi-Split Heat Recovery Heat Pump, Free Delivery (Non-ducted)
Ducted High Velocity | ·SDHV-HRCU-A-CB = Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled
Air to Water Heat Pumps (Residential Only)
Criteria is as follows:
•Minimum COP of 1.7 while delivering 110°F supply water at an outside temperature of 5°F.
•Fully displacing existing hydronic heating
•Maximum 6 tons nominal capacity
Integrated Controls
Integrated controls automatically switch between a heat pump and fossil fuel heating system at a pre-set outdoor temperature.
Eligibility
For residential heat pump rebates: |  | click here
For commercial heat pump rebates |  | click here
To note, effective January 1, 2025, the Consortium for Energy Efficiency (CEE) published updates to the CEE Residential Electric HVAC and Water Heating performance requirements, which serve as the basis of eligibility for federal 25C tax credits. These credits could be subject to change in the future. For tax advice, consult a tax professional.

## High Velocity ASHPs
AHRI Certified Reference Number | Date No Longer Eligible | Equipment Type | Outdoor Unit Brand Name | AHRI Type | Outdoor Unit Model Number | Indoor Unit Brand Name | Indoor Unit Type | Indoor Unit Model Number(s) | Furnace Model Number | Cooling Capacity (AFull) - Single or High Stage (95F), btuh | SEER2 | HSPF2 (Region IV) | Heating Capacity (47F), btuh | Heating Capacity at 5°F as calculated by M1 | Heating Capacity Ratio @ 5°F | Heating COP at 5°F as calculated by M1 | EER (95F) | IEER | COP at 47°F | COP at 17°F | Refrigerant Type | Tonnage | Rebate Type
217655872 | N/A | Central HP < 5.4 tons | HISENSE | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | AUWR-6024P | UNICO SYSTEM |  | M4860C*1-B***+M4860B**-EC**+TXV-5T-454 |  | 50500 | 13.35 | 6.1 | 45000 | 34200 | 76% | 1.84 |  |  |  |  | R-454B | 4.2083 | Residential & Commercial
217048334 | N/A | Central HP < 5.4 tons | BOSCH | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | BOVA-36RTB-M20S | UNICO SYSTEM |  | M3036C*1-B***+M3036B**-EC**+TXV-3T-454 |  | 26400 | 14.1 | 7.4 | 27200 | 19400 | 71.32% | 1.55 |  |  |  |  | R-454B | 2.2 | Residential & Commercial
217654510 | N/A | Central HP < 5.4 tons | AMERISTAR | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | A5HL5048A1 | UNICO SYSTEM |  | V3642B-*EC*E***+TXV-4T-454 |  | 36000 | 12 | 6.8 | 40500 | 35400 | 87.41% | 1.58 |  |  |  |  | R-454B | 3 | Residential & Commercial
217656828 | N/A | Central HP < 5.4 tons | HISENSE | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | AUWR-3624P | UNICO SYSTEM |  | M3642C*1-BA***+M3642B**-EC**+TXV-4T-454 |  | 32600 | 12.75 | 7.2 | 28600 | 26000 | 90.91% | 1.84 |  |  |  |  | R-454B | 2.7167 | Residential & Commercial
217654509 | N/A | Central HP < 5.4 tons | AMERISTAR | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | A5HL5048A1 | UNICO SYSTEM |  | M3642C*1-E***+M3642B**-EC**+TXV-4T-454 |  | 36000 | 12 | 6.8 | 40500 | 35400 | 87.41% | 1.56 |  |  |  |  | R-454B | 3 | Residential & Commercial
217048386 | N/A | Central HP < 5.4 tons | BOSCH | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | BOVA-60RTB-M20S | UNICO SYSTEM |  | M3642C*1-B***+M3642B**-EC**+TXV-3T-454 |  | 41500 | 14.2 | 7.6 | 42200 | 31000 | 73.46% | 1.65 |  |  |  |  | R-454B | 3.4583 | Residential & Commercial

## Air to Water HPs (AWHPs)
Last update: 12/22/2025
Manufacturer | System Type | Model Name | Model # | Nominal Capacity in Tons | COP @ A5W110*
Aermec | Mono-bloc | ANK | ANK030H | 2.5 | 1.85
Aermec | Mono-bloc | ANK | ANK030HP | 2.5 | 1.85
Aermec | Mono-bloc | ANK | ANK030HA | 2.5 | 1.85
Aermec | Mono-bloc | ANK | ANK045H | 3 | 1.95
Aermec | Mono-bloc | ANK | ANK045HP | 3 | 1.95
Aermec | Mono-bloc | ANK | ANK045HA | 3 | 1.95
Aermec | Mono-bloc | ANK | ANK050H | 4 | 2.07
Aermec | Mono-bloc | ANK | ANK050HP | 4 | 2.07
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-3.5T. | 3.5 | 2.46
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-5T. | 5 | 2.34
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-6T. | 6 | 2.34
Arctic Heat Pumps | Mono-bloc |  | 035ZA/BE-R32 | 2.5 | 2.2
Arctic Heat Pumps | Mono-bloc |  | 050ZA/BE-R32 | 4 | 2.45
Arctic Heat Pumps | Mono-bloc |  | 060ZA/BE-R32 | 5 | 2.39
Arctic Heat Pumps | Mono-bloc |  | 030ZA/BEH2 | 4 | 2.03
Arctic Heat Pumps | Mono-bloc |  | MAHRW030A (BEH2)-R32 | 4 | 1.84
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 020A | 2.5 | 2.26
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 040A | 4 | 2.18
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 060A | 5 | 2.26
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | MACRW035ZA/(BE) | 2.5 | 2.2
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | MACRW050ZA/(BE) | 4 | 2.22
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | MACRW060ZA/(BE) | 5 | 2.25
Chiltrix Inc. | R32 Air To Water Heat Pump | CX50 | CX50 | 4.8 | 2.18
Chiltrix Inc. | Mono-bloc | CX34 | CX34-ODU | 3 | 2
Chiltrix Inc. | Mono-bloc | CX35 | CX35 | 3.5 | 2.187
Daikin | Mono-bloc | Altherma 3 H HT | UPRA036DAVJ | 2.9 | 2.2
Daikin | Mono-bloc | Altherma 3 H HT | UPRA043DAVJ | 2.9 | 2.17
ECOER | Mono-bloc | Smart Green One | ESMA-060ADP | 5.2 | 2.04
ECOER | Mono-bloc | Smart Green One | ESBM-060GPP | 5.5 | 2.27
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 1-7 PRO (81001/P) | 1 | 2.5
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 1-9 PRO (81004/P) | 1.3 | 2.31
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 3-12 PRO (81002/P) | 1.75 | 2.23
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 3-18 PRO (81005/P2) | 2.75 | 2.42
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR EVI 4-20 (81003) | 3.79 | 2.92
Enertech Global | Mono-bloc | Advantage | EAV030A1AAABTSS | 2.5 | 2.25
Enertech Global | Mono-bloc | Advantage | EAV060A1AAABTSS | 5 | 2.55
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-1H | 2 | 2.3
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-2H | 3 | 2.3
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-11 | 2 | 2.3
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-12 | 2 | 2.3
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-13 | 3 | 2.3
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-14 | 4 | 2.3
LG | Mono-bloc | LATS AWHP | KPHTC411M | 3.41 | 2.5
LG | Mono-bloc | LATS AWHP | KPHTC481M | 4 | 2.15
LG | Mono-bloc | LATS AWHP | KPHTC551M | 4.58 | 2.38
Lochinvar | Mono-bloc | Lochinvar | RAH040 | 3.42 | 1.9
Midea | Split | M Thermal Arctic Split | MHA-V12WD2MN8-B2 | 3.5 | 2.11
Midea | Split | M Thermal Arctic Split | MHA-V14WD2MN8-B2 | 4 | 2.08
Midea | Split | M Thermal Arctic Split | MHA-V16WD2MN8-B2 | 4.5 | 2.06
Midea | Split | M Thermal Arctic Split | MHA-V16WD2MN8 / HB–A160CMGN8 | 4 | 2.1
NTI Boilers Inc. | Mono-bloc | Verta | NHP32-036 | 2.7 | 1.94
NTI Boilers Inc. | Mono-bloc | Verta | NHP32-060 | 4.7 | 2
Nordic | Split | ATW Series | ATW-45-HACW | 3 | 1.80*
Nordic | Split | ATW Series | ATW-55-HACW | 4 | 1.80*
Nordic | Split | ATW Series | ATW-65-HACW | 5 | 1.80*
Nordic | Split | ATW Series | ATW-75-HACW | 6 | 1.80*
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA24NMZ-U1 | 2 | 1.98
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA36NMZ-U1 | 3 | 1.93
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA48NMZ-U1 | 4 | 1.99
Mitsubishi Electric | Split | Ecodan Hydro Box Indoor Unit | ERSF-NM6E | Dependant on Connected ODU | Dependant on connected IDU
Samsung | Split | Hydro Unit HE | AM036CNBDCH/AA | 3 | 1.9
Samsung | Split | Hydro Unit HE | AM048CNBDCH/AA | 4 | 1.9
Samsung | Split | Hydro Unit HT | AM048CNBFCB/AA | 4 | 1.82
SpacePak | Split | Solstice Inverter Split | 45SIS-060A4 | 5 | 1.9
SpacePak | Monobloc | Solstice Inverter Extreme | 45ILAHP48A4 | 4 | 2.6
SpacePak | Monobloc | Solstice Inverter Monobloc | 45SIM-036A4 | 3 | 1.93
SpacePak | Monobloc | Solstice Inverter Monobloc | 45SIM-060A4 | 5 | 1.75
SpacePak | Monobloc | Solstice R32 Series | CC32-18 | 1.7 | 1.54
SpacePak | Monobloc | Solstice R32 Series | CC32-40 | 2.8 | 2.83
SpacePak | Monobloc | Solstice R32 Series | CC32-60 | 4.3 | 2.39
Stiebel Eltron, Inc. | Air To Water Heat Pump | WPL | WPL 15 A2W Premium | 2.1 | 2.51
Stiebel Eltron, Inc. | Air To Water Heat Pump | WPL | WPL 25 A2W Premium | 4.09 | 2.77
Taco Comfort Solutions | Mono-bloc | System M | SystemM-1 | 3 | 2.2
U.S. Boiler Company, LLC | Mono-bloc | Ambient Heat Pump System (HPS) | HPS-5T60-DF | 5 | 1.9
U.S. Boiler Company, LLC | Mono-bloc | Ambient Heat Pump System (HPS) | HPS-5T60 | 5 | 1.9
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 41 | 2.62 | 2.11
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 48 | 2.76 | 2.08
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 55 | 2.79 | 2.06
Viessmann | Split | Vitocal 100-AW | AM2V 034043 | 3 | 2.2
Viessmann | Split | Vitocal 100-AW | AM2V 051078 | 4.3 | 1.9
* Equivalent value. Equipment automatically reduces outlet water temperature to 110°F when ambient conditions drop to 5°F.

## Commercial Air Source VRF
AHRI Certified Reference Number | Date No Longer Eligible | Outdoor Unit Brand Name | AHRI Type | Module Model Number 1 | Module Model Number 2 | Module Model Number 3 | Module Model Number 4 | Outdoor Unit Model Number | Indoor Type | Full Load Cooling Capacity (Btuh) | EER | IEER | Heating Capacity 47°F (Btuh) | COP 47°F | Heating Capacity 17°F (Btuh) | COP 17°F | Refrigerant Type | Tonnage
209445576 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Non-Ducted Indoor Units | 69000 | 12.3 | 24.2 | 76000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
209445577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Ducted Indoor Units | 69000 | 12 | 21.5 | 76000 | 4.1 | 56000 | 2.65 | R-410A | 5.75
209937596 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 22.85 | 76000 | 4.2 | 56000 | 2.67 | R-410A | 5.75
209937595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.3 | 103000 | 3.9 | 76000 | 2.53 | R-410A | 7.6667
209445578 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Non-Ducted Indoor Units | 92000 | 12 | 23.4 | 103000 | 4 | 76000 | 2.6 | R-410A | 7.6667
209445579 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Ducted Indoor Units | 92000 | 11.8 | 21.2 | 103000 | 3.8 | 76000 | 2.47 | R-410A | 7.6667
209445580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Non-Ducted Indoor Units | 114000 | 11.8 | 24.5 | 129000 | 3.9 | 92000 | 2.5 | R-410A | 9.5
209445573 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Ducted Indoor Units | 114000 | 11.4 | 21 | 129000 | 3.65 | 92000 | 2.37 | R-410A | 9.5
209937594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.75 | 129000 | 3.77 | 92000 | 2.43 | R-410A | 9.5
209938003 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 22.85 | 76000 | 4.2 | 56000 | 2.67 | R-410A | 5.75
209447005 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Non-Ducted Indoor Units | 69000 | 12.3 | 24.2 | 76000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
209447006 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Ducted Indoor Units | 69000 | 12 | 21.5 | 76000 | 4.1 | 56000 | 2.65 | R-410A | 5.75
209447007 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Non-Ducted Indoor Units | 92000 | 12 | 23.4 | 103000 | 4 | 76000 | 2.6 | R-410A | 7.6667
209447008 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Ducted Indoor Units | 92000 | 11.8 | 21.2 | 103000 | 3.8 | 76000 | 2.47 | R-410A | 7.6667
209938002 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.3 | 103000 | 3.9 | 76000 | 2.53 | R-410A | 7.6667
209938001 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.75 | 129000 | 3.77 | 92000 | 2.43 | R-410A | 9.5
209445574 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Non-Ducted Indoor Units | 114000 | 11.8 | 24.5 | 129000 | 3.9 | 92000 | 2.5 | R-410A | 9.5
209445575 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Ducted Indoor Units | 114000 | 11.4 | 21 | 129000 | 3.65 | 92000 | 2.37 | R-410A | 9.5
213886432 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886360 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886392 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602170 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602243 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
216602117 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602124 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602253 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
216602177 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886364 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
213886396 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886436 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886430 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886358 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886390 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602167 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602237 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
216602113 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602120 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602248 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
216602173 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886394 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886362 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886434 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886398 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886366 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602180 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602258 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
216602127 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602111 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602166 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602235 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886357 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886389 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
213886429 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886433 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886393 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886361 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602172 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602246 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
216602119 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602126 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602256 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
216602179 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886365 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
213886397 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886437 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886431 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886359 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886391 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602169 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602240 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
216602115 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602122 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602251 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
216602175 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886395 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886363 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886435 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886439 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886399 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886367 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602182 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602260 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
216602129 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602108 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602164 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602232 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886388 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
213886356 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886428 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
210135420 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
210135423 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
210135408 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
208758264 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
208758265 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
208758266 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
208758267 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
208758268 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
208758269 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
210135409 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
210135410 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
210135424 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
210135425 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
210135411 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
210135412 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
208758270 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
208758271 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
213897015 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.2 | 69000 | 3.64 | 51000 | 2.4 | R-410A | 5.75
213897041 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Ducted Indoor Units | 69000 | 12.2 | 19.8 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213897059 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.5 | 69000 | 3.62 | 51000 | 2.4 | R-410A | 5.75
213897060 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 21.5 | 92000 | 3.45 | 66000 | 2.4 | R-410A | 7.6667
213897042 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Ducted Indoor Units | 92000 | 12 | 19.4 | 92000 | 3.4 | 66000 | 2.4 | R-410A | 7.6667
213897016 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Non-Ducted Indoor Units | 92000 | 12.2 | 23.6 | 92000 | 3.5 | 66000 | 2.4 | R-410A | 7.6667
213897043 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* |  |  |  | RXYQ120AATJ* | Ducted Indoor Units | 114000 | 11.1 | 19.3 | 110000 | 3.4 | 72000 | 2.25 | R-410A | 9.5
213897028 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.2 | 69000 | 3.64 | 51000 | 2.4 | R-410A | 5.75
213897068 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.5 | 69000 | 3.62 | 51000 | 2.4 | R-410A | 5.75
213897050 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Ducted Indoor Units | 69000 | 12.2 | 19.8 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213897051 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Ducted Indoor Units | 92000 | 12 | 19.4 | 92000 | 3.4 | 66000 | 2.4 | R-410A | 7.6667
213897069 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 21.5 | 92000 | 3.45 | 66000 | 2.4 | R-410A | 7.6667
213897029 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Non-Ducted Indoor Units | 92000 | 12.2 | 23.6 | 92000 | 3.5 | 66000 | 2.4 | R-410A | 7.6667
213897052 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* |  |  |  | RXYQ120AAYD* | Ducted Indoor Units | 114000 | 11.1 | 19.3 | 110000 | 3.4 | 72000 | 2.25 | R-410A | 9.5
213885856 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
213885853 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
215685126 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
215685127 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) |  |  |  | GMV-VQ96WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.8 | 20.55 | 103000 | 3.95 | 76000 | 2.25 | R-410A | 7.6667
213885857 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) |  |  |  | GMV-VQ96WM/C-F(U) | Ducted Indoor Units | 92000 | 11.6 | 20.2 | 103000 | 3.9 | 78000 | 2.25 | R-410A | 7.6667
213885858 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) |  |  |  | GMV-VQ120WM/C-F(U) | Ducted Indoor Units | 114000 | 11 | 19.7 | 129000 | 3.8 | 81000 | 2.25 | R-410A | 9.5
215685128 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) |  |  |  | GMV-VQ120WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.5 | 20.05 | 129000 | 3.87 | 81000 | 2.25 | R-410A | 9.5
213895002 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.23 | 56000 | 2.88 | R-410A | 5.75
213894090 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 77000 | 4.46 | 56000 | 2.94 | R-410A | 5.75
213894109 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 22.1 | 77000 | 4.01 | 56000 | 2.82 | R-410A | 5.75
213894116 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Ducted Indoor Units | 92000 | 12 | 21.9 | 103000 | 3.83 | 76000 | 2.61 | R-410A | 7.6667
213894091 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Non-Ducted Indoor Units | 92000 | 11.8 | 23.7 | 103000 | 4.21 | 76000 | 2.72 | R-410A | 7.6667
213895006 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.8 | 103000 | 4.02 | 76000 | 2.66 | R-410A | 7.6667
213895010 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 22 | 129000 | 3.96 | 92000 | 2.81 | R-410A | 9.5
213894092 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 129000 | 4.09 | 92000 | 2.85 | R-410A | 9.5
213894123 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Ducted Indoor Units | 114000 | 11.7 | 21.2 | 129000 | 3.83 | 92000 | 2.78 | R-410A | 9.5
213895004 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.15 | 23.6 | 77000 | 4.37 | 64000 | 2.84 | R-410A | 5.75
213894107 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Non-Ducted Indoor Units | 69000 | 13.6 | 24.4 | 77000 | 4.52 | 64000 | 2.91 | R-410A | 5.75
213894111 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Ducted Indoor Units | 69000 | 12.7 | 22.8 | 77000 | 4.23 | 64000 | 2.78 | R-410A | 5.75
213894114 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Non-Ducted Indoor Units | 92000 | 12.1 | 23.4 | 103000 | 4.49 | 87000 | 2.84 | R-410A | 7.6667
213894118 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Ducted Indoor Units | 92000 | 11.8 | 20 | 103000 | 4.22 | 87000 | 2.73 | R-410A | 7.6667
213895008 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 21.7 | 103000 | 4.35 | 87000 | 2.78 | R-410A | 7.6667
213895012 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.05 | 129000 | 4.02 | 116000 | 2.55 | R-410A | 9.5
213894121 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Non-Ducted Indoor Units | 114000 | 11.2 | 22.7 | 129000 | 4.13 | 116000 | 2.51 | R-410A | 9.5
213894125 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Ducted Indoor Units | 114000 | 12 | 21.4 | 129000 | 3.92 | 116000 | 2.59 | R-410A | 9.5
213894110 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 22.1 | 77000 | 4.01 | 56000 | 2.82 | R-410A | 5.75
213894106 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 77000 | 4.46 | 56000 | 2.94 | R-410A | 5.75
213895003 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.23 | 56000 | 2.88 | R-410A | 5.75
213895007 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.8 | 103000 | 4.02 | 76000 | 2.66 | R-410A | 7.6667
213894117 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Ducted Indoor Units | 92000 | 12 | 21.9 | 103000 | 3.83 | 76000 | 2.61 | R-410A | 7.6667
213894113 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Non-Ducted Indoor Units | 92000 | 11.8 | 23.7 | 103000 | 4.21 | 76000 | 2.72 | R-410A | 7.6667
213894120 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 129000 | 4.09 | 92000 | 2.85 | R-410A | 9.5
213894124 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Ducted Indoor Units | 114000 | 11.7 | 21.2 | 129000 | 3.83 | 92000 | 2.78 | R-410A | 9.5
213895011 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 22 | 129000 | 3.96 | 92000 | 2.81 | R-410A | 9.5
213895005 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.15 | 23.6 | 77000 | 4.37 | 64000 | 2.84 | R-410A | 5.75
213894112 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Ducted Indoor Units | 69000 | 12.7 | 22.8 | 77000 | 4.23 | 64000 | 2.78 | R-410A | 5.75
213894108 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Non-Ducted Indoor Units | 69000 | 13.6 | 24.4 | 77000 | 4.52 | 64000 | 2.91 | R-410A | 5.75
213894115 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Non-Ducted Indoor Units | 92000 | 12.1 | 23.4 | 103000 | 4.49 | 87000 | 2.84 | R-410A | 7.6667
213894119 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Ducted Indoor Units | 92000 | 11.8 | 20 | 103000 | 4.22 | 87000 | 2.73 | R-410A | 7.6667
213895009 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 21.7 | 103000 | 4.35 | 87000 | 2.78 | R-410A | 7.6667
213895013 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.05 | 129000 | 4.02 | 116000 | 2.55 | R-410A | 9.5
213894122 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Non-Ducted Indoor Units | 114000 | 11.2 | 22.7 | 129000 | 4.13 | 116000 | 2.51 | R-410A | 9.5
213894126 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Ducted Indoor Units | 114000 | 12 | 21.4 | 129000 | 3.92 | 116000 | 2.59 | R-410A | 9.5
214728275 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP072C432Y2 |  |  |  | VEP072C432Y2 | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
215685129 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP072C432Y2 |  |  |  | VEP072C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.72 | 20.8 | 77000 | 3.81 | 64000 | 2.25 | R-410A | 5.75
215685121 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/C-F(U) |  |  |  | GMV-Q72WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.72 | 20.8 | 77000 | 3.81 | 64000 | 2.25 | R-410A | 5.75
213880759 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/C-F(U) |  |  |  | GMV-Q72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
213928536 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/C-F(U) |  |  |  | GMV-Q96WM/C-F(U) | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
215685122 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/C-F(U) |  |  |  | GMV-Q96WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
215685130 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP096C432Y2 |  |  |  | VEP096C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
214728280 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP096C432Y2 |  |  |  | VEP096C432Y2 | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
213686135 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
213686136 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
213686137 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
213686138 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
213686139 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
213686140 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
213686141 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
213686142 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
213686143 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
213884892 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 56000 | 2.8 | R-410A | 5.75
213885174 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 56000 | 2.75 | R-410A | 5.75
213884896 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 56000 | 2.7 | R-410A | 5.75
213884900 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL |  |  |  | MMY-MUP0961FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.1 | 26 | 103000 | 4.45 | 74000 | 2.7 | R-410A | 7.6667
213884904 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL |  |  |  | MMY-MUP0961FT6P-UL | Ducted Indoor Units | 92000 | 10.9 | 21.2 | 103000 | 3.88 | 74000 | 2.6 | R-410A | 7.6667
213885178 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL |  |  |  | MMY-MUP0961FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 23.6 | 103000 | 4.16 | 74000 | 2.65 | R-410A | 7.6667
213885182 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.3 | 129000 | 4.02 | 92000 | 2.56 | R-410A | 9.5833
213884908 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Non-Ducted Indoor Units | 115000 | 12.1 | 24.6 | 129000 | 4.2 | 92000 | 2.68 | R-410A | 9.5833
213884912 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Ducted Indoor Units | 115000 | 11.6 | 22 | 129000 | 3.84 | 92000 | 2.44 | R-410A | 9.5833
213885175 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 64000 | 2.75 | R-410A | 5.75
213884898 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 64000 | 2.7 | R-410A | 5.75
213884894 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 64000 | 2.8 | R-410A | 5.75
213884902 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Non-Ducted Indoor Units | 92000 | 13.3 | 25.3 | 103000 | 4.8 | 86000 | 2.95 | R-410A | 7.6667
213884906 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Ducted Indoor Units | 92000 | 12.2 | 21.6 | 103000 | 4.1 | 86000 | 2.69 | R-410A | 7.6667
213885179 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 23.45 | 103000 | 4.45 | 86000 | 2.82 | R-410A | 7.6667
213885183 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.2 | 23.65 | 129000 | 4.17 | 110000 | 2.69 | R-410A | 9.5833
213884910 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24.8 | 129000 | 4.43 | 110000 | 2.8 | R-410A | 9.5833
213884914 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Ducted Indoor Units | 115000 | 12 | 22.5 | 129000 | 3.91 | 110000 | 2.58 | R-410A | 9.5833
213884897 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 56000 | 2.7 | R-410A | 5.75
213885173 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 56000 | 2.75 | R-410A | 5.75
213884893 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 56000 | 2.8 | R-410A | 5.75
213885177 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL |  |  |  | MMY-MUP0961FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 23.6 | 103000 | 4.16 | 74000 | 2.65 | R-410A | 7.6667
213884901 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL |  |  |  | MMY-MUP0961FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.1 | 26 | 103000 | 4.45 | 74000 | 2.7 | R-410A | 7.6667
213884905 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL |  |  |  | MMY-MUP0961FT9P-UL | Ducted Indoor Units | 92000 | 10.9 | 21.2 | 103000 | 3.88 | 74000 | 2.6 | R-410A | 7.6667
213884909 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Non-Ducted Indoor Units | 115000 | 12.1 | 24.6 | 129000 | 4.2 | 92000 | 2.68 | R-410A | 9.5833
213884913 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Ducted Indoor Units | 115000 | 11.6 | 22 | 129000 | 3.84 | 92000 | 2.44 | R-410A | 9.5833
213885181 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.3 | 129000 | 4.02 | 92000 | 2.56 | R-410A | 9.5833
213885176 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 64000 | 2.75 | R-410A | 5.75
213884899 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 64000 | 2.7 | R-410A | 5.75
213884895 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 64000 | 2.8 | R-410A | 5.75
213884903 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Non-Ducted Indoor Units | 92000 | 13.3 | 25.3 | 103000 | 4.8 | 86000 | 2.95 | R-410A | 7.6667
213884907 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Ducted Indoor Units | 92000 | 12.2 | 21.6 | 103000 | 4.1 | 86000 | 2.69 | R-410A | 7.6667
213885180 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 23.45 | 103000 | 4.45 | 86000 | 2.82 | R-410A | 7.6667
213885184 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.2 | 23.65 | 129000 | 4.17 | 110000 | 2.69 | R-410A | 9.5833
213884911 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24.8 | 129000 | 4.43 | 110000 | 2.8 | R-410A | 9.5833
213884915 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Ducted Indoor Units | 115000 | 12 | 22.5 | 129000 | 3.91 | 110000 | 2.58 | R-410A | 9.5833
213893629 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213894863 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213916540 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916555 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213894865 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213893631 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893634 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893635 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916541 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916556 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893638 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893639 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213894867 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894875 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213916542 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213916557 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213894877 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213894869 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213893524 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893525 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916490 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916509 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893528 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893529 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893532 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893533 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916491 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916510 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893536 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893537 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213894871 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894879 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213916492 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213916511 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213894881 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213894873 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213893828 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893825 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213916528 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916534 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893826 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893829 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893540 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893541 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213916530 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916536 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893544 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893545 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893770 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893771 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916699 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916701 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893772 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893859 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893773 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893774 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916703 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916705 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893775 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893776 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213894966 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894967 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213916707 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213916709 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213894968 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894969 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213893777 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893778 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893787 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893788 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893854 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893855 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213916773 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916777 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916781 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916775 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893856 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893860 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213916779 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893789 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893790 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916783 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893779 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893780 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893857 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213894883 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213916794 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916796 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213894957 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213893858 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893821 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893822 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916798 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916800 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893823 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893824 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213894990 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894991 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213916802 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213916804 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213894992 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894993 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213893562 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893563 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916529 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916535 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893566 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893567 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213895982 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896102 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
214050138 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
214050142 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 |  |  |  | PURY-EP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
213896106 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 |  |  |  | PURY-EP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
214050078 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 |  |  |  | PURY-EP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896658 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 |  |  |  | PURY-EP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
213896100 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895980 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
214050136 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
214050140 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 |  |  |  | PURY-EP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
213896104 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 |  |  |  | PURY-EP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
214050076 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 |  |  |  | PURY-EP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896656 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 |  |  |  | PURY-EP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
213896130 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895998 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
214050162 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
214050166 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
213896002 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896134 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050146 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120YNU-A1 |  |  |  | PURY-HP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896662 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120YNU-A1 |  |  |  | PURY-HP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
214050160 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
213896127 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895996 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896000 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896132 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050164 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
214050144 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120TNU-A1 |  |  |  | PURY-HP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896660 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120TNU-A1 |  |  |  | PURY-HP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
213896150 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896014 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
214050210 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
214050214 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 |  |  |  | PURY-P96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896154 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 |  |  |  | PURY-P96YNU-A1 | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896666 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 |  |  |  | PURY-P120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
214050208 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
213896148 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896012 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896152 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 |  |  |  | PURY-P96TNU-A1 | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
214050212 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 |  |  |  | PURY-P96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896664 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 |  |  |  | PURY-P120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
213896158 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896022 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
214050284 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
214050288 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN |  |  |  | TURYE0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
213896162 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN |  |  |  | TURYE0964AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
214050292 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN |  |  |  | TURYE1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896670 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN |  |  |  | TURYE1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
213896156 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896020 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
214050282 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
214050286 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN |  |  |  | TURYE0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
213896160 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN |  |  |  | TURYE0963AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
214050290 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN |  |  |  | TURYE1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896668 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN |  |  |  | TURYE1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
213896190 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896046 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
214050352 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
214050356 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
213896050 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896194 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050360 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AN41AN |  |  |  | TURYH1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896674 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AN41AN |  |  |  | TURYH1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
214050350 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
213896188 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896044 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896048 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896192 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050354 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
214050358 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AN41AN |  |  |  | TURYH1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896672 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AN41AN |  |  |  | TURYH1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
213896206 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896062 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
214050376 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
214050380 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN |  |  |  | TURYP0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896210 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN |  |  |  | TURYP0964AN41AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896678 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN |  |  |  | TURYP1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
214050374 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
213896060 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896204 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896208 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN |  |  |  | TURYP0963AN41AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
214050378 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN |  |  |  | TURYP0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896676 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN |  |  |  | TURYP1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
217729292 | N/A | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.05 | 51000 | 2.75 | R-32 | 5.75
217729293 | N/A | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Ducted Indoor Units | 69000 | 11.9 | 19.7 | 77000 | 3.85 | 51000 | 2.65 | R-32 | 5.75
217729759 | N/A | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 21.9 | 77000 | 3.95 | 51000 | 2.7 | R-32 | 5.75
217729760 | N/A | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 23.3 | 103000 | 4.17 | 67000 | 2.85 | R-32 | 7.6667
217729294 | N/A | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Non-Ducted Indoor Units | 92000 | 13.3 | 27.6 | 103000 | 4.45 | 67000 | 2.95 | R-32 | 7.6667
217729295 | N/A | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Ducted Indoor Units | 92000 | 11 | 19 | 103000 | 3.9 | 67000 | 2.75 | R-32 | 7.6667
217729296 | N/A | LG | HMSR-A-CB | ZRUM121BTE6 |  |  |  | ZRUM121BTE6 | Non-Ducted Indoor Units | 114000 | 12.1 | 25.9 | 129000 | 4.13 | 84000 | 2.9 | R-32 | 9.5
217729761 | N/A | LG | HMSR-A-CB | ZRUM121BTE6 |  |  |  | ZRUM121BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.15 | 22.45 | 129000 | 3.88 | 84000 | 2.77 | R-32 | 9.5
217729780 | N/A | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 21.9 | 77000 | 3.95 | 51000 | 2.7 | R-32 | 5.75
217729298 | N/A | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.05 | 51000 | 2.75 | R-32 | 5.75
217729299 | N/A | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Ducted Indoor Units | 69000 | 11.9 | 19.7 | 77000 | 3.85 | 51000 | 2.65 | R-32 | 5.75
217729300 | N/A | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Non-Ducted Indoor Units | 92000 | 13.3 | 27.6 | 103000 | 4.45 | 67000 | 2.95 | R-32 | 7.6667
217729301 | N/A | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Ducted Indoor Units | 92000 | 11 | 19 | 103000 | 3.9 | 67000 | 2.75 | R-32 | 7.6667
217729781 | N/A | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 23.3 | 103000 | 4.17 | 67000 | 2.85 | R-32 | 7.6667
217729782 | N/A | LG | HMSR-A-CB | ZRUM121DTE6 |  |  |  | ZRUM121DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.15 | 22.45 | 129000 | 3.88 | 84000 | 2.77 | R-32 | 9.5
217729302 | N/A | LG | HMSR-A-CB | ZRUM121DTE6 |  |  |  | ZRUM121DTE6 | Non-Ducted Indoor Units | 114000 | 12.1 | 25.9 | 129000 | 4.13 | 84000 | 2.9 | R-32 | 9.5
217734265 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217734323 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734380 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217734382 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734325 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734266 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Non-Ducted Indoor Units | 92000 | 10.9 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734267 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Non-Ducted Indoor Units | 115000 | 11.5 | 23.3 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217734327 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Ducted Indoor Units | 115000 | 11.6 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734384 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.55 | 22.5 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217734361 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734307 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734418 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734420 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 23 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217734309 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Non-Ducted Indoor Units | 92000 | 11.8 | 24.3 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217734363 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734365 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Ducted Indoor Units | 115000 | 12.1 | 21.8 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734311 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217734422 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.25 | 22.9 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734288 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217734324 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734381 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217734383 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734326 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734289 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Non-Ducted Indoor Units | 92000 | 10.9 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734290 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Non-Ducted Indoor Units | 115000 | 11.5 | 23.3 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217734328 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Ducted Indoor Units | 115000 | 11.6 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734385 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.55 | 22.5 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217734362 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734308 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734419 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734421 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 23 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217734310 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Non-Ducted Indoor Units | 92000 | 11.8 | 24.3 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217734364 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734366 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Ducted Indoor Units | 115000 | 12.1 | 21.8 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734312 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217734423 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.25 | 22.9 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734975 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734976 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217735082 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217735086 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.9 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734983 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734984 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Non-Ducted Indoor Units | 92000 | 10.7 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217735090 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.45 | 22.35 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217734991 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Ducted Indoor Units | 115000 | 11.5 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734992 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Non-Ducted Indoor Units | 115000 | 11.4 | 23 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217734979 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734980 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217735084 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217735088 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.95 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217734987 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734988 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Non-Ducted Indoor Units | 92000 | 11.7 | 24.2 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217734995 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Ducted Indoor Units | 115000 | 11.9 | 21.7 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734996 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217735092 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.15 | 22.85 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217735083 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217734977 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734978 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217734985 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734986 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Non-Ducted Indoor Units | 92000 | 10.7 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217735087 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.9 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217735091 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.45 | 22.35 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217734993 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Ducted Indoor Units | 115000 | 11.5 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734994 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Non-Ducted Indoor Units | 115000 | 11.4 | 23 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217734981 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734982 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217735085 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217735089 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.95 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217734989 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734990 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Non-Ducted Indoor Units | 92000 | 11.7 | 24.2 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217734997 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Ducted Indoor Units | 115000 | 11.9 | 21.7 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734998 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217735093 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.15 | 22.85 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217883041 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217883043 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217883045 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217901715 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM72TXU-A |  |  |  | PURY-EM72TXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901719 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM72TXU-A |  |  |  | PURY-EM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901723 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM96TXU-A |  |  |  | PURY-EM96TXU-A | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217901727 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM96TXU-A |  |  |  | PURY-EM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217901731 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A |  |  |  | PURY-EM120TXU-A | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217901735 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A |  |  |  | PURY-EM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217901721 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A |  |  |  | PURY-HM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901717 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A |  |  |  | PURY-HM72TXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901725 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A |  |  |  | PURY-HM96TXU-A | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217901729 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A |  |  |  | PURY-HM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217901737 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A |  |  |  | PURY-HM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217901733 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A |  |  |  | PURY-HM120TXU-A | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217901720 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM72YXU-A |  |  |  | PURY-EM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901716 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM72YXU-A |  |  |  | PURY-EM72YXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901728 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM96YXU-A |  |  |  | PURY-EM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217901724 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM96YXU-A |  |  |  | PURY-EM96YXU-A | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217901736 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A |  |  |  | PURY-EM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217901732 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A |  |  |  | PURY-EM120YXU-A | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217901722 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A |  |  |  | PURY-HM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901718 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A |  |  |  | PURY-HM72YXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901726 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A |  |  |  | PURY-HM96YXU-A | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217901730 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A |  |  |  | PURY-HM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217901738 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A |  |  |  | PURY-HM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217901734 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A |  |  |  | PURY-HM120YXU-A | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217902259 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AMM0AN |  |  |  | TURYE0723AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902261 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AMM0AN |  |  |  | TURYE0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902267 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AMM0AN |  |  |  | TURYE0963AMM0AN | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217902269 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AMM0AN |  |  |  | TURYE0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217902275 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN |  |  |  | TURYE1203AMM0AN | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217902277 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN |  |  |  | TURYE1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217902262 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN |  |  |  | TURYH0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902260 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN |  |  |  | TURYH0723AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902268 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN |  |  |  | TURYH0963AMM0AN | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217902270 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN |  |  |  | TURYH0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217902276 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN |  |  |  | TURYH1203AMM0AN | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217902278 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN |  |  |  | TURYH1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217902265 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AMM0AN |  |  |  | TURYE0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902263 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AMM0AN |  |  |  | TURYE0724AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902273 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AMM0AN |  |  |  | TURYE0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217902271 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AMM0AN |  |  |  | TURYE0964AMM0AN | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217902279 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN |  |  |  | TURYE1204AMM0AN | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217902281 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN |  |  |  | TURYE1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217902264 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN |  |  |  | TURYH0724AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902266 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN |  |  |  | TURYH0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902272 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN |  |  |  | TURYH0964AMM0AN | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217902274 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN |  |  |  | TURYH0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217902282 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN |  |  |  | TURYH1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217902280 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN |  |  |  | TURYH1204AMM0AN | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217901675 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72TXU-A |  |  |  | PUHY-EM72TXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901676 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72TXU-A |  |  |  | PUHY-EM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901683 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96TXU-A |  |  |  | PUHY-EM96TXU-A | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217901684 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96TXU-A |  |  |  | PUHY-EM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217901691 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A |  |  |  | PUHY-EM120TXU-A | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217901692 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A |  |  |  | PUHY-EM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217901679 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A |  |  |  | PUHY-HM72TXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901680 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A |  |  |  | PUHY-HM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901687 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A |  |  |  | PUHY-HM96TXU-A | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217901688 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A |  |  |  | PUHY-HM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217901695 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A |  |  |  | PUHY-HM120TXU-A | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217901696 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A |  |  |  | PUHY-HM120TXU-A | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217901677 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72YXU-A |  |  |  | PUHY-EM72YXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901678 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72YXU-A |  |  |  | PUHY-EM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901685 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96YXU-A |  |  |  | PUHY-EM96YXU-A | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217901686 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96YXU-A |  |  |  | PUHY-EM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217901693 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A |  |  |  | PUHY-EM120YXU-A | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217901694 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A |  |  |  | PUHY-EM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217901681 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A |  |  |  | PUHY-HM72YXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901682 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A |  |  |  | PUHY-HM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901689 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A |  |  |  | PUHY-HM96YXU-A | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217901690 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A |  |  |  | PUHY-HM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217901697 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A |  |  |  | PUHY-HM120YXU-A | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217901698 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A |  |  |  | PUHY-HM120YXU-A | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217902187 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AMM0AN |  |  |  | TUHYE0723AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902189 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AMM0AN |  |  |  | TUHYE0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902195 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AMM0AN |  |  |  | TUHYE0963AMM0AN | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217902197 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AMM0AN |  |  |  | TUHYE0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217902203 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN |  |  |  | TUHYE1203AMM0AN | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217902205 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN |  |  |  | TUHYE1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217902190 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN |  |  |  | TUHYH0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902188 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN |  |  |  | TUHYH0723AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902196 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN |  |  |  | TUHYH0963AMM0AN | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217902198 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN |  |  |  | TUHYH0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217902204 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN |  |  |  | TUHYH1203AMM0AN | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217902206 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN |  |  |  | TUHYH1203AMM0AN | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217902193 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AMM0AN |  |  |  | TUHYE0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902191 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AMM0AN |  |  |  | TUHYE0724AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902201 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AMM0AN |  |  |  | TUHYE0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217902199 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AMM0AN |  |  |  | TUHYE0964AMM0AN | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217902207 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN |  |  |  | TUHYE1204AMM0AN | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217902209 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN |  |  |  | TUHYE1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217902192 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN |  |  |  | TUHYH0724AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902194 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN |  |  |  | TUHYH0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902200 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN |  |  |  | TUHYH0964AMM0AN | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217902202 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN |  |  |  | TUHYH0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217902210 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN |  |  |  | TUHYH1204AMM0AN | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217902208 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN |  |  |  | TUHYH1204AMM0AN | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
218003044 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218003112 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004887 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218004891 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003116 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003048 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003052 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004895 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218004385 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003045 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218003113 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004888 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218004892 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003117 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003049 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003053 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004896 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218004386 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003046 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218003114 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004889 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218004893 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003118 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003050 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003054 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004897 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218004387 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003047 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218003115 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004890 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218004894 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003119 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003051 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003055 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004898 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218004388 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218005667 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005699 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005739 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005743 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005703 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005671 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005675 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005707 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005747 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005740 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005700 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005668 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005672 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005704 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005744 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005748 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005708 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005676 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005701 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005669 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005741 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005745 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005673 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005705 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005677 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005709 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005749 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005742 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005702 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005670 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005674 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005706 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005746 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005750 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005710 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005678 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
213895919 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Ducted Indoor Units | 69000 | 11.8 | 19 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213895937 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 20 | 69000 | 3.7 | 51000 | 2.35 | R-410A | 5.75
213895897 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Non-Ducted Indoor Units | 69000 | 12.2 | 21 | 69000 | 3.8 | 51000 | 2.3 | R-410A | 5.75
213895898 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Non-Ducted Indoor Units | 92000 | 11.4 | 22.1 | 92000 | 3.8 | 72000 | 2.3 | R-410A | 7.6667
213895716 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Ducted Indoor Units | 92000 | 11.9 | 19.3 | 92000 | 3.6 | 72000 | 2.25 | R-410A | 7.6667
213895938 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.65 | 20.7 | 92000 | 3.7 | 72000 | 2.27 | R-410A | 7.6667
213896246 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* |  |  |  | REYQ120AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.75 | 20.1 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213896224 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* |  |  |  | REYQ120AATJ* | Non-Ducted Indoor Units | 114000 | 10.6 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213895908 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Non-Ducted Indoor Units | 69000 | 12.2 | 21 | 69000 | 3.8 | 51000 | 2.3 | R-410A | 5.75
213895928 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Ducted Indoor Units | 69000 | 11.8 | 19 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213895947 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 20 | 69000 | 3.7 | 51000 | 2.35 | R-410A | 5.75
213895948 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.65 | 20.7 | 92000 | 3.7 | 72000 | 2.27 | R-410A | 7.6667
213895718 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Ducted Indoor Units | 92000 | 11.9 | 19.3 | 92000 | 3.6 | 72000 | 2.25 | R-410A | 7.6667
213895909 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Non-Ducted Indoor Units | 92000 | 11.4 | 22.1 | 92000 | 3.8 | 72000 | 2.3 | R-410A | 7.6667
213896228 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* |  |  |  | REYQ120AAYD* | Non-Ducted Indoor Units | 114000 | 10.6 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213896254 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* |  |  |  | REYQ120AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.75 | 20.1 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213893881 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
213893925 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893987 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602343 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602443 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602547 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602450 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
216602354 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602337 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893929 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893885 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893877 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893889 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893933 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893991 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602362 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602457 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602553 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893989 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
213893927 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893883 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602550 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602447 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602349 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602340 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602357 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602454 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893887 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893879 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893931 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893993 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893891 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893935 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602461 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602557 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602366 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893988 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
213893926 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893882 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602795 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602549 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602446 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602346 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
214826411 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
214826412 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602356 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602338 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602452 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
216602797 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893886 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893878 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893930 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893992 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893890 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893934 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602799 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602555 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602459 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602364 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
214826413 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893990 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
213893928 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893884 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602552 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602449 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602351 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602342 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602360 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602455 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893888 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893880 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893932 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893994 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893892 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893936 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602462 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602558 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602369 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
208811482 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Non-Ducted Indoor Units | 69000 | 14.9 | 29 | 77000 | 4.42 | 56000 | 2.65 | R-410A | 5.75
208812532 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Ducted Indoor Units | 69000 | 12.3 | 21.2 | 77000 | 3.77 | 56000 | 2.45 | R-410A | 5.75
208812533 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Ducted Indoor Units | 92000 | 11.7 | 19.9 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
208811483 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Non-Ducted Indoor Units | 92000 | 13.2 | 28 | 103000 | 4 | 73000 | 2.52 | R-410A | 7.6667
208811484 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Non-Ducted Indoor Units | 115000 | 13.5 | 28.4 | 129000 | 3.69 | 87000 | 2.43 | R-410A | 9.5833
208812534 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Ducted Indoor Units | 115000 | 11.3 | 19.8 | 129000 | 3.65 | 87000 | 2.43 | R-410A | 9.5833
208812537 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Ducted Indoor Units | 69000 | 12.3 | 21.2 | 77000 | 3.77 | 56000 | 2.45 | R-410A | 5.75
208811487 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Non-Ducted Indoor Units | 69000 | 14.9 | 29 | 77000 | 4.42 | 56000 | 2.65 | R-410A | 5.75
208811488 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Non-Ducted Indoor Units | 92000 | 13.2 | 28 | 103000 | 4 | 73000 | 2.52 | R-410A | 7.6667
208812538 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Ducted Indoor Units | 92000 | 11.7 | 19.9 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
208812539 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Ducted Indoor Units | 115000 | 11.3 | 19.8 | 129000 | 3.65 | 87000 | 2.43 | R-410A | 9.5833
208811489 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Non-Ducted Indoor Units | 115000 | 13.5 | 28.4 | 129000 | 3.69 | 87000 | 2.43 | R-410A | 9.5833
213916331 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 10.5 | 21.8 | 77000 | 3.62 | 54000 | 2.4 | R-410A | 5.75
213916332 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 10.3 | 21.8 | 77000 | 4.04 | 54000 | 2.5 | R-410A | 5.75
213916335 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.4 | 21.8 | 77000 | 3.83 | 54000 | 2.45 | R-410A | 5.75
214094474 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094178 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094330 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094331 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094554 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094258 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094410 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094411 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094570 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094274 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094426 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094427 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094362 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094210 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094506 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094363 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094378 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094226 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094522 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094379 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094314 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094458 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094162 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094315 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
9990279 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
9990277 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
9990278 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
211123650 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
214091436 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091580 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091724 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091581 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091596 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091452 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091740 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091597 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091532 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091676 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214078203 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091533 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091548 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091404 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091549 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091484 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091628 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091772 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091629 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091500 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091644 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091788 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091645 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
213916286 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916287 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916284 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916854 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916288 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
213916309 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916289 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916291 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916862 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916292 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
6687539 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
207742258 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
6687541 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
6687542 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
6687543 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
7850818 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
7850820 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
7850821 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
7850822 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
7850838 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
7850840 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
7850841 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
7850842 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
202583512 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Non-Ducted Indoor Units | 92000 | 11.6 | 23.1 | 103000 | 3.87 | 73000 | 2.52 | R-410A | 7.6667
202583511 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Non-Ducted Indoor Units | 69000 | 12.1 | 23.9 | 77000 | 4.19 | 56000 | 2.64 | R-410A | 5.75
202583513 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Non-Ducted Indoor Units | 114000 | 11.6 | 24.2 | 129000 | 3.77 | 87000 | 2.42 | R-410A | 9.5
214094242 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094394 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094538 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094395 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094194 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094346 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094490 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094347 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094290 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094442 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094586 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094443 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091468 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091612 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091756 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091613 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091564 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091708 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091420 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091565 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091516 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091660 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091804 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091661 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
213896679 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896710 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896728 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896729 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* |  |  |  | REYQ96XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896680 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* |  |  |  | REYQ96XBTJ* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896690 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* |  |  |  | REYQ120XBTJ* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896773 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* |  |  |  | REYQ120XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896734 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896696 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896716 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896697 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* |  |  |  | REYQ96XBYD* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896735 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* |  |  |  | REYQ96XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896817 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* |  |  |  | REYQ120XBYD* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896837 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* |  |  |  | REYQ120XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896740 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896722 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896703 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896704 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* |  |  |  | REYQ96XBYC* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896741 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* |  |  |  | REYQ96XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896821 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* |  |  |  | REYQ120XBYC* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896841 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* |  |  |  | REYQ120XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896746 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XBYC* |  |  |  | RXYQ72XBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 18.9 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896805 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* |  |  |  | RXYQ96XBYC* | Non-Ducted Indoor Units | 92000 | 10.5 | 19.8 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* |  |  |  | RXYQ120XBYC* | Non-Ducted Indoor Units | 114000 | 10.3 | 19.3 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBTJ* |  |  |  | RXLQ72TBTJ* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896883 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBYD* |  |  |  | RXLQ72TBYD* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896887 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBYC* |  |  |  | RXLQ72TBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896876 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBTJ* |  |  |  | RELQ72TBTJ* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896909 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBYD* |  |  |  | RELQ72TBYD* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896915 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBYC* |  |  |  | RELQ72TBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
214289936 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME2CA* |  |  |  | MVHQ072ME2CA* | Ducted Indoor Units | 69000 | 12 | 20.5 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289937 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME2CA* |  |  |  | MVHQ072ME2CA* | Non-Ducted Indoor Units | 69000 | 12.6 | 23.6 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289957 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME2CA* |  |  |  | MVHQ096ME2CA* | Ducted Indoor Units | 91000 | 12.2 | 21.8 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289958 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME2CA* |  |  |  | MVHQ096ME2CA* | Non-Ducted Indoor Units | 91000 | 11.9 | 23.1 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289972 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* |  |  |  | MVHQ120ME2CA* | Ducted Indoor Units | 115000 | 11.2 | 21.6 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289973 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* |  |  |  | MVHQ120ME2CA* | Non-Ducted Indoor Units | 115000 | 11.6 | 23 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289938 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME4CA* |  |  |  | MVHQ072ME4CA* | Ducted Indoor Units | 69000 | 12 | 20.5 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289939 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME4CA* |  |  |  | MVHQ072ME4CA* | Non-Ducted Indoor Units | 69000 | 12.6 | 23.6 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289959 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME4CA* |  |  |  | MVHQ096ME4CA* | Ducted Indoor Units | 91000 | 12.2 | 21.8 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289960 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME4CA* |  |  |  | MVHQ096ME4CA* | Non-Ducted Indoor Units | 91000 | 11.9 | 23.1 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289974 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* |  |  |  | MVHQ120ME4CA* | Ducted Indoor Units | 115000 | 11.2 | 21.6 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289975 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* |  |  |  | MVHQ120ME4CA* | Non-Ducted Indoor Units | 115000 | 11.6 | 23 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214296004 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B33CW |  |  |  | HVAHR120B33CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189682 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B33CW |  |  |  | HVAHR120B33CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
214296014 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B43CW |  |  |  | HVAHR120B43CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B43CW |  |  |  | HVAHR120B43CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
215828403 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B53CW |  |  |  | HVAHR120B53CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189702 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B53CW |  |  |  | HVAHR120B53CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
214825941 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C |  |  |  | TVRF-VQ72WM/C | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
214825944 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C |  |  |  | TVRF-VQ72WM/C | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
214825945 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C |  |  |  | TVRF-VQ96WM/C | Ducted Indoor Units | 92000 | 11.6 | 20.2 | 103000 | 3.9 | 78000 | 2.25 | R-410A | 7.6667
214825946 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ120WM/C |  |  |  | TVRF-VQ120WM/C | Ducted Indoor Units | 114000 | 11 | 19.7 | 129000 | 3.8 | 81000 | 2.25 | R-410A | 9.5
214825938 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD72K/220V |  |  |  | TVRF-SHD72K/220V | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
214825949 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD96K/220V |  |  |  | TVRF-SHD96K/220V | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
214826363 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
214826372 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
214826403 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602708 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602723 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602775 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602778 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602724 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602710 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826404 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
214826373 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
214826364 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826365 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
214826374 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
214826405 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602711 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602725 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602780 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
214826383 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072DXVGQR |  |  |  | AM072DXVGQR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
214826392 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072DXVGQR |  |  |  | AM072DXVGQR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602741 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4J |  |  |  | VRC072S4M-4J | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602756 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4J |  |  |  | VRC072S4M-4J | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602758 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J |  |  |  | VRC096S4M-4J | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602742 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J |  |  |  | VRC096S4M-4J | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826393 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR |  |  |  | AM096DXVGQR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
214826384 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR |  |  |  | AM096DXVGQR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826385 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR |  |  |  | AM120DXVGQR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
214826394 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR |  |  |  | AM120DXVGQR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602744 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J |  |  |  | VRC120S4M-4J | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602759 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J |  |  |  | VRC120S4M-4J | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213916323 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916691 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916324 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916316 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916325 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
217284733 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
217284734 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
217284739 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
217284736 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-W |  |  |  | GMV-VQ96WM/C-W | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
217284737 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-W |  |  |  | GMV-VQ96WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
217563467 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
217563468 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
217563533 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
217650552 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C-W |  |  |  | TVRF-VQ96WM/C-W | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
217650553 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C-W |  |  |  | TVRF-VQ96WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
213896312 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-B |  |  |  | PURY-P72ZKMU-B | Non-Ducted Indoor Units | 69000 | 11.4 | 19.8 | 76000 | 3.46 | 56000 | 2.26 | R-410A | 5.75
214050548 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-B |  |  |  | PURY-P72ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.35 | 19.1 | 76000 | 3.54 | 56000 | 2.26 | R-410A | 5.75
214050555 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B |  |  |  | PURY-P96ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.95 | 19.95 | 103000 | 3.46 | 71000 | 2.26 | R-410A | 7.6667
213896357 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B |  |  |  | PURY-P96ZKMU-B | Ducted Indoor Units | 92000 | 10.9 | 21.1 | 103000 | 3.46 | 71000 | 2.26 | R-410A | 7.6667
213896293 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Non-Ducted Indoor Units | 69000 | 12.4 | 22.2 | 76000 | 3.85 | 56000 | 2.25 | R-410A | 5.75
213896282 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Ducted Indoor Units | 69000 | 12.3 | 20.2 | 76000 | 3.74 | 56000 | 2.59 | R-410A | 5.75
213916477 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.2 | 76000 | 3.79 | 56000 | 2.42 | R-410A | 5.75
213916478 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12 | 21.15 | 103000 | 3.73 | 76000 | 2.56 | R-410A | 7.6667
213896294 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Non-Ducted Indoor Units | 92000 | 12.1 | 20.1 | 103000 | 3.74 | 76000 | 2.42 | R-410A | 7.6667
213896337 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Ducted Indoor Units | 92000 | 11.9 | 22.2 | 103000 | 3.73 | 76000 | 2.71 | R-410A | 7.6667
213896316 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B |  |  |  | PUHY-P120ZKMU-B | Ducted Indoor Units | 115000 | 11.4 | 19.5 | 129000 | 3.62 | 92000 | 2.51 | R-410A | 9.5833
213886448 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213886408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886376 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602197 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602281 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602143 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886442 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886446 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213886402 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886406 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886414 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886370 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886374 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213893875 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213893863 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893867 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893871 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602187 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602193 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602207 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602214 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602267 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602276 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602311 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602318 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602333 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
216602325 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602133 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602139 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602146 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602285 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602200 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886378 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886410 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886450 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602132 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602138 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602265 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602274 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602309 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602185 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602191 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602205 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602212 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602316 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602323 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602331 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886369 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886373 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213886401 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886405 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886413 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886441 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886445 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213893862 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893866 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893870 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893874 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886449 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213886409 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886377 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602198 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602283 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602144 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886443 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886447 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213886403 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886407 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886419 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886415 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886375 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213886371 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213893876 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213893864 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893872 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893868 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602195 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602188 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602208 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602216 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602279 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602269 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602319 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602312 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602328 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602335 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
216602141 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602135 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602148 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602287 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602202 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886379 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886411 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886451 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602130 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602136 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602262 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602272 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602314 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602321 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602308 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602183 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602190 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602203 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602210 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602330 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886368 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886372 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213886400 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886404 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886412 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886416 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886440 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886444 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213893869 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893873 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213893865 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893861 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
208758272 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
208758274 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB |  |  |  | CHV6-144URB | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
210135414 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 144FFFH |  |  |  | AVWT - 144FFFH | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
210135426 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 144FFFH |  |  |  | AVWT - 144FFFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
210135427 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 22.45 | 170000 | 3.32 | 115000 | 2.17 | R-410A | 13.3333
210135418 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Ducted Indoor Units | 160000 | 10.9 | 20.8 | 170000 | 3.26 | 115000 | 2.07 | R-410A | 13.3333
210135419 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
208758276 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Ducted Indoor Units | 160000 | 10.9 | 20.8 | 170000 | 3.26 | 115000 | 2.07 | R-410A | 13.3333
208758277 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
208758278 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
208758280 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-192URB |  |  |  | CHV6-192URB | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
210135428 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 192FFFH |  |  |  | AVWT - 192FFFH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
210135416 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 192FFFH |  |  |  | AVWT - 192FFFH | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
213897062 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 20.3 | 138000 | 3.32 | 90000 | 2.1 | R-410A | 11.5
213897044 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Ducted Indoor Units | 138000 | 10.9 | 18.8 | 138000 | 3.35 | 90000 | 2.1 | R-410A | 11.5
213897018 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Non-Ducted Indoor Units | 138000 | 11 | 21.8 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213897111 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.25 | 20.05 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897085 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Non-Ducted Indoor Units | 156000 | 10.3 | 21.7 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897095 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Ducted Indoor Units | 156000 | 10.2 | 18.4 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897019 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Non-Ducted Indoor Units | 184000 | 11.3 | 21.8 | 184000 | 3.48 | 130000 | 2.22 | R-410A | 15.3333
213897045 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Ducted Indoor Units | 184000 | 11.2 | 18.6 | 184000 | 3.4 | 130000 | 2.22 | R-410A | 15.3333
213897063 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.25 | 20.2 | 184000 | 3.44 | 130000 | 2.22 | R-410A | 15.3333
213897086 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Non-Ducted Indoor Units | 206000 | 10.3 | 20.8 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897112 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.6 | 19.6 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213895075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Ducted Indoor Units | 206000 | 10.9 | 18.4 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897113 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.25 | 19 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897096 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Ducted Indoor Units | 228000 | 9.9 | 18 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897020 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Non-Ducted Indoor Units | 228000 | 10.6 | 20 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897053 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Ducted Indoor Units | 138000 | 10.9 | 18.8 | 138000 | 3.35 | 90000 | 2.1 | R-410A | 11.5
213897071 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 20.3 | 138000 | 3.32 | 90000 | 2.1 | R-410A | 11.5
213897031 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Non-Ducted Indoor Units | 138000 | 11 | 21.8 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213897103 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Ducted Indoor Units | 156000 | 10.2 | 18.4 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897090 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Non-Ducted Indoor Units | 156000 | 10.3 | 21.7 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897120 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.25 | 20.05 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897032 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Non-Ducted Indoor Units | 184000 | 11.3 | 21.8 | 184000 | 3.48 | 130000 | 2.22 | R-410A | 15.3333
213897072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.25 | 20.2 | 184000 | 3.44 | 130000 | 2.22 | R-410A | 15.3333
213897054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Ducted Indoor Units | 184000 | 11.2 | 18.6 | 184000 | 3.4 | 130000 | 2.22 | R-410A | 15.3333
213897121 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.6 | 19.6 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897091 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Non-Ducted Indoor Units | 206000 | 10.3 | 20.8 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213895076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Ducted Indoor Units | 206000 | 10.9 | 18.4 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897104 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Ducted Indoor Units | 228000 | 9.9 | 18 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897122 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.25 | 19 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897033 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Non-Ducted Indoor Units | 228000 | 10.6 | 20 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
214091398 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) | GMV-VQ72WM/C-F(U) |  |  | GMV-VQ144WM/C-F(U) | Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 4 | 131000 | 2.07 | R-410A | 11.5
214091401 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) | GMV-VQ72WM/C-F(U) |  |  | GMV-VQ144WM/C-F(U) | Ducted Indoor Units | 138000 | 11.7 | 22.4 | 154000 | 3.95 | 131000 | 2.07 | R-410A | 11.5
214091402 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) | GMV-VQ96WM/C-F(U) |  |  | GMV-VQ192WM/C-F(U) | Ducted Indoor Units | 184000 | 11.1 | 20.3 | 206000 | 3.66 | 150000 | 2.07 | R-410A | 15.3333
214091399 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) | GMV-VQ96WM/C-F(U) |  |  | GMV-VQ192WM/C-F(U) | Non-Ducted Indoor Units | 184000 | 10.3 | 20.4 | 206000 | 3.93 | 150000 | 2.07 | R-410A | 15.3333
214091403 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) | GMV-VQ120WM/C-F(U) |  |  | GMV-VQ240WM/C-F(U) | Ducted Indoor Units | 228000 | 10.5 | 19.5 | 256000 | 3.41 | 170000 | 2.07 | R-410A | 19
213895054 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP1921HT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 22.4 | 206000 | 4 | 154000 | 2.51 | R-410A | 15.3333
213895059 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP1921HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 22.3 | 206000 | 4.13 | 154000 | 2.6 | R-410A | 15.3333
213895022 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP1921HT6P-UL | Non-Ducted Indoor Units | 184000 | 10.3 | 22.2 | 206000 | 4.26 | 154000 | 2.69 | R-410A | 15.3333
213894130 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 21.6 | 154000 | 3.64 | 109000 | 2.53 | R-410A | 11.5
213894136 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Ducted Indoor Units | 206000 | 11.6 | 20.9 | 232000 | 4.01 | 164000 | 2.74 | R-410A | 17.1667
213894093 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Non-Ducted Indoor Units | 138000 | 11.1 | 22.7 | 154000 | 3.93 | 109000 | 2.66 | R-410A | 11.5
213894095 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 232000 | 4.04 | 164000 | 2.76 | R-410A | 17.1667
213895014 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.25 | 22.15 | 154000 | 3.78 | 109000 | 2.59 | R-410A | 11.5
213895023 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.25 | 21.3 | 232000 | 4.02 | 164000 | 2.75 | R-410A | 17.1667
213895025 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2401HT6P-UL | Non-Ducted Indoor Units | 230000 | 10.3 | 21.4 | 258000 | 3.95 | 182000 | 2.67 | R-410A | 19.1667
213895071 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2401HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 20.65 | 258000 | 3.91 | 182000 | 2.63 | R-410A | 19.1667
213895067 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2401HT6P-UL | Ducted Indoor Units | 230000 | 11.2 | 19.9 | 258000 | 3.88 | 182000 | 2.6 | R-410A | 19.1667
213895018 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL |  |  |  | MMY-MUP1681HT6P-UL | Ducted Indoor Units | 160000 | 10.6 | 21 | 180000 | 3.56 | 132000 | 2.35 | R-410A | 13.3333
213895020 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL |  |  |  | MMY-MUP1681HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.35 | 180000 | 3.59 | 132000 | 2.25 | R-410A | 13.3333
213894094 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL |  |  |  | MMY-MUP1681HT6P-UL | Non-Ducted Indoor Units | 160000 | 11.4 | 21.7 | 180000 | 3.63 | 132000 | 2.16 | R-410A | 13.3333
213895053 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1921HT6P-UL |  |  |  | MMY-MUP1921HT6P-UL | Non-Ducted Indoor Units | 184000 | 10.6 | 22.7 | 206000 | 3.43 | 154000 | 2.29 | R-410A | 15.3333
213895063 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1921HT6P-UL |  |  |  | MMY-MUP1921HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.4 | 206000 | 3.43 | 154000 | 2.29 | R-410A | 15.3333
213895058 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1921HT6P-UL |  |  |  | MMY-MUP1921HT6P-UL | Ducted Indoor Units | 184000 | 10.6 | 20.1 | 206000 | 3.43 | 154000 | 2.29 | R-410A | 15.3333
213895016 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.95 | 23.1 | 154000 | 4.47 | 128000 | 2.74 | R-410A | 11.5
213894132 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Ducted Indoor Units | 138000 | 11.6 | 22.3 | 154000 | 4.21 | 128000 | 2.64 | R-410A | 11.5
213894128 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Non-Ducted Indoor Units | 138000 | 12.3 | 23.9 | 154000 | 4.74 | 128000 | 2.84 | R-410A | 11.5
213895061 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.3 | 206000 | 4.37 | 174000 | 2.66 | R-410A | 15.3333
213895056 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Ducted Indoor Units | 184000 | 10.8 | 21 | 206000 | 4.33 | 174000 | 2.58 | R-410A | 15.3333
213895051 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Non-Ducted Indoor Units | 184000 | 10.8 | 21.6 | 206000 | 4.41 | 174000 | 2.75 | R-410A | 15.3333
213895065 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Non-Ducted Indoor Units | 230000 | 12 | 22.5 | 258000 | 3.92 | 232000 | 2.44 | R-410A | 19.1667
213895069 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Ducted Indoor Units | 230000 | 11.3 | 20.1 | 258000 | 3.99 | 232000 | 2.61 | R-410A | 19.1667
213895073 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.65 | 21.3 | 258000 | 3.95 | 232000 | 2.52 | R-410A | 19.1667
213895060 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP1921HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 22.3 | 206000 | 4.13 | 154000 | 2.6 | R-410A | 15.3333
213895050 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP1921HT9P-UL | Non-Ducted Indoor Units | 184000 | 10.3 | 22.2 | 206000 | 4.26 | 154000 | 2.69 | R-410A | 15.3333
213895055 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP1921HT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 22.4 | 206000 | 4 | 154000 | 2.51 | R-410A | 15.3333
213895015 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.25 | 22.15 | 154000 | 3.78 | 109000 | 2.59 | R-410A | 11.5
213895024 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.25 | 21.3 | 232000 | 4.02 | 164000 | 2.75 | R-410A | 17.1667
213895072 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2401HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 20.65 | 258000 | 3.91 | 182000 | 2.63 | R-410A | 19.1667
213895068 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2401HT9P-UL | Ducted Indoor Units | 230000 | 11.2 | 19.9 | 258000 | 3.88 | 182000 | 2.6 | R-410A | 19.1667
213895064 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2401HT9P-UL | Non-Ducted Indoor Units | 230000 | 10.3 | 21.4 | 258000 | 3.95 | 182000 | 2.67 | R-410A | 19.1667
213894131 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 21.6 | 154000 | 3.64 | 109000 | 2.53 | R-410A | 11.5
213894135 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 232000 | 4.04 | 164000 | 2.76 | R-410A | 17.1667
213894137 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Ducted Indoor Units | 206000 | 11.6 | 20.9 | 232000 | 4.01 | 164000 | 2.74 | R-410A | 17.1667
213894127 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Non-Ducted Indoor Units | 138000 | 11.1 | 22.7 | 154000 | 3.93 | 109000 | 2.66 | R-410A | 11.5
213894134 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL |  |  |  | MMY-MUP1681HT9P-UL | Non-Ducted Indoor Units | 160000 | 11.4 | 21.7 | 180000 | 3.63 | 132000 | 2.16 | R-410A | 13.3333
213895021 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL |  |  |  | MMY-MUP1681HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.35 | 180000 | 3.59 | 132000 | 2.25 | R-410A | 13.3333
213895019 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL |  |  |  | MMY-MUP1681HT9P-UL | Ducted Indoor Units | 160000 | 10.6 | 21 | 180000 | 3.56 | 132000 | 2.35 | R-410A | 13.3333
213895017 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.95 | 23.1 | 154000 | 4.47 | 128000 | 2.74 | R-410A | 11.5
213894133 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Ducted Indoor Units | 138000 | 11.6 | 22.3 | 154000 | 4.21 | 128000 | 2.64 | R-410A | 11.5
213894129 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Non-Ducted Indoor Units | 138000 | 12.3 | 23.9 | 154000 | 4.74 | 128000 | 2.84 | R-410A | 11.5
213895052 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Non-Ducted Indoor Units | 184000 | 10.8 | 21.6 | 206000 | 4.41 | 174000 | 2.75 | R-410A | 15.3333
213895057 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Ducted Indoor Units | 184000 | 10.8 | 21 | 206000 | 4.33 | 174000 | 2.58 | R-410A | 15.3333
213895062 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.3 | 206000 | 4.37 | 174000 | 2.66 | R-410A | 15.3333
213895066 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Non-Ducted Indoor Units | 230000 | 12 | 22.5 | 258000 | 3.92 | 232000 | 2.44 | R-410A | 19.1667
213895070 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Ducted Indoor Units | 230000 | 11.3 | 20.1 | 258000 | 3.99 | 232000 | 2.61 | R-410A | 19.1667
213895074 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.65 | 21.3 | 258000 | 3.95 | 232000 | 2.52 | R-410A | 19.1667
213928537 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q144WM/C-F(U) |  |  |  | GMV-Q144WM/C-F(U) | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
215685124 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q144WM/C-F(U) |  |  |  | GMV-Q144WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 19.65 | 154000 | 3.44 | 100000 | 2.07 | R-410A | 11.5
215685132 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP144C432Y2 |  |  |  | VEP144C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 19.65 | 154000 | 3.44 | 100000 | 2.07 | R-410A | 11.5
214728281 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP144C432Y2 |  |  |  | VEP144C432Y2 | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
213686145 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH |  |  |  | AVWT-144FLFSH | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
213686146 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH |  |  |  | AVWT-144FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
213686148 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FLFSH |  |  |  | AVWT-168FLFSH | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
213686149 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FLFSH |  |  |  | AVWT-168FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 22.45 | 170000 | 3.29 | 115000 | 2.16 | R-410A | 13.3333
213686151 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FLFSH |  |  |  | AVWT-192FLFSH | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
213686152 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FLFSH |  |  |  | AVWT-192FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
213884928 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.1 | 24.7 | 206000 | 4.4 | 148000 | 2.48 | R-410A | 15.3333
213884932 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 22 | 206000 | 3.81 | 148000 | 2.45 | R-410A | 15.3333
213885192 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.8 | 23.35 | 206000 | 4.1 | 148000 | 2.46 | R-410A | 15.3333
213884916 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Non-Ducted Indoor Units | 138000 | 11.9 | 24.3 | 154000 | 4 | 100000 | 2.65 | R-410A | 11.5
213884918 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 21.6 | 154000 | 3.81 | 100000 | 2.6 | R-410A | 11.5
213884938 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 23.9 | 232000 | 4.33 | 156000 | 2.75 | R-410A | 17.1667
213884940 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Ducted Indoor Units | 206000 | 11.3 | 21.9 | 232000 | 3.63 | 156000 | 2.65 | R-410A | 17.1667
213884942 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 22.9 | 258000 | 4.18 | 174000 | 2.55 | R-410A | 19.1667
213884946 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Ducted Indoor Units | 230000 | 11.2 | 21.8 | 258000 | 3.47 | 174000 | 2.53 | R-410A | 19.1667
213885186 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22.95 | 154000 | 3.9 | 100000 | 2.62 | R-410A | 11.5
213885197 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 22.9 | 232000 | 3.98 | 156000 | 2.7 | R-410A | 17.1667
213885199 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.55 | 22.35 | 258000 | 3.82 | 174000 | 2.54 | R-410A | 19.1667
213885189 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 22.85 | 180000 | 3.69 | 122000 | 2.52 | R-410A | 13.3333
213884924 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Non-Ducted Indoor Units | 160000 | 11.2 | 24.2 | 180000 | 3.85 | 122000 | 2.57 | R-410A | 13.3333
213884926 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Ducted Indoor Units | 160000 | 10.7 | 21.5 | 180000 | 3.54 | 122000 | 2.47 | R-410A | 13.3333
213884936 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 10.7 | 21.4 | 206000 | 3.64 | 146000 | 2.29 | R-410A | 15.3333
213884937 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.7 | 206000 | 3.37 | 146000 | 2.25 | R-410A | 15.3333
213885195 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.7 | 21.05 | 206000 | 3.5 | 146000 | 2.27 | R-410A | 15.3333
213885187 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.15 | 24.2 | 154000 | 4.49 | 128000 | 2.75 | R-410A | 11.5
213884920 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Non-Ducted Indoor Units | 138000 | 13.4 | 25 | 154000 | 4.87 | 128000 | 2.77 | R-410A | 11.5
213884922 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Ducted Indoor Units | 138000 | 12.9 | 23.4 | 154000 | 4.12 | 128000 | 2.73 | R-410A | 11.5
213884934 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Ducted Indoor Units | 184000 | 12.5 | 22.5 | 206000 | 3.92 | 172000 | 2.62 | R-410A | 15.3333
213884930 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Non-Ducted Indoor Units | 184000 | 13.2 | 23.3 | 206000 | 4.53 | 172000 | 2.63 | R-410A | 15.3333
213885193 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.85 | 22.9 | 206000 | 4.22 | 172000 | 2.62 | R-410A | 15.3333
213885200 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.35 | 22.9 | 258000 | 4 | 220000 | 2.48 | R-410A | 19.1667
213884948 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Ducted Indoor Units | 230000 | 12.1 | 22.5 | 258000 | 3.6 | 220000 | 2.43 | R-410A | 19.1667
213884944 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Non-Ducted Indoor Units | 230000 | 12.6 | 23.3 | 258000 | 4.4 | 220000 | 2.54 | R-410A | 19.1667
213885191 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.8 | 23.35 | 206000 | 4.1 | 148000 | 2.46 | R-410A | 15.3333
213884929 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.1 | 24.7 | 206000 | 4.4 | 148000 | 2.48 | R-410A | 15.3333
213884933 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 22 | 206000 | 3.81 | 148000 | 2.45 | R-410A | 15.3333
213885185 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22.95 | 154000 | 3.9 | 100000 | 2.62 | R-410A | 11.5
213885198 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.55 | 22.35 | 258000 | 3.82 | 174000 | 2.54 | R-410A | 19.1667
213885196 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 22.9 | 232000 | 3.98 | 156000 | 2.7 | R-410A | 17.1667
213884919 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 21.6 | 154000 | 3.81 | 100000 | 2.6 | R-410A | 11.5
213884917 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Non-Ducted Indoor Units | 138000 | 11.9 | 24.3 | 154000 | 4 | 100000 | 2.65 | R-410A | 11.5
213884939 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 23.9 | 232000 | 4.33 | 156000 | 2.75 | R-410A | 17.1667
213884943 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 22.9 | 258000 | 4.18 | 174000 | 2.55 | R-410A | 19.1667
213884941 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Ducted Indoor Units | 206000 | 11.3 | 21.9 | 232000 | 3.63 | 156000 | 2.65 | R-410A | 17.1667
213884947 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Ducted Indoor Units | 230000 | 11.2 | 21.8 | 258000 | 3.47 | 174000 | 2.53 | R-410A | 19.1667
213884927 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Ducted Indoor Units | 160000 | 10.7 | 21.5 | 180000 | 3.54 | 122000 | 2.47 | R-410A | 13.3333
213884925 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Non-Ducted Indoor Units | 160000 | 11.2 | 24.2 | 180000 | 3.85 | 122000 | 2.57 | R-410A | 13.3333
213885190 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 22.85 | 180000 | 3.69 | 122000 | 2.52 | R-410A | 13.3333
213885188 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.15 | 24.2 | 154000 | 4.49 | 128000 | 2.75 | R-410A | 11.5
213884923 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Ducted Indoor Units | 138000 | 12.9 | 23.4 | 154000 | 4.12 | 128000 | 2.73 | R-410A | 11.5
213884921 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Non-Ducted Indoor Units | 138000 | 13.4 | 25 | 154000 | 4.87 | 128000 | 2.77 | R-410A | 11.5
213884935 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Ducted Indoor Units | 184000 | 12.5 | 22.5 | 206000 | 3.92 | 172000 | 2.62 | R-410A | 15.3333
213884931 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Non-Ducted Indoor Units | 184000 | 13.2 | 23.3 | 206000 | 4.53 | 172000 | 2.63 | R-410A | 15.3333
213885194 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.85 | 22.9 | 206000 | 4.22 | 172000 | 2.62 | R-410A | 15.3333
213885201 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.35 | 22.9 | 258000 | 4 | 220000 | 2.48 | R-410A | 19.1667
213884949 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Ducted Indoor Units | 230000 | 12.1 | 22.5 | 258000 | 3.6 | 220000 | 2.43 | R-410A | 19.1667
213884945 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Non-Ducted Indoor Units | 230000 | 12.6 | 23.3 | 258000 | 4.4 | 220000 | 2.54 | R-410A | 19.1667
213893577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213893573 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213894795 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213894787 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213916544 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916545 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213916559 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916560 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213894789 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213894797 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213893575 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893579 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213894815 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894823 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213916546 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213916561 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213894825 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213894817 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213893569 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213894767 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213916543 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213916558 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213894769 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213893571 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213893471 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893464 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893465 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213894799 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Ducted Indoor Units | 206000 | 10.5 | 21.2 | 232000 | 3.65 | 196000 | 2.12 | R-410A | 17.1667
213916498 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213916496 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916515 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916517 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213894801 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Ducted Indoor Units | 206000 | 10.5 | 21.2 | 232000 | 3.65 | 196000 | 2.12 | R-410A | 17.1667
213893468 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893469 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893473 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213894818 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894827 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213916500 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213916519 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213894829 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213894820 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213893459 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213894771 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213916493 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213916512 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213894773 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213893461 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213894775 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894779 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213916494 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213916513 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213894777 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894781 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213894782 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894784 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213916495 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213916514 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213894785 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213894783 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894791 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Ducted Indoor Units | 206000 | 9.9 | 20.2 | 232000 | 3.3 | 162000 | 2.12 | R-410A | 17.1667
213894803 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Non-Ducted Indoor Units | 206000 | 9.9 | 21.7 | 232000 | 3.72 | 162000 | 2.31 | R-410A | 17.1667
213916497 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 9.9 | 20.95 | 232000 | 3.51 | 162000 | 2.21 | R-410A | 17.1667
213916516 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 9.9 | 20.95 | 232000 | 3.51 | 162000 | 2.21 | R-410A | 17.1667
213894805 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Non-Ducted Indoor Units | 206000 | 9.9 | 21.7 | 232000 | 3.72 | 162000 | 2.31 | R-410A | 17.1667
213894793 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Ducted Indoor Units | 206000 | 9.9 | 20.2 | 232000 | 3.3 | 162000 | 2.12 | R-410A | 17.1667
213894806 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894811 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213916499 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213916518 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213894813 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213894807 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213893832 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893830 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213916531 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916537 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893834 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893843 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893555 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213894831 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213916533 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213916539 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213894833 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213893557 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893740 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893741 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213916720 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916723 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213893742 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893743 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213894984 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894985 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213916735 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213916739 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213894988 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894989 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213893738 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213894890 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213916711 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213916713 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213894891 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213893739 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213894970 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894971 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213916715 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213916717 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213894972 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894973 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213894974 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894975 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213916718 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213916721 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213894976 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894977 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213894982 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894983 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213916733 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213916737 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213894986 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894987 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213893845 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893846 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916785 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916938 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916939 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893847 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893781 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893782 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916788 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213916940 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213916936 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893783 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893785 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213894926 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213916791 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213916937 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213916941 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213893786 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893793 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893795 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213894910 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213894898 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213916814 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213916810 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916816 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213916812 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213894899 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213894911 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213893796 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213893794 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213894994 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894995 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213916818 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213916820 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213894996 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894997 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213893791 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213894884 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213916806 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213916808 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213894885 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213893792 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213893548 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893549 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916532 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213916538 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893552 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893553 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
214050094 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
213896078 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213895966 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896082 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896386 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
214050102 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
214050082 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 |  |  |  | PURY-EP144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
213896466 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 |  |  |  | PURY-EP144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
213896470 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 |  |  |  | PURY-EP168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
214050086 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 |  |  |  | PURY-EP168YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
214050092 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896474 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896378 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
214050090 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
213895964 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896076 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896080 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896382 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
214050098 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
214050080 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 |  |  |  | PURY-EP144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
213896464 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 |  |  |  | PURY-EP144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
213896468 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 |  |  |  | PURY-EP168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
214050084 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 |  |  |  | PURY-EP168TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
214050088 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896472 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896376 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
213896113 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895990 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
214050150 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
214050154 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
213895994 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896123 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
214050148 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
213896109 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895988 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213895992 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896118 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
214050152 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
214050182 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
213896006 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
213896138 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896410 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896502 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
214050186 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
214050174 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YNU-A1 |  |  |  | PURY-P144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896494 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YNU-A1 |  |  |  | PURY-P144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
213896498 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168YNU-A1 |  |  |  | PURY-P168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
213896004 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
213896136 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
214050180 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
214050184 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
213896500 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
213896408 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896492 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TNU-A1 |  |  |  | PURY-P144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
214050172 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TNU-A1 |  |  |  | PURY-P144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896496 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168TNU-A1 |  |  |  | PURY-P168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
214050308 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
213896030 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896166 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896170 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896434 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
214050316 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
214050296 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN |  |  |  | TURYE1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
213896510 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN |  |  |  | TURYE1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
213896514 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN |  |  |  | TURYE1684AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
214050300 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN |  |  |  | TURYE1684AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
214050306 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896518 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896426 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
214050304 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
213896028 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896164 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896168 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896430 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
214050312 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
214050294 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN |  |  |  | TURYE1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
213896508 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN |  |  |  | TURYE1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
213896512 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN |  |  |  | TURYE1683AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
214050298 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN |  |  |  | TURYE1683AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
214050302 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896516 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896424 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
213896198 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896054 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
214050364 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
214050368 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
213896058 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896202 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
214050362 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
213896196 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896052 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896056 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896200 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
214050366 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
214050396 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
213896070 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
213896214 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896458 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896546 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
214050400 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
214050388 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1444AN41AN |  |  |  | TURYP1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896538 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1444AN41AN |  |  |  | TURYP1444AN41AN | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
213896542 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1684AN41AN |  |  |  | TURYP1684AN41AN | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
213896212 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896068 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
214050394 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
214050398 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
213896544 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
213896456 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896536 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1443AN41AN |  |  |  | TURYP1443AN41AN | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
214050386 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1443AN41AN |  |  |  | TURYP1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896540 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1683AN41AN |  |  |  | TURYP1683AN41AN | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
217729762 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 152000 | 3.9 | 98000 | 2.75 | R-32 | 11.5
217729304 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.5 | 152000 | 4 | 98000 | 2.8 | R-32 | 11.5
217729305 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Ducted Indoor Units | 138000 | 11.6 | 20.5 | 152000 | 3.8 | 98000 | 2.7 | R-32 | 11.5
217729306 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Non-Ducted Indoor Units | 160000 | 11 | 22.6 | 180000 | 3.7 | 117000 | 2.57 | R-32 | 13.3333
217729307 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Ducted Indoor Units | 160000 | 11.1 | 19.8 | 180000 | 3.47 | 117000 | 2.62 | R-32 | 13.3333
217729763 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.05 | 21.2 | 180000 | 3.58 | 117000 | 2.59 | R-32 | 13.3333
217729764 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.25 | 206000 | 3.54 | 134000 | 2.65 | R-32 | 15.3333
217729308 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.1 | 206000 | 3.78 | 134000 | 2.7 | R-32 | 15.3333
217729309 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Ducted Indoor Units | 184000 | 10.9 | 20.4 | 206000 | 3.3 | 134000 | 2.61 | R-32 | 15.3333
217729310 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Non-Ducted Indoor Units | 206000 | 10.5 | 22.3 | 230000 | 3.73 | 150000 | 2.7 | R-32 | 17.1667
217729311 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Ducted Indoor Units | 206000 | 11.5 | 22.1 | 230000 | 3.45 | 150000 | 2.67 | R-32 | 17.1667
217729765 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.2 | 230000 | 3.59 | 150000 | 2.68 | R-32 | 17.1667
217729766 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 10.6 | 21.75 | 256000 | 3.39 | 168000 | 2.55 | R-32 | 18.5
217729312 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Non-Ducted Indoor Units | 222000 | 10.3 | 21.8 | 256000 | 3.53 | 168000 | 2.6 | R-32 | 18.5
217729313 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Ducted Indoor Units | 222000 | 10.9 | 21.7 | 256000 | 3.25 | 168000 | 2.51 | R-32 | 18.5
217729319 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.5 | 152000 | 4 | 98000 | 2.8 | R-32 | 11.5
217729320 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Ducted Indoor Units | 138000 | 11.6 | 20.5 | 152000 | 3.8 | 98000 | 2.7 | R-32 | 11.5
217729783 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 152000 | 3.9 | 98000 | 2.75 | R-32 | 11.5
217729784 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.05 | 21.2 | 180000 | 3.58 | 117000 | 2.59 | R-32 | 13.3333
217729321 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Non-Ducted Indoor Units | 160000 | 11 | 22.6 | 180000 | 3.7 | 117000 | 2.57 | R-32 | 13.3333
217729322 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Ducted Indoor Units | 160000 | 11.1 | 19.8 | 180000 | 3.47 | 117000 | 2.62 | R-32 | 13.3333
217729323 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.1 | 206000 | 3.78 | 134000 | 2.7 | R-32 | 15.3333
217729324 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Ducted Indoor Units | 184000 | 10.9 | 20.4 | 206000 | 3.3 | 134000 | 2.61 | R-32 | 15.3333
217729785 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.25 | 206000 | 3.54 | 134000 | 2.65 | R-32 | 15.3333
217729786 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.2 | 230000 | 3.59 | 150000 | 2.68 | R-32 | 17.1667
217729325 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Non-Ducted Indoor Units | 206000 | 10.5 | 22.3 | 230000 | 3.73 | 150000 | 2.7 | R-32 | 17.1667
217729326 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Ducted Indoor Units | 206000 | 11.5 | 22.1 | 230000 | 3.45 | 150000 | 2.67 | R-32 | 17.1667
217729327 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Non-Ducted Indoor Units | 222000 | 10.3 | 21.8 | 256000 | 3.53 | 168000 | 2.6 | R-32 | 18.5
217729328 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Ducted Indoor Units | 222000 | 10.9 | 21.7 | 256000 | 3.25 | 168000 | 2.51 | R-32 | 18.5
217729787 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 10.6 | 21.75 | 256000 | 3.39 | 168000 | 2.55 | R-32 | 18.5
217734390 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.3 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217734333 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.6 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217734270 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.2 | 24 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217734392 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.25 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217734386 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217734394 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 22 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217734329 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217734335 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217734337 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Ducted Indoor Units | 230000 | 10.6 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217734268 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217734271 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.1 | 23.3 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217734272 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.9 | 22.9 | 258000 | 3.99 | 174000 | 2.44 | R-454B | 19.1667
217734269 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217734331 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Ducted Indoor Units | 160000 | 10.6 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217734388 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217734367 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217734313 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217734424 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217734426 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 22.35 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217734315 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Non-Ducted Indoor Units | 184000 | 13 | 23.3 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217734369 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Ducted Indoor Units | 184000 | 12.2 | 21.4 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217734371 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Ducted Indoor Units | 230000 | 11.7 | 21.4 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217734317 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Non-Ducted Indoor Units | 230000 | 12 | 23.3 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217734428 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.85 | 22.35 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217734391 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.3 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217734334 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.6 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217734293 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.2 | 24 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217734393 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.25 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217734387 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217734395 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 22 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217734330 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217734338 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Ducted Indoor Units | 230000 | 10.6 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217734336 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217734291 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217734294 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.1 | 23.3 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217734295 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.9 | 22.9 | 258000 | 3.99 | 174000 | 2.44 | R-454B | 19.1667
217734292 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217734332 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Ducted Indoor Units | 160000 | 10.6 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217734389 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217734368 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217734314 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217734425 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217734427 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 22.35 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217734316 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Non-Ducted Indoor Units | 184000 | 13 | 23.3 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217734370 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Ducted Indoor Units | 184000 | 12.2 | 21.4 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217734372 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Ducted Indoor Units | 230000 | 11.7 | 21.4 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217734318 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Non-Ducted Indoor Units | 230000 | 12 | 23.3 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217734429 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.85 | 22.35 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217735011 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Ducted Indoor Units | 184000 | 10.4 | 20.5 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217735012 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Non-Ducted Indoor Units | 184000 | 9.9 | 23.8 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217735100 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.15 | 22.15 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217735018 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217735019 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Non-Ducted Indoor Units | 206000 | 9.9 | 22.8 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217735022 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2401HT6P-UL | Ducted Indoor Units | 230000 | 10.5 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217734999 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217735000 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Non-Ducted Indoor Units | 138000 | 11.2 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217735094 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.35 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217735104 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.4 | 22 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217735106 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2401HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.85 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217735096 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217735003 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Ducted Indoor Units | 160000 | 10.4 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217735004 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217735007 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217735008 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.6 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217735098 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 22.85 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217735102 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217735014 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Ducted Indoor Units | 184000 | 10.9 | 21.2 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217735015 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Non-Ducted Indoor Units | 184000 | 11.1 | 23 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217735026 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Ducted Indoor Units | 230000 | 10.9 | 21.2 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217735027 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Non-Ducted Indoor Units | 230000 | 11.1 | 23 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217735108 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 22.1 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217735013 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Ducted Indoor Units | 184000 | 10.4 | 20.5 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217735136 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.15 | 22.15 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217735101 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Non-Ducted Indoor Units | 184000 | 9.9 | 23.8 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217735024 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2401HT9P-UL | Ducted Indoor Units | 230000 | 10.5 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217735020 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217735021 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Non-Ducted Indoor Units | 206000 | 9.9 | 22.8 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217735001 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217735002 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Non-Ducted Indoor Units | 138000 | 11.2 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217735095 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.35 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217735105 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.4 | 22 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217735107 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2401HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.85 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217735097 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217735005 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Ducted Indoor Units | 160000 | 10.4 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217735006 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217735009 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217735010 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.6 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217735099 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 22.85 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217735103 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217735016 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Ducted Indoor Units | 184000 | 10.9 | 21.2 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217735017 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Non-Ducted Indoor Units | 184000 | 11.1 | 23 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217735028 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Ducted Indoor Units | 230000 | 10.9 | 21.2 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217735029 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Non-Ducted Indoor Units | 230000 | 11.1 | 23 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217735109 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 22.1 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217883042 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 112000 | 2.7 | R-454B | 11.5
217883044 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 112000 | 2.56 | R-454B | 11.5
217883046 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 112000 | 2.63 | R-454B | 11.5
217901739 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A |  |  |  | PURY-EM144TXU-A | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217901741 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A |  |  |  | PURY-EM144TXU-A | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217901743 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A |  |  |  | PURY-EM168TXU-A | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217901745 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A |  |  |  | PURY-EM168TXU-A | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217901747 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A |  |  |  | PURY-EM192TXU-A | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217901751 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A |  |  |  | PURY-EM192TXU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902155 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A | PURY-HM72TXU-A |  |  | PURY-HM144TSXU-A | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902157 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A | PURY-HM72TXU-A |  |  | PURY-HM144TSXU-A | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217901753 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A | PURY-HM96TXU-A |  |  | PURY-HM192TSXU-A | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217901749 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A | PURY-HM96TXU-A |  |  | PURY-HM192TSXU-A | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217902159 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A | PURY-HM120TXU-A |  |  | PURY-HM240TSXU-A | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902161 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A | PURY-HM120TXU-A |  |  | PURY-HM240TSXU-A | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
217901740 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A |  |  |  | PURY-EM144YXU-A | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217901742 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A |  |  |  | PURY-EM144YXU-A | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217901744 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A |  |  |  | PURY-EM168YXU-A | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217901746 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A |  |  |  | PURY-EM168YXU-A | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217901748 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A |  |  |  | PURY-EM192YXU-A | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217901752 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A |  |  |  | PURY-EM192YXU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902158 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A | PURY-HM72YXU-A |  |  | PURY-HM144YSXU-A | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217902156 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A | PURY-HM72YXU-A |  |  | PURY-HM144YSXU-A | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217901754 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A | PURY-HM96YXU-A |  |  | PURY-HM192YSXU-A | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217901750 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A | PURY-HM96YXU-A |  |  | PURY-HM192YSXU-A | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217902162 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A | PURY-HM120YXU-A |  |  | PURY-HM240YSXU-A | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
217902160 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A | PURY-HM120YXU-A |  |  | PURY-HM240YSXU-A | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902285 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN |  |  |  | TURYE1443AMM0AN | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217902283 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN |  |  |  | TURYE1443AMM0AN | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217902291 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN |  |  |  | TURYE1683AMM0AN | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217902292 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN |  |  |  | TURYE1683AMM0AN | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217902295 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN |  |  |  | TURYE1923AMM0AN | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217902297 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN |  |  |  | TURYE1923AMM0AN | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902286 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN | TURYH0723AMM0AN |  |  | TURYH1443BMM0AN | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217902284 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN | TURYH0723AMM0AN |  |  | TURYH1443BMM0AN | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902298 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN | TURYH0963AMM0AN |  |  | TURYH1923BMM0AN | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217902296 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN | TURYH0963AMM0AN |  |  | TURYH1923BMM0AN | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217902303 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN | TURYH1203AMM0AN |  |  | TURYH2403BMM0AN | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902304 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN | TURYH1203AMM0AN |  |  | TURYH2403BMM0AN | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
217902289 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN |  |  |  | TURYE1444AMM0AN | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217902287 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN |  |  |  | TURYE1444AMM0AN | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217902293 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN |  |  |  | TURYE1684AMM0AN | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217902294 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN |  |  |  | TURYE1684AMM0AN | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217902299 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN |  |  |  | TURYE1924AMM0AN | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217902301 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN |  |  |  | TURYE1924AMM0AN | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902290 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN | TURYH0724AMM0AN |  |  | TURYH1444BMM0AN | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217902288 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN | TURYH0724AMM0AN |  |  | TURYH1444BMM0AN | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902300 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN | TURYH0964AMM0AN |  |  | TURYH1924BMM0AN | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217902302 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN | TURYH0964AMM0AN |  |  | TURYH1924BMM0AN | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217902305 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN | TURYH1204AMM0AN |  |  | TURYH2404BMM0AN | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902306 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN | TURYH1204AMM0AN |  |  | TURYH2404BMM0AN | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
217901699 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A |  |  |  | PUHY-EM144TXU-A | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217901700 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A |  |  |  | PUHY-EM144TXU-A | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217901703 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A |  |  |  | PUHY-EM168TXU-A | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217901704 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A |  |  |  | PUHY-EM168TXU-A | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217901707 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A |  |  |  | PUHY-EM192TXU-A | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217901708 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A |  |  |  | PUHY-EM192TXU-A | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902123 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A | PUHY-HM72TXU-A |  |  | PUHY-HM144TSXU-A | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902124 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A | PUHY-HM72TXU-A |  |  | PUHY-HM144TSXU-A | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217901711 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A | PUHY-HM96TXU-A |  |  | PUHY-HM192TSXU-A | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217901712 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A | PUHY-HM96TXU-A |  |  | PUHY-HM192TSXU-A | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902127 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A | PUHY-HM120TXU-A |  |  | PUHY-HM240TSXU-A | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902128 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A | PUHY-HM120TXU-A |  |  | PUHY-HM240TSXU-A | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
217901701 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A |  |  |  | PUHY-EM144YXU-A | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217901702 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A |  |  |  | PUHY-EM144YXU-A | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217901705 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A |  |  |  | PUHY-EM168YXU-A | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217901706 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A |  |  |  | PUHY-EM168YXU-A | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217901709 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A |  |  |  | PUHY-EM192YXU-A | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217901710 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A |  |  |  | PUHY-EM192YXU-A | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902125 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A | PUHY-HM72YXU-A |  |  | PUHY-HM144YSXU-A | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902126 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A | PUHY-HM72YXU-A |  |  | PUHY-HM144YSXU-A | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217901713 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A | PUHY-HM96YXU-A |  |  | PUHY-HM192YSXU-A | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217901714 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A | PUHY-HM96YXU-A |  |  | PUHY-HM192YSXU-A | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902129 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A | PUHY-HM120YXU-A |  |  | PUHY-HM240YSXU-A | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902130 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A | PUHY-HM120YXU-A |  |  | PUHY-HM240YSXU-A | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
217902211 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN |  |  |  | TUHYE1443AMM0AN | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217902213 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN |  |  |  | TUHYE1443AMM0AN | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217902219 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN |  |  |  | TUHYE1683AMM0AN | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217902220 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN |  |  |  | TUHYE1683AMM0AN | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217902223 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN |  |  |  | TUHYE1923AMM0AN | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217902225 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN |  |  |  | TUHYE1923AMM0AN | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902214 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN | TUHYH0723AMM0AN |  |  | TUHYH1443BMM0AN | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217902212 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN | TUHYH0723AMM0AN |  |  | TUHYH1443BMM0AN | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902226 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN | TUHYH0963AMM0AN |  |  | TUHYH1923BMM0AN | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902224 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN | TUHYH0963AMM0AN |  |  | TUHYH1923BMM0AN | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217902231 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN | TUHYH1203AMM0AN |  |  | TUHYH2403BMM0AN | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902232 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN | TUHYH1203AMM0AN |  |  | TUHYH2403BMM0AN | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
217902217 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN |  |  |  | TUHYE1444AMM0AN | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217902215 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN |  |  |  | TUHYE1444AMM0AN | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217902221 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN |  |  |  | TUHYE1684AMM0AN | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217902222 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN |  |  |  | TUHYE1684AMM0AN | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217902227 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN |  |  |  | TUHYE1924AMM0AN | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217902229 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN |  |  |  | TUHYE1924AMM0AN | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902218 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN | TUHYH0724AMM0AN |  |  | TUHYH1444BMM0AN | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217902216 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN | TUHYH0724AMM0AN |  |  | TUHYH1444BMM0AN | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902228 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN | TUHYH0964AMM0AN |  |  | TUHYH1924BMM0AN | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217902230 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN | TUHYH0964AMM0AN |  |  | TUHYH1924BMM0AN | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902233 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN | TUHYH1204AMM0AN |  |  | TUHYH2404BMM0AN | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902234 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN | TUHYH1204AMM0AN |  |  | TUHYH2404BMM0AN | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
218003068 | N/A | SAMSUNG | HMSV-A-CB | AM216HCVGFG |  |  |  | AM216HCVGFG | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004911 | N/A | SAMSUNG | HMSV-A-CB | AM216HCVGFG |  |  |  | AM216HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218003072 | N/A | SAMSUNG | HMSV-A-CB | AM240HCVGFG |  |  |  | AM240HCVGFG | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003069 | N/A | SAMSUNG | HMSR-A-CB | AM216HCVGFS |  |  |  | AM216HCVGFS | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004912 | N/A | SAMSUNG | HMSR-A-CB | AM216HCVGFS |  |  |  | AM216HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218003073 | N/A | SAMSUNG | HMSR-A-CB | AM240HCVGFS |  |  |  | AM240HCVGFS | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003070 | N/A | SAMSUNG | HMSV-A-CB | AM216HCVGJG |  |  |  | AM216HCVGJG | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004913 | N/A | SAMSUNG | HMSV-A-CB | AM216HCVGJG |  |  |  | AM216HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218003074 | N/A | SAMSUNG | HMSV-A-CB | AM240HCVGJG |  |  |  | AM240HCVGJG | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003071 | N/A | SAMSUNG | HMSR-A-CB | AM216HCVGJS |  |  |  | AM216HCVGJS | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004914 | N/A | SAMSUNG | HMSR-A-CB | AM216HCVGJS |  |  |  | AM216HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218003075 | N/A | SAMSUNG | HMSR-A-CB | AM240HCVGJS |  |  |  | AM240HCVGJS | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218004899 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003120 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003056 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003060 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003124 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004903 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218004907 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG |  |  |  | AM192HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003064 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG |  |  |  | AM192HCVGFG | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004900 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003121 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003057 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003061 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003125 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004904 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218004908 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS |  |  |  | AM192HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003065 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS |  |  |  | AM192HCVGFS | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004901 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003122 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003058 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003062 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003126 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004905 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218004909 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG |  |  |  | AM192HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003066 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG |  |  |  | AM192HCVGJG | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004902 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003123 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003059 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003063 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003127 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004906 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218004910 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS |  |  |  | AM192HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003067 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS |  |  |  | AM192HCVGJS | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218005679 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005683 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005711 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005715 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005723 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM072HCVTFG |  | AM216HCVTFG | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218005727 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM096HCVTFG |  | AM240HCVTFG | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218005751 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005755 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218009371 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM072HCVTFG |  | AM216HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218009363 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM072HCVTFG |  | AM216HCVTFG | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218009367 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM096HCVTFG |  | AM240HCVTFG | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218009375 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM096HCVTFG |  | AM240HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218005759 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG | AM096HCVTFG |  |  | AM192HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218005719 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG | AM096HCVTFG |  |  | AM192HCVTFG | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218005687 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG | AM096HCVTFG |  |  | AM192HCVTFG | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218005752 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005756 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218005712 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005716 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005728 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM096HCVTFS |  | AM240HCVTFS | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218005724 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM072HCVTFS |  | AM216HCVTFS | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218005680 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005684 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218009376 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM096HCVTFS |  | AM240HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218009368 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM096HCVTFS |  | AM240HCVTFS | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218009364 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM072HCVTFS |  | AM216HCVTFS | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218009372 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM072HCVTFS |  | AM216HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218005688 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS | AM096HCVTFS |  |  | AM192HCVTFS | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218005720 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS | AM096HCVTFS |  |  | AM192HCVTFS | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218005760 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS | AM096HCVTFS |  |  | AM192HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218005681 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005685 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005713 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005717 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005725 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM072HCVTJG |  | AM216HCVTJG | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218005729 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM096HCVTJG |  | AM240HCVTJG | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218005753 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005757 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218009373 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM072HCVTJG |  | AM216HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218009365 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM072HCVTJG |  | AM216HCVTJG | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218009369 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM096HCVTJG |  | AM240HCVTJG | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218009377 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM096HCVTJG |  | AM240HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218005761 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG | AM096HCVTJG |  |  | AM192HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218005721 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG | AM096HCVTJG |  |  | AM192HCVTJG | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218005689 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG | AM096HCVTJG |  |  | AM192HCVTJG | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218005754 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005758 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218005714 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005718 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005730 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM096HCVTJS |  | AM240HCVTJS | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218005726 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM072HCVTJS |  | AM216HCVTJS | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218005682 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005686 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218009378 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM096HCVTJS |  | AM240HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218009370 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM096HCVTJS |  | AM240HCVTJS | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218009366 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM072HCVTJS |  | AM216HCVTJS | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218009374 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM072HCVTJS |  | AM216HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218005690 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS | AM096HCVTJS |  |  | AM192HCVTJS | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218005722 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS | AM096HCVTJS |  |  | AM192HCVTJS | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218005762 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS | AM096HCVTJS |  |  | AM192HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
213895710 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* |  |  |  | REYQ144AATJ* | Non-Ducted Indoor Units | 138000 | 11.2 | 21.5 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213895939 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* |  |  |  | REYQ144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 19.8 | 138000 | 3.25 | 90000 | 2.1 | R-410A | 11.5
213896247 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* |  |  |  | REYQ168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.45 | 18.95 | 156000 | 3.25 | 104000 | 2.07 | R-410A | 13
213895949 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* |  |  |  | REYQ144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 19.8 | 138000 | 3.25 | 90000 | 2.1 | R-410A | 11.5
213895713 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* |  |  |  | REYQ144AAYD* | Non-Ducted Indoor Units | 138000 | 11.2 | 21.5 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213896255 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* |  |  |  | REYQ168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.45 | 18.95 | 156000 | 3.25 | 104000 | 2.07 | R-410A | 13
216602560 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602464 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602371 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893995 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893937 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893893 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893941 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213918736 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213916416 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602470 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602661 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602621 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602669 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y |  |  |  | VPC192S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602477 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y |  |  |  | VPC192S4M-4Y | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213918740 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH |  |  |  | AM192BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213893945 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH |  |  |  | AM192BXVGFH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893949 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM216BXVGFH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
213918744 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM216BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602483 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4Y |  |  |  | VPC216S4M-4Y | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602678 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4Y |  |  |  | VPC216S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602490 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4Y |  |  |  | VPC240S4M-4Y | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893953 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240BXVGFH |  |  |  | AM240BXVGFH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602375 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602563 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602467 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893939 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893895 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893997 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893943 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213916418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
213918738 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602473 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602665 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602624 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602480 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G |  |  |  | VPC192S4M-4G | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
216602675 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G |  |  |  | VPC192S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213918742 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH |  |  |  | AM192BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213893947 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH |  |  |  | AM192BXVGJH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893951 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM216BXVGJH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
213918746 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM216BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602680 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4G |  |  |  | VPC216S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602486 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4G |  |  |  | VPC216S4M-4G | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602493 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4G |  |  |  | VPC240S4M-4G | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893955 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240BXVGJH |  |  |  | AM240BXVGJH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826414 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602373 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602562 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602465 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602801 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893938 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893894 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893996 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893942 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213918737 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213916417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602804 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602472 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602663 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602623 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
214826415 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
214826416 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602672 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602478 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4Y | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
216602806 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213918741 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213893946 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192BXVGFR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893950 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216BXVGFR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
213918745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602808 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602679 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602485 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4Y | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
214826417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602492 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4Y |  |  |  | VRC240S4M-4Y | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893954 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240BXVGFR |  |  |  | AM240BXVGFR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602378 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602565 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602469 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893940 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893896 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893998 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893944 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213916419 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
213918739 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602475 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602667 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602626 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602481 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G |  |  |  | VRC192S4M-4G | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
216602676 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G |  |  |  | VRC192S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213918743 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR |  |  |  | AM192BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213893948 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR |  |  |  | AM192BXVGJR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893952 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM216BXVGJR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
213918747 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM216BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602681 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4G |  |  |  | VRC216S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602488 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4G |  |  |  | VRC216S4M-4G | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602495 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4G |  |  |  | VRC240S4M-4G | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893956 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240BXVGJR |  |  |  | AM240BXVGJR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
208811485 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208811486 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Non-Ducted Indoor Units | 230000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208812535 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812536 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Ducted Indoor Units | 230000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931709 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Non-Ducted Indoor Units | 138000 | 14.4 | 28.2 | 154000 | 4.07 | 106000 | 2.48 | R-410A | 11.5
208931864 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Ducted Indoor Units | 138000 | 12.2 | 20.4 | 154000 | 3.82 | 106000 | 2.4 | R-410A | 11.5
208931866 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Ducted Indoor Units | 160000 | 11.5 | 19.9 | 180000 | 3.61 | 124000 | 2.3 | R-410A | 13.3333
208931711 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Non-Ducted Indoor Units | 160000 | 12.2 | 25.7 | 180000 | 3.78 | 124000 | 2.32 | R-410A | 13.3333
208931713 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Non-Ducted Indoor Units | 184000 | 11 | 24.6 | 206000 | 3.48 | 140000 | 2.16 | R-410A | 15.3333
208931868 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 206000 | 3.48 | 140000 | 2.23 | R-410A | 15.3333
208812540 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812541 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Ducted Indoor Units | 230000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208811490 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208811491 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Non-Ducted Indoor Units | 230000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931731 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Non-Ducted Indoor Units | 138000 | 14.4 | 28.2 | 154000 | 4.07 | 106000 | 2.48 | R-410A | 11.5
208931886 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Ducted Indoor Units | 138000 | 12.2 | 20.4 | 154000 | 3.82 | 106000 | 2.4 | R-410A | 11.5
208931888 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Ducted Indoor Units | 160000 | 11.5 | 19.9 | 180000 | 3.61 | 124000 | 2.3 | R-410A | 13.3333
208931732 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Non-Ducted Indoor Units | 160000 | 12.2 | 25.7 | 180000 | 3.78 | 124000 | 2.32 | R-410A | 13.3333
208931734 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Non-Ducted Indoor Units | 184000 | 11 | 24.6 | 206000 | 3.48 | 140000 | 2.16 | R-410A | 15.3333
208931890 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 206000 | 3.48 | 140000 | 2.23 | R-410A | 15.3333
214432094 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S | HVAHR096B42S |  |  | HVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094333 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094182 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432098 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S | YVAHR096B32S |  |  | YVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094413 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094262 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432134 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S | YVAHR096B42S |  |  | YVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094429 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094278 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432132 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B32S | TVAHR096B32S |  |  | TVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094365 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094214 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311059 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B42S | TVAHR096B42S |  |  | TVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094381 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094230 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311057 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S | HVAHR096B32S |  |  | HVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094317 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094166 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
9990282 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
9990283 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990284 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
9990280 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990281 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
214432114 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B32S | TVAHP096B32S |  |  | TVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091583 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091440 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311042 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B42S | TVAHP096B42S |  |  | TVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091599 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091456 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311040 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S | HVAHP096B32S |  |  | HVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091535 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214078207 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432076 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S | HVAHP096B42S |  |  | HVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091551 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091408 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432080 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S | YVAHP096B32S |  |  | YVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091631 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091488 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432116 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S | YVAHP096B42S |  |  | YVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091647 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091504 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
213916293 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916298 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916856 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916857 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916295 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
213916300 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
213916858 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
213916304 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916310 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916864 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916865 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916306 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
213916312 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
213916866 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
6687545 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
207742259 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687547 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687549 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
6687551 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6687553 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850824 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850826 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850828 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
7850830 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850832 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850844 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850846 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850848 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
7850850 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850852 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
214432096 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B52S | TVAHR096B52S |  |  | TVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094397 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094246 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432130 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S | HVAHR096B52S |  |  | HVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094349 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094198 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311061 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S | YVAHR096B52S |  |  | YVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094445 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094294 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432078 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B52S | TVAHP096B52S |  |  | TVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091615 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091472 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432112 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S | HVAHP096B52S |  |  | HVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091567 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091424 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311044 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S | YVAHP096B52S |  |  | YVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091663 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091520 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
213896730 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896731 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ120XBTJ* |  |  | REYQ216XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896712 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896682 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896683 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ120XBTJ* |  |  | REYQ216XBTJ* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896684 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* |  |  | REYQ240XBTJ* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896774 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* |  |  | REYQ240XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896797 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBTJ* |  |  |  | REYQ144XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896718 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896699 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896700 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ120XBYD* |  |  | REYQ216XBYD* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896736 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896737 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ120XBYD* |  |  | REYQ216XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896750 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* |  |  | REYQ240XBYD* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896778 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* |  |  | REYQ240XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896800 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBYD* |  |  |  | REYQ144XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896706 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896707 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ120XBYC* |  |  | REYQ216XBYC* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896724 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896742 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896743 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ120XBYC* |  |  | REYQ216XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896754 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* |  |  | REYQ240XBYC* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896782 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* |  |  | REYQ240XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896803 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBYC* |  |  |  | REYQ144XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896747 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* | RXYQ96XBYC* |  |  | RXYQ192XBYC* | Non-Ducted Indoor Units | 184000 | 10.7 | 18.4 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896809 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* | RXYQ120XBYC* |  |  | RXYQ216XBYC* | Non-Ducted Indoor Units | 206000 | 10.2 | 18.4 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896810 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* |  |  | RXYQ240XBYC* | Non-Ducted Indoor Units | 228000 | 9.9 | 18.6 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
214389359 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME2CA* |  |  |  | MVHQ144ME2CA* | Ducted Indoor Units | 138000 | 10.8 | 20.3 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214389360 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME2CA* |  |  |  | MVHQ144ME2CA* | Non-Ducted Indoor Units | 138000 | 10.8 | 20 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214229577 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME2CA* |  |  |  | MVHQ168ME2CA* | Ducted Indoor Units | 160000 | 11.5 | 21.5 | 180000 | 3.4 | 122000 | 2.4 | R-410A | 13.3333
214229578 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME2CA* |  |  |  | MVHQ168ME2CA* | Non-Ducted Indoor Units | 160000 | 11.4 | 23.2 | 180000 | 3.6 | 122000 | 2.5 | R-410A | 13.3333
214264484 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* |  |  |  | MVHQ192ME2CA* | Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.3 | 138000 | 2.4 | R-410A | 15.3333
214264485 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* |  |  |  | MVHQ192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.2 | 22.2 | 206000 | 3.5 | 138000 | 2.4 | R-410A | 15.3333
214097889 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME2CA* |  |  |  | MVHQ216ME2CA* | Ducted Indoor Units | 206000 | 11.3 | 20.8 | 232000 | 3.3 | 156000 | 2.4 | R-410A | 17.1667
214097890 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME2CA* |  |  |  | MVHQ216ME2CA* | Non-Ducted Indoor Units | 206000 | 10.9 | 22 | 232000 | 3.5 | 156000 | 2.4 | R-410A | 17.1667
214264488 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME2CA* |  |  |  | MVHQ240ME2CA* | Ducted Indoor Units | 222000 | 10.7 | 20.3 | 240000 | 3.3 | 168000 | 2.3 | R-410A | 18.5
214264490 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME2CA* |  |  |  | MVHQ240ME2CA* | Non-Ducted Indoor Units | 222000 | 10.1 | 20.3 | 240000 | 3.4 | 168000 | 2.4 | R-410A | 18.5
214389361 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME4CA* |  |  |  | MVHQ144ME4CA* | Ducted Indoor Units | 138000 | 10.8 | 20.3 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214389362 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME4CA* |  |  |  | MVHQ144ME4CA* | Non-Ducted Indoor Units | 138000 | 10.8 | 20 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214229579 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME4CA* |  |  |  | MVHQ168ME4CA* | Ducted Indoor Units | 160000 | 11.5 | 21.5 | 180000 | 3.4 | 122000 | 2.4 | R-410A | 13.3333
214229580 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME4CA* |  |  |  | MVHQ168ME4CA* | Non-Ducted Indoor Units | 160000 | 11.4 | 23.2 | 180000 | 3.6 | 122000 | 2.5 | R-410A | 13.3333
214264486 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* |  |  |  | MVHQ192ME4CA* | Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.3 | 138000 | 2.4 | R-410A | 15.3333
214264487 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* |  |  |  | MVHQ192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.2 | 22.2 | 206000 | 3.5 | 138000 | 2.4 | R-410A | 15.3333
214065405 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME4CA* |  |  |  | MVHQ216ME4CA* | Ducted Indoor Units | 206000 | 11.3 | 20.8 | 232000 | 3.3 | 156000 | 2.4 | R-410A | 17.1667
214065406 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME4CA* |  |  |  | MVHQ216ME4CA* | Non-Ducted Indoor Units | 206000 | 10.9 | 22 | 232000 | 3.5 | 156000 | 2.4 | R-410A | 17.1667
214264491 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME4CA* |  |  |  | MVHQ240ME4CA* | Non-Ducted Indoor Units | 222000 | 10.1 | 20.3 | 240000 | 3.4 | 168000 | 2.4 | R-410A | 18.5
214264489 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME4CA* |  |  |  | MVHQ240ME4CA* | Ducted Indoor Units | 222000 | 10.7 | 20.3 | 240000 | 3.3 | 168000 | 2.3 | R-410A | 18.5
217189685 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B33CW | HVAHR096B33CW |  |  | HVAHR192B33CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
214296007 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B33CW | HVAHR096B33CW |  |  | HVAHR192B33CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
217189695 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B43CW | HVAHR096B43CW |  |  | HVAHR192B43CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
214296017 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B43CW | HVAHR096B43CW |  |  | HVAHR192B43CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
217189704 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B53CW | HVAHR072B53CW |  |  | HVAHR168B53CW* | Non-Ducted Indoor Units | 160000 | 11.2 | 18.7 | 180000 | 4.2 | 124000 | 2.6 | R-410A | 13.3333
217189705 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B53CW | HVAHR096B53CW |  |  | HVAHR192B53CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
215828405 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B53CW | HVAHR072B53CW |  |  | HVAHR168B53CW | Non-Ducted Indoor Units | 160000 | 11.2 | 18.7 | 180000 | 4.2 | 124000 | 2.6 | R-410A | 13.3333
215828406 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B53CW | HVAHR096B53CW |  |  | HVAHR192B53CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
215828408 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B53CW | HVAHR120B53CW |  |  | HVAHR240B53CW | Non-Ducted Indoor Units | 230000 | 12 | 18.6 | 258000 | 4.1 | 178000 | 2.55 | R-410A | 19.1667
217189707 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B53CW | HVAHR120B53CW |  |  | HVAHR240B53CW* | Non-Ducted Indoor Units | 230000 | 12 | 18.6 | 258000 | 4.1 | 178000 | 2.55 | R-410A | 19.1667
217190041 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 18 | 154000 | 3.6 | 110000 | 2.4 | R-410A | 11.5
217189703 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW* | Non-Ducted Indoor Units | 138000 | 11.7 | 18.7 | 154000 | 3.8 | 110000 | 2.6 | R-410A | 11.5
215828414 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 18 | 154000 | 3.6 | 110000 | 2.4 | R-410A | 11.5
215828404 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW | Non-Ducted Indoor Units | 138000 | 11.7 | 18.7 | 154000 | 3.8 | 110000 | 2.6 | R-410A | 11.5
214825950 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD144K/220V |  |  |  | TVRF-SHD144K/220V | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
216602783 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602727 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602713 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826406 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
214826375 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
214826366 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826367 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
214826376 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
214826407 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602714 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602728 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602786 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602788 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J |  |  |  | VPC192S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602716 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J |  |  |  | VPC192S4M-4J | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH |  |  |  | AM192DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
214826368 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH |  |  |  | AM192DXVGQH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826369 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216DXVGQH |  |  |  | AM216DXVGQH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
214826409 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216DXVGQH |  |  |  | AM216DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602717 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4J |  |  |  | VPC216S4M-4J | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602791 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4J |  |  |  | VPC216S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602719 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4J |  |  |  | VPC240S4M-4J | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826370 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240DXVGQH |  |  |  | AM240DXVGQH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602761 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4J |  |  |  | VRC144S4M-4J | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602746 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4J |  |  |  | VRC144S4M-4J | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826395 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144DXVGQR |  |  |  | AM144DXVGQR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
214826386 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144DXVGQR |  |  |  | AM144DXVGQR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826387 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168DXVGQR |  |  |  | AM168DXVGQR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
214826396 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168DXVGQR |  |  |  | AM168DXVGQR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602748 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4J |  |  |  | VRC168S4M-4J | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602763 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4J |  |  |  | VRC168S4M-4J | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602749 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J |  |  |  | VRC192S4M-4J | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826388 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR |  |  |  | AM192DXVGQR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826389 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216DXVGQR |  |  |  | AM216DXVGQR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602751 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4J |  |  |  | VRC216S4M-4J | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602753 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4J |  |  |  | VRC240S4M-4J | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826390 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240DXVGQR |  |  |  | AM240DXVGQR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213916693 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916326 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916318 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916694 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916695 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
213916328 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
213916320 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
214050519 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P96ZKMU-B |  |  | PURY-P192ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.4 | 18.65 | 204000 | 3.42 | 142000 | 2.13 | R-410A | 15.3333
214050513 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P72ZKMU-B |  |  | PURY-P168ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 18.3 | 178000 | 3.44 | 119000 | 2.12 | R-410A | 13.3333
213896343 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P72ZKMU-B |  |  | PURY-P168ZSKMU-B | Ducted Indoor Units | 160000 | 10.6 | 19.1 | 178000 | 3.6 | 119000 | 2.13 | R-410A | 13.3333
213896345 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P96ZKMU-B |  |  | PURY-P192ZSKMU-B | Ducted Indoor Units | 184000 | 10.3 | 19.6 | 204000 | 3.48 | 142000 | 2.1 | R-410A | 15.3333
213896322 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P192ZSKMU-B | Ducted Indoor Units | 184000 | 11 | 18.7 | 204000 | 3.48 | 150000 | 2.45 | R-410A | 15.3333
213896320 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Ducted Indoor Units | 160000 | 11.3 | 20.7 | 178000 | 3.54 | 132000 | 2.6 | R-410A | 13.3333
213896285 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Non-Ducted Indoor Units | 160000 | 11.4 | 19.2 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
213916481 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.35 | 19.95 | 178000 | 3.68 | 132000 | 2.39 | R-410A | 13.3333
213916482 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P192ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 18.25 | 204000 | 3.58 | 150000 | 2.31 | R-410A | 15.3333
213916483 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P216ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 18.8 | 232000 | 3.53 | 164000 | 2.28 | R-410A | 17.1667
213896324 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P216ZSKMU-B | Ducted Indoor Units | 206000 | 10.8 | 19.8 | 232000 | 3.51 | 164000 | 2.48 | R-410A | 17.1667
213896318 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144ZKMU-B |  |  |  | PUHY-P144ZKMU-B | Ducted Indoor Units | 138000 | 9.9 | 18.5 | 152000 | 3.46 | 109000 | 2.32 | R-410A | 11.5
213886458 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH | AM120BXVTJH |  | AM288BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886454 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM120BXVTJH |  | AM264BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886386 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH | AM120BXVTJH |  | AM288BXVTJH | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886382 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM120BXVTJH |  | AM264BXVTJH | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602294 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC120L4M-4G |  | VPC264L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602303 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G | VPC120L4M-4G |  | VPC288L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
216602154 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC120L4M-4G |  | VPC264L4M-4G | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602161 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G | VPC120L4M-4G |  | VPC288L4M-4G | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602159 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y | VRC120L4M-4Y |  | VRC288L4M-4Y | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602152 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC120L4M-4Y |  | VRC264L4M-4Y | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602292 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC120L4M-4Y |  | VRC264L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602301 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y | VRC120L4M-4Y |  | VRC288L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886381 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM120BXVTFR |  | AM264BXVTFR | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
213886385 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR | AM120BXVTFR |  | AM288BXVTFR | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886453 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM120BXVTFR |  | AM264BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886457 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR | AM120BXVTFR |  | AM288BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886455 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM120BXVTJR |  | AM264BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886459 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR | AM120BXVTJR |  | AM288BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886387 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR | AM120BXVTJR |  | AM288BXVTJR | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886383 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM120BXVTJR |  | AM264BXVTJR | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602297 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC120L4M-4G |  | VRC264L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602305 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G | VRC120L4M-4G |  | VRC288L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
216602155 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC120L4M-4G |  | VRC264L4M-4G | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602162 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G | VRC120L4M-4G |  | VRC288L4M-4G | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602150 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC120L4M-4Y |  | VPC264L4M-4Y | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602157 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y | VPC120L4M-4Y |  | VPC288L4M-4Y | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602290 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC120L4M-4Y |  | VPC264L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602299 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y | VPC120L4M-4Y |  | VPC288L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886380 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM120BXVTFH |  | AM264BXVTFH | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
213886384 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH | AM120BXVTFH |  | AM288BXVTFH | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886452 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM120BXVTFH |  | AM264BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886456 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH | AM120BXVTFH |  | AM288BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213897021 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* | RXYQ144AATJ* |  |  | RXYQ264AATJ* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-410A | 21
213897064 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* | RXYQ144AATJ* |  |  | RXYQ264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 19.9 | 252000 | 3.3 | 168000 | 2.2 | R-410A | 21
213897065 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.35 | 274000 | 3.37 | 194000 | 2.15 | R-410A | 22.8333
213897066 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ168AATJ* |  |  | RXYQ312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.1 | 19 | 296000 | 3.35 | 212000 | 2.13 | R-410A | 24.6667
213897047 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Ducted Indoor Units | 274000 | 10.4 | 18 | 274000 | 3.25 | 194000 | 2.1 | R-410A | 22.8333
213897022 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.7 | 274000 | 3.5 | 194000 | 2.2 | R-410A | 22.8333
213897023 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ168AATJ* |  |  | RXYQ312AATJ* | Non-Ducted Indoor Units | 296000 | 10.2 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-410A | 24.6667
213897024 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-410A | 28.5
213897087 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ168AATJ* |  |  | RXYQ336AATJ* | Non-Ducted Indoor Units | 316000 | 9.3 | 18.4 | 310000 | 3.5 | 222000 | 2.1 | R-410A | 26.3333
213897098 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Ducted Indoor Units | 342000 | 9.3 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-410A | 28.5
213897114 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ168AATJ* |  |  | RXYQ336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.3 | 17.8 | 310000 | 3.35 | 222000 | 2.08 | R-410A | 26.3333
213897115 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.8 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-410A | 28.5
213897116 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.6 | 18.3 | 388000 | 3.35 | 276000 | 2.1 | R-410A | 32.3333
213897099 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Ducted Indoor Units | 388000 | 9.2 | 17 | 388000 | 3.25 | 276000 | 2.1 | R-410A | 32.3333
213897025 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Non-Ducted Indoor Units | 364000 | 10.4 | 20 | 364000 | 3.45 | 264000 | 2.1 | R-410A | 30.3333
213897026 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Non-Ducted Indoor Units | 388000 | 10 | 19.6 | 388000 | 3.45 | 276000 | 2.1 | R-410A | 32.3333
213897049 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Ducted Indoor Units | 364000 | 9.8 | 17.6 | 364000 | 3.25 | 264000 | 2.1 | R-410A | 30.3333
213897067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.1 | 18.8 | 364000 | 3.35 | 264000 | 2.1 | R-410A | 30.3333
213897027 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Non-Ducted Indoor Units | 404000 | 9.6 | 19 | 404000 | 3.3 | 278000 | 2.07 | R-410A | 33.6667
213897100 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Ducted Indoor Units | 404000 | 9.1 | 16.5 | 404000 | 3.25 | 278000 | 2.1 | R-410A | 33.6667
213897101 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Ducted Indoor Units | 424000 | 9.1 | 16.4 | 414000 | 3.25 | 280000 | 2.1 | R-410A | 35.3333
213897088 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Non-Ducted Indoor Units | 424000 | 9.4 | 18.4 | 414000 | 3.3 | 280000 | 2.1 | R-410A | 35.3333
213897117 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 404000 | 9.35 | 17.75 | 404000 | 3.27 | 278000 | 2.08 | R-410A | 33.6667
213897118 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.25 | 17.4 | 414000 | 3.27 | 280000 | 2.1 | R-410A | 35.3333
213897089 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* | RXYQ240AATJ* |  |  | RXYQ480AATJ* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.2 | 424000 | 3.25 | 282000 | 2.1 | R-410A | 36.3333
213897034 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* | RXYQ144AAYD* |  |  | RXYQ264AAYD* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-410A | 21
213897073 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* | RXYQ144AAYD* |  |  | RXYQ264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 19.9 | 252000 | 3.3 | 168000 | 2.2 | R-410A | 21
213897056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Ducted Indoor Units | 274000 | 10.4 | 18 | 274000 | 3.25 | 194000 | 2.1 | R-410A | 22.8333
213897074 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.35 | 274000 | 3.37 | 194000 | 2.15 | R-410A | 22.8333
213897075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ168AAYD* |  |  | RXYQ312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.1 | 19 | 296000 | 3.35 | 212000 | 2.13 | R-410A | 24.6667
213897035 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.7 | 274000 | 3.5 | 194000 | 2.2 | R-410A | 22.8333
213897036 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ168AAYD* |  |  | RXYQ312AAYD* | Non-Ducted Indoor Units | 296000 | 10.2 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-410A | 24.6667
213897037 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-410A | 28.5
213897092 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ168AAYD* |  |  | RXYQ336AAYD* | Non-Ducted Indoor Units | 316000 | 9.3 | 18.4 | 310000 | 3.5 | 222000 | 2.1 | R-410A | 26.3333
213897106 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Ducted Indoor Units | 342000 | 9.3 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-410A | 28.5
213897123 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ168AAYD* |  |  | RXYQ336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.3 | 17.8 | 310000 | 3.35 | 222000 | 2.08 | R-410A | 26.3333
213897124 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.8 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-410A | 28.5
213897125 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.6 | 18.3 | 388000 | 3.35 | 276000 | 2.1 | R-410A | 32.3333
213897107 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Ducted Indoor Units | 388000 | 9.2 | 17 | 388000 | 3.25 | 276000 | 2.1 | R-410A | 32.3333
213897038 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Non-Ducted Indoor Units | 364000 | 10.4 | 20 | 364000 | 3.45 | 264000 | 2.1 | R-410A | 30.3333
213897039 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Non-Ducted Indoor Units | 388000 | 10 | 19.6 | 388000 | 3.45 | 276000 | 2.1 | R-410A | 32.3333
213897076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.1 | 18.8 | 364000 | 3.35 | 264000 | 2.1 | R-410A | 30.3333
213897058 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Ducted Indoor Units | 364000 | 9.8 | 17.6 | 364000 | 3.25 | 264000 | 2.1 | R-410A | 30.3333
213897040 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Non-Ducted Indoor Units | 404000 | 9.6 | 19 | 404000 | 3.3 | 278000 | 2.07 | R-410A | 33.6667
213897108 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Ducted Indoor Units | 404000 | 9.1 | 16.5 | 404000 | 3.25 | 278000 | 2.1 | R-410A | 33.6667
213897109 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Ducted Indoor Units | 424000 | 9.1 | 16.4 | 414000 | 3.25 | 280000 | 2.1 | R-410A | 35.3333
213897093 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Non-Ducted Indoor Units | 424000 | 9.4 | 18.4 | 414000 | 3.3 | 280000 | 2.1 | R-410A | 35.3333
213897126 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 404000 | 9.35 | 17.75 | 404000 | 3.27 | 278000 | 2.08 | R-410A | 33.6667
213897127 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.25 | 17.4 | 414000 | 3.27 | 280000 | 2.1 | R-410A | 35.3333
213897094 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* | RXYQ240AAYD* |  |  | RXYQ480AAYD* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.2 | 424000 | 3.25 | 282000 | 2.1 | R-410A | 36.3333
213894144 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Ducted Indoor Units | 276000 | 10.8 | 21.4 | 308000 | 3.81 | 216000 | 2.56 | R-410A | 23
213894097 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Non-Ducted Indoor Units | 276000 | 9.95 | 20.6 | 308000 | 3.61 | 216000 | 2.27 | R-410A | 23
213894101 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Non-Ducted Indoor Units | 366000 | 9.6 | 18.4 | 412000 | 3.45 | 294000 | 2.28 | R-410A | 30.5
213894162 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Ducted Indoor Units | 366000 | 11 | 18.9 | 412000 | 3.48 | 294000 | 2.29 | R-410A | 30.5
213895028 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.37 | 21 | 308000 | 3.71 | 216000 | 2.41 | R-410A | 23
213895040 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.3 | 18.65 | 412000 | 3.46 | 294000 | 2.28 | R-410A | 30.5
213895044 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.95 | 18.05 | 462000 | 3.34 | 328000 | 2.29 | R-410A | 34.3333
213895046 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP1201HT6P-UL |  | MMY-UP4561HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.65 | 17.45 | 488000 | 3.3 | 350000 | 2.28 | R-410A | 36.1667
213895042 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.1 | 18.15 | 438000 | 3.36 | 310000 | 2.29 | R-410A | 32.5
213895036 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.42 | 18.9 | 386000 | 3.47 | 284000 | 2.29 | R-410A | 28.5
213895032 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 20.2 | 334000 | 3.57 | 236000 | 2.44 | R-410A | 24.8333
213895034 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 19.6 | 360000 | 3.49 | 268000 | 2.3 | R-410A | 26.6667
213895026 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.3 | 20.6 | 284000 | 3.78 | 200000 | 2.52 | R-410A | 21
213894165 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Ducted Indoor Units | 390000 | 10.4 | 18.4 | 438000 | 3.38 | 310000 | 2.39 | R-410A | 32.5
213894168 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Ducted Indoor Units | 412000 | 9.9 | 17.6 | 462000 | 3.35 | 328000 | 2.41 | R-410A | 34.3333
213894152 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Ducted Indoor Units | 320000 | 10 | 18.4 | 360000 | 3.46 | 268000 | 2.39 | R-410A | 26.6667
213894157 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Ducted Indoor Units | 342000 | 11.2 | 19.4 | 386000 | 3.5 | 284000 | 2.45 | R-410A | 28.5
213894171 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP1201HT6P-UL |  | MMY-UP4561HT6P-UL | Ducted Indoor Units | 434000 | 9.5 | 17.3 | 488000 | 3.33 | 350000 | 2.36 | R-410A | 36.1667
213894096 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Non-Ducted Indoor Units | 252000 | 10.3 | 20.2 | 284000 | 3.74 | 200000 | 2.49 | R-410A | 21
213894102 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Non-Ducted Indoor Units | 390000 | 9.8 | 17.9 | 438000 | 3.34 | 310000 | 2.19 | R-410A | 32.5
213894103 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Non-Ducted Indoor Units | 412000 | 10 | 18.5 | 462000 | 3.33 | 328000 | 2.17 | R-410A | 34.3333
213894104 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP1201HT6P-UL |  | MMY-UP4561HT6P-UL | Non-Ducted Indoor Units | 434000 | 9.8 | 17.6 | 488000 | 3.28 | 350000 | 2.21 | R-410A | 36.1667
213894098 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Non-Ducted Indoor Units | 298000 | 9.6 | 20 | 334000 | 3.54 | 236000 | 2.44 | R-410A | 24.8333
213894099 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 20.8 | 360000 | 3.53 | 268000 | 2.21 | R-410A | 26.6667
213894100 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Non-Ducted Indoor Units | 342000 | 9.65 | 18.4 | 386000 | 3.44 | 284000 | 2.13 | R-410A | 28.5
213894149 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Ducted Indoor Units | 298000 | 10.1 | 20.4 | 334000 | 3.6 | 236000 | 2.44 | R-410A | 24.8333
213894139 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Ducted Indoor Units | 252000 | 10.3 | 21 | 284000 | 3.82 | 200000 | 2.55 | R-410A | 21
213894146 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Ducted Indoor Units | 276000 | 11.2 | 18.8 | 308000 | 4.08 | 260000 | 2.48 | R-410A | 23
213894142 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Non-Ducted Indoor Units | 276000 | 11 | 19.3 | 308000 | 3.82 | 260000 | 2.31 | R-410A | 23
213895030 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 19.05 | 308000 | 3.95 | 260000 | 2.39 | R-410A | 23
213895038 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 19.4 | 386000 | 3.75 | 348000 | 2.47 | R-410A | 28.5
213894159 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Ducted Indoor Units | 342000 | 10.8 | 19.5 | 386000 | 3.8 | 348000 | 2.48 | R-410A | 28.5
213894155 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Non-Ducted Indoor Units | 342000 | 10.1 | 19.3 | 386000 | 3.7 | 348000 | 2.46 | R-410A | 28.5
213895041 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.3 | 18.65 | 412000 | 3.46 | 294000 | 2.28 | R-410A | 30.5
213895029 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.37 | 21 | 308000 | 3.71 | 216000 | 2.41 | R-410A | 23
213894145 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Ducted Indoor Units | 276000 | 10.8 | 21.4 | 308000 | 3.81 | 216000 | 2.56 | R-410A | 23
213894141 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Non-Ducted Indoor Units | 276000 | 9.95 | 20.6 | 308000 | 3.61 | 216000 | 2.27 | R-410A | 23
213894163 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Ducted Indoor Units | 366000 | 11 | 18.9 | 412000 | 3.48 | 294000 | 2.29 | R-410A | 30.5
213894161 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Non-Ducted Indoor Units | 366000 | 9.6 | 18.4 | 412000 | 3.45 | 294000 | 2.28 | R-410A | 30.5
213894148 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Non-Ducted Indoor Units | 298000 | 9.6 | 20 | 334000 | 3.54 | 236000 | 2.44 | R-410A | 24.8333
213894164 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Non-Ducted Indoor Units | 390000 | 9.8 | 17.9 | 438000 | 3.34 | 310000 | 2.19 | R-410A | 32.5
213894169 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Ducted Indoor Units | 412000 | 9.9 | 17.6 | 462000 | 3.35 | 328000 | 2.41 | R-410A | 34.3333
213894170 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP1201HT9P-UL |  | MMY-UP4561HT9P-UL | Non-Ducted Indoor Units | 434000 | 9.8 | 17.6 | 488000 | 3.28 | 350000 | 2.21 | R-410A | 36.1667
213894166 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Ducted Indoor Units | 390000 | 10.4 | 18.4 | 438000 | 3.38 | 310000 | 2.39 | R-410A | 32.5
213894167 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Non-Ducted Indoor Units | 412000 | 10 | 18.5 | 462000 | 3.33 | 328000 | 2.17 | R-410A | 34.3333
213894153 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Ducted Indoor Units | 320000 | 10 | 18.4 | 360000 | 3.46 | 268000 | 2.39 | R-410A | 26.6667
213894154 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Non-Ducted Indoor Units | 342000 | 9.65 | 18.4 | 386000 | 3.44 | 284000 | 2.13 | R-410A | 28.5
213894158 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Ducted Indoor Units | 342000 | 11.2 | 19.4 | 386000 | 3.5 | 284000 | 2.45 | R-410A | 28.5
213894172 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP1201HT9P-UL |  | MMY-UP4561HT9P-UL | Ducted Indoor Units | 434000 | 9.5 | 17.3 | 488000 | 3.33 | 350000 | 2.36 | R-410A | 36.1667
213894138 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Non-Ducted Indoor Units | 252000 | 10.3 | 20.2 | 284000 | 3.74 | 200000 | 2.49 | R-410A | 21
213894140 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Ducted Indoor Units | 252000 | 10.3 | 21 | 284000 | 3.82 | 200000 | 2.55 | R-410A | 21
213894150 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Ducted Indoor Units | 298000 | 10.1 | 20.4 | 334000 | 3.6 | 236000 | 2.44 | R-410A | 24.8333
213894151 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 20.8 | 360000 | 3.53 | 268000 | 2.21 | R-410A | 26.6667
213895047 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP1201HT9P-UL |  | MMY-UP4561HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.65 | 17.45 | 488000 | 3.3 | 350000 | 2.28 | R-410A | 36.1667
213895045 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.95 | 18.05 | 462000 | 3.34 | 328000 | 2.29 | R-410A | 34.3333
213895035 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 19.6 | 360000 | 3.49 | 268000 | 2.3 | R-410A | 26.6667
213895033 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 20.2 | 334000 | 3.57 | 236000 | 2.44 | R-410A | 24.8333
213895043 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.1 | 18.15 | 438000 | 3.36 | 310000 | 2.29 | R-410A | 32.5
213895037 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.42 | 18.9 | 386000 | 3.47 | 284000 | 2.29 | R-410A | 28.5
213895027 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.3 | 20.6 | 284000 | 3.78 | 200000 | 2.52 | R-410A | 21
213894147 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Ducted Indoor Units | 276000 | 11.2 | 18.8 | 308000 | 4.08 | 260000 | 2.48 | R-410A | 23
213894143 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Non-Ducted Indoor Units | 276000 | 11 | 19.3 | 308000 | 3.82 | 260000 | 2.31 | R-410A | 23
213895031 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 19.05 | 308000 | 3.95 | 260000 | 2.39 | R-410A | 23
213895039 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 19.4 | 386000 | 3.75 | 348000 | 2.47 | R-410A | 28.5
213894160 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Ducted Indoor Units | 342000 | 10.8 | 19.5 | 386000 | 3.8 | 348000 | 2.48 | R-410A | 28.5
213894156 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Non-Ducted Indoor Units | 342000 | 10.1 | 19.3 | 386000 | 3.7 | 348000 | 2.46 | R-410A | 28.5
213884954 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.6 | 22.8 | 308000 | 3.88 | 200000 | 2.45 | R-410A | 23
213884958 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Ducted Indoor Units | 276000 | 10.6 | 21.7 | 308000 | 3.27 | 200000 | 2.43 | R-410A | 23
213885204 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 22.25 | 308000 | 3.57 | 200000 | 2.44 | R-410A | 23
213884978 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3841FT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 20.4 | 412000 | 3.53 | 274000 | 2.6 | R-410A | 30.5
213885217 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3841FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.4 | 19.5 | 412000 | 3.38 | 274000 | 2.57 | R-410A | 30.5
213885219 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4081FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.15 | 19.2 | 438000 | 3.37 | 296000 | 2.57 | R-410A | 32.5
213885203 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.2 | 22.35 | 284000 | 3.6 | 196000 | 2.44 | R-410A | 21
213885208 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.95 | 21.6 | 334000 | 3.55 | 222000 | 2.43 | R-410A | 24.8333
213885210 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL |  |  | MMY-UP3361FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 20.85 | 360000 | 3.4 | 244000 | 2.43 | R-410A | 26.6667
213885212 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3601FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 20.05 | 386000 | 3.39 | 270000 | 2.5 | R-410A | 28.5
213885221 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4321FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.85 | 19.1 | 462000 | 3.35 | 318000 | 2.51 | R-410A | 34.3333
213885223 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4561FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.85 | 18.95 | 488000 | 3.34 | 322000 | 2.49 | R-410A | 36.1667
213885225 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4801FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 456000 | 9.7 | 18.95 | 514000 | 3.29 | 344000 | 2.47 | R-410A | 38
213884982 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4081FT6P-UL | Non-Ducted Indoor Units | 390000 | 10.3 | 20.2 | 438000 | 3.51 | 296000 | 2.58 | R-410A | 32.5
213884986 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4321FT6P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.48 | 318000 | 2.52 | R-410A | 34.3333
213884990 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4561FT6P-UL | Non-Ducted Indoor Units | 434000 | 9.9 | 19.8 | 488000 | 3.45 | 322000 | 2.5 | R-410A | 36.1667
213884962 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Non-Ducted Indoor Units | 298000 | 11.3 | 22.2 | 334000 | 3.86 | 222000 | 2.44 | R-410A | 24.8333
213884964 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Ducted Indoor Units | 298000 | 10.6 | 21 | 334000 | 3.25 | 222000 | 2.42 | R-410A | 24.8333
213884966 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL |  |  | MMY-UP3361FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 21.4 | 360000 | 3.57 | 244000 | 2.44 | R-410A | 26.6667
213884970 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3601FT6P-UL | Non-Ducted Indoor Units | 342000 | 10.6 | 20.5 | 386000 | 3.54 | 270000 | 2.51 | R-410A | 28.5
213884998 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL |  | MMY-UP5041FT6P-UL | Non-Ducted Indoor Units | 480000 | 9.4 | 19.6 | 540000 | 3.27 | 366000 | 2.48 | R-410A | 40
213884994 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4801FT6P-UL | Non-Ducted Indoor Units | 456000 | 9.7 | 19.8 | 514000 | 3.37 | 344000 | 2.49 | R-410A | 38
213884952 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Ducted Indoor Units | 252000 | 10.7 | 21.8 | 284000 | 3.28 | 196000 | 2.43 | R-410A | 21
213884950 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 284000 | 3.92 | 196000 | 2.46 | R-410A | 21
213884956 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Non-Ducted Indoor Units | 276000 | 12.6 | 21 | 308000 | 3.9 | 258000 | 2.48 | R-410A | 23
213884960 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.59 | 258000 | 2.42 | R-410A | 23
213885206 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.1 | 20.4 | 308000 | 3.74 | 258000 | 2.45 | R-410A | 23
213885214 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.65 | 20.25 | 386000 | 3.62 | 330000 | 2.42 | R-410A | 28.5
213884972 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Non-Ducted Indoor Units | 342000 | 11.9 | 20.9 | 386000 | 3.69 | 330000 | 2.45 | R-410A | 28.5
213884976 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Ducted Indoor Units | 342000 | 11.4 | 19.6 | 386000 | 3.55 | 330000 | 2.4 | R-410A | 28.5
213885205 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 22.25 | 308000 | 3.57 | 200000 | 2.44 | R-410A | 23
213884979 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3841FT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 20.4 | 412000 | 3.53 | 274000 | 2.6 | R-410A | 30.5
213884959 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Ducted Indoor Units | 276000 | 10.6 | 21.7 | 308000 | 3.27 | 200000 | 2.43 | R-410A | 23
213884955 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.6 | 22.8 | 308000 | 3.88 | 200000 | 2.45 | R-410A | 23
213885216 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3841FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.4 | 19.5 | 412000 | 3.38 | 274000 | 2.57 | R-410A | 30.5
213885220 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4321FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.85 | 19.1 | 462000 | 3.35 | 318000 | 2.51 | R-410A | 34.3333
213885218 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4081FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.15 | 19.2 | 438000 | 3.37 | 296000 | 2.57 | R-410A | 32.5
213885209 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.95 | 21.6 | 334000 | 3.55 | 222000 | 2.43 | R-410A | 24.8333
213885213 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3601FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 20.05 | 386000 | 3.39 | 270000 | 2.5 | R-410A | 28.5
213885211 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL |  |  | MMY-UP3361FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 20.85 | 360000 | 3.4 | 244000 | 2.43 | R-410A | 26.6667
213885226 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL |  | MMY-UP5041FT9P-UL | Non-Ducted Indoor Units | 480000 | 9.4 | 19.6 | 540000 | 3.27 | 366000 | 2.48 | R-410A | 40
213885224 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4801FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 456000 | 9.7 | 18.95 | 514000 | 3.29 | 344000 | 2.47 | R-410A | 38
213885222 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4561FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.85 | 18.95 | 488000 | 3.34 | 322000 | 2.49 | R-410A | 36.1667
213884953 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Ducted Indoor Units | 252000 | 10.7 | 21.8 | 284000 | 3.28 | 196000 | 2.43 | R-410A | 21
213884951 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 284000 | 3.92 | 196000 | 2.46 | R-410A | 21
213884983 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4081FT9P-UL | Non-Ducted Indoor Units | 390000 | 10.3 | 20.2 | 438000 | 3.51 | 296000 | 2.58 | R-410A | 32.5
213884991 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4561FT9P-UL | Non-Ducted Indoor Units | 434000 | 9.9 | 19.8 | 488000 | 3.45 | 322000 | 2.5 | R-410A | 36.1667
213884987 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4321FT9P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.48 | 318000 | 2.52 | R-410A | 34.3333
213884971 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3601FT9P-UL | Non-Ducted Indoor Units | 342000 | 10.6 | 20.5 | 386000 | 3.54 | 270000 | 2.51 | R-410A | 28.5
213884963 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Non-Ducted Indoor Units | 298000 | 11.3 | 22.2 | 334000 | 3.86 | 222000 | 2.44 | R-410A | 24.8333
213884967 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL |  |  | MMY-UP3361FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 21.4 | 360000 | 3.57 | 244000 | 2.44 | R-410A | 26.6667
213884965 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Ducted Indoor Units | 298000 | 10.6 | 21 | 334000 | 3.25 | 222000 | 2.42 | R-410A | 24.8333
213885202 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.2 | 22.35 | 284000 | 3.6 | 196000 | 2.44 | R-410A | 21
213884995 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4801FT9P-UL | Non-Ducted Indoor Units | 456000 | 9.7 | 19.8 | 514000 | 3.37 | 344000 | 2.49 | R-410A | 38
213884957 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Non-Ducted Indoor Units | 276000 | 12.6 | 21 | 308000 | 3.9 | 258000 | 2.48 | R-410A | 23
213884961 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.59 | 258000 | 2.42 | R-410A | 23
213885207 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.1 | 20.4 | 308000 | 3.74 | 258000 | 2.45 | R-410A | 23
213885215 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.65 | 20.25 | 386000 | 3.62 | 330000 | 2.42 | R-410A | 28.5
213884973 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Non-Ducted Indoor Units | 342000 | 11.9 | 20.9 | 386000 | 3.69 | 330000 | 2.45 | R-410A | 28.5
213884977 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Ducted Indoor Units | 342000 | 11.4 | 19.6 | 386000 | 3.55 | 330000 | 2.4 | R-410A | 28.5
213893582 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893583 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893590 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893591 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893598 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893599 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213916547 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916548 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916549 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916562 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916563 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916564 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893586 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893587 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893602 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893603 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893606 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893607 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916550 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916565 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893610 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893611 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893613 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893617 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893621 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213894835 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894839 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213894847 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213916551 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916552 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916553 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213916566 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916567 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916568 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213894849 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213894841 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213894837 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213893619 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893615 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893623 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893625 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213894855 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213916554 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213916569 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213894857 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213893627 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893476 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893477 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893484 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893485 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893492 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893493 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213916501 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916502 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916503 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916520 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916521 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916522 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893488 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893489 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893496 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893497 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893480 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893481 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893500 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893501 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916504 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916523 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893504 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893505 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893515 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893508 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893509 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893519 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213894851 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213894843 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213916505 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916506 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916507 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213916524 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916525 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916526 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213894845 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213894853 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213893517 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893512 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893513 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893521 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893837 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894861 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213916508 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916527 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894860 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213893839 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893746 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893747 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893750 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893751 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893754 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893755 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213916741 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916745 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916749 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916751 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916747 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916743 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213893756 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893757 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893752 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893753 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893748 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893749 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893758 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893759 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916753 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916755 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893760 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893761 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893762 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893763 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893766 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893768 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213894944 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213894936 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213916757 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916761 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916765 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213916767 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213916763 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916759 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213894937 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213894945 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213893769 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893767 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893764 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893765 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893849 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894953 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213916769 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916771 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894954 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213893850 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893797 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893798 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893801 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893802 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893805 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893806 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213916822 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916826 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916830 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916828 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916824 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916832 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893807 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893808 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893803 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893804 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893799 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893800 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893809 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893810 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916834 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916836 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893811 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893812 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893813 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893817 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893815 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213894930 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894946 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213894938 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213916838 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916842 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916846 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213916844 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916840 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916848 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213894939 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213894947 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213894931 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213893816 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893818 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893814 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893819 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213894948 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213916850 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213916852 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213894882 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213893820 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213896090 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 | PURY-EP144YNU-A1 |  |  | PURY-EP288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213895970 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 | PURY-EP120YNU-A1 |  |  | PURY-EP264YSNU-A1 | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050126 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 | PURY-EP168YNU-A1 |  |  | PURY-EP336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896088 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 | PURY-EP144TNU-A1 |  |  | PURY-EP288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213895968 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 | PURY-EP120TNU-A1 |  |  | PURY-EP264TSNU-A1 | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050124 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 | PURY-EP168TNU-A1 |  |  | PURY-EP336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896178 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN | TURYE1444AN41AN |  |  | TURYE2884BN41AN | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213896034 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN | TURYE1204AN41AN |  |  | TURYE2644BN41AN | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050340 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN | TURYE1684AN41AN |  |  | TURYE3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896176 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN | TURYE1443AN41AN |  |  | TURYE2883BN41AN | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213896032 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN | TURYE1203AN41AN |  |  | TURYE2643BN41AN | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050338 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN | TURYE1683AN41AN |  |  | TURYE3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
217729768 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 282000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729769 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11 | 21.5 | 308000 | 3.6 | 198000 | 2.54 | R-32 | 23
217729316 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 282000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729334 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 282000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729335 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Non-Ducted Indoor Units | 276000 | 11.1 | 21.8 | 308000 | 3.66 | 198000 | 2.62 | R-32 | 23
217729336 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Ducted Indoor Units | 276000 | 10.9 | 21.2 | 308000 | 3.54 | 198000 | 2.46 | R-32 | 23
217729337 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Non-Ducted Indoor Units | 298000 | 10.8 | 21.2 | 332000 | 3.63 | 222000 | 2.55 | R-32 | 24.8333
217729338 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Ducted Indoor Units | 298000 | 10.6 | 20.8 | 332000 | 3.47 | 222000 | 2.41 | R-32 | 24.8333
217729770 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21 | 332000 | 3.55 | 222000 | 2.48 | R-32 | 24.8333
217729351 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Non-Ducted Indoor Units | 480000 | 9.3 | 18.4 | 506000 | 3.37 | 348000 | 2.33 | R-32 | 40
217729352 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Ducted Indoor Units | 480000 | 9.3 | 17.8 | 506000 | 3.37 | 348000 | 2.15 | R-32 | 40
217729771 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.5 | 358000 | 3.5 | 234000 | 2.42 | R-32 | 26.6667
217729778 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 480000 | 9.3 | 18.1 | 506000 | 3.37 | 348000 | 2.24 | R-32 | 40
217729317 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Ducted Indoor Units | 320000 | 10.3 | 20.4 | 358000 | 3.4 | 234000 | 2.36 | R-32 | 26.6667
217729339 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Non-Ducted Indoor Units | 320000 | 10.2 | 20.6 | 358000 | 3.61 | 234000 | 2.48 | R-32 | 26.6667
217729340 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Non-Ducted Indoor Units | 344000 | 10.5 | 21.2 | 364000 | 3.58 | 248000 | 2.37 | R-32 | 28.6667
217729341 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Non-Ducted Indoor Units | 366000 | 10.2 | 20.6 | 388000 | 3.5 | 266000 | 2.35 | R-32 | 30.5
217729342 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Ducted Indoor Units | 366000 | 10.1 | 19.5 | 388000 | 3.38 | 266000 | 2.34 | R-32 | 30.5
217729343 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Non-Ducted Indoor Units | 390000 | 9.9 | 20 | 412000 | 3.44 | 284000 | 2.32 | R-32 | 32.5
217729344 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Ducted Indoor Units | 390000 | 9.8 | 18.9 | 412000 | 3.38 | 284000 | 2.21 | R-32 | 32.5
217729345 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Non-Ducted Indoor Units | 410000 | 9.3 | 19.3 | 436000 | 3.44 | 298000 | 2.44 | R-32 | 34.1667
217729346 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Ducted Indoor Units | 410000 | 9.6 | 19.6 | 436000 | 3.38 | 298000 | 2.28 | R-32 | 34.1667
217729318 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Ducted Indoor Units | 344000 | 10.4 | 20.1 | 364000 | 3.39 | 248000 | 2.36 | R-32 | 28.6667
217729772 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 20.65 | 364000 | 3.48 | 248000 | 2.36 | R-32 | 28.6667
217729773 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.15 | 20.05 | 388000 | 3.44 | 266000 | 2.34 | R-32 | 30.5
217729774 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.85 | 19.45 | 412000 | 3.41 | 284000 | 2.26 | R-32 | 32.5
217729775 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 19.45 | 436000 | 3.41 | 298000 | 2.36 | R-32 | 34.1667
217729776 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.45 | 18.8 | 458000 | 3.38 | 318000 | 2.34 | R-32 | 36.1667
217729777 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 454000 | 9.3 | 18.75 | 484000 | 3.37 | 332000 | 2.26 | R-32 | 37.8333
217729347 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Non-Ducted Indoor Units | 434000 | 9.3 | 19 | 458000 | 3.39 | 318000 | 2.42 | R-32 | 36.1667
217729348 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Ducted Indoor Units | 434000 | 9.6 | 18.6 | 458000 | 3.38 | 318000 | 2.26 | R-32 | 36.1667
217729349 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Non-Ducted Indoor Units | 454000 | 9.3 | 18.8 | 484000 | 3.37 | 332000 | 2.38 | R-32 | 37.8333
217729350 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Ducted Indoor Units | 454000 | 9.3 | 18.7 | 484000 | 3.37 | 332000 | 2.15 | R-32 | 37.8333
217729314 | N/A | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 256000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729315 | N/A | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 256000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729767 | N/A | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 256000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729789 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 282000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729790 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11 | 21.5 | 308000 | 3.6 | 198000 | 2.54 | R-32 | 23
217729331 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 282000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729353 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 282000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729354 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Non-Ducted Indoor Units | 276000 | 11.1 | 21.8 | 308000 | 3.66 | 198000 | 2.62 | R-32 | 23
217729355 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Ducted Indoor Units | 276000 | 10.9 | 21.2 | 308000 | 3.54 | 198000 | 2.46 | R-32 | 23
217729356 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Non-Ducted Indoor Units | 298000 | 10.8 | 21.2 | 332000 | 3.63 | 222000 | 2.55 | R-32 | 24.8333
217729357 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Ducted Indoor Units | 298000 | 10.6 | 20.8 | 332000 | 3.47 | 222000 | 2.41 | R-32 | 24.8333
217729791 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21 | 332000 | 3.55 | 222000 | 2.48 | R-32 | 24.8333
217729792 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.5 | 358000 | 3.5 | 234000 | 2.42 | R-32 | 26.6667
217729799 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 480000 | 9.3 | 18.1 | 506000 | 3.37 | 348000 | 2.24 | R-32 | 40
217729358 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Non-Ducted Indoor Units | 320000 | 10.2 | 20.6 | 358000 | 3.61 | 234000 | 2.48 | R-32 | 26.6667
217729332 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Ducted Indoor Units | 320000 | 10.3 | 20.4 | 358000 | 3.4 | 234000 | 2.36 | R-32 | 26.6667
217729370 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Non-Ducted Indoor Units | 480000 | 9.3 | 18.4 | 506000 | 3.37 | 348000 | 2.33 | R-32 | 40
217729371 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Ducted Indoor Units | 480000 | 9.3 | 17.8 | 506000 | 3.37 | 348000 | 2.15 | R-32 | 40
217729333 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Ducted Indoor Units | 344000 | 10.4 | 20.1 | 364000 | 3.39 | 248000 | 2.36 | R-32 | 28.6667
217729359 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Non-Ducted Indoor Units | 344000 | 10.5 | 21.2 | 364000 | 3.58 | 248000 | 2.37 | R-32 | 28.6667
217729360 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Non-Ducted Indoor Units | 366000 | 10.2 | 20.6 | 388000 | 3.5 | 266000 | 2.35 | R-32 | 30.5
217729361 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Ducted Indoor Units | 366000 | 10.1 | 19.5 | 388000 | 3.38 | 266000 | 2.34 | R-32 | 30.5
217729362 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Non-Ducted Indoor Units | 390000 | 9.9 | 20 | 412000 | 3.44 | 284000 | 2.32 | R-32 | 32.5
217729363 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Ducted Indoor Units | 390000 | 9.8 | 18.9 | 412000 | 3.38 | 284000 | 2.21 | R-32 | 32.5
217729364 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Non-Ducted Indoor Units | 410000 | 9.3 | 19.3 | 436000 | 3.44 | 298000 | 2.44 | R-32 | 34.1667
217729365 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Ducted Indoor Units | 410000 | 9.6 | 19.6 | 436000 | 3.38 | 298000 | 2.28 | R-32 | 34.1667
217729793 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 20.65 | 364000 | 3.48 | 248000 | 2.36 | R-32 | 28.6667
217729794 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.15 | 20.05 | 388000 | 3.44 | 266000 | 2.34 | R-32 | 30.5
217729795 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.85 | 19.45 | 412000 | 3.41 | 284000 | 2.26 | R-32 | 32.5
217729796 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 19.45 | 436000 | 3.41 | 298000 | 2.36 | R-32 | 34.1667
217729797 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.45 | 18.8 | 458000 | 3.38 | 318000 | 2.34 | R-32 | 36.1667
217729798 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 454000 | 9.3 | 18.75 | 484000 | 3.37 | 332000 | 2.26 | R-32 | 37.8333
217729366 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Non-Ducted Indoor Units | 434000 | 9.3 | 19 | 458000 | 3.39 | 318000 | 2.42 | R-32 | 36.1667
217729367 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Ducted Indoor Units | 434000 | 9.6 | 18.6 | 458000 | 3.38 | 318000 | 2.26 | R-32 | 36.1667
217729368 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Non-Ducted Indoor Units | 454000 | 9.3 | 18.8 | 484000 | 3.37 | 332000 | 2.38 | R-32 | 37.8333
217729369 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Ducted Indoor Units | 454000 | 9.3 | 18.7 | 484000 | 3.37 | 332000 | 2.15 | R-32 | 37.8333
217729788 | N/A | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 256000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729329 | N/A | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 256000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729330 | N/A | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 256000 | 3.3 | 182000 | 2.2 | R-32 | 21
217734398 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.55 | 21.9 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217734341 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Ducted Indoor Units | 276000 | 10.5 | 21 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217734274 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 22.8 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217734273 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2641FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.6 | 22.8 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217734275 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.5 | 22.2 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217734276 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL |  |  | MMY-UB3361FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.5 | 21.4 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217734277 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Non-Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217734278 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Non-Ducted Indoor Units | 366000 | 10.1 | 20.4 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217734279 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Non-Ducted Indoor Units | 390000 | 10 | 20.2 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217734280 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217734281 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4561FT6P-UL | Non-Ducted Indoor Units | 436000 | 9.9 | 19.8 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217734282 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4801FT6P-UL | Non-Ducted Indoor Units | 458000 | 9.4 | 19.8 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217734343 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Ducted Indoor Units | 298000 | 10.4 | 20.1 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217734347 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Ducted Indoor Units | 344000 | 9.6 | 18.2 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217734349 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Ducted Indoor Units | 366000 | 9.6 | 17.7 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217734400 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 21.15 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217734396 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2641FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.95 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217734402 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL |  |  | MMY-UB3361FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 20.55 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217734404 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 19.35 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217734406 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.85 | 19.05 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217734408 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217734410 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.7 | 18.45 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217734412 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4561FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.7 | 17.8 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217734414 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4801FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.4 | 17.8 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217734351 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Ducted Indoor Units | 390000 | 9.6 | 17.4 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217734353 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Ducted Indoor Units | 412000 | 9.5 | 16.9 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217734430 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 20.4 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217734319 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Non-Ducted Indoor Units | 276000 | 11 | 21 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217734373 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217734375 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Ducted Indoor Units | 344000 | 10.8 | 19 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217734321 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Non-Ducted Indoor Units | 344000 | 11 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217734432 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.9 | 19.95 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217734399 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.55 | 21.9 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217734342 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Ducted Indoor Units | 276000 | 10.5 | 21 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217734297 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 22.8 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217734296 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2641FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.6 | 22.8 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217734298 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.5 | 22.2 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217734299 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL |  |  | MMY-UB3361FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.5 | 21.4 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217734300 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Non-Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217734301 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Non-Ducted Indoor Units | 366000 | 10.1 | 20.4 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217734302 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Non-Ducted Indoor Units | 390000 | 10 | 20.2 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217734303 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217734304 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4561FT9P-UL | Non-Ducted Indoor Units | 436000 | 9.9 | 19.8 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217734305 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4801FT9P-UL | Non-Ducted Indoor Units | 458000 | 9.4 | 19.8 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217734350 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Ducted Indoor Units | 366000 | 9.6 | 17.7 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217734348 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Ducted Indoor Units | 344000 | 9.6 | 18.2 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217734344 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Ducted Indoor Units | 298000 | 10.4 | 20.1 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217734401 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 21.15 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217734397 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2641FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.95 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217734415 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4801FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.4 | 17.8 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217734413 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4561FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.7 | 17.8 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217734411 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.7 | 18.45 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217734409 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217734407 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.85 | 19.05 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217734405 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 19.35 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217734403 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL |  |  | MMY-UB3361FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 20.55 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217734354 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Ducted Indoor Units | 412000 | 9.5 | 16.9 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217734352 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Ducted Indoor Units | 390000 | 9.6 | 17.4 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217734431 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 20.4 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217734320 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Non-Ducted Indoor Units | 276000 | 11 | 21 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217734374 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217734376 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Ducted Indoor Units | 344000 | 10.8 | 19 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217734322 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Non-Ducted Indoor Units | 344000 | 11 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217734433 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.9 | 19.95 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217735034 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 20.6 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217735035 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Non-Ducted Indoor Units | 276000 | 9.7 | 22.3 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217735112 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 21.45 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217735110 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2641HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.75 | 21.5 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217735116 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.55 | 20.7 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217735118 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL |  |  | MMY-UB3361HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.5 | 20.25 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217735120 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 18.95 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217735124 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.1 | 18.85 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217735126 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 18.45 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217735128 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 18.05 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217735130 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4561HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.1 | 17.4 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217735132 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4801HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.1 | 17.4 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217735031 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2641HT6P-UL | Non-Ducted Indoor Units | 252000 | 9.7 | 22.3 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217735042 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Ducted Indoor Units | 298000 | 9.7 | 19.7 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217735043 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Non-Ducted Indoor Units | 298000 | 9.4 | 21.7 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217735047 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL |  |  | MMY-UB3361HT6P-UL | Non-Ducted Indoor Units | 320000 | 9.4 | 21.2 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217735050 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Ducted Indoor Units | 344000 | 9.1 | 17.8 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217735051 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Non-Ducted Indoor Units | 344000 | 9.1 | 20.1 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217735075 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4801HT6P-UL | Non-Ducted Indoor Units | 458000 | 9.1 | 19.3 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217735058 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Ducted Indoor Units | 366000 | 9.1 | 17.6 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217735059 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Non-Ducted Indoor Units | 366000 | 9.1 | 20.1 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217735062 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Ducted Indoor Units | 390000 | 9.1 | 17.2 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217735063 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Non-Ducted Indoor Units | 390000 | 9.1 | 19.7 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217735066 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Ducted Indoor Units | 412000 | 9.1 | 16.6 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217735067 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Non-Ducted Indoor Units | 412000 | 9.1 | 19.5 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217735071 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4561HT6P-UL | Non-Ducted Indoor Units | 436000 | 9.1 | 19.3 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217735114 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.6 | 20.25 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217735038 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Ducted Indoor Units | 276000 | 10.9 | 19.6 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217735039 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Non-Ducted Indoor Units | 276000 | 10.3 | 20.9 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217735054 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Ducted Indoor Units | 344000 | 10.3 | 18.8 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217735055 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Non-Ducted Indoor Units | 344000 | 10 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217735122 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 19.85 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217735036 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 20.6 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217735037 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Non-Ducted Indoor Units | 276000 | 9.7 | 22.3 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217735113 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 21.45 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217735111 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2641HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.75 | 21.5 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217735117 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.55 | 20.7 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217735121 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 18.95 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217735119 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL |  |  | MMY-UB3361HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.5 | 20.25 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217735125 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.1 | 18.85 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217735129 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 18.05 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217735127 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 18.45 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217735133 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4801HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.1 | 17.4 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217735131 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4561HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.1 | 17.4 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217735033 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2641HT9P-UL | Non-Ducted Indoor Units | 252000 | 9.7 | 22.3 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217735052 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Ducted Indoor Units | 344000 | 9.1 | 17.8 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217735053 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Non-Ducted Indoor Units | 344000 | 9.1 | 20.1 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217735049 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL |  |  | MMY-UB3361HT9P-UL | Non-Ducted Indoor Units | 320000 | 9.4 | 21.2 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217735044 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Ducted Indoor Units | 298000 | 9.7 | 19.7 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217735045 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Non-Ducted Indoor Units | 298000 | 9.4 | 21.7 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217735077 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4801HT9P-UL | Non-Ducted Indoor Units | 458000 | 9.1 | 19.3 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217735073 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4561HT9P-UL | Non-Ducted Indoor Units | 436000 | 9.1 | 19.3 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217735068 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Ducted Indoor Units | 412000 | 9.1 | 16.6 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217735069 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Non-Ducted Indoor Units | 412000 | 9.1 | 19.5 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217735064 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Ducted Indoor Units | 390000 | 9.1 | 17.2 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217735065 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Non-Ducted Indoor Units | 390000 | 9.1 | 19.7 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217735060 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Ducted Indoor Units | 366000 | 9.1 | 17.6 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217735061 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Non-Ducted Indoor Units | 366000 | 9.1 | 20.1 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217735115 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.6 | 20.25 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217735040 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Ducted Indoor Units | 276000 | 10.9 | 19.6 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217735041 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Non-Ducted Indoor Units | 276000 | 10.3 | 20.9 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217735056 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Ducted Indoor Units | 344000 | 10.3 | 18.8 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217735057 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Non-Ducted Indoor Units | 344000 | 10 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217735123 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 19.85 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217902163 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A | PURY-EM144TXU-A |  |  | PURY-EM264TSXU-A | Non-Ducted Indoor Units | 250000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 20.8333
217902165 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A | PURY-EM144TXU-A |  |  | PURY-EM264TSXU-A | Ducted Indoor Units | 250000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 20.8333
217902167 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM144TXU-A |  |  | PURY-EM288TSXU-A | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902168 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM144TXU-A |  |  | PURY-EM288TSXU-A | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902171 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM168TXU-A |  |  | PURY-EM312TSXU-A | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902172 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM168TXU-A |  |  | PURY-EM312TSXU-A | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902175 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM168TXU-A |  |  | PURY-EM336TSXU-A | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902176 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM168TXU-A |  |  | PURY-EM336TSXU-A | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902179 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM192TXU-A |  |  | PURY-EM360TSXU-A | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902180 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM192TXU-A |  |  | PURY-EM360TSXU-A | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902183 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A | PURY-EM192TXU-A |  |  | PURY-EM384TSXU-A | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902184 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A | PURY-EM192TXU-A |  |  | PURY-EM384TSXU-A | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902166 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A | PURY-EM144YXU-A |  |  | PURY-EM264YSXU-A | Ducted Indoor Units | 250000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 20.8333
217902164 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A | PURY-EM144YXU-A |  |  | PURY-EM264YSXU-A | Non-Ducted Indoor Units | 250000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 20.8333
217902169 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM144YXU-A |  |  | PURY-EM288YSXU-A | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902170 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM144YXU-A |  |  | PURY-EM288YSXU-A | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902173 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM168YXU-A |  |  | PURY-EM312YSXU-A | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902174 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM168YXU-A |  |  | PURY-EM312YSXU-A | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902177 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM168YXU-A |  |  | PURY-EM336YSXU-A | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902178 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM168YXU-A |  |  | PURY-EM336YSXU-A | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902181 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM192YXU-A |  |  | PURY-EM360YSXU-A | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902182 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM192YXU-A |  |  | PURY-EM360YSXU-A | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902185 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A | PURY-EM192YXU-A |  |  | PURY-EM384YSXU-A | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902186 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A | PURY-EM192YXU-A |  |  | PURY-EM384YSXU-A | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902307 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN | TURYE1443AMM0AN |  |  | TURYE2643BMM0AN | Ducted Indoor Units | 252000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 21
217902308 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN | TURYE1443AMM0AN |  |  | TURYE2643BMM0AN | Non-Ducted Indoor Units | 252000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 21
217902311 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1443AMM0AN |  |  | TURYE2883BMM0AN | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902312 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1443AMM0AN |  |  | TURYE2883BMM0AN | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902315 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1683AMM0AN |  |  | TURYE3123BMM0AN | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902316 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1683AMM0AN |  |  | TURYE3123BMM0AN | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902319 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1683AMM0AN |  |  | TURYE3363BMM0AN | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902320 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1683AMM0AN |  |  | TURYE3363BMM0AN | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902323 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1923AMM0AN |  |  | TURYE3603BMM0AN | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902324 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1923AMM0AN |  |  | TURYE3603BMM0AN | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902327 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN | TURYE1923AMM0AN |  |  | TURYE3843BMM0AN | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902328 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN | TURYE1923AMM0AN |  |  | TURYE3843BMM0AN | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902309 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN | TURYE1444AMM0AN |  |  | TURYE2644BMM0AN | Ducted Indoor Units | 252000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 21
217902310 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN | TURYE1444AMM0AN |  |  | TURYE2644BMM0AN | Non-Ducted Indoor Units | 252000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 21
217902317 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1684AMM0AN |  |  | TURYE3124BMM0AN | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902318 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1684AMM0AN |  |  | TURYE3124BMM0AN | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902313 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1444AMM0AN |  |  | TURYE2884BMM0AN | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902314 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1444AMM0AN |  |  | TURYE2884BMM0AN | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902325 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1924AMM0AN |  |  | TURYE3604BMM0AN | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902326 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1924AMM0AN |  |  | TURYE3604BMM0AN | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902321 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1684AMM0AN |  |  | TURYE3364BMM0AN | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902322 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1684AMM0AN |  |  | TURYE3364BMM0AN | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902329 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN | TURYE1924AMM0AN |  |  | TURYE3844BMM0AN | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902330 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN | TURYE1924AMM0AN |  |  | TURYE3844BMM0AN | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902131 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM264TSXU-A | Ducted Indoor Units | 250000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 20.8333
217902132 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM264TSXU-A | Non-Ducted Indoor Units | 250000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 20.8333
217902135 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM288TSXU-A | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902136 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM288TSXU-A | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902139 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM312TSXU-A | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902140 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM312TSXU-A | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902143 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM336TSXU-A | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902144 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM336TSXU-A | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902147 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM360TSXU-A | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902148 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM360TSXU-A | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902151 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM384TSXU-A | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902152 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM384TSXU-A | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
217902133 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM264YSXU-A | Ducted Indoor Units | 250000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 20.8333
217902134 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM264YSXU-A | Non-Ducted Indoor Units | 250000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 20.8333
217902137 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM288YSXU-A | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902138 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM288YSXU-A | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902141 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM312YSXU-A | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902142 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM312YSXU-A | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902145 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM336YSXU-A | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902146 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM336YSXU-A | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902149 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM360YSXU-A | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902150 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM360YSXU-A | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902153 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM384YSXU-A | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902154 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM384YSXU-A | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
217902235 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2643BMM0AN | Ducted Indoor Units | 252000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 21
217902236 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2643BMM0AN | Non-Ducted Indoor Units | 252000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 21
217902239 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2883BMM0AN | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902240 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2883BMM0AN | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902243 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3123BMM0AN | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902244 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3123BMM0AN | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902247 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3363BMM0AN | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902248 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3363BMM0AN | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902251 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3603BMM0AN | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902252 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3603BMM0AN | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902255 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3843BMM0AN | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902256 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3843BMM0AN | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
217902237 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2644BMM0AN | Ducted Indoor Units | 252000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 21
217902238 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2644BMM0AN | Non-Ducted Indoor Units | 252000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 21
217902245 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3124BMM0AN | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902246 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3124BMM0AN | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902241 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2884BMM0AN | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902242 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2884BMM0AN | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902253 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3604BMM0AN | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902254 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3604BMM0AN | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902249 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3364BMM0AN | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902250 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3364BMM0AN | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902257 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3844BMM0AN | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902258 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3844BMM0AN | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
218004919 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218004923 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004927 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218003140 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003144 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003148 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003152 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003076 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003080 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003084 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003088 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218004931 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004935 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM240HCVGFG |  |  | AM360HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218003092 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM240HCVGFG |  |  | AM360HCVGFG | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218003104 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM120HCVGFG | AM192HCVGFG |  | AM432HCVGFG | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218003172 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM144HCVGFG | AM192HCVGFG |  | AM456HCVGFG | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218003160 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003164 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003096 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218003100 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218004939 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004943 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218004928 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004924 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004920 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003141 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003153 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003149 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003145 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003077 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003089 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003085 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003081 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218004932 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004936 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM240HCVGFS |  |  | AM360HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218003093 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM240HCVGFS |  |  | AM360HCVGFS | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218003105 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM120HCVGFS | AM192HCVGFS |  | AM432HCVGFS | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218003173 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM144HCVGFS | AM192HCVGFS |  | AM456HCVGFS | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218003165 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003161 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003101 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003097 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218004944 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218004940 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004921 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218004925 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004929 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218003142 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003154 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003146 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003150 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003078 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003090 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003082 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003086 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218004933 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004937 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM240HCVGJG |  |  | AM360HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218003094 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM240HCVGJG |  |  | AM360HCVGJG | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218003106 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM120HCVGJG | AM192HCVGJG |  | AM432HCVGJG | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218003174 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM144HCVGJG | AM192HCVGJG |  | AM456HCVGJG | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218003162 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003166 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003098 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218003102 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218004941 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004945 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218004930 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004926 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004922 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003143 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003155 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003151 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003147 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003079 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003091 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003087 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003083 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218004934 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004938 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM240HCVGJS |  |  | AM360HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218003095 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM240HCVGJS |  |  | AM360HCVGJS | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218003107 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM120HCVGJS | AM192HCVGJS |  | AM432HCVGJS | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218003175 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM144HCVGJS | AM192HCVGJS |  | AM456HCVGJS | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218003167 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003163 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003103 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003099 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218004946 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218004942 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218005691 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005695 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005731 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005735 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005763 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005767 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005768 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005764 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005736 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005732 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005696 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005692 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005693 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005697 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005733 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005737 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005765 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005769 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005770 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005766 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005738 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005734 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005698 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005694 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
213895940 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* | REYQ144AATJ* |  |  | REYQ264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.65 | 19.6 | 252000 | 3.45 | 168000 | 2.2 | R-410A | 21
213895899 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* | REYQ144AATJ* |  |  | REYQ264AATJ* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.2 | 252000 | 3.7 | 168000 | 2.2 | R-410A | 21
213895900 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ144AATJ* |  |  | REYQ288AATJ* | Non-Ducted Indoor Units | 274000 | 11.4 | 20.7 | 274000 | 3.4 | 194000 | 2.2 | R-410A | 22.8333
213895901 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ168AATJ* |  |  | REYQ312AATJ* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.4 | 296000 | 3.4 | 212000 | 2.2 | R-410A | 24.6667
213895941 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ144AATJ* |  |  | REYQ288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.25 | 274000 | 3.3 | 194000 | 2.15 | R-410A | 22.8333
213895942 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ168AATJ* |  |  | REYQ312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19 | 296000 | 3.3 | 212000 | 2.15 | R-410A | 24.6667
213895943 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* | REYQ168AATJ* |  |  | REYQ336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.5 | 310000 | 3.3 | 222000 | 2.1 | R-410A | 26.3333
213895902 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* | REYQ168AATJ* |  |  | REYQ336AATJ* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.7 | 310000 | 3.4 | 222000 | 2.1 | R-410A | 26.3333
213895910 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* | REYQ144AAYD* |  |  | REYQ264AAYD* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.2 | 252000 | 3.7 | 168000 | 2.2 | R-410A | 21
213895950 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* | REYQ144AAYD* |  |  | REYQ264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.65 | 19.6 | 252000 | 3.45 | 168000 | 2.2 | R-410A | 21
213895951 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ144AAYD* |  |  | REYQ288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.25 | 274000 | 3.3 | 194000 | 2.15 | R-410A | 22.8333
213895952 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ168AAYD* |  |  | REYQ312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19 | 296000 | 3.3 | 212000 | 2.15 | R-410A | 24.6667
213895911 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ144AAYD* |  |  | REYQ288AAYD* | Non-Ducted Indoor Units | 274000 | 11.4 | 20.7 | 274000 | 3.4 | 194000 | 2.2 | R-410A | 22.8333
213895912 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ168AAYD* |  |  | REYQ312AAYD* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.4 | 296000 | 3.4 | 212000 | 2.2 | R-410A | 24.6667
213895913 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* | REYQ168AAYD* |  |  | REYQ336AAYD* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.7 | 310000 | 3.4 | 222000 | 2.1 | R-410A | 26.3333
213895953 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* | REYQ168AAYD* |  |  | REYQ336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.5 | 310000 | 3.3 | 222000 | 2.1 | R-410A | 26.3333
216602517 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602497 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602503 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602510 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602567 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602573 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602579 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602585 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602398 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602407 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602380 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602389 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893999 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894003 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213894007 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894011 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213893957 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893961 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893965 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893969 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893897 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893901 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893905 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893909 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893913 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM240BXVGFH |  |  | AM360BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213893973 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM240BXVGFH |  |  | AM360BXVGFH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213916410 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM120BXVGFH | AM192BXVGFH |  | AM432BXVGFH1 | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
213916432 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM120BXVGFH | AM192BXVGFH |  | AM432BXVGFH1 | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
213916436 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM144BXVGFH | AM192BXVGFH |  | AM456BXVGFH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
213918752 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM120BXVGFH | AM192BXVGFH |  | AM432BXVGFH1 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602417 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC240S4M-4Y |  |  | VPC360S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602612 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602647 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602654 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC144S4M-4Y | VPC192S4M-4Y |  | VPC456S4M-4Y | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602524 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC240S4M-4Y |  |  | VPC360S4M-4Y | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602688 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602605 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602598 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602531 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602537 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602435 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602426 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893921 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213893917 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893977 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893981 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213894019 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213894023 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602384 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602411 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602403 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602394 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602521 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602514 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602507 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602500 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602588 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602582 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602576 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602570 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213893911 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893907 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893903 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893899 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213894013 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213894009 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894005 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213894001 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213893959 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893967 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893963 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893971 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893975 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM240BXVGJH |  |  | AM360BXVGJH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213893915 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM240BXVGJH |  |  | AM360BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213918754 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM120BXVGJH | AM192BXVGJH |  | AM432BXVGJH1 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
213916434 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM120BXVGJH | AM192BXVGJH |  | AM432BXVGJH1 | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
213916411 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM120BXVGJH | AM192BXVGJH |  | AM432BXVGJH1 | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
213916438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM144BXVGJH | AM192BXVGJH |  | AM456BXVGJH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602613 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602657 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC144S4M-4G | VPC192S4M-4G |  | VPC456S4M-4G | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602651 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602528 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC240S4M-4G |  |  | VPC360S4M-4G | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602694 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602421 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC240S4M-4G |  |  | VPC360S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602608 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602602 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602540 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602534 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602430 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602438 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213893923 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213893919 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893983 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213893979 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213894021 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213894025 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602382 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602391 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602400 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602409 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602519 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602499 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602505 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602512 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602568 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602574 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602580 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602587 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213893906 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893910 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893898 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893902 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213894000 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894004 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213894008 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894012 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213893958 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893962 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893966 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893970 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893974 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM240BXVGFR |  |  | AM360BXVGFR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213893985 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
213893914 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM240BXVGFR |  |  | AM360BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213916433 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
213916437 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM144BXVGFR | AM192BXVGFR |  | AM456BXVGFR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
213918753 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602691 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602649 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602656 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC144S4M-4Y | VRC192S4M-4Y |  | VRC456S4M-4Y | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602526 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4Y |  |  | VRC360S4M-4Y | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602544 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602419 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4Y |  |  | VRC360S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602436 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602428 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602607 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602600 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602539 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602532 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893922 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213893918 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893978 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893982 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213894024 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
213894020 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602386 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602414 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602405 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602396 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602523 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602515 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602508 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602502 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602590 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602584 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602578 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602571 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213893912 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893908 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893904 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893900 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213894014 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213894010 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894006 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213894002 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213893960 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893968 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893964 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893972 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893976 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM240BXVGJR |  |  | AM360BXVGJR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213893986 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM120BXVGJR | AM192BXVGJR |  | AM432BXVGJR1 | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
213893916 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM240BXVGJR |  |  | AM360BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213918755 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM120BXVGJR | AM192BXVGJR |  | AM432BXVGJR1 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.3 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
213916435 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM120BXVGJR | AM192BXVGJR |  | AM432BXVGJR1 | Non-Ducted Indoor Units | 412000 | 9.3 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
213916439 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM144BXVGJR | AM192BXVGJR |  | AM456BXVGJR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602659 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC144S4M-4G | VRC192S4M-4G |  | VRC456S4M-4G | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602652 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Non-Ducted Indoor Units | 412000 | 9.3 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602529 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC240S4M-4G |  |  | VRC360S4M-4G | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602546 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602696 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.3 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602423 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC240S4M-4G |  |  | VRC360S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602603 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602610 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602542 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602535 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602432 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602441 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213893924 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213893920 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893984 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213893980 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213894022 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213894026 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
208931715 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931718 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Non-Ducted Indoor Units | 276000 | 9.8 | 22.4 | 308000 | 3.39 | 210000 | 2.16 | R-410A | 23
208931728 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Non-Ducted Indoor Units | 390000 | 11 | 22.7 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931729 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Non-Ducted Indoor Units | 412000 | 10.8 | 22.9 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931870 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Ducted Indoor Units | 252000 | 11.2 | 17.3 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931872 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Ducted Indoor Units | 276000 | 10 | 17.2 | 308000 | 3.37 | 210000 | 2.16 | R-410A | 23
208931882 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Ducted Indoor Units | 390000 | 11 | 17.6 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931884 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Ducted Indoor Units | 412000 | 10.8 | 17.5 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931874 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Ducted Indoor Units | 298000 | 10 | 17.2 | 320000 | 3.37 | 214000 | 2.16 | R-410A | 24.8333
208931876 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Ducted Indoor Units | 320000 | 10 | 17.2 | 338000 | 3.37 | 224000 | 2.16 | R-410A | 26.6667
208931721 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Non-Ducted Indoor Units | 298000 | 9.8 | 22.4 | 320000 | 3.39 | 214000 | 2.16 | R-410A | 24.8333
208931723 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Non-Ducted Indoor Units | 320000 | 9.8 | 22.4 | 338000 | 3.39 | 224000 | 2.16 | R-410A | 26.6667
208931725 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Non-Ducted Indoor Units | 344000 | 9.8 | 22.4 | 346000 | 3.39 | 232000 | 2.16 | R-410A | 28.6667
208931726 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Non-Ducted Indoor Units | 366000 | 9.8 | 22.4 | 354000 | 3.39 | 240000 | 2.16 | R-410A | 30.5
208931878 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Ducted Indoor Units | 344000 | 10 | 17.2 | 346000 | 3.37 | 232000 | 2.16 | R-410A | 28.6667
208931880 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Ducted Indoor Units | 366000 | 10 | 17.2 | 354000 | 3.37 | 240000 | 2.16 | R-410A | 30.5
208931736 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931738 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Non-Ducted Indoor Units | 276000 | 9.8 | 22.4 | 308000 | 3.39 | 210000 | 2.16 | R-410A | 23
208931904 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Ducted Indoor Units | 390000 | 11 | 17.6 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931906 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Ducted Indoor Units | 412000 | 10.8 | 17.5 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931892 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Ducted Indoor Units | 252000 | 11.2 | 17.3 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931894 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Ducted Indoor Units | 276000 | 10 | 17.2 | 308000 | 3.37 | 210000 | 2.16 | R-410A | 23
208931749 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Non-Ducted Indoor Units | 390000 | 11 | 22.7 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931751 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Non-Ducted Indoor Units | 412000 | 10.8 | 22.9 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931896 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Ducted Indoor Units | 298000 | 10 | 17.2 | 320000 | 3.37 | 214000 | 2.16 | R-410A | 24.8333
208931898 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Ducted Indoor Units | 320000 | 10 | 17.2 | 338000 | 3.37 | 224000 | 2.16 | R-410A | 26.6667
208931741 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Non-Ducted Indoor Units | 298000 | 9.8 | 22.4 | 320000 | 3.39 | 214000 | 2.16 | R-410A | 24.8333
208931743 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Non-Ducted Indoor Units | 320000 | 9.8 | 22.4 | 338000 | 3.39 | 224000 | 2.16 | R-410A | 26.6667
208931745 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Non-Ducted Indoor Units | 344000 | 9.8 | 22.4 | 346000 | 3.39 | 232000 | 2.16 | R-410A | 28.6667
208931747 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Non-Ducted Indoor Units | 366000 | 9.8 | 22.4 | 354000 | 3.39 | 240000 | 2.16 | R-410A | 30.5
208931900 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Ducted Indoor Units | 344000 | 10 | 17.2 | 346000 | 3.37 | 232000 | 2.16 | R-410A | 28.6667
208931902 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Ducted Indoor Units | 366000 | 10 | 17.2 | 354000 | 3.37 | 240000 | 2.16 | R-410A | 30.5
214094489 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S | HVAHR144B42S |  | HVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094341 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094569 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S | YVAHR144B32S |  | YVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094421 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094585 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S | YVAHR144B42S |  | YVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094521 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S | TVAHR144B32S |  | TVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094373 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094537 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S | TVAHR144B42S |  | TVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094389 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094473 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S | HVAHR144B32S |  | HVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094325 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094437 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
9990285 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
9990286 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
214091739 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S | TVAHP144B32S |  | TVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091591 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091755 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S | TVAHP144B42S |  | TVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091607 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091691 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S | HVAHP144B32S |  | HVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091543 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091707 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S | HVAHP144B42S |  | HVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091559 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091787 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S | YVAHP144B32S |  | YVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091639 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091803 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S | YVAHP144B42S |  | YVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091655 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
213916869 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916337 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916344 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916345 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916338 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916870 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916871 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916873 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916875 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
213916365 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916339 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
213916880 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916383 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916372 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916373 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916384 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916881 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916882 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916884 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916886 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
213916385 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916374 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
6687555 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
6687557 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
7850834 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
7850836 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
7850854 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
7850856 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
213894856 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P432YSNU-A | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
214094553 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S | TVAHR144B52S |  | TVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094405 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094505 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S | HVAHR144B52S |  | HVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094357 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094601 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S | YVAHR144B52S |  | YVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094453 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091771 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S | TVAHP144B52S |  | TVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091623 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091723 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S | HVAHP144B52S |  | HVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091575 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091819 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S | YVAHP144B52S |  | YVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091671 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
213896685 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ144XBTJ* |  |  | REYQ264XBTJ* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896688 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* | REYQ120XBTJ* |  | REYQ360XBTJ* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896775 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ144XBTJ* |  |  | REYQ264XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896776 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* | REYQ120XBTJ* |  | REYQ360XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896751 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ144XBYD* |  |  | REYQ264XBYD* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896752 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* | REYQ120XBYD* |  | REYQ360XBYD* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896779 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ144XBYD* |  |  | REYQ264XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896780 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* | REYQ120XBYD* |  | REYQ360XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896755 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ144XBYC* |  |  | REYQ264XBYC* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896756 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* | REYQ120XBYC* |  | REYQ360XBYC* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896783 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ144XBYC* |  |  | REYQ264XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896784 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* | REYQ120XBYC* |  | REYQ360XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ144XBYC* |  |  | RXYQ264XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.45 | 17 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* | RXYQ120XBYC* |  | RXYQ360XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 338000 | 9.1 | 16.4 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.1667
213896813 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* | RXYQ120XBYC* |  | RXYQ360XBYC* | Non-Ducted Indoor Units | 338000 | 9.1 | 17.4 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.1667
213896748 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ144XBYC* |  |  | RXYQ264XBYC* | Non-Ducted Indoor Units | 252000 | 9.8 | 18.4 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
214608165 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* | MVHQ144ME2CA* |  |  | MVHQ264ME2CA* | Ducted Indoor Units | 252000 | 9.8 | 19.4 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214608166 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* | MVHQ144ME2CA* |  |  | MVHQ264ME2CA* | Non-Ducted Indoor Units | 252000 | 10.1 | 18.8 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214717494 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* | MVHQ192ME2CA* |  |  | MVHQ384ME2CA* | Ducted Indoor Units | 364000 | 9.4 | 18.5 | 384000 | 3.3 | 268000 | 2.3 | R-410A | 30.3333
214608167 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* | MVHQ144ME4CA* |  |  | MVHQ264ME4CA* | Ducted Indoor Units | 252000 | 9.8 | 19.4 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214608168 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* | MVHQ144ME4CA* |  |  | MVHQ264ME4CA* | Non-Ducted Indoor Units | 252000 | 10.1 | 18.8 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214717496 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* | MVHQ192ME4CA* |  |  | MVHQ384ME4CA* | Ducted Indoor Units | 364000 | 9.4 | 18.5 | 384000 | 3.3 | 268000 | 2.3 | R-410A | 30.3333
217190026 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190027 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
217189688 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189689 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217189658 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296040 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
214296041 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
214295978 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296010 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
214296011 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217190036 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190037 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
217189698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189699 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217189668 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296020 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
214296021 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
214295986 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
214296051 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
217189708 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189709 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217189678 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
217190046 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190047 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
215828419 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
215828420 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
215828409 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
215828410 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
215828399 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
216602813 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602815 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602817 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602736 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602737 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602739 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602864 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602869 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602871 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602721 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602827 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
214833153 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
214833154 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
214833155 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
214833161 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
214836585 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
214836586 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
214836587 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
214836588 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
214826371 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
214826380 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
214826381 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
214826382 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
214836589 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM240DXVGQH |  |  | AM360DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
214833165 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
214833166 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM144DXVGQH | AM192DXVGQH |  | AM456DXVGQH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
214836592 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
214833159 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
214833156 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM240DXVGQH |  |  | AM360DXVGQH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602837 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC144S4M-4J | VPC192S4M-4J |  | VPC456S4M-4J | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602824 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602873 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC240S4M-4J |  |  | VPC360S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602819 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC240S4M-4J |  |  | VPC360S4M-4J | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602820 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602822 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602876 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602878 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
214833157 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
214833158 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
214833163 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
214833164 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
214836590 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
214836591 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602771 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC168S4M-4J |  |  | VRC264S4M-4J | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602772 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC192S4M-4J |  |  | VRC288S4M-4J | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602774 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC216S4M-4J |  |  | VRC312S4M-4J | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602839 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC168S4M-4J |  |  | VRC264S4M-4J | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602841 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC192S4M-4J |  |  | VRC288S4M-4J | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602842 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC216S4M-4J |  |  | VRC312S4M-4J | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4J |  |  | VRC264S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4J |  |  | VRC288S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602889 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4J |  |  | VRC312S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602891 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4J |  |  | VRC336S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC240S4M-4J |  |  | VRC336S4M-4J | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216598841 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216598842 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216598843 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216598844 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216598845 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216598846 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216598847 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216598853 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216598859 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216598860 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216598861 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216598862 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602754 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC240S4M-4J |  |  | VRC336S4M-4J | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216598863 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM240DXVGQR |  |  | AM360DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216598851 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216598857 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216598858 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM144DXVGQR | AM192DXVGQR |  | AM456DXVGQR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216598848 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM240DXVGQR |  |  | AM360DXVGQR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216598866 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602849 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602893 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4J |  |  | VRC360S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC240S4M-4J |  |  | VRC360S4M-4J | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC144S4M-4J | VRC192S4M-4J |  | VRC456S4M-4J | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602846 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC192S4M-4J |  |  | VRC384S4M-4J | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602847 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC216S4M-4J |  |  | VRC408S4M-4J | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4J |  |  | VRC384S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602898 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4J |  |  | VRC408S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602856 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC192S4M-4J |  |  | VRC384S4M-4J | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602858 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC216S4M-4J |  |  | VRC408S4M-4J | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216598849 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216598850 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216598855 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216598856 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216598864 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216598865 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213916355 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916348 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916891 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916892 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916349 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916356 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916350 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
213916398 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916893 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916895 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916897 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
213896326 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Ducted Indoor Units | 252000 | 11.3 | 18.2 | 280000 | 3.47 | 200000 | 2.52 | R-410A | 21
213896330 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Ducted Indoor Units | 298000 | 11 | 17.3 | 334000 | 3.46 | 236000 | 2.43 | R-410A | 24.8333
213896328 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Ducted Indoor Units | 276000 | 11.1 | 18.1 | 308000 | 3.49 | 216000 | 2.53 | R-410A | 23
213896288 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Non-Ducted Indoor Units | 252000 | 10.8 | 19 | 280000 | 3.62 | 200000 | 2.16 | R-410A | 21
213896289 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Non-Ducted Indoor Units | 276000 | 10.6 | 18.9 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 23
213896290 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Non-Ducted Indoor Units | 298000 | 10 | 17.5 | 334000 | 3.59 | 236000 | 2.22 | R-410A | 24.8333
213916485 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.05 | 18.6 | 280000 | 3.54 | 200000 | 2.34 | R-410A | 21
213916486 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.85 | 18.5 | 308000 | 3.54 | 216000 | 2.37 | R-410A | 23
213916487 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.5 | 17.4 | 334000 | 3.52 | 236000 | 2.32 | R-410A | 24.8333
213916488 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 17.65 | 360000 | 3.42 | 268000 | 2.25 | R-410A | 26.6667
213896291 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Non-Ducted Indoor Units | 320000 | 10.1 | 17.4 | 360000 | 3.42 | 268000 | 2.13 | R-410A | 26.6667
213896332 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Ducted Indoor Units | 320000 | 10.9 | 17.9 | 360000 | 3.42 | 268000 | 2.38 | R-410A | 26.6667
213896334 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P360ZSKMU-B | Ducted Indoor Units | 344000 | 10.8 | 17.4 | 386000 | 3.32 | 284000 | 2.32 | R-410A | 28.6667
213916489 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P360ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 17.1 | 386000 | 3.36 | 284000 | 2.18 | R-410A | 28.6667
208812542 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 25.1 | 77000 | 4.09 | 56000 | 2.55 | R-410A | 5.75
208812543 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.45 | 23.95 | 103000 | 3.86 | 73000 | 2.49 | R-410A | 7.6667
208812544 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.4 | 24.1 | 129000 | 3.67 | 87000 | 2.43 | R-410A | 9.5833
208812547 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 25.1 | 77000 | 4.09 | 56000 | 2.55 | R-410A | 5.75
208812548 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.45 | 23.95 | 103000 | 3.86 | 73000 | 2.49 | R-410A | 7.6667
208812549 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.4 | 24.1 | 129000 | 3.67 | 87000 | 2.43 | R-410A | 9.5833
206568879 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* |  |  |  | MVHP072ME4CA* | Ducted Indoor Units | 69000 | 12.1 | 21 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568881 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* |  |  |  | MVHP072ME4CA* | Non-Ducted Indoor Units | 69000 | 13.5 | 25 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568882 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* |  |  |  | MVHR072ME4CA* | Ducted Indoor Units | 69000 | 11.9 | 20 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568883 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* |  |  |  | MVHR072ME4CA* | Non-Ducted Indoor Units | 69000 | 13 | 24.5 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568885 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* |  |  |  | MVHP096ME4CA* | Ducted Indoor Units | 92000 | 12.1 | 22.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568886 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* |  |  |  | MVHP096ME4CA* | Non-Ducted Indoor Units | 92000 | 12 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568887 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* |  |  |  | MVHR096ME4CA* | Ducted Indoor Units | 92000 | 11.9 | 21.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568888 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* |  |  |  | MVHR096ME4CA* | Non-Ducted Indoor Units | 92000 | 12.3 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568890 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* |  |  |  | MVHP120ME4CA* | Ducted Indoor Units | 115000 | 12.1 | 23 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568891 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* |  |  |  | MVHP120ME4CA* | Non-Ducted Indoor Units | 115000 | 12.1 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568892 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* |  |  |  | MVHR120ME4CA* | Ducted Indoor Units | 115000 | 11.9 | 21.9 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568893 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* |  |  |  | MVHR120ME4CA* | Non-Ducted Indoor Units | 115000 | 11.9 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
9956601 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER120C432Y |  |  |  | VER120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
9956607 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
208102081 | 1/1/2027 | LENNOX | HMSR-A-CB | VER120C432Y |  |  |  | VER120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
9121814 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-F(U) |  |  |  | GMV-Q120WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
9133443 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
9133481 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
206799422 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799428 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
207699044 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 28.85 | 103000 | 3.95 | 103000 | 2.41 | R-410A | 7.6667
207699040 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
208102000 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
208102077 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
10306439 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) |  |  |  | IOV120H3CDC720(A) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
7849630 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
9133488 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC72K/220V |  |  |  | TVRF-SHC72K/220V | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
9133489 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/220V |  |  |  | TVRF-SHC96K/220V | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
205782688 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/220V |  |  |  | TVRF-SHC96K/220V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
205782689 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC120K/220V |  |  |  | TVRF-SHC120K/220V | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.25 | 22.4 | 126000 | 3.4 | 82000 | 2.25 | R-410A | 9.3333
203360783 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-SHC120K/220V |  |  |  | TVRF-SHC120K/220V | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
212512538 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
9990292 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
9990290 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
9990291 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
206799420 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
212511071 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
212511072 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
212512455 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
212512458 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
212511075 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
212511076 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
212511079 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
212511080 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
212512461 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
212512456 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
212511073 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
212511074 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
212511077 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
212511078 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
212512459 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
212512462 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
212511081 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
212511082 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
207591078 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
207591079 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
204723100 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
204723101 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201994758 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201994759 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850183 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850184 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850300 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850301 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
202073617 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.75 | 77000 | 3.77 | 54000 | 2.43 | R-410A | 5.75
201830293 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201830294 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201830295 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1* | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
202073618 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.7 | 21.1 | 103000 | 3.5 | 72000 | 2.31 | R-410A | 7.6667
201850302 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201850185 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201994761 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
204723102 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
207591080 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
207591104 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
207591105 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
204723126 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
204723127 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850326 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850327 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850209 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850210 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
202073630 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.75 | 77000 | 3.77 | 54000 | 2.43 | R-410A | 5.75
201994802 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201994804 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201830319 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201830320 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201830321 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1* | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201994806 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
202073631 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.7 | 21.1 | 103000 | 3.5 | 72000 | 2.31 | R-410A | 7.6667
201850211 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201850328 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
204723128 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
207591106 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
206799430 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
10103123 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10103129 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10103102 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10103103 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10103130 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10103124 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10103125 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
10103131 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10103104 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
6691437 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
6691438 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
6691439 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
204442713 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH |  |  |  | AM072FXVAFH | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442728 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH |  |  |  | AM072FXVAJH | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
207385918 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 25.2 | 77000 | 3.58 | 51000 | 2.59 | R-410A | 5.75
207382951 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442714 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
206799423 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
206799425 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204442729 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
206799424 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
207382953 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
207385920 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 26.55 | 103000 | 3.74 | 67000 | 2.63 | R-410A | 7.6667
206799426 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
205000539 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH |  |  |  | AM120FXVAFH | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
205000540 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH |  |  |  | AM120FXVAJH | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
207385922 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 25.85 | 129000 | 3.43 | 84000 | 2.54 | R-410A | 9.5
207382954 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
205000541 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR |  |  |  | AM120FXVAJR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
208102003 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
7849628 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
9956564 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10306433 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
208102015 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
9956574 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
7850858 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
7850859 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
7850860 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
7850868 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
7850869 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
7850870 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
204442775 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
206799419 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799421 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204442783 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
204442776 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
206799427 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
206799429 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204442784 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
212511003 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
212511024 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
212512523 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
212512524 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
212511025 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
212511004 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
212511005 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
212511026 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
212512525 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
212512454 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
212511039 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
212511061 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
212511062 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
212511040 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
212512457 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
212512460 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
212511041 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
212511063 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
207591014 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
207591015 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
204723036 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
204723037 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201830229 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201830230 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850119 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850120 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201994655 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201994656 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850236 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850237 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
202073585 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.22 | 20.57 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
202073586 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 19.94 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
201850238 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201994657 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201850121 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830231 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
204723038 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
207591016 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
207591046 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
207591047 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
204723068 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
204723069 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201830261 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201830262 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850151 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850152 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201994705 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201994707 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850268 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850269 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
202073601 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 20.57 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
202073602 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 19.94 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
201850270 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201994709 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201850153 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830263 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
204723070 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
207591048 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
202583518 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.1 | 103000 | 3.76 | 73000 | 2.49 | R-410A | 7.6667
202583517 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 4.1 | 56000 | 2.64 | R-410A | 5.75
202583519 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.55 | 129000 | 3.7 | 87000 | 2.38 | R-410A | 9.5
202882193 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202882194 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202891635 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918830 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202891636 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202883243 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883244 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202883245 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883246 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202891643 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918941 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918942 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918943 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918938 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918939 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918940 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202891644 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202883247 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883248 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202891633 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891634 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202897134 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918839 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918836 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918837 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918838 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202897135 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202891637 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891638 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202891639 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891640 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202897136 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918947 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918948 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918949 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918944 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918945 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918946 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202897137 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202891641 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891642 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202897138 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897139 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202897176 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918845 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918846 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918847 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918842 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918843 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918844 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897177 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897144 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897145 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202897146 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897147 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202897178 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918953 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918954 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918955 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918950 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918951 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918952 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897179 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897148 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897149 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
213916633 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A |  |  |  | PUHY-P72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213893630 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A |  |  |  | PUHY-P72YNU-A | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893636 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893637 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916634 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A |  |  |  | PUHY-P72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213893628 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A |  |  |  | PUHY-P72TNU-A | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893632 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893633 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916609 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893526 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893527 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893534 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893535 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916610 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893522 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893523 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916570 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916571 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893530 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893531 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916627 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893842 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893559 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893564 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893565 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916628 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916629 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893542 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893543 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893558 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893827 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213916588 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916589 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893560 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893561 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893538 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893539 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213916590 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916795 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN |  |  |  | TUHYP0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213893703 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN |  |  |  | TUHYP0724AN40AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893706 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893707 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916799 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916793 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN |  |  |  | TUHYP0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213893702 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN |  |  |  | TUHYP0723AN40AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893704 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893705 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916797 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916700 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893642 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893643 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893646 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893647 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916704 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893640 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893641 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916698 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916702 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893644 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893645 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916774 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893682 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893683 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893686 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893687 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916778 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916782 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893690 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893691 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893688 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893689 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893680 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893681 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893684 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893685 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916780 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916776 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916772 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213896013 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A |  |  |  | PURY-P72YNU-A | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896149 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A |  |  |  | PURY-P72YNU-A | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896153 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A |  |  |  | PURY-P96YNU-A | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896147 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A |  |  |  | PURY-P72TNU-A | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896011 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A |  |  |  | PURY-P72TNU-A | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896151 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A |  |  |  | PURY-P96TNU-A | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896061 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN40AN |  |  |  | TURYP0724AN40AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896205 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN40AN |  |  |  | TURYP0724AN40AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896209 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN40AN |  |  |  | TURYP0964AN40AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896203 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN40AN |  |  |  | TURYP0723AN40AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896059 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN40AN |  |  |  | TURYP0723AN40AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896207 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN40AN |  |  |  | TURYP0963AN40AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896101 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A |  |  |  | PURY-EP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895981 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A |  |  |  | PURY-EP72YNU-A | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896105 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A |  |  |  | PURY-EP96YNU-A | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896099 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A |  |  |  | PURY-EP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895979 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A |  |  |  | PURY-EP72TNU-A | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896103 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A |  |  |  | PURY-EP96TNU-A | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896157 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN40AN |  |  |  | TURYE0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896021 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN40AN |  |  |  | TURYE0724AN40AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896161 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN |  |  |  | TURYE0964AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896155 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN40AN |  |  |  | TURYE0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896019 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN40AN |  |  |  | TURYE0723AN40AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896159 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN |  |  |  | TURYE0963AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896128 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A |  |  |  | PURY-HP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895997 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A |  |  |  | PURY-HP72YNU-A | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896001 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A |  |  |  | PURY-HP96YNU-A | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896133 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A |  |  |  | PURY-HP96YNU-A | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896125 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A |  |  |  | PURY-HP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895995 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A |  |  |  | PURY-HP72TNU-A | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213895999 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A |  |  |  | PURY-HP96TNU-A | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896131 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A |  |  |  | PURY-HP96TNU-A | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896045 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN |  |  |  | TURYH0724AN40AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896189 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN |  |  |  | TURYH0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896193 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN |  |  |  | TURYH0964AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896049 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN |  |  |  | TURYH0964AN40AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896043 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN |  |  |  | TURYH0723AN40AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896187 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN |  |  |  | TURYH0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896191 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN |  |  |  | TURYH0963AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896047 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN |  |  |  | TURYH0963AN40AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
203364244 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203334986 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203334936 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203334937 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203334987 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203364245 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203364246 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
203334988 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
203334938 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
203335003 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203334953 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203364261 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203364262 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203334954 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203335004 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203335005 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
203334955 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
203364263 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
203364278 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203334970 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203335020 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203335021 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203334971 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203364279 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203364280 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
203334972 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
203335022 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
204793015 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* |  |  |  | MVHP072ME2CA* | Ducted Indoor Units | 69000 | 12.1 | 21 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793016 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* |  |  |  | MVHP072ME2CA* | Non-Ducted Indoor Units | 69000 | 13.5 | 25 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793017 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* |  |  |  | MVHR072ME2CA* | Ducted Indoor Units | 69000 | 11.9 | 20 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793018 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* |  |  |  | MVHR072ME2CA* | Non-Ducted Indoor Units | 69000 | 13 | 24.5 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793019 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* |  |  |  | MVHP096ME2CA* | Ducted Indoor Units | 92000 | 12.1 | 22.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793020 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* |  |  |  | MVHP096ME2CA* | Non-Ducted Indoor Units | 92000 | 12 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793021 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* |  |  |  | MVHR096ME2CA* | Ducted Indoor Units | 92000 | 11.9 | 21.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793022 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* |  |  |  | MVHR096ME2CA* | Non-Ducted Indoor Units | 92000 | 12.3 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793023 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* |  |  |  | MVHP120ME2CA* | Ducted Indoor Units | 115000 | 12.1 | 23 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793024 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* |  |  |  | MVHP120ME2CA* | Non-Ducted Indoor Units | 115000 | 12.1 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793025 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* |  |  |  | MVHR120ME2CA* | Ducted Indoor Units | 115000 | 11.9 | 21.9 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793026 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* |  |  |  | MVHR120ME2CA* | Non-Ducted Indoor Units | 115000 | 11.9 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
205048202 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
205048203 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
205708872 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
205708873 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.5 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
205048204 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Ducted Indoor Units | 92000 | 11.2 | 19 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
205048205 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
205048206 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/460V |  |  |  | TVRF-OC120KHP/460V | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
205708874 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/460V |  |  |  | TVRF-OC120KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
205048213 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC72K/460V |  |  |  | TVRF-SHC72K/460V | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
205048215 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/460V |  |  |  | TVRF-SHC96K/460V | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
205048217 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC120K/460V |  |  |  | TVRF-SHC120K/460V | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205233054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* |  |  |  | RXYQ72XATJ* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
205234814 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* |  |  |  | RXYQ72XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
205234815 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
205233065 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
205233055 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
205233056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* |  |  |  | RXYQ120XATJ* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205234816 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* |  |  |  | RXYQ120XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
205234819 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* |  |  |  | RXYQ72XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
205233059 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* |  |  |  | RXYQ72XAYD* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
205233060 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
205233070 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
205234820 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
205234821 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* |  |  |  | RXYQ120XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
205233061 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* |  |  |  | RXYQ120XAYD* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205234780 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
205234828 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
205234860 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
205234861 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 21.6 | 103000 | 3.97 | 72000 | 2.49 | R-410A | 7.6667
205234829 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Ducted Indoor Units | 92000 | 11.4 | 18.9 | 103000 | 3.61 | 72000 | 2.32 | R-410A | 7.6667
205234781 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Non-Ducted Indoor Units | 92000 | 13.6 | 24.3 | 103000 | 4.33 | 72000 | 2.66 | R-410A | 7.6667
205234782 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Non-Ducted Indoor Units | 114000 | 12.5 | 23.3 | 129000 | 3.89 | 88000 | 2.58 | R-410A | 9.5
205234830 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Ducted Indoor Units | 114000 | 11.1 | 19 | 129000 | 3.54 | 88000 | 2.3 | R-410A | 9.5
205234862 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 21.15 | 129000 | 3.71 | 88000 | 2.44 | R-410A | 9.5
205811858 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205811859 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205818928 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205811954 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205818832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205818833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205818834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205818835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205811955 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205818929 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205811860 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205811861 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205811862 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205811863 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205818930 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205811956 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205818836 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205818837 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205818838 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205818839 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205811957 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205818931 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205811864 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205811865 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205811866 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205811867 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205818932 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205811958 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205818840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205818841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205818842 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205818843 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205811959 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205818933 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205811868 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205811869 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205811870 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205811871 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205818934 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205811960 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205818844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205818845 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205818846 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205818847 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205811961 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205818935 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205811872 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205811873 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205811874 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205811875 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205818936 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205811962 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205818848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205818849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205818850 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205818851 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205811963 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205818937 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205811876 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205811877 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205811878 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205811879 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205818938 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205811964 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205818852 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205818853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205818854 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205818855 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205811965 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205818939 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205811880 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205811881 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
10515227 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10515237 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10515247 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10515248 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10515238 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10515228 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10515229 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10515239 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10515249 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10515250 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10515240 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10515230 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10515231 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
10515241 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
10515251 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10515252 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10515242 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
10515232 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
201992879 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
202021864 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202022813 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202022814 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202021865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
201992880 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
201992871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
202021866 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202022815 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202022816 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
201993477 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
202021867 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
202021868 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
201993478 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
202022817 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
202022818 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
202021869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
201993173 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
202021870 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
201993479 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
202022819 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
202022820 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
201993480 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
202021871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
202021872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
202022821 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
201993174 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
201902897 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10267502 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10306463 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
9121821 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
213896311 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-A |  |  |  | PURY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 11.4 | 19.8 | 76000 | 3.46 | 56000 | 2.26 | R-410A | 5.75
213916464 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.2 | 76000 | 3.79 | 56000 | 2.42 | R-410A | 5.75
213896280 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 12.4 | 22.2 | 76000 | 3.85 | 56000 | 2.25 | R-410A | 5.75
213896335 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Ducted Indoor Units | 69000 | 12.3 | 20.2 | 76000 | 3.74 | 56000 | 2.59 | R-410A | 5.75
213896336 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.73 | 76000 | 2.71 | R-410A | 7.6667
213896281 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Non-Ducted Indoor Units | 92000 | 12.1 | 22.2 | 103000 | 3.74 | 76000 | 2.42 | R-410A | 7.6667
213916465 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12 | 21.15 | 103000 | 3.73 | 76000 | 2.56 | R-410A | 7.6667
213896315 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A |  |  |  | PUHY-P120ZKMU-A | Ducted Indoor Units | 115000 | 11.4 | 19.5 | 129000 | 3.62 | 92000 | 2.51 | R-410A | 9.5833
202519343 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y72WM/C-F(U) |  |  |  | GMV-Y72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
202519344 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y72WM/C-F(U) |  |  |  | GMV-Y72WM/C-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 22 | 77000 | 3.5 | 51000 | 2.4 | R-410A | 5.75
202519346 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/C-F(U) |  |  |  | GMV-Y96WM/C-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 22 | 103000 | 3.5 | 67000 | 2.3 | R-410A | 7.6667
10479766 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 21 | 77000 | 3.5 | 60000 | 2.25 | R-410A | 5.75
208102075 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432G |  |  |  | VER096C432G | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
8849290 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-F(U) |  |  |  | GMV-Q72WM/B-F(U) | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
208102016 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
10306434 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10509439 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10509440 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10306432 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
9956565 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
9956563 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
208102002 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
7793597 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
7793598 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
208102004 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
204442760 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
204442759 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR |  |  |  | AM072FXVAJR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
9133441 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
9133442 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
204442791 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
204442799 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
9956605 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER072C432Y |  |  |  | VER072C432Y | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
10509445 | 1/1/2027 | AC PRO.COM | HMSR-A-CB | GMV-Q72WM/B-F(U) |  |  |  | GMV-Q72WM/B-F(U) | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
203266414 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266443 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) |  |  |  | IOV120H3CDC720(A) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266444 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266445 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
208102073 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432Y |  |  |  | VER072C432Y | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
208102085 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432Y | VER072C432Y |  |  | VER144C432Y | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
10342541 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-F(U) | GMV-Q72WM/B-F(U) |  |  | GMV-Q144WM/B-F(U) | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
10509447 | 1/1/2027 | AC PRO.COM | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
208102078 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
208102001 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
204442800 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
203360784 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V |  |  |  | TVRF-OC120KHP/220V | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
9133449 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9133480 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
203266412 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-F(U) |  |  |  | GMV-Q120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
9956608 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
8849292 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
10479769 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V96W/A-F(U) |  |  |  | GMV-V96W/A-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 21 | 103000 | 3.5 | 68000 | 2.25 | R-410A | 7.6667
10341439 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-U(U) | GMV-Q72WM/B-U(U) |  |  | GMV-Q144WM/B-U(U) | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
201903147 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER072C432G | VER072C432G |  |  | VER144C432G | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
203400954 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-U(U) |  |  |  | GMV-Q120WM/B-U(U) | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
208102083 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432G | VER072C432G |  |  | VER144C432G | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
10341435 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-U(U) |  |  |  | GMV-Q96WM/B-U(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
201903141 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432G |  |  |  | VER096C432G | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
10306464 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10306462 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10267500 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10267501 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
201902894 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
201902896 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
207337153 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
8175947 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.25 | 24.85 | 76000 | 3.92 | 56000 | 2.35 | R-410A | 5.75
8175948 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.9 | 103000 | 3.82 | 76000 | 2.49 | R-410A | 7.6667
8175949 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.8 | 23.4 | 129000 | 3.87 | 92000 | 2.34 | R-410A | 9.5
8175962 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.25 | 24.85 | 76000 | 3.92 | 56000 | 2.35 | R-410A | 5.75
8175963 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.9 | 103000 | 3.82 | 76000 | 2.49 | R-410A | 7.6667
8175964 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.8 | 23.4 | 129000 | 3.87 | 92000 | 2.34 | R-410A | 9.5
8175977 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 76000 | 3.72 | 56000 | 2.26 | R-410A | 5.75
8175978 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 24.3 | 103000 | 3.54 | 71000 | 2.27 | R-410A | 7.6667
8175979 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.75 | 129000 | 3.66 | 87000 | 2.26 | R-410A | 9.5
8175991 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 76000 | 3.72 | 56000 | 2.26 | R-410A | 5.75
8175992 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 24.3 | 103000 | 3.54 | 71000 | 2.27 | R-410A | 7.6667
8175993 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.75 | 129000 | 3.66 | 87000 | 2.26 | R-410A | 9.5
8552536 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PCTJ |  |  |  | REYQ120PCTJ | Non-Ducted Indoor Units | 110000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.1667
8552584 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PCYD |  |  |  | REYQ120PCYD | Non-Ducted Indoor Units | 110000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.1667
8552651 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ144PCTJ |  |  |  | REYQ144PCTJ | Non-Ducted Indoor Units | 124000 | 11.2 | 18.9 | 148000 | 3.6 | 103000 | 2.4 | R-410A | 10.3333
8553652 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCTJ |  |  |  | REYQ72PCTJ | Ducted Indoor Units | 69000 | 13.7 | 21.3 | 77000 | 3.4 | 52000 | 2.5 | R-410A | 5.75
8554086 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCYD |  |  |  | REYQ72PCYD | Ducted Indoor Units | 69000 | 13.7 | 21.3 | 77000 | 3.4 | 52000 | 2.5 | R-410A | 5.75
8556740 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCTJ |  |  |  | REYQ72PCTJ | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.55 | 23.2 | 77000 | 3.8 | 52000 | 2.72 | R-410A | 5.75
8556904 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCYD |  |  |  | REYQ72PCYD | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.55 | 23.2 | 77000 | 3.8 | 52000 | 2.72 | R-410A | 5.75
8551200 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCTJ |  |  |  | REYQ72PCTJ | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
8551238 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCYD |  |  |  | REYQ72PCYD | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
9133165 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9133166 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9133167 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9133168 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9133169 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DXN1 |  |  |  | MV5-2R120DXN1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133170 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DXN1 |  |  |  | MV5-2R120DXN1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133181 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9133182 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9133183 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9133184 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9133185 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DZN1 |  |  |  | MV5-2R120DZN1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133186 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DZN1 |  |  |  | MV5-2R120DZN1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133197 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9133198 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9133199 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DXN1 |  |  |  | MV5-2R120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133205 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9133206 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9133207 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DZN1 |  |  |  | MV5-2R120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487690 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487691 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487692 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487694 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487695 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487696 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487731 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9487732 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9487733 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9487735 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9487736 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9487737 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9487738 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9487739 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9487740 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9487741 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9487743 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9487744 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9487745 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487746 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487747 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487748 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487749 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487750 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487785 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9487787 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9487788 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9487789 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9487790 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9487791 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9487792 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9487793 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9487795 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9487796 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9487797 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9487798 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
200084014 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
200084015 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
200084016 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
9956571 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
10306436 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
200084023 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
200084024 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
200084025 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
202517456 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 |  |  |  | ARUB121BTE4 | Ducted Indoor Units | 114000 | 12.6 | 23.5 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
202517457 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 |  |  |  | ARUB121BTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202517458 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 |  |  |  | ARUB121DTE4 | Ducted Indoor Units | 114000 | 12.6 | 23.5 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
202517459 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 |  |  |  | ARUB121DTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202517460 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 |  |  |  | ARUN121BTE4 | Ducted Indoor Units | 114000 | 12.6 | 23 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
202517461 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 |  |  |  | ARUN121BTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202524541 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
202524542 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
202524543 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
202524544 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
9550137 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Non-Ducted Indoor Units | 69000 | 15.4 | 28.4 | 77000 | 4.11 | 56000 | 2.82 | R-410A | 5.75
9550159 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Ducted Indoor Units | 69000 | 13.2 | 20.6 | 77000 | 3.5 | 56000 | 2.49 | R-410A | 5.75
9680959 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.3 | 24.5 | 77000 | 3.8 | 56000 | 2.65 | R-410A | 5.75
9088680 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 |  |  |  | IOV096H3CDC736 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
9121934 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9121935 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9121936 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9121937 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9121938 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
10479770 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V96W/A-F(U) |  |  |  | GMV-V96W/A-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 20 | 103000 | 3.5 | 70000 | 2.25 | R-410A | 7.6667
10594255 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
10594256 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
10594257 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
10594258 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
202515497 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 |  |  |  | ARUN072BTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
202515520 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202515521 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202515522 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
202515523 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 |  |  |  | ARUN072BTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
202516169 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
202516171 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
202516172 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 |  |  |  | ARUN096DTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
202516173 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 |  |  |  | ARUN096DTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202516175 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
202516176 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
202516178 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 |  |  |  | ARUN121DTE4 | Ducted Indoor Units | 114000 | 12.6 | 23 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
202516179 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 |  |  |  | ARUN121DTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202515347 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 |  |  |  | ARUN072DTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
202534251 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 |  |  |  | ARUB096DTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202534253 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 |  |  |  | ARUN096BTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202534254 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 |  |  |  | ARUN096BTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
202534255 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 |  |  |  | ARUB096DTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
202534256 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 |  |  |  | ARUB096BTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
202534257 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 |  |  |  | ARUB096BTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
203297452 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.5 | 129000 | 3.49 | 87000 | 2.26 | R-410A | 9.5
203297456 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.5 | 129000 | 3.49 | 87000 | 2.26 | R-410A | 9.5
203297553 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Ducted Indoor Units | 69000 | 13.9 | 20 | 76000 | 3.75 | 56000 | 2.58 | R-410A | 5.75
203297554 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Non-Ducted Indoor Units | 69000 | 15.5 | 20.9 | 76000 | 3.66 | 56000 | 2.45 | R-410A | 5.75
203297555 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
203297558 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Ducted Indoor Units | 69000 | 13.9 | 20 | 76000 | 3.75 | 56000 | 2.58 | R-410A | 5.75
203297559 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Non-Ducted Indoor Units | 69000 | 15.5 | 20.9 | 76000 | 3.66 | 56000 | 2.45 | R-410A | 5.75
203297560 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.5 | 21.9 | 76000 | 3.59 | 56000 | 2.26 | R-410A | 5.75
203297561 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
203297566 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Non-Ducted Indoor Units | 92000 | 13.6 | 20.1 | 103000 | 3.66 | 76000 | 2.46 | R-410A | 7.6667
203297567 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
203297570 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Non-Ducted Indoor Units | 92000 | 13.6 | 20.1 | 103000 | 3.66 | 76000 | 2.46 | R-410A | 7.6667
203297571 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 3.49 | 71000 | 2.25 | R-410A | 7.6667
203297572 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
203300875 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Ducted Indoor Units | 92000 | 12.2 | 18.9 | 103000 | 3.6 | 76000 | 2.44 | R-410A | 7.6667
203300876 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Ducted Indoor Units | 92000 | 12.2 | 18.9 | 103000 | 3.6 | 76000 | 2.44 | R-410A | 7.6667
203300877 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 3.49 | 71000 | 2.25 | R-410A | 7.6667
203300907 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.5 | 21.9 | 76000 | 3.59 | 56000 | 2.26 | R-410A | 5.75
203301894 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TKMU-A |  |  |  | PURY-P120TKMU-A | Non-Ducted Indoor Units | 114000 | 12.2 | 20.3 | 129000 | 3.57 | 92000 | 2.4 | R-410A | 9.5
203301895 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YKMU-A |  |  |  | PURY-P120YKMU-A | Non-Ducted Indoor Units | 114000 | 12.2 | 20.3 | 129000 | 3.57 | 92000 | 2.4 | R-410A | 9.5
203301896 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
203301897 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
203381168 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TKMU-A |  |  |  | PURY-P120TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.95 | 19.25 | 129000 | 3.49 | 92000 | 2.34 | R-410A | 9.5
203381170 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.55 | 129000 | 3.64 | 87000 | 2.26 | R-410A | 9.5
203381172 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YKMU-A |  |  |  | PURY-P120YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.95 | 19.25 | 129000 | 3.49 | 92000 | 2.34 | R-410A | 9.5
203381174 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.55 | 129000 | 3.64 | 87000 | 2.26 | R-410A | 9.5
203381254 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.7 | 20.45 | 76000 | 3.7 | 56000 | 2.51 | R-410A | 5.75
203381256 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 23.5 | 76000 | 3.69 | 56000 | 2.26 | R-410A | 5.75
203381258 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.7 | 20.45 | 76000 | 3.7 | 56000 | 2.51 | R-410A | 5.75
203381260 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 23.5 | 76000 | 3.69 | 56000 | 2.26 | R-410A | 5.75
203381263 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.9 | 19.5 | 103000 | 3.63 | 76000 | 2.45 | R-410A | 7.6667
203381265 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 23.85 | 103000 | 3.52 | 71000 | 2.25 | R-410A | 7.6667
203381267 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.9 | 19.5 | 103000 | 3.63 | 76000 | 2.45 | R-410A | 7.6667
203381269 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 23.85 | 103000 | 3.52 | 71000 | 2.25 | R-410A | 7.6667
201760441 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-*G |  |  |  | VRA072H4M-*G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201760442 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-*G |  |  |  | VRA072H4M-*G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201760443 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-*G |  |  |  | VPA072H4M-*G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201760445 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-*G |  |  |  | VPA072H4M-*G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201760446 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-*Y |  |  |  | VRA072H4M-*Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201760447 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-*Y |  |  |  | VRA072H4M-*Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201760449 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-*Y |  |  |  | VPA072H4M-*Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201760450 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-*Y |  |  |  | VPA072H4M-*Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201830205 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201830213 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830214 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830215 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201830219 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830220 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830224 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830225 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830349 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201830350 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847109 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2G |  |  |  | VPA072H4M-2G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847110 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2G |  |  |  | VPA072H4M-2G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201847111 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2Y |  |  |  | VPA072H4M-2Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847112 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2Y |  |  |  | VPA072H4M-2Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201847113 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G |  |  |  | VPA096H4M-2G | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847114 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G |  |  |  | VPA096H4M-2G | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847115 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y |  |  |  | VPA096H4M-2Y | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847116 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y |  |  |  | VPA096H4M-2Y | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847118 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G |  |  |  | VPA120H4M-2G | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847120 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y |  |  |  | VPA120H4M-2Y | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847169 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2Y |  |  |  | VRA072H4M-2Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847170 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2Y |  |  |  | VRA072H4M-2Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201847171 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2G |  |  |  | VRA072H4M-2G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847172 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2G |  |  |  | VRA072H4M-2G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201847173 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y |  |  |  | VRA096H4M-2Y | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847174 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y |  |  |  | VRA096H4M-2Y | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847175 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G |  |  |  | VRA096H4M-2G | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847176 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G |  |  |  | VRA096H4M-2G | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847177 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y |  |  |  | VRA120H4M-2Y | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847179 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G |  |  |  | VRA120H4M-2G | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856718 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) |  |  |  | MV5-RC72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856719 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) |  |  |  | MV5-RC72DXN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856720 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) |  |  |  | MV5-RC96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201856722 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) |  |  |  | MV5-RC120DXN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856742 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) |  |  |  | MV5-RC72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856743 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) |  |  |  | MV5-RC72DZN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856744 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) |  |  |  | MV5-RC96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201856746 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) |  |  |  | MV5-RC120DZN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856766 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) |  |  |  | MV5-XC72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856767 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) |  |  |  | MV5-XC72DXN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856768 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) |  |  |  | MV5-XC96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201856770 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) |  |  |  | MV5-XC120DXN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856788 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) |  |  |  | MV5-XC72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856789 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) |  |  |  | MV5-XC72DZN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856790 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) |  |  |  | MV5-XC96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201856792 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) |  |  |  | MV5-XC120DZN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862854 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y |  |  |  | VRA072L4M-2Y | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862855 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y |  |  |  | VRA072L4M-2Y | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862856 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y |  |  |  | VRA096L4M-2Y | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201862858 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y |  |  |  | VRA120L4M-2Y | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862878 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G |  |  |  | VRA072L4M-2G | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862879 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G |  |  |  | VRA072L4M-2G | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862880 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G |  |  |  | VRA096L4M-2G | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201862882 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G |  |  |  | VRA120L4M-2G | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862902 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y |  |  |  | VPA072L4M-2Y | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862903 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y |  |  |  | VPA072L4M-2Y | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y |  |  |  | VPA096L4M-2Y | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201862906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y |  |  |  | VPA120L4M-2Y | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862924 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G |  |  |  | VPA072L4M-2G | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862925 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G |  |  |  | VPA072L4M-2G | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862926 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G |  |  |  | VPA096L4M-2G | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201862928 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G |  |  |  | VPA120L4M-2G | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864458 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864459 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864460 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C6000AA |  |  |  | 4TVR0096C6000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864461 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C6000AA |  |  |  | 4TVR0096C6000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864462 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0115C6000AA |  |  |  | 4TVR0115C6000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864466 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864467 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864468 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C4000AA |  |  |  | 4TVR0096C4000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864469 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C4000AA |  |  |  | 4TVR0096C4000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864470 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0115C4000AA |  |  |  | 4TVR0115C4000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864474 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C6000AA |  |  |  | 4TVH0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864475 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C6000AA |  |  |  | 4TVH0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864476 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C6000AA |  |  |  | 4TVH0096C6000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864477 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C6000AA |  |  |  | 4TVH0096C6000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864478 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0115C6000AA |  |  |  | 4TVH0115C6000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864482 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C4000AA |  |  |  | 4TVH0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864483 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C4000AA |  |  |  | 4TVH0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864484 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C4000AA |  |  |  | 4TVH0096C4000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864485 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C4000AA |  |  |  | 4TVH0096C4000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864486 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0115C4000AA |  |  |  | 4TVH0115C4000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201874025 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
201874026 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
201874027 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
201874028 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
201874035 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
201874036 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
201874037 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
201874038 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
201874039 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
201874040 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
201874041 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
201874042 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
207172462 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
207172463 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
207172466 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
207574204 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574205 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574206 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574207 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574208 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574209 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574210 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574212 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574216 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574217 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574218 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574219 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574220 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574221 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574222 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574224 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574228 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574229 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574230 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574231 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574232 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574233 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574234 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574236 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574240 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574241 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574242 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574243 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574244 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574245 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574246 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574248 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574252 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574253 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574254 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574255 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574256 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574257 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574258 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574260 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574264 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574265 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574266 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574267 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574268 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574269 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574270 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574272 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574276 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574277 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574278 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574279 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574280 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574281 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574282 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574284 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574288 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574289 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574290 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574291 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574292 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574293 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574294 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574296 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202515434 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
202583514 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Ducted Indoor Units | 69000 | 11.9 | 21.5 | 77000 | 4.01 | 56000 | 2.64 | R-410A | 5.75
202583515 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Ducted Indoor Units | 92000 | 11.6 | 21.1 | 103000 | 3.66 | 73000 | 2.47 | R-410A | 7.6667
202583516 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Ducted Indoor Units | 114000 | 11.6 | 20.9 | 129000 | 3.64 | 87000 | 2.35 | R-410A | 9.5
205281456 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
205281458 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
205281459 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
205281461 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
205281462 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
205281464 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
210691220 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
210691221 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
210691222 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
210691223 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
210691224 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
210691225 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
210691226 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
210713380 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
210713381 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
210720743 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
210845528 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
210845822 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
212924814 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Ducted Indoor Units | 72000 | 12 | 19.5 | 81000 | 3.65 | 52500 | 2.45 | R-410A | 6
212924815 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Non-Ducted Indoor Units | 72000 | 12.5 | 23 | 81000 | 4.25 | 52500 | 2.67 | R-410A | 6
212924816 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Ducted Indoor Units | 96000 | 11.7 | 19.7 | 103000 | 3.75 | 70000 | 2.45 | R-410A | 8
212924817 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Non-Ducted Indoor Units | 96000 | 12.5 | 22.6 | 103000 | 4.05 | 70000 | 2.55 | R-410A | 8
212924818 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Ducted Indoor Units | 120000 | 12 | 20.65 | 129000 | 3.71 | 81000 | 2.4 | R-410A | 10
212924819 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Non-Ducted Indoor Units | 120000 | 12 | 22.1 | 129000 | 3.9 | 81000 | 2.53 | R-410A | 10
212924821 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Ducted Indoor Units | 72000 | 12 | 19.5 | 81000 | 3.65 | 52500 | 2.45 | R-410A | 6
212924822 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Non-Ducted Indoor Units | 72000 | 12.5 | 23 | 81000 | 4.25 | 52500 | 2.67 | R-410A | 6
212924823 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Ducted Indoor Units | 96000 | 11.7 | 19.7 | 103000 | 3.75 | 70000 | 2.45 | R-410A | 8
212924824 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Non-Ducted Indoor Units | 96000 | 12.5 | 22.6 | 103000 | 4.05 | 70000 | 2.55 | R-410A | 8
212924825 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Ducted Indoor Units | 120000 | 12 | 20.65 | 129000 | 3.71 | 81000 | 2.4 | R-410A | 10
212924826 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Non-Ducted Indoor Units | 120000 | 12 | 22.1 | 129000 | 3.9 | 81000 | 2.53 | R-410A | 10
212924829 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 12.25 | 21.25 | 81000 | 3.95 | 52500 | 2.56 | R-410A | 6
212924830 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 96000 | 12.1 | 21.15 | 103000 | 3.9 | 70000 | 2.5 | R-410A | 8
212924831 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 120000 | 12 | 21.37 | 129000 | 3.8 | 81000 | 2.46 | R-410A | 10
212924832 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 12.25 | 21.25 | 81000 | 3.95 | 52500 | 2.56 | R-410A | 6
212924833 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 96000 | 12.1 | 21.15 | 103000 | 3.9 | 70000 | 2.5 | R-410A | 8
212924834 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 120000 | 12 | 21.37 | 129000 | 3.8 | 81000 | 2.46 | R-410A | 10
213500518 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-96H8FH3H2 |  |  |  | AVW-96H8FH3H2 | Non-Ducted Indoor Units | 92000 | 11.5 | 25.4 | 103000 | 3.6 | 70000 | 2.4 | R-410A | 7.6667
213500519 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-76H8FH3H2 |  |  |  | AVW-76H8FH3H2 | Non-Ducted Indoor Units | 72000 | 11.6 | 26.5 | 81000 | 3.7 | 52500 | 2.6 | R-410A | 6
213500525 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-96H8FH3H2 |  |  |  | AVW-96H8FH3H2 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.25 | 21.75 | 103000 | 3.45 | 70000 | 2.35 | R-410A | 7.6667
213500526 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-76H8FH3H2 |  |  |  | AVW-76H8FH3H2 | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 11.35 | 22.55 | 81000 | 3.55 | 52500 | 2.5 | R-410A | 6
206453538 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
206453539 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
206453540 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
206453542 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
206453543 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
206453545 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
208102009 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
10103108 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10103109 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Non-Ducted Indoor Units | 92000 | 14.6 | 25.1 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
10103110 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.1 | 23.4 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
10103135 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Ducted Indoor Units | 69000 | 13.8 | 20.8 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
10103136 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Ducted Indoor Units | 92000 | 12.3 | 19.3 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
10103137 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
10103149 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.8 | 22.4 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
10103150 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.45 | 22.2 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
10103151 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 21.5 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
10206676 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206677 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206678 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206690 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206691 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206704 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206705 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206706 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206718 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206719 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206720 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206732 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206733 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206734 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206746 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206747 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206748 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206760 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206761 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206762 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206774 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206775 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206776 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206788 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206789 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206790 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206802 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206803 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206804 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206816 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206817 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206818 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206830 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206831 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206832 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10207510 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207511 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207512 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207524 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207525 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207526 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207538 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207539 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207540 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207552 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207553 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207554 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207566 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207567 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207568 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207580 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207581 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207582 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
9363538 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9363539 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9363540 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9363541 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9363542 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9363544 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9363545 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9363546 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9363547 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9363549 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9363550 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9363551 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9302802 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9302803 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9302804 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9302805 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9302806 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9302807 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9302808 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9302809 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9302810 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9302811 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9302812 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9302813 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9363440 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9363441 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9363442 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9363443 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9363444 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9363445 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9989439 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* |  |  |  | RXYQ72TATJ* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
9989440 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
9990029 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* |  |  |  | RXYQ72TAYD* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
9990030 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
9990031 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* |  |  |  | RXYQ120TATJ* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
9990046 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
9990047 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
9990048 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* |  |  |  | RXYQ120TAYD* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
9990087 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* |  |  |  | RXYQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
9990088 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* |  |  |  | RXYQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
9990089 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
9990090 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
9990091 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* |  |  |  | RXYQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
9990092 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* |  |  |  | RXYQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
9990287 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
9990288 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
9990289 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
10035438 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Non-Ducted Indoor Units | 69000 | 11.3 | 29.3 | 77000 | 3.41 | 77000 | 2.25 | R-410A | 5.75
10035439 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Non-Ducted Indoor Units | 92000 | 11.9 | 28.3 | 103000 | 3.61 | 103000 | 2.25 | R-410A | 7.6667
10035456 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Non-Ducted Indoor Units | 69000 | 11.3 | 29.3 | 77000 | 3.41 | 77000 | 2.25 | R-410A | 5.75
10035457 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Non-Ducted Indoor Units | 92000 | 11.9 | 28.3 | 103000 | 3.61 | 103000 | 2.25 | R-410A | 7.6667
10323534 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323535 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323536 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323550 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323551 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323552 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323566 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323567 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323568 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323582 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323583 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323584 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323598 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323599 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323600 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323614 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323615 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323616 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323630 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323631 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323632 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323646 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323647 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323648 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323662 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323663 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323664 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323678 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323679 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323680 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323694 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323695 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323696 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323710 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323711 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323712 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323728 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323729 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323730 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323744 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323745 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323746 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323760 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323761 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323762 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323777 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323778 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323779 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323793 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323794 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323795 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323809 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323810 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323811 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10340639 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/A-F(U) |  |  |  | GMV-Y96WM/A-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 22 | 103000 | 3.5 | 67000 | 2.3 | R-410A | 7.6667
10340640 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/A-F(U) |  |  |  | GMV-Y96WM/A-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.2 | 21 | 103000 | 3.4 | 67000 | 2.27 | R-410A | 7.6667
10612394 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
10612395 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
10612396 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
10612397 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
10612398 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
10612399 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
10612437 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
10612438 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
10612439 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
10612440 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612441 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612442 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612443 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
10612444 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
10612445 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
10612446 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
10612447 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
10612448 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
10612449 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
10612450 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
10612451 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
10612452 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
10612546 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
10612547 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612548 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
10612549 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612550 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
10612551 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612552 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
10612553 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
10612554 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
10612555 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
10612556 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
10612557 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
10612558 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
10612559 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
10612560 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
10612561 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
10612562 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
9302718 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9302719 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9302720 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9302721 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9302722 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9302723 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9088673 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 |  |  |  | IOV072H3CDC712 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
9088683 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC714 |  |  |  | IOV120H3CDC714 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
9121941 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 |  |  |  | MV5-H120DXN1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9121942 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 |  |  |  | MV5-H120DXN1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9121943 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9121944 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 |  |  |  | MV5-H120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9121951 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9121952 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9121953 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9121954 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9121981 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 |  |  |  | MV5-H120DZN1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9121982 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 |  |  |  | MV5-H120DZN1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9122304 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9122305 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9122306 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 |  |  |  | MV5-H120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9122947 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Non-Ducted Indoor Units | 69000 | 15.4 | 28.4 | 77000 | 4.11 | 56000 | 2.82 | R-410A | 5.75
9122948 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Non-Ducted Indoor Units | 92000 | 14.5 | 30.1 | 103000 | 4.31 | 76000 | 2.8 | R-410A | 7.6667
9122949 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Non-Ducted Indoor Units | 114000 | 13 | 29 | 129000 | 3.95 | 92000 | 2.6 | R-410A | 9.5
9122968 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Ducted Indoor Units | 69000 | 13.2 | 20.6 | 77000 | 3.5 | 56000 | 2.49 | R-410A | 5.75
9122969 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Non-Ducted Indoor Units | 69000 | 15.4 | 28.4 | 77000 | 4.11 | 56000 | 2.82 | R-410A | 5.75
9122970 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Ducted Indoor Units | 69000 | 13.2 | 20.6 | 77000 | 3.5 | 56000 | 2.49 | R-410A | 5.75
9122971 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Ducted Indoor Units | 92000 | 12.2 | 22.8 | 103000 | 3.8 | 76000 | 2.6 | R-410A | 7.6667
9122972 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Non-Ducted Indoor Units | 92000 | 14.5 | 30.1 | 103000 | 4.31 | 76000 | 2.8 | R-410A | 7.6667
9122973 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Ducted Indoor Units | 92000 | 12.2 | 22.8 | 103000 | 3.8 | 76000 | 2.6 | R-410A | 7.6667
9122974 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Ducted Indoor Units | 114000 | 12.3 | 21.1 | 129000 | 3.53 | 92000 | 2.5 | R-410A | 9.5
9122975 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Non-Ducted Indoor Units | 114000 | 13 | 29 | 129000 | 3.95 | 92000 | 2.6 | R-410A | 9.5
9122976 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Ducted Indoor Units | 114000 | 12.3 | 21.1 | 129000 | 3.53 | 92000 | 2.5 | R-410A | 9.5
9123031 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.3 | 24.5 | 77000 | 3.8 | 56000 | 2.65 | R-410A | 5.75
9123032 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.3 | 24.5 | 77000 | 3.8 | 56000 | 2.65 | R-410A | 5.75
9123033 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.35 | 26.45 | 103000 | 4.05 | 76000 | 2.7 | R-410A | 7.6667
9123034 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.35 | 26.45 | 103000 | 4.05 | 76000 | 2.7 | R-410A | 7.6667
9123035 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.65 | 25.05 | 129000 | 3.74 | 92000 | 2.55 | R-410A | 9.5
9123036 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.65 | 25.05 | 129000 | 3.74 | 92000 | 2.55 | R-410A | 9.5
8552534 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCTJ |  |  |  | REYQ96PCTJ | Non-Ducted Indoor Units | 90000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.5
8656992 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72ZKMU-A |  |  |  | PURY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 13.1 | 21.3 | 76000 | 3.62 | 56000 | 2.26 | R-410A | 5.75
8656994 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A |  |  |  | PURY-P96ZKMU-A | Non-Ducted Indoor Units | 92000 | 12.4 | 22.7 | 103000 | 3.46 | 71000 | 2.26 | R-410A | 7.6667
8656996 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120ZKMU-A |  |  |  | PURY-P120ZKMU-A | Non-Ducted Indoor Units | 114000 | 13.2 | 22.3 | 129000 | 3.5 | 87000 | 2.26 | R-410A | 9.5
8657012 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 13.6 | 25.9 | 76000 | 3.85 | 56000 | 2.25 | R-410A | 5.75
8657014 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Non-Ducted Indoor Units | 92000 | 13.2 | 25.6 | 103000 | 3.74 | 76000 | 2.42 | R-410A | 7.6667
8657016 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A |  |  |  | PUHY-P120ZKMU-A | Non-Ducted Indoor Units | 114000 | 13.7 | 24.2 | 129000 | 3.87 | 92000 | 2.3 | R-410A | 9.5
9045746 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045748 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045770 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045772 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045794 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045796 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9085396 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Non-Ducted Indoor Units | 69000 | 15 | 29 | 77000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
9085397 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Ducted Indoor Units | 69000 | 13.7 | 23.4 | 77000 | 3.88 | 56000 | 2.8 | R-410A | 5.75
9085398 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Non-Ducted Indoor Units | 92000 | 15.3 | 30.2 | 103000 | 4.8 | 76000 | 2.95 | R-410A | 7.6667
9085399 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Ducted Indoor Units | 92000 | 13.5 | 23.1 | 103000 | 4.1 | 76000 | 2.9 | R-410A | 7.6667
9085400 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Non-Ducted Indoor Units | 114000 | 13 | 25.4 | 129000 | 4 | 92000 | 2.8 | R-410A | 9.5
9085401 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Ducted Indoor Units | 114000 | 12.2 | 22.3 | 129000 | 3.95 | 92000 | 2.8 | R-410A | 9.5
9085438 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.35 | 26.2 | 77000 | 4.09 | 56000 | 2.75 | R-410A | 5.75
9085439 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.4 | 26.65 | 103000 | 4.45 | 76000 | 2.92 | R-410A | 7.6667
9085440 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.6 | 23.85 | 129000 | 3.97 | 92000 | 2.8 | R-410A | 9.5
8556905 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCTJ |  |  |  | REYQ96PCTJ | Mixed Ducted and Non-Ducted Indoor Units | 90000 | 12.2 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.5
8554690 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCTJ |  |  |  | REYQ96PCTJ | Ducted Indoor Units | 90000 | 11.2 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.5
8554691 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCYD |  |  |  | REYQ96PCYD | Ducted Indoor Units | 90000 | 11.2 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.5
8635954 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCYD |  |  |  | REYQ96PCYD | Non-Ducted Indoor Units | 90000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.5
8635955 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCYD |  |  |  | REYQ96PCYD | Mixed Ducted and Non-Ducted Indoor Units | 90000 | 12.2 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.5
8989551 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Non-Ducted Indoor Units | 69000 | 15 | 29 | 77000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
8989552 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Non-Ducted Indoor Units | 92000 | 15.3 | 30.2 | 103000 | 4.8 | 76000 | 2.95 | R-410A | 7.6667
8989553 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Non-Ducted Indoor Units | 114000 | 13 | 25.4 | 129000 | 4 | 92000 | 2.8 | R-410A | 9.5
8989566 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Ducted Indoor Units | 69000 | 13.7 | 23.4 | 77000 | 3.88 | 56000 | 2.8 | R-410A | 5.75
8989567 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Ducted Indoor Units | 92000 | 13.5 | 23.1 | 103000 | 4.1 | 76000 | 2.9 | R-410A | 7.6667
8989568 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Ducted Indoor Units | 114000 | 12.2 | 22.3 | 129000 | 3.95 | 92000 | 2.8 | R-410A | 9.5
8989607 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.35 | 26.2 | 77000 | 4.09 | 56000 | 2.75 | R-410A | 5.75
8989608 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.4 | 26.65 | 103000 | 4.45 | 76000 | 2.92 | R-410A | 7.6667
8989609 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.6 | 23.85 | 129000 | 3.97 | 92000 | 2.8 | R-410A | 9.5
8683032 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVHFH |  |  |  | AM072KXVHFH | Non-Ducted Indoor Units | 69000 | 15.5 | 40 | 77000 | 4.5 | 77000 | 2.45 | R-410A | 5.75
8683033 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVHFH |  |  |  | AM096KXVHFH | Non-Ducted Indoor Units | 92000 | 15.5 | 38.6 | 103000 | 4.65 | 103000 | 2.4 | R-410A | 7.6667
8683034 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVHJH |  |  |  | AM072KXVHJH | Non-Ducted Indoor Units | 69000 | 15.5 | 40 | 77000 | 4.5 | 77000 | 2.45 | R-410A | 5.75
8683035 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVHJH |  |  |  | AM096KXVHJH | Non-Ducted Indoor Units | 92000 | 15.5 | 38.6 | 103000 | 4.65 | 103000 | 2.4 | R-410A | 7.6667
8797068 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Non-Ducted Indoor Units | 69000 | 11.3 | 29.3 | 77000 | 3.41 | 77000 | 2.25 | R-410A | 5.75
8797069 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Non-Ducted Indoor Units | 92000 | 11.9 | 28.3 | 103000 | 3.61 | 103000 | 2.25 | R-410A | 7.6667
8797070 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Non-Ducted Indoor Units | 69000 | 11.3 | 29.3 | 77000 | 3.41 | 77000 | 2.25 | R-410A | 5.75
8797071 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Non-Ducted Indoor Units | 92000 | 11.9 | 28.3 | 103000 | 3.61 | 103000 | 2.25 | R-410A | 7.6667
7041873 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU |  |  |  | RXYQ72TTJU | Ducted Indoor Units | 69000 | 13.5 | 22.8 | 77000 | 3.58 | 43000 | 2.25 | R-410A | 5.75
7041874 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN |  |  |  | RXYQ72TYDN | Ducted Indoor Units | 69000 | 13.5 | 22.8 | 77000 | 3.58 | 43000 | 2.25 | R-410A | 5.75
7041875 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU |  |  |  | RXYQ72TTJU | Non-Ducted Indoor Units | 69000 | 15 | 26.5 | 77000 | 4.21 | 43000 | 2.49 | R-410A | 5.75
7041876 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN |  |  |  | RXYQ72TYDN | Non-Ducted Indoor Units | 69000 | 15 | 26.5 | 77000 | 4.21 | 43000 | 2.49 | R-410A | 5.75
7041877 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU |  |  |  | RXYQ96TTJU | Ducted Indoor Units | 92000 | 13 | 22.7 | 103000 | 3.99 | 67000 | 2.61 | R-410A | 7.6667
7041878 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN |  |  |  | RXYQ96TYDN | Ducted Indoor Units | 92000 | 13 | 22.7 | 103000 | 3.99 | 67000 | 2.61 | R-410A | 7.6667
7041879 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU |  |  |  | RXYQ96TTJU | Non-Ducted Indoor Units | 92000 | 15.1 | 28 | 103000 | 4.59 | 67000 | 2.86 | R-410A | 7.6667
7041880 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN |  |  |  | RXYQ96TYDN | Non-Ducted Indoor Units | 92000 | 15.1 | 28 | 103000 | 4.59 | 67000 | 2.86 | R-410A | 7.6667
7041881 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU |  |  |  | RXYQ120TTJU | Ducted Indoor Units | 114000 | 12.1 | 21.4 | 129000 | 3.46 | 85000 | 2.58 | R-410A | 9.5
7041882 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN |  |  |  | RXYQ120TYDN | Ducted Indoor Units | 114000 | 12.1 | 21.4 | 129000 | 3.46 | 85000 | 2.58 | R-410A | 9.5
7041883 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU |  |  |  | RXYQ120TTJU | Non-Ducted Indoor Units | 114000 | 13.2 | 23.5 | 129000 | 3.79 | 85000 | 2.61 | R-410A | 9.5
7041884 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN |  |  |  | RXYQ120TYDN | Non-Ducted Indoor Units | 114000 | 13.2 | 23.5 | 129000 | 3.79 | 85000 | 2.61 | R-410A | 9.5
7042709 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU |  |  |  | RXYQ72TTJU | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.25 | 24.65 | 77000 | 3.89 | 43000 | 2.37 | R-410A | 5.75
7042710 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN |  |  |  | RXYQ72TYDN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.25 | 24.65 | 77000 | 3.89 | 43000 | 2.37 | R-410A | 5.75
7042711 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU |  |  |  | RXYQ96TTJU | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.05 | 25.35 | 103000 | 4.29 | 67000 | 2.73 | R-410A | 7.6667
7042712 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN |  |  |  | RXYQ96TYDN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.05 | 25.35 | 103000 | 4.29 | 67000 | 2.73 | R-410A | 7.6667
7042713 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU |  |  |  | RXYQ120TTJU | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.65 | 22.45 | 129000 | 3.62 | 85000 | 2.59 | R-410A | 9.5
7042714 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN |  |  |  | RXYQ120TYDN | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.65 | 22.45 | 129000 | 3.62 | 85000 | 2.59 | R-410A | 9.5
7159057 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-96ME2U9 |  |  |  | U-96ME2U9 | Non-Ducted Indoor Units | 92000 | 12.5 | 25.3 | 103000 | 3.92 | 67000 | 2.71 | R-410A | 7.6667
7159060 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-120ME2U9 |  |  |  | U-120ME2U9 | Non-Ducted Indoor Units | 114000 | 12.1 | 26.4 | 129000 | 3.7 | 75000 | 2.48 | R-410A | 9.5
7160224 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-72ME2U9 |  |  |  | U-72ME2U9 | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 13.25 | 21.8 | 77000 | 4.08 | 52000 | 2.85 | R-410A | 6
7465339 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7465340 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7465341 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
7465342 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A) | Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
7465343 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A) | Non-Ducted Indoor Units | 114000 | 12.2 | 22.8 | 120000 | 3.66 | 80000 | 2.38 | R-410A | 9.5
7465344 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A) | Ducted Indoor Units | 114000 | 11.4 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
7465345 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7465346 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7465347 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
7465348 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A) | Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
7465349 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A) | Non-Ducted Indoor Units | 114000 | 12.2 | 22.8 | 120000 | 3.66 | 80000 | 2.38 | R-410A | 9.5
7465350 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A) | Ducted Indoor Units | 114000 | 11.4 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
7490338 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U |  |  |  | PUHY-P120TKMU-U | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
7490339 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U |  |  |  | PUHY-P120TKMU-U | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
7490340 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U |  |  |  | PUHY-P120YKMU-U | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
7490341 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U |  |  |  | PUHY-P120YKMU-U | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
7490413 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-U |  |  |  | PUHY-P72TKMU-U | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
7490415 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-U |  |  |  | PUHY-P72TKMU-U | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
7490417 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-U |  |  |  | PUHY-P72YKMU-U | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
7490419 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-U |  |  |  | PUHY-P72YKMU-U | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
7490421 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-U |  |  |  | PUHY-P96TKMU-U | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
7490423 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-U |  |  |  | PUHY-P96TKMU-U | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
7490424 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-U |  |  |  | PUHY-P96YKMU-U | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
7490425 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-U |  |  |  | PUHY-P96YKMU-U | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
7490427 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-U |  |  |  | PURY-P120TKMU-U | Non-Ducted Indoor Units | 114000 | 12.2 | 20.8 | 129000 | 3.61 | 92000 | 2.42 | R-410A | 9.5
7490429 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-U |  |  |  | PURY-P120YKMU-U | Non-Ducted Indoor Units | 114000 | 12.2 | 20.8 | 129000 | 3.61 | 92000 | 2.42 | R-410A | 9.5
7490464 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-U |  |  |  | PURY-P72TKMU-U | Ducted Indoor Units | 69000 | 13.9 | 21.1 | 76000 | 3.81 | 56000 | 2.62 | R-410A | 5.75
7490465 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-U |  |  |  | PURY-P72TKMU-U | Non-Ducted Indoor Units | 69000 | 15.5 | 22.1 | 76000 | 3.72 | 56000 | 2.49 | R-410A | 5.75
7490467 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-U |  |  |  | PURY-P72YKMU-U | Ducted Indoor Units | 69000 | 13.9 | 21.1 | 76000 | 3.81 | 56000 | 2.62 | R-410A | 5.75
7490468 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-U |  |  |  | PURY-P72YKMU-U | Non-Ducted Indoor Units | 69000 | 15.5 | 22.1 | 76000 | 3.72 | 56000 | 2.49 | R-410A | 5.75
7490470 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U |  |  |  | PURY-P96TKMU-U | Ducted Indoor Units | 92000 | 12.2 | 19.7 | 103000 | 3.64 | 76000 | 2.47 | R-410A | 7.6667
7490471 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U |  |  |  | PURY-P96TKMU-U | Non-Ducted Indoor Units | 92000 | 13.6 | 20.9 | 103000 | 3.71 | 76000 | 2.49 | R-410A | 7.6667
7490472 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U |  |  |  | PURY-P96YKMU-U | Ducted Indoor Units | 92000 | 12.2 | 19.7 | 103000 | 3.64 | 76000 | 2.47 | R-410A | 7.6667
7490473 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U |  |  |  | PURY-P96YKMU-U | Non-Ducted Indoor Units | 92000 | 13.6 | 20.9 | 103000 | 3.71 | 76000 | 2.49 | R-410A | 7.6667
7499011 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7499012 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7499013 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
7499014 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A) | Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
7499015 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A) | Non-Ducted Indoor Units | 112000 | 12.2 | 22.8 | 120000 | 3.66 | 80000 | 2.38 | R-410A | 9.3333
7499016 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7499017 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7499018 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
7499019 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A) | Ducted Indoor Units | 92000 | 12.3 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
7499020 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A) | Non-Ducted Indoor Units | 114000 | 12.2 | 22.5 | 120000 | 3.66 | 80000 | 2.38 | R-410A | 9.5
7499021 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A) | Ducted Indoor Units | 114000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
7499022 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A) | Ducted Indoor Units | 112000 | 11.4 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
7502097 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7502098 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7502109 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7502110 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7505310 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
7505311 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
7505343 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PBTJ |  |  |  | REYQ120PBTJ | Non-Ducted Indoor Units | 114000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.5
7505344 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PBYD |  |  |  | REYQ120PBYD | Non-Ducted Indoor Units | 114000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.5
7505355 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Ducted Indoor Units | 69000 | 13.8 | 21.3 | 77000 | 3.8 | 52000 | 2.6 | R-410A | 5.75
7505356 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Ducted Indoor Units | 69000 | 13.8 | 21.3 | 77000 | 3.8 | 52000 | 2.6 | R-410A | 5.75
7505357 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Non-Ducted Indoor Units | 92000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.6667
7505358 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Ducted Indoor Units | 92000 | 12.1 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.6667
7505359 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Non-Ducted Indoor Units | 92000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.6667
7505360 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Ducted Indoor Units | 92000 | 12.1 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.6667
7505428 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.6 | 23.2 | 77000 | 4 | 52000 | 2.77 | R-410A | 5.75
7505429 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.6 | 23.2 | 77000 | 4 | 52000 | 2.77 | R-410A | 5.75
7505430 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.65 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.6667
7505431 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.65 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.6667
7628329 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU |  |  |  | REYQ72TTJU | Non-Ducted Indoor Units | 67000 | 15.8 | 26.2 | 75000 | 4.29 | 54000 | 2.77 | R-410A | 5.5833
7628332 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN |  |  |  | REYQ72TYDN | Non-Ducted Indoor Units | 67000 | 15.8 | 26.2 | 75000 | 4.29 | 54000 | 2.77 | R-410A | 5.5833
7628545 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU |  |  |  | REYQ96TTJU | Non-Ducted Indoor Units | 90000 | 15.1 | 29.3 | 100000 | 4.25 | 70000 | 2.63 | R-410A | 7.5
7628548 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN |  |  |  | REYQ96TYDN | Non-Ducted Indoor Units | 90000 | 15.1 | 29.3 | 100000 | 4.25 | 70000 | 2.63 | R-410A | 7.5
7628550 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU |  |  |  | REYQ120TTJU | Non-Ducted Indoor Units | 111000 | 13.9 | 25.4 | 126000 | 3.98 | 86000 | 2.54 | R-410A | 9.25
7628553 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN |  |  |  | REYQ120TYDN | Non-Ducted Indoor Units | 111000 | 13.9 | 25.4 | 126000 | 3.98 | 86000 | 2.54 | R-410A | 9.25
7628613 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU |  |  |  | REYQ72TTJU | Ducted Indoor Units | 67000 | 13.4 | 21.1 | 75000 | 3.82 | 54000 | 2.63 | R-410A | 5.5833
7628614 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN |  |  |  | REYQ72TYDN | Ducted Indoor Units | 67000 | 13.4 | 21.1 | 75000 | 3.82 | 54000 | 2.63 | R-410A | 5.5833
7628617 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU |  |  |  | REYQ96TTJU | Ducted Indoor Units | 90000 | 13.1 | 24.3 | 100000 | 3.72 | 70000 | 2.31 | R-410A | 7.5
7628619 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN |  |  |  | REYQ96TYDN | Ducted Indoor Units | 90000 | 13.1 | 24.3 | 100000 | 3.72 | 70000 | 2.31 | R-410A | 7.5
7628621 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU |  |  |  | REYQ120TTJU | Ducted Indoor Units | 111000 | 12.6 | 22.6 | 126000 | 3.51 | 86000 | 2.32 | R-410A | 9.25
7628623 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN |  |  |  | REYQ120TYDN | Ducted Indoor Units | 111000 | 12.6 | 22.6 | 126000 | 3.51 | 86000 | 2.32 | R-410A | 9.25
7628952 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU |  |  |  | REYQ144TTJU | Non-Ducted Indoor Units | 134000 | 12.9 | 24.2 | 150000 | 3.81 | 106000 | 2.56 | R-410A | 11.1667
7628953 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN |  |  |  | REYQ144TYDN | Non-Ducted Indoor Units | 134000 | 12.9 | 24.2 | 150000 | 3.81 | 106000 | 2.56 | R-410A | 11.1667
7628979 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU |  |  |  | REYQ144TTJU | Ducted Indoor Units | 134000 | 11.9 | 22.2 | 150000 | 3.55 | 106000 | 2.35 | R-410A | 11.1667
7628982 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN |  |  |  | REYQ144TYDN | Ducted Indoor Units | 134000 | 11.9 | 22.2 | 150000 | 3.55 | 106000 | 2.35 | R-410A | 11.1667
7629573 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU |  |  |  | REYQ72TTJU | Mixed Ducted and Non-Ducted Indoor Units | 67000 | 14.6 | 23.65 | 75000 | 4.05 | 54000 | 2.7 | R-410A | 5.5833
7629575 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN |  |  |  | REYQ72TYDN | Mixed Ducted and Non-Ducted Indoor Units | 67000 | 14.6 | 23.65 | 75000 | 4.05 | 54000 | 2.7 | R-410A | 5.5833
7629577 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU |  |  |  | REYQ96TTJU | Mixed Ducted and Non-Ducted Indoor Units | 90000 | 14.1 | 26.8 | 100000 | 3.98 | 70000 | 2.47 | R-410A | 7.5
7629579 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN |  |  |  | REYQ96TYDN | Mixed Ducted and Non-Ducted Indoor Units | 90000 | 14.1 | 26.8 | 100000 | 3.98 | 70000 | 2.47 | R-410A | 7.5
7629581 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU |  |  |  | REYQ120TTJU | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 13.25 | 24 | 126000 | 3.74 | 86000 | 2.43 | R-410A | 9.25
7629584 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN |  |  |  | REYQ120TYDN | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 13.25 | 24 | 126000 | 3.74 | 86000 | 2.43 | R-410A | 9.25
7629586 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU |  |  |  | REYQ144TTJU | Mixed Ducted and Non-Ducted Indoor Units | 134000 | 12.4 | 23.2 | 150000 | 3.68 | 106000 | 2.45 | R-410A | 11.1667
7629589 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN |  |  |  | REYQ144TYDN | Mixed Ducted and Non-Ducted Indoor Units | 134000 | 12.4 | 23.2 | 150000 | 3.68 | 106000 | 2.45 | R-410A | 11.1667
7849629 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
7850819 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
7850823 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
7850839 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
7850843 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
7987126 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987127 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987128 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987129 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987130 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987131 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
7987172 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987173 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987174 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S |  |  |  | TVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987176 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S |  |  |  | TVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987218 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987219 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987220 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987221 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987222 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987223 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
7987264 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987265 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987266 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S |  |  |  | HVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987268 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S |  |  |  | HVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987310 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987311 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987312 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987313 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987314 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987315 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
7987356 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987357 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987358 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S |  |  |  | YVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987360 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S |  |  |  | YVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987403 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987404 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987405 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987406 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987407 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987408 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
7987409 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987410 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987411 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S |  |  |  | TVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987413 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S |  |  |  | TVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987415 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987416 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987417 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987418 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987419 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987420 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
7987421 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987422 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987423 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S |  |  |  | HVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987425 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S |  |  |  | HVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987427 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987428 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987429 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987430 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987431 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987432 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
7987433 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987434 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987435 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S |  |  |  | YVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987437 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S |  |  |  | YVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7990690 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990691 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990692 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 20.45 | 129000 | 3.65 | 89000 | 2.3 | R-410A | 9.5833
7990704 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990705 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990706 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.1 | 19.9 | 129000 | 3.66 | 89000 | 2.3 | R-410A | 9.5833
7990717 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990731 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990744 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990745 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990746 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 20.45 | 129000 | 3.65 | 89000 | 2.3 | R-410A | 9.5833
7990757 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990758 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990759 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.1 | 19.9 | 129000 | 3.66 | 89000 | 2.3 | R-410A | 9.5833
7990771 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990784 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990798 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990799 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990800 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 20.45 | 129000 | 3.65 | 89000 | 2.3 | R-410A | 9.5833
7990811 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990812 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990813 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.1 | 19.9 | 129000 | 3.66 | 89000 | 2.3 | R-410A | 9.5833
7990824 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990837 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
8175478 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
8175479 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
8175480 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
8175481 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
8175482 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
8175483 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
8175508 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
8175509 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
8175510 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
8175511 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
8175512 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
8175513 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
8175891 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.5 | 23.1 | 76000 | 3.65 | 56000 | 2.26 | R-410A | 5.75
8175892 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
8175893 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Ducted Indoor Units | 92000 | 12 | 24.1 | 103000 | 3.53 | 71000 | 2.28 | R-410A | 7.6667
8175894 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
8175895 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.9 | 129000 | 3.52 | 87000 | 2.26 | R-410A | 9.5
8175896 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
8175919 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.5 | 23.1 | 76000 | 3.65 | 56000 | 2.26 | R-410A | 5.75
8175920 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
8175921 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Ducted Indoor Units | 92000 | 12 | 24.1 | 103000 | 3.53 | 71000 | 2.28 | R-410A | 7.6667
8175922 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
8175923 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.9 | 129000 | 3.52 | 87000 | 2.26 | R-410A | 9.5
8175924 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
4677057 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ |  |  |  | RXYQ72PBTJ | Non-Ducted Indoor Units | 69000 | 14.1 | 25.8 | 77000 | 4 | 51000 | 2.65 | R-410A | 5.75
4677058 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ |  |  |  | RXYQ72PBTJ | Ducted Indoor Units | 69000 | 12.8 | 21.5 | 77000 | 3.71 | 51000 | 2.4 | R-410A | 5.75
4677059 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ |  |  |  | RXYQ72PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.65 | 77000 | 3.85 | 51000 | 2.52 | R-410A | 5.75
4677060 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ |  |  |  | RXYQ96PBTJ | Non-Ducted Indoor Units | 92000 | 13.5 | 23 | 103000 | 4.2 | 67000 | 2.85 | R-410A | 7.6667
4677062 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ |  |  |  | RXYQ96PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13 | 20.9 | 103000 | 3.92 | 67000 | 2.67 | R-410A | 7.6667
4677063 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ120PBTJ |  |  |  | RXYQ120PBTJ | Non-Ducted Indoor Units | 114000 | 12.5 | 20.4 | 129000 | 3.8 | 84000 | 2.65 | R-410A | 9.5
4677090 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD |  |  |  | RXYQ72PBYD | Non-Ducted Indoor Units | 69000 | 14.1 | 25.8 | 77000 | 4 | 51000 | 2.65 | R-410A | 5.75
4677091 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD |  |  |  | RXYQ72PBYD | Ducted Indoor Units | 69000 | 12.8 | 21.5 | 77000 | 3.71 | 51000 | 2.4 | R-410A | 5.75
4677092 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD |  |  |  | RXYQ72PBYD | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.65 | 77000 | 3.85 | 51000 | 2.52 | R-410A | 5.75
4677093 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD |  |  |  | RXYQ96PBYD | Non-Ducted Indoor Units | 92000 | 13.5 | 23 | 103000 | 4.2 | 67000 | 2.85 | R-410A | 7.6667
4677095 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD |  |  |  | RXYQ96PBYD | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13 | 20.9 | 103000 | 3.92 | 67000 | 2.67 | R-410A | 7.6667
4677096 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ120PBYD |  |  |  | RXYQ120PBYD | Non-Ducted Indoor Units | 114000 | 12.5 | 20.4 | 129000 | 3.8 | 84000 | 2.65 | R-410A | 9.5
4677123 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PBTJ |  |  |  | REYQ120PBTJ | Non-Ducted Indoor Units | 114000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.5
4679526 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 |  |  |  | ARUB072BT3 | Ducted Indoor Units | 69000 | 12.4 | 21.8 | 77000 | 3.62 | 51000 | 2.47 | R-410A | 5.75
4679527 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 |  |  |  | ARUB072BT3 | Non-Ducted Indoor Units | 69000 | 13.6 | 24.5 | 77000 | 3.87 | 51000 | 2.59 | R-410A | 5.75
4679528 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 |  |  |  | ARUB072DT3 | Ducted Indoor Units | 69000 | 12.4 | 21.8 | 77000 | 3.62 | 51000 | 2.47 | R-410A | 5.75
4679529 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 |  |  |  | ARUB072DT3 | Non-Ducted Indoor Units | 69000 | 13.6 | 24.5 | 77000 | 3.87 | 51000 | 2.59 | R-410A | 5.75
4679530 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BT3 |  |  |  | ARUB096BT3 | Ducted Indoor Units | 92000 | 12.6 | 20.2 | 103000 | 3.57 | 67000 | 2.63 | R-410A | 7.6667
4679531 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BT3 |  |  |  | ARUB096BT3 | Non-Ducted Indoor Units | 92000 | 14.3 | 23.2 | 103000 | 3.88 | 67000 | 2.75 | R-410A | 7.6667
4679532 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DT3 |  |  |  | ARUB096DT3 | Ducted Indoor Units | 92000 | 12.6 | 20.2 | 103000 | 3.57 | 67000 | 2.63 | R-410A | 7.6667
4679533 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DT3 |  |  |  | ARUB096DT3 | Non-Ducted Indoor Units | 92000 | 14.3 | 23.2 | 103000 | 3.88 | 67000 | 2.75 | R-410A | 7.6667
4679534 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BT3 |  |  |  | ARUB121BT3 | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
4679535 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BT3 |  |  |  | ARUB121BT3 | Non-Ducted Indoor Units | 114000 | 12.9 | 20.6 | 129000 | 3.73 | 84000 | 2.67 | R-410A | 9.5
4679536 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DT3 |  |  |  | ARUB121DT3 | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
4679537 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DT3 |  |  |  | ARUB121DT3 | Non-Ducted Indoor Units | 114000 | 12.9 | 20.6 | 129000 | 3.73 | 84000 | 2.67 | R-410A | 9.5
4679570 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 |  |  |  | ARUN072BT3 | Ducted Indoor Units | 69000 | 12.4 | 21.8 | 77000 | 3.62 | 51000 | 2.47 | R-410A | 5.75
4679571 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 |  |  |  | ARUN072BT3 | Non-Ducted Indoor Units | 69000 | 13.6 | 24.5 | 77000 | 3.87 | 51000 | 2.59 | R-410A | 5.75
4679572 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 |  |  |  | ARUN072DT3 | Ducted Indoor Units | 69000 | 12.4 | 21.8 | 77000 | 3.62 | 51000 | 2.47 | R-410A | 5.75
4679573 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 |  |  |  | ARUN072DT3 | Non-Ducted Indoor Units | 69000 | 13.6 | 24.5 | 77000 | 3.87 | 51000 | 2.59 | R-410A | 5.75
4679574 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BT3 |  |  |  | ARUN096BT3 | Ducted Indoor Units | 92000 | 12.6 | 20.2 | 103000 | 3.57 | 67000 | 2.63 | R-410A | 7.6667
4679575 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BT3 |  |  |  | ARUN096BT3 | Non-Ducted Indoor Units | 92000 | 14.3 | 23.2 | 103000 | 3.88 | 67000 | 2.75 | R-410A | 7.6667
4679576 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DT3 |  |  |  | ARUN096DT3 | Ducted Indoor Units | 92000 | 12.6 | 20.2 | 103000 | 3.57 | 67000 | 2.63 | R-410A | 7.6667
4679577 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DT3 |  |  |  | ARUN096DT3 | Non-Ducted Indoor Units | 92000 | 14.3 | 23.2 | 103000 | 3.88 | 67000 | 2.75 | R-410A | 7.6667
4679578 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BT3 |  |  |  | ARUN121BT3 | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
4679579 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BT3 |  |  |  | ARUN121BT3 | Non-Ducted Indoor Units | 114000 | 12.9 | 20.6 | 129000 | 3.73 | 84000 | 2.67 | R-410A | 9.5
4679580 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DT3 |  |  |  | ARUN121DT3 | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
4679581 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DT3 |  |  |  | ARUN121DT3 | Non-Ducted Indoor Units | 114000 | 12.9 | 20.6 | 129000 | 3.73 | 84000 | 2.67 | R-410A | 9.5
5039448 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
5039449 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Ducted Indoor Units | 69000 | 13.8 | 21.3 | 77000 | 3.8 | 52000 | 2.6 | R-410A | 5.75
5039450 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.6 | 23.2 | 77000 | 4 | 52000 | 2.77 | R-410A | 5.75
5039451 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PBYD |  |  |  | REYQ120PBYD | Non-Ducted Indoor Units | 114000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.5
5198211 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV |  |  |  | AOUA72RLBV | Non-Ducted Indoor Units | 69000 | 12.5 | 21.7 | 77000 | 3.76 | 56000 | 2.3 | R-410A | 5.75
5198213 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV |  |  |  | AOUA72RLBV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 19.95 | 77000 | 3.7 | 56000 | 2.3 | R-410A | 5.75
5198214 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV |  |  |  | AOUA96RLBV | Non-Ducted Indoor Units | 92000 | 11.7 | 20.8 | 103000 | 3.55 | 73000 | 2.5 | R-410A | 7.6667
5198216 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV |  |  |  | AOUA96RLBV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.65 | 19.3 | 103000 | 3.51 | 73000 | 2.45 | R-410A | 7.6667
5358519 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
5358520 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
5358521 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 20.55 | 76000 | 4.01 | 56000 | 2.49 | R-410A | 5.75
5358522 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
5358523 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
5358524 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.15 | 20.2 | 103000 | 4.08 | 76000 | 2.69 | R-410A | 7.6667
5358525 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
5358526 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
5358527 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.6 | 19.1 | 129000 | 3.74 | 92000 | 2.44 | R-410A | 9.5
5358561 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
5358562 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
5358563 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 20.55 | 76000 | 4.01 | 56000 | 2.49 | R-410A | 5.75
5358564 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
5358565 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
5358566 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.15 | 20.2 | 103000 | 4.08 | 76000 | 2.69 | R-410A | 7.6667
5358567 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
5358568 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
5358569 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.6 | 19.1 | 129000 | 3.74 | 92000 | 2.44 | R-410A | 9.5
5358600 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Ducted Indoor Units | 69000 | 13.9 | 21.1 | 76000 | 3.81 | 56000 | 2.62 | R-410A | 5.75
5358601 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Non-Ducted Indoor Units | 69000 | 15.5 | 20.9 | 76000 | 3.66 | 56000 | 2.45 | R-410A | 5.75
5358602 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.7 | 21.6 | 76000 | 3.73 | 56000 | 2.53 | R-410A | 5.75
5358603 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Ducted Indoor Units | 92000 | 12.2 | 19.7 | 103000 | 3.64 | 76000 | 2.47 | R-410A | 7.6667
5358604 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Non-Ducted Indoor Units | 92000 | 13.6 | 20.1 | 103000 | 3.66 | 76000 | 2.46 | R-410A | 7.6667
5358605 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.9 | 20.3 | 103000 | 3.65 | 76000 | 2.46 | R-410A | 7.6667
5358607 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A |  |  |  | PURY-P120YKMU-A | Non-Ducted Indoor Units | 114000 | 12.2 | 20.3 | 129000 | 3.57 | 92000 | 2.4 | R-410A | 9.5
5358608 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A |  |  |  | PURY-P120YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.95 | 19.7 | 129000 | 3.51 | 92000 | 2.35 | R-410A | 9.5
5358633 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Ducted Indoor Units | 92000 | 12.2 | 19.7 | 103000 | 3.64 | 76000 | 2.47 | R-410A | 7.6667
5358634 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Non-Ducted Indoor Units | 92000 | 13.6 | 20.1 | 103000 | 3.66 | 76000 | 2.46 | R-410A | 7.6667
5358635 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.9 | 20.3 | 103000 | 3.65 | 76000 | 2.46 | R-410A | 7.6667
5358637 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A |  |  |  | PURY-P120TKMU-A | Non-Ducted Indoor Units | 114000 | 12.2 | 20.3 | 129000 | 3.57 | 92000 | 2.4 | R-410A | 9.5
5358638 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A |  |  |  | PURY-P120TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.95 | 19.7 | 129000 | 3.51 | 92000 | 2.35 | R-410A | 9.5
5359039 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Ducted Indoor Units | 69000 | 13.9 | 21.1 | 76000 | 3.81 | 56000 | 2.62 | R-410A | 5.75
5359040 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Non-Ducted Indoor Units | 69000 | 15.5 | 20.9 | 76000 | 3.66 | 56000 | 2.45 | R-410A | 5.75
5359041 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.7 | 21.6 | 76000 | 3.73 | 56000 | 2.53 | R-410A | 5.75
5360175 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Non-Ducted Indoor Units | 92000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.6667
5360176 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Ducted Indoor Units | 92000 | 12.1 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.6667
5360177 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.65 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.6667
5360178 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Non-Ducted Indoor Units | 92000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.6667
5360179 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Ducted Indoor Units | 92000 | 12.1 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.6667
5360180 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.65 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.6667
5360174 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.6 | 23.2 | 77000 | 4 | 52000 | 2.77 | R-410A | 5.75
5360173 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Ducted Indoor Units | 69000 | 13.8 | 21.3 | 77000 | 3.8 | 52000 | 2.6 | R-410A | 5.75
5360172 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
5733023 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Non-Ducted Indoor Units | 92000 | 11.5 | 27.9 | 103000 | 3.47 | 67000 | 2.25 | R-410A | 7.6667
5733027 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Non-Ducted Indoor Units | 92000 | 11.5 | 27.9 | 103000 | 3.47 | 67000 | 2.25 | R-410A | 7.6667
5924239 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT9UL |  |  |  | MMY-MAP0724HT9UL | Mixed Ducted and Non-Ducted Indoor Units | 70000 | 11.25 | 19.3 | 81000 | 3.48 | 42000 | 2.44 | R-410A | 5.8333
5924240 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT6UL |  |  |  | MMY-MAP0724HT6UL | Mixed Ducted and Non-Ducted Indoor Units | 70000 | 11.25 | 18.9 | 81000 | 3.48 | 42000 | 2.44 | R-410A | 5.8333
6334547 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT9UL |  |  |  | MMY-MAP0724FT9UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.7 | 19.05 | 77000 | 3.41 | 55000 | 2.33 | R-410A | 5.75
6334567 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT9UL |  |  |  | MMY-MAP0724FT9UL | Non-Ducted Indoor Units | 69000 | 11.7 | 21.5 | 77000 | 3.46 | 55000 | 2.34 | R-410A | 5.75
6334568 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT9UL |  |  |  | MMY-MAP0964FT9UL | Non-Ducted Indoor Units | 92000 | 11.7 | 20 | 103000 | 3.4 | 60000 | 2.27 | R-410A | 7.6667
6334574 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT6UL |  |  |  | MMY-MAP0724FT6UL | Non-Ducted Indoor Units | 69000 | 11.7 | 20.9 | 77000 | 3.46 | 55000 | 2.34 | R-410A | 5.75
6334575 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT6UL |  |  |  | MMY-MAP0964FT6UL | Non-Ducted Indoor Units | 92000 | 11.7 | 19.6 | 103000 | 3.4 | 60000 | 2.27 | R-410A | 7.6667
6687540 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
6687544 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
201874139 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
201874140 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
201874147 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
201874148 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
201874150 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
201874151 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
201978071 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
201978072 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
201978090 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
201978091 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
201978092 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
201981539 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
201992872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
201992873 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Non-Ducted Indoor Units | 92000 | 13.6 | 24.3 | 103000 | 4.33 | 72000 | 2.66 | R-410A | 7.6667
201992874 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Non-Ducted Indoor Units | 114000 | 12.5 | 23.3 | 129000 | 3.89 | 88000 | 2.58 | R-410A | 9.5
202021882 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Ducted Indoor Units | 92000 | 11.4 | 18.9 | 103000 | 3.61 | 72000 | 2.32 | R-410A | 7.6667
202021883 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Ducted Indoor Units | 114000 | 11.1 | 19 | 129000 | 3.54 | 88000 | 2.3 | R-410A | 9.5
202022800 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 21.6 | 103000 | 3.97 | 72000 | 2.49 | R-410A | 7.6667
202022801 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 21.15 | 129000 | 3.71 | 88000 | 2.44 | R-410A | 9.5
202022845 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202022846 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202073573 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073574 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.35 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202073576 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073577 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.35 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202073579 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073580 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202073582 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073583 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202515348 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 |  |  |  | ARUN072DTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
202606694 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606695 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606696 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606697 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606699 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606700 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606701 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606702 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606703 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606704 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606705 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606706 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606707 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606708 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606709 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606710 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606711 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606712 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606713 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606714 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606715 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606716 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606717 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606730 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606731 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606732 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606736 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606737 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606738 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606742 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606743 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606744 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606745 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S |  |  |  | TVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606746 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S |  |  |  | HVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606747 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S |  |  |  | YVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606748 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606749 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606750 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606751 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S |  |  |  | TVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606752 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S |  |  |  | HVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606753 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S |  |  |  | YVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606760 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606761 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606762 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606763 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606764 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606765 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606766 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
202606767 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
202606768 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
202606772 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
202606773 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
202606774 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
202607341 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607342 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607343 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607344 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607345 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607346 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607347 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607348 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607349 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607350 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607351 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607352 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607353 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607354 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607355 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607356 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607357 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607358 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607359 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607360 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607361 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607362 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607363 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607364 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607365 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607366 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607367 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607368 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607369 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607370 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607371 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607372 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607373 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607374 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607375 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607376 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607377 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607378 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607379 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607380 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607381 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607382 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607383 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607384 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607385 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607386 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607387 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607388 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607389 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607390 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607391 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607392 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607393 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607394 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607395 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607396 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607397 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607398 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607399 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607400 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607451 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607452 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607453 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607454 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S |  |  |  | TVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607455 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S |  |  |  | HVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607456 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S |  |  |  | YVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607457 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607458 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607459 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607460 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S |  |  |  | TVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607461 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S |  |  |  | HVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607462 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S |  |  |  | YVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607463 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607464 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607465 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607466 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607467 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607468 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607469 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607470 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607471 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607472 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607473 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607474 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607926 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607927 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607928 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607929 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607930 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607931 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607932 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607933 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607934 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607935 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607936 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607937 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607956 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607957 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607958 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607959 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607960 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607961 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607962 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607963 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607964 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607965 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607966 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607967 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607980 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607981 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607982 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607983 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607984 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607985 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607986 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607987 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607988 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607989 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607990 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607991 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
203906567 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906568 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906569 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906570 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906571 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906573 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906599 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906600 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906601 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906602 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906603 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906604 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906605 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906606 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906607 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906608 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906609 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906610 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906612 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906613 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906614 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906615 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906616 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906617 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906618 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906619 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906620 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906621 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906622 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906624 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906625 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906626 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906627 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906628 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906629 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906630 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906631 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906632 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906633 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906634 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906635 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906636 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906637 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906638 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906639 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906640 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906641 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906642 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906643 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906644 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906646 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906647 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906648 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906649 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906650 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906651 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906652 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906653 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906654 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906655 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906656 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906657 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906658 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906660 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906661 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906662 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906713 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906714 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906715 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906716 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906717 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906718 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906719 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906720 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906721 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906722 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906723 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906725 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203993607 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993609 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993611 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993614 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993616 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993618 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
204268347 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268350 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268352 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268375 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268376 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268378 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268392 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268393 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268394 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268408 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268409 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268410 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268424 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268425 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268426 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268441 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268442 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268443 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268471 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268472 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268473 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268495 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268497 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268499 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268530 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268531 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268533 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268557 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268558 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268559 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268580 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268581 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268582 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268596 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268597 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268598 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204269024 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269025 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269026 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269040 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269041 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269042 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269056 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269057 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269058 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269072 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269073 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269074 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269088 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269089 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269090 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269104 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269105 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269106 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204442744 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
204442792 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
204572223 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572238 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572253 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572268 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572282 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572283 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204572290 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572291 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204572298 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572299 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204572306 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572307 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
205000511 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
8656991 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72ZKMU-A |  |  |  | PURY-P72ZKMU-A | Ducted Indoor Units | 69000 | 12.5 | 21.6 | 76000 | 3.51 | 56000 | 2.26 | R-410A | 5.75
8657015 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A |  |  |  | PUHY-P120ZKMU-A | Ducted Indoor Units | 114000 | 12.5 | 21.4 | 129000 | 3.62 | 92000 | 2.51 | R-410A | 9.5
8657013 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Ducted Indoor Units | 92000 | 12.3 | 22.4 | 103000 | 3.73 | 76000 | 2.71 | R-410A | 7.6667
8657011 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Ducted Indoor Units | 69000 | 13 | 22.5 | 76000 | 3.74 | 56000 | 2.59 | R-410A | 5.75
8656995 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120ZKMU-A |  |  |  | PURY-P120ZKMU-A | Ducted Indoor Units | 114000 | 12.2 | 19.5 | 129000 | 3.4 | 87000 | 2.26 | R-410A | 9.5
8656993 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A |  |  |  | PURY-P96ZKMU-A | Ducted Indoor Units | 92000 | 11.8 | 20.5 | 103000 | 3.5 | 71000 | 2.26 | R-410A | 7.6667
206453544 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
206453541 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
206453576 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
205287345 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
205281463 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
205281460 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
205281457 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202566095 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202566098 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
202566099 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
202566100 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
202566101 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
202534320 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 |  |  |  | ARUB096CTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202534321 | 1/1/2027 | LG | HMSR-A-CB | ARUB121CTE4 |  |  |  | ARUB121CTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202534332 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 |  |  |  | ARUB096CTE4 | Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.71 | 67000 | 2.71 | R-410A | 7.6667
202534333 | 1/1/2027 | LG | HMSR-A-CB | ARUB121CTE4 |  |  |  | ARUB121CTE4 | Ducted Indoor Units | 114000 | 12.5 | 21.8 | 129000 | 3.5 | 84000 | 2.57 | R-410A | 9.5
202534344 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 |  |  |  | ARUN096CTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202534345 | 1/1/2027 | LG | HMSV-A-CB | ARUN121CTE4 |  |  |  | ARUN121CTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202534356 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 |  |  |  | ARUN096CTE4 | Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.71 | 67000 | 2.71 | R-410A | 7.6667
202534357 | 1/1/2027 | LG | HMSV-A-CB | ARUN121CTE4 |  |  |  | ARUN121CTE4 | Ducted Indoor Units | 114000 | 12.5 | 21.8 | 129000 | 3.5 | 84000 | 2.57 | R-410A | 9.5
202515498 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 |  |  |  | ARUN072CTE4 | Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 3.81 | 51000 | 2.52 | R-410A | 5.75
202515499 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 |  |  |  | ARUN072CTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
202515495 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 |  |  |  | ARUB072CTE4 | Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 3.81 | 51000 | 2.52 | R-410A | 5.75
202515496 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 |  |  |  | ARUB072CTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
10619421 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120ZKMU-A |  |  |  | PURY-P120ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.7 | 20.9 | 129000 | 3.45 | 87000 | 2.26 | R-410A | 9.5
10619422 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A |  |  |  | PURY-P96ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 21.6 | 103000 | 3.48 | 71000 | 2.26 | R-410A | 7.6667
200084008 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R72WMBK |  |  |  | V5BV-R72WMBK | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
200084009 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R72WMBK |  |  |  | V5BV-R72WMBK | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
200084010 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R72WMBK |  |  |  | V5BV-R72WMBK | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
10509441 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
10509442 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9088681 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 |  |  |  | IOV096H3CDC736 | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
9956570 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
200084026 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Non-Ducted Indoor Units | 111000 | 11.5 | 24 | 126000 | 3.5 | 83000 | 2.25 | R-410A | 9.25
200084027 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Non-Ducted Indoor Units | 111000 | 11.5 | 24 | 126000 | 3.5 | 83000 | 2.25 | R-410A | 9.25
200084028 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Non-Ducted Indoor Units | 111000 | 11.5 | 24 | 126000 | 3.5 | 83000 | 2.25 | R-410A | 9.25
10306437 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
9956572 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
200084017 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
200084018 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
200084019 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
202515518 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 |  |  |  | ARUB072DTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
202515519 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 |  |  |  | ARUB072DTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
203398521 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72W/A-F(U) |  |  |  | GMV-VQ72W/A-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 21 | 77000 | 3.4 | 60000 | 2.25 | R-410A | 5.75
203293238 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Ducted Indoor Units | 69000 | 11.2 | 20 | 77000 | 3.4 | 60000 | 2.25 | R-410A | 5.75
202515493 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 |  |  |  | ARUB072BTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
208102008 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
208102010 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
10306435 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9088674 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 |  |  |  | IOV072H3CDC712 | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
9088679 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 |  |  |  | IOV096H3CDC736 | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9088684 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC714 |  |  |  | IOV120H3CDC714 | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
9088672 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 |  |  |  | IOV072H3CDC712 | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10479767 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.25 | 20.5 | 77000 | 3.55 | 60000 | 2.25 | R-410A | 5.75
7835428 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
7845593 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
202515494 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 |  |  |  | ARUB072BTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
10274220 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-072UHSPB |  |  |  | AVWT-072UHSPB | Ducted Indoor Units | 69000 | 13.2 | 23.5 | 76000 | 4 | 55000 | 2.6 | R-410A | 5.75
10274221 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-072UHSPB |  |  |  | AVWT-072UHSPB | Non-Ducted Indoor Units | 69000 | 15.6 | 31.8 | 76000 | 4.9 | 55000 | 3 | R-410A | 5.75
10274222 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-096UHSQB |  |  |  | AVWT-096UHSQB | Ducted Indoor Units | 92000 | 11.8 | 23.8 | 103000 | 3.7 | 76000 | 2.5 | R-410A | 7.6667
10274223 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-096UHSQB |  |  |  | AVWT-096UHSQB | Non-Ducted Indoor Units | 92000 | 12.2 | 26.4 | 103000 | 4.5 | 76000 | 2.9 | R-410A | 7.6667
10274224 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120UHSQB |  |  |  | AVWT-120UHSQB | Ducted Indoor Units | 114000 | 11.5 | 23.5 | 126000 | 3.7 | 89000 | 2.3 | R-410A | 9.5
10274225 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120UHSQB |  |  |  | AVWT-120UHSQB | Non-Ducted Indoor Units | 114000 | 12.1 | 26.5 | 126000 | 4.2 | 89000 | 2.6 | R-410A | 9.5
10274227 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-096UHSQB |  |  |  | AVWT-096UHSQB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12 | 25.1 | 103000 | 4.1 | 76000 | 2.7 | R-410A | 7.6667
10274228 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120UHSQB |  |  |  | AVWT-120UHSQB | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 25 | 126000 | 3.95 | 89000 | 2.45 | R-410A | 9.5
9119332 | 1/1/2027 | LG | HMSV-A-CB | ARUN072QTE4 |  |  |  | ARUN072QTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
9119333 | 1/1/2027 | LG | HMSV-A-CB | ARUN072QTE4 |  |  |  | ARUN072QTE4 | Non-Ducted Indoor Units | 69000 | 14.5 | 29 | 77000 | 4.3 | 51000 | 2.75 | R-410A | 5.75
9119334 | 1/1/2027 | LG | HMSV-A-CB | ARUN096QTE4 |  |  |  | ARUN096QTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
9119335 | 1/1/2027 | LG | HMSV-A-CB | ARUN096QTE4 |  |  |  | ARUN096QTE4 | Non-Ducted Indoor Units | 92000 | 15.1 | 38.5 | 103000 | 4.3 | 67000 | 2.82 | R-410A | 7.6667
9119336 | 1/1/2027 | LG | HMSV-A-CB | ARUN121QTE4 |  |  |  | ARUN121QTE4 | Ducted Indoor Units | 114000 | 12.6 | 23 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
9119337 | 1/1/2027 | LG | HMSV-A-CB | ARUN121QTE4 |  |  |  | ARUN121QTE4 | Non-Ducted Indoor Units | 114000 | 14.5 | 29 | 129000 | 3.9 | 84000 | 2.72 | R-410A | 9.5
203400951 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-72U8SNB |  |  |  | AVWT-72U8SNB | Ducted Indoor Units | 69000 | 12.3 | 23 | 76000 | 3.55 | 52000 | 2.35 | R-410A | 5.75
203400952 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-72U8SNB |  |  |  | AVWT-72U8SNB | Non-Ducted Indoor Units | 69000 | 15 | 30.7 | 76000 | 4.2 | 52000 | 2.84 | R-410A | 5.75
203400953 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-72U8SNB |  |  |  | AVWT-72U8SNB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 26.85 | 76000 | 3.87 | 52000 | 2.59 | R-410A | 5.75
10562601 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-072U8SNB |  |  |  | AVWT-072U8SNB | Ducted Indoor Units | 69000 | 12.3 | 23 | 76000 | 3.55 | 52000 | 2.35 | R-410A | 5.75
10562602 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-072U8SNB |  |  |  | AVWT-072U8SNB | Non-Ducted Indoor Units | 69000 | 15 | 30.7 | 76000 | 4.2 | 52000 | 2.84 | R-410A | 5.75
10567397 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120U8STB |  |  |  | AVWT-120U8STB | Non-Ducted Indoor Units | 115000 | 13.2 | 30.55 | 129000 | 4.12 | 83000 | 2.72 | R-410A | 9.5833
10567398 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120U8STB |  |  |  | AVWT-120U8STB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.4 | 26.97 | 129000 | 3.73 | 83000 | 2.51 | R-410A | 9.5833
10594382 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-96U8STB |  |  |  | AVWT-96U8STB | Ducted Indoor Units | 92000 | 12.25 | 23.3 | 103000 | 3.45 | 67000 | 2.3 | R-410A | 7.6667
10594383 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-96U8STB |  |  |  | AVWT-96U8STB | Non-Ducted Indoor Units | 92000 | 14.15 | 31.65 | 103000 | 4.1 | 67000 | 2.6 | R-410A | 7.6667
10594384 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-96U8STB |  |  |  | AVWT-96U8STB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.2 | 27.47 | 103000 | 3.77 | 67000 | 2.45 | R-410A | 7.6667
209842408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209863184 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209863185 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH | AM120BXVTFH |  |  | AM240BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209842409 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH | AM120BXVTFH |  |  | AM240BXVTFH | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209842427 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842437 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209863193 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209863194 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209842438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209842428 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842429 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH | AM120BXVTJH |  |  | AM240BXVTJH | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209863195 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH | AM120BXVTJH |  |  | AM240BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209863173 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209842199 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209842189 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842190 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842200 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209863174 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209863175 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR | AM120BXVTFR |  |  | AM240BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209842191 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR | AM120BXVTFR |  |  | AM240BXVTFR | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209842447 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842457 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209863203 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209863204 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209842458 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209842448 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842449 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR | AM120BXVTJR |  |  | AM240BXVTJR | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209863205 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR | AM120BXVTJR |  |  | AM240BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209863183 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209842407 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842417 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
213893744 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN |  |  | TUHYE2163BN41AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916727 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN |  |  | TUHYE2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213916731 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN |  |  | TUHYE2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893745 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN |  |  | TUHYE2164BN41AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
208812545 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812546 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931865 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.3 | 24.3 | 154000 | 3.94 | 106000 | 2.44 | R-410A | 11.5
208931867 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.85 | 22.8 | 180000 | 3.69 | 124000 | 2.31 | R-410A | 13.3333
208931869 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.95 | 206000 | 3.48 | 140000 | 2.19 | R-410A | 15.3333
208812550 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812551 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931887 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.3 | 24.3 | 154000 | 3.94 | 106000 | 2.44 | R-410A | 11.5
208931889 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.85 | 22.8 | 180000 | 3.69 | 124000 | 2.31 | R-410A | 13.3333
208931891 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.95 | 206000 | 3.48 | 140000 | 2.19 | R-410A | 15.3333
207168488 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* | MVHP096ME4CA* |  |  | MVHP168ME4CA* | Ducted Indoor Units | 161000 | 11.4 | 21.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168489 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* | MVHP096ME4CA* |  |  | MVHP168ME4CA* | Non-Ducted Indoor Units | 161000 | 11.6 | 22.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168490 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* | MVHR096ME4CA* |  |  | MVHR168ME4CA* | Ducted Indoor Units | 161000 | 11.2 | 20.7 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168491 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* | MVHR096ME4CA* |  |  | MVHR168ME4CA* | Non-Ducted Indoor Units | 161000 | 11.4 | 22 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168492 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* | MVHP096ME4CA* |  |  | MVHP192ME4CA* | Ducted Indoor Units | 184000 | 11.1 | 20.6 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168493 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* | MVHP096ME4CA* |  |  | MVHP192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.6 | 21.4 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168494 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* | MVHR096ME4CA* |  |  | MVHR192ME4CA* | Ducted Indoor Units | 184000 | 11.2 | 19.7 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168495 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* | MVHR096ME4CA* |  |  | MVHR192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.4 | 20.4 | 206000 | 3.4 | 138000 | 2.3 | R-410A | 15.3333
207168496 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* | MVHP096ME4CA* |  |  | MVHP216ME4CA* | Ducted Indoor Units | 207000 | 10.9 | 20.7 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168497 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* | MVHP096ME4CA* |  |  | MVHP216ME4CA* | Non-Ducted Indoor Units | 207000 | 11.5 | 20.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168498 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* | MVHR096ME4CA* |  |  | MVHR216ME4CA* | Ducted Indoor Units | 207000 | 10.9 | 19.8 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168499 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* | MVHR096ME4CA* |  |  | MVHR216ME4CA* | Non-Ducted Indoor Units | 207000 | 11.4 | 19.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
206568895 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME4CA* |  |  |  | MVHP144ME4CA* | Ducted Indoor Units | 138000 | 11.7 | 21.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568896 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME4CA* |  |  |  | MVHP144ME4CA* | Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568897 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME4CA* |  |  |  | MVHR144ME4CA* | Ducted Indoor Units | 138000 | 11 | 20.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568898 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME4CA* |  |  |  | MVHR144ME4CA* | Non-Ducted Indoor Units | 138000 | 11.4 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
9133446 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC96KHP/220V |  |  | TVRF-OC192KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.15 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
9133487 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC240KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 21.7 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
206799442 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799468 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799476 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799450 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000547 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
206799456 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
207699045 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.3 | 25.8 | 206000 | 3.66 | 206000 | 2.2 | R-410A | 15.3333
207699041 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
10267483 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-240WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
201903115 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
208102040 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
205000512 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR |  |  |  | AM168HXVAFR | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
205000544 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR |  |  |  | AM168HXVAJR | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
204442716 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAFH |  |  |  | AM192HXVAFH | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
204442731 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH |  |  |  | AM192HXVAJH | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
212512539 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 11.45 | 21.5 | 162000 | 3.67 | 109000 | 2.55 | R-410A | 12
212512452 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Non-Ducted Indoor Units | 144000 | 11.8 | 23 | 162000 | 3.77 | 109000 | 2.57 | R-410A | 12
212512453 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Ducted Indoor Units | 144000 | 11.1 | 20 | 162000 | 3.57 | 109000 | 2.54 | R-410A | 12
9989457 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 200000 | 3.85 | 146000 | 2.38 | R-410A | 15.3333
9989794 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Ducted Indoor Units | 184000 | 12.3 | 21.1 | 200000 | 3.67 | 146000 | 2.26 | R-410A | 15.3333
9989849 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 22 | 200000 | 3.76 | 146000 | 2.32 | R-410A | 15.3333
9989850 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 22 | 200000 | 3.76 | 146000 | 2.32 | R-410A | 15.3333
9989795 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Ducted Indoor Units | 184000 | 12.3 | 21.1 | 200000 | 3.67 | 146000 | 2.26 | R-410A | 15.3333
9989782 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 200000 | 3.85 | 146000 | 2.38 | R-410A | 15.3333
9989799 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Non-Ducted Indoor Units | 228000 | 11.9 | 21.9 | 250000 | 3.68 | 178000 | 2.24 | R-410A | 19
9989796 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Ducted Indoor Units | 206000 | 12.2 | 20.8 | 226000 | 3.66 | 160000 | 2.18 | R-410A | 17.1667
9989759 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Non-Ducted Indoor Units | 206000 | 12.5 | 23 | 226000 | 3.74 | 160000 | 2.32 | R-410A | 17.1667
9989851 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 21.9 | 226000 | 3.7 | 160000 | 2.25 | R-410A | 17.1667
9989853 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 20.85 | 250000 | 3.59 | 178000 | 2.16 | R-410A | 19
9989819 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Ducted Indoor Units | 228000 | 11.6 | 19.8 | 250000 | 3.51 | 178000 | 2.09 | R-410A | 19
9989820 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Ducted Indoor Units | 228000 | 11.6 | 19.8 | 250000 | 3.51 | 178000 | 2.09 | R-410A | 19
9989854 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 20.85 | 250000 | 3.59 | 178000 | 2.16 | R-410A | 19
9989852 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 21.9 | 226000 | 3.7 | 160000 | 2.25 | R-410A | 17.1667
9989797 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Ducted Indoor Units | 206000 | 12.2 | 20.8 | 226000 | 3.66 | 160000 | 2.18 | R-410A | 17.1667
9989783 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Non-Ducted Indoor Units | 206000 | 12.5 | 23 | 226000 | 3.74 | 160000 | 2.32 | R-410A | 17.1667
9989809 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Non-Ducted Indoor Units | 228000 | 11.9 | 21.9 | 250000 | 3.68 | 178000 | 2.24 | R-410A | 19
9990311 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
9990312 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990313 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
9990309 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990310 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
207699038 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
207699039 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
207699042 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.35 | 26.4 | 154000 | 3.65 | 154000 | 2.22 | R-410A | 11.5
207699043 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.45 | 26.2 | 180000 | 3.67 | 180000 | 2.2 | R-410A | 13.3333
206799466 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799474 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799448 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799440 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
212512472 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
212511091 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
212511092 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
212511095 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
212511096 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
212511099 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
212511100 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
212511107 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
212512477 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
212512474 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
212512464 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
212512481 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
212511103 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
212511104 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
212511083 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
212511084 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
212511087 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
212511093 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
212511094 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
212512473 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
212512475 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
212512478 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
212511109 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
212511101 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
212511102 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
212511097 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
212511098 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
212511105 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
212511106 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
212511085 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
212511086 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
212512465 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
212512482 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
212511089 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
206799458 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
10103105 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10103132 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10103126 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
201830309 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1* | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201994787 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850199 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850316 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
202073625 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 21.05 | 256000 | 3.45 | 172000 | 2.31 | R-410A | 19.1667
207591094 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
204723116 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
204723142 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
207591120 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
202073638 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 21.05 | 256000 | 3.45 | 172000 | 2.31 | R-410A | 19.1667
201994829 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850226 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850342 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201830335 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1* | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
10103127 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10103133 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10103106 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10103107 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10103134 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10103128 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
206799438 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
6691440 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
6691441 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6691442 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
6691443 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6691444 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
204442718 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM168HXVAFH |  |  | AM240JXVAFH | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204442733 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM168HXVAJH |  |  | AM240JXVAJH | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
206799435 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204442715 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
204442730 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
206799437 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
206799436 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
207382956 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
207385924 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 22.45 | 154000 | 3.62 | 100000 | 2.54 | R-410A | 11.5
7849631 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-72WM/B-F(U) |  |  | GMV-144WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
208102018 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
9956559 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
9088668 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 | IOV072H3CDC712 |  |  | IOV144H3CDC724 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
10306442 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV072H3CDC712(A) |  |  | IOV144H3CDC725(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
7850861 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850862 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850863 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
7850864 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850865 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850871 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850872 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850873 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
7850874 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850875 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
205000542 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH |  |  |  | AM168HXVAFH | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
205000543 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH |  |  |  | AM168HXVAJH | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
204442777 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442779 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442780 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
205000545 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
206799473 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799465 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799447 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799439 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799441 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799467 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799475 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799449 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000546 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
204442785 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442787 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442788 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
204442778 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
206799455 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
206799457 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204442786 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204442807 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Non-Ducted Indoor Units | 206000 | 11 | 24.5 | 230000 | 3.82 | 150000 | 2.7 | R-410A | 17.1667
206799463 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
212512527 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
212511028 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
212511009 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
212511010 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
212511012 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
212511029 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
212511031 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
212511037 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
212511038 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
212512528 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
212512537 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
212512530 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
212512526 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
212512529 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
212511027 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
212511030 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
212511006 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
212511011 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
212511007 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
212511008 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
212512466 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
212511065 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
212511045 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
212512470 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
212512471 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
212512476 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
212512480 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
212511046 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
212511047 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
212511049 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
212511066 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
212511067 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
212511069 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
212511064 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
212511068 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
212511042 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
212511048 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
212512463 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
212512479 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
212512467 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
212511043 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
212511044 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
202073589 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.35 | 19.73 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
202073590 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 10.8 | 19.3 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
201994665 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201994667 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201994668 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201994670 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850244 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850245 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850246 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850247 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850127 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850128 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850129 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850130 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201830237 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201830238 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201830239 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201830240 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
204723044 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
204723045 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
204723046 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
204723047 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
207591022 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
207591023 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
207591024 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
207591025 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
202073605 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.35 | 19.73 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
202073606 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 10.8 | 19.3 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
201994719 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201994721 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201994723 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201994724 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850276 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850277 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850278 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850279 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850159 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850160 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850161 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850162 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201830269 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201830270 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201830271 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201830272 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
204723076 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
204723077 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
204723078 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
204723079 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
207591054 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
207591055 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
207591056 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
207591057 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
202897164 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897165 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918869 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918870 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918871 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897234 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897235 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897194 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897195 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918867 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918868 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897203 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R120DXN1 |  |  | MV6-R240DXN1 | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202918977 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918978 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918979 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202918984 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB120H4M-3Y |  |  | VRB240H4M-3Y | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202897196 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897197 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202897236 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202897237 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202897198 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897199 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918981 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB120H4M-3G |  |  | VRB240H4M-3G | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202918974 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918975 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918976 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202897205 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R120DZN1 |  |  | MV6-R240DZN1 | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202897140 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897141 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897180 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918851 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918852 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918853 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918850 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897181 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897150 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897151 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897152 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897153 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897182 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918959 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918960 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918961 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918956 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918957 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918958 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897183 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897154 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897155 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897142 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897143 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202897184 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202918857 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918858 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918859 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202918854 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918855 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918856 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897185 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897156 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897157 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202897158 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897159 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202897186 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202918965 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918966 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918967 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202918962 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918963 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918964 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897187 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897160 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897161 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
213893574 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P96YNU-A |  |  | PUHY-P192YSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
203378434 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203381124 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203376873 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
213893572 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P96TNU-A |  |  | PUHY-P192TSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
203376884 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203381123 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203378436 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
213893472 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  |  | PUHY-EP216YSNU-A | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893466 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893467 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213916614 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916616 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  |  | PUHY-EP216YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893460 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A |  |  |  | PUHY-EP144YNU-A | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
203381081 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203376896 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203376962 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
213916575 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  |  | PUHY-EP216TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893470 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  |  | PUHY-EP216TSNU-A | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893462 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893463 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893458 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A |  |  |  | PUHY-EP144TNU-A | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
203376971 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203376908 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203381079 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
213916630 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893833 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893844 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893550 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893551 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916631 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893556 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A | PUHY-HP120YNU-A |  |  | PUHY-HP240YSNU-A | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893835 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893831 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916591 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916592 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893546 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893547 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893554 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A | PUHY-HP120TNU-A |  |  | PUHY-HP240TSNU-A | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893711 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP0964AN40AN |  |  | TUHYP1924BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
203378442 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203378392 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203381327 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
213893710 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP0963AN40AN |  |  | TUHYP1923BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
203378391 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203378441 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203381326 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
213893652 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893653 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893655 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN |  |  | TUHYE2164BN40AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916722 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916730 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN |  |  | TUHYE2164BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893649 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN |  |  |  | TUHYE1444AN40AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
203381284 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203378327 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203378328 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
213916719 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916726 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN |  |  | TUHYE2163BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893654 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN |  |  | TUHYE2163BN40AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893650 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893651 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893648 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN |  |  |  | TUHYE1443AN40AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
203378323 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203378324 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203381282 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
213916786 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893694 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893695 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893698 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893699 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916789 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893701 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN | TUHYH1204AN40AN |  |  | TUHYH2404BN40AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893692 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893693 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916784 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916787 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893696 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893697 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893700 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN40AN | TUHYH1203AN40AN |  |  | TUHYH2403BN40AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213896137 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A | PURY-P96YNU-A |  |  | PURY-P192YSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896135 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A | PURY-P96TNU-A |  |  | PURY-P192TSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896213 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN40AN | TURYP0964AN40AN |  |  | TURYP1924BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896211 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN40AN | TURYP0963AN40AN |  |  | TURYP1923BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213895965 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A | PURY-EP96YNU-A |  |  | PURY-EP192YSNU-A | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896077 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A | PURY-EP96YNU-A |  |  | PURY-EP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213895963 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A | PURY-EP96TNU-A |  |  | PURY-EP192TSNU-A | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896075 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A | PURY-EP96TNU-A |  |  | PURY-EP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896029 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN | TURYE0964AN40AN |  |  | TURYE1924BN40AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896165 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN | TURYE0964AN40AN |  |  | TURYE1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896027 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN | TURYE0963AN40AN |  |  | TURYE1923BN40AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896163 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN | TURYE0963AN40AN |  |  | TURYE1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896110 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A | PURY-HP72YNU-A |  |  | PURY-HP144YSNU-A | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895989 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A | PURY-HP72YNU-A |  |  | PURY-HP144YSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213895993 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A | PURY-HP96YNU-A |  |  | PURY-HP192YSNU-A | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896120 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A | PURY-HP96YNU-A |  |  | PURY-HP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896107 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A | PURY-HP72TNU-A |  |  | PURY-HP144TSNU-A | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895987 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A | PURY-HP72TNU-A |  |  | PURY-HP144TSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213895991 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A | PURY-HP96TNU-A |  |  | PURY-HP192TSNU-A | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896115 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A | PURY-HP96TNU-A |  |  | PURY-HP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896053 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN | TURYH0724AN40AN |  |  | TURYH1444BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896197 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN | TURYH0724AN40AN |  |  | TURYH1444BN40AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896201 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN | TURYH0964AN40AN |  |  | TURYH1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896057 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN | TURYH0964AN40AN |  |  | TURYH1924BN40AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896051 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN | TURYH0723AN40AN |  |  | TURYH1443BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896195 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN | TURYH0723AN40AN |  |  | TURYH1443BN40AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896199 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN | TURYH0963AN40AN |  |  | TURYH1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896055 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN | TURYH0963AN40AN |  |  | TURYH1923BN40AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
203334991 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203334992 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203334941 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334942 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203364249 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364250 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203364251 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
203334943 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203334993 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203334939 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203334989 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
203364247 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
208480482 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* |  |  |  | REYQ168XATJ* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
203364266 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364267 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203334958 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334959 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203335008 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203335009 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203335010 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203334960 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203364268 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
203364264 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
203334956 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203335006 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
208480483 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* |  |  |  | REYQ168XAYD* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
203335025 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203335026 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203334975 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334976 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203364283 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364284 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203364285 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
203334977 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203335027 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203335023 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
203334973 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203364281 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
208480484 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* |  |  |  | REYQ168XAYC* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
205749941 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* | MVHP096ME2CA* |  |  | MVHP168ME2CA* | Ducted Indoor Units | 161000 | 11.4 | 21.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749966 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* | MVHP096ME2CA* |  |  | MVHP168ME2CA* | Non-Ducted Indoor Units | 161000 | 11.6 | 22.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749967 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* | MVHR096ME2CA* |  |  | MVHR168ME2CA* | Non-Ducted Indoor Units | 161000 | 11.4 | 22 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749942 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* | MVHR096ME2CA* |  |  | MVHR168ME2CA* | Ducted Indoor Units | 161000 | 11.2 | 20.7 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749943 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* | MVHP096ME2CA* |  |  | MVHP192ME2CA* | Ducted Indoor Units | 184000 | 11.1 | 20.6 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749968 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* | MVHP096ME2CA* |  |  | MVHP192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.6 | 21.4 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749969 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* | MVHR096ME2CA* |  |  | MVHR192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.4 | 20.4 | 206000 | 3.4 | 138000 | 2.3 | R-410A | 15.3333
205749944 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* | MVHR096ME2CA* |  |  | MVHR192ME2CA* | Ducted Indoor Units | 184000 | 11.2 | 19.7 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749945 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* | MVHP096ME2CA* |  |  | MVHP216ME2CA* | Ducted Indoor Units | 207000 | 10.9 | 20.7 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749970 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* | MVHP096ME2CA* |  |  | MVHP216ME2CA* | Non-Ducted Indoor Units | 207000 | 11.5 | 20.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749971 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* | MVHR096ME2CA* |  |  | MVHR216ME2CA* | Non-Ducted Indoor Units | 207000 | 11.4 | 19.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749946 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* | MVHR096ME2CA* |  |  | MVHR216ME2CA* | Ducted Indoor Units | 207000 | 10.9 | 19.8 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
204793027 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME2CA* |  |  |  | MVHP144ME2CA* | Ducted Indoor Units | 138000 | 11.7 | 21.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793028 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME2CA* |  |  |  | MVHP144ME2CA* | Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793029 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME2CA* |  |  |  | MVHR144ME2CA* | Ducted Indoor Units | 138000 | 11 | 20.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793030 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME2CA* |  |  |  | MVHR144ME2CA* | Non-Ducted Indoor Units | 138000 | 11.4 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
205234700 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
205234792 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
205234840 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
205234841 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
205234793 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
205234701 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
205234702 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
205234794 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
205234842 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
205234850 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
205234802 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
205234770 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
205234771 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
205234803 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
205234851 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
205234852 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
205234804 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
205234772 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
205234865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 20.55 | 206000 | 3.81 | 150000 | 2.45 | R-410A | 15.3333
205234866 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.55 | 20.4 | 232000 | 3.71 | 164000 | 2.28 | R-410A | 17.1667
205234833 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Ducted Indoor Units | 184000 | 11.8 | 19.2 | 206000 | 3.72 | 150000 | 2.39 | R-410A | 15.3333
205234834 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Ducted Indoor Units | 206000 | 11.3 | 19.1 | 232000 | 3.58 | 164000 | 2.22 | R-410A | 17.1667
205234785 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Non-Ducted Indoor Units | 184000 | 12.4 | 21.9 | 206000 | 3.91 | 150000 | 2.52 | R-410A | 15.3333
205234786 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Non-Ducted Indoor Units | 206000 | 11.8 | 21.7 | 232000 | 3.84 | 164000 | 2.35 | R-410A | 17.1667
205234787 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 256000 | 3.77 | 182000 | 2.39 | R-410A | 19
205234835 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Ducted Indoor Units | 228000 | 10.7 | 18.1 | 256000 | 3.46 | 182000 | 2.18 | R-410A | 19
205234867 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 19.45 | 256000 | 3.61 | 182000 | 2.28 | R-410A | 19
205234863 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.2 | 154000 | 3.65 | 109000 | 2.17 | R-410A | 11.5
205234831 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Ducted Indoor Units | 138000 | 10.8 | 18.2 | 154000 | 3.46 | 109000 | 2.14 | R-410A | 11.5
205234783 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Non-Ducted Indoor Units | 138000 | 11.5 | 22.2 | 154000 | 3.84 | 109000 | 2.2 | R-410A | 11.5
205234817 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
205233057 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
205233067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
205234822 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
205233062 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
205233072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
205811882 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205811883 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205818940 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205811966 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205818856 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205818857 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205818858 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205818859 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205811967 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205818941 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205811884 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205811885 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205811886 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205811887 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205818942 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205811968 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205818860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205818861 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205818862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205818863 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205811969 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205818943 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205811888 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205811889 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205811890 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205811891 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205818944 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205811970 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205818864 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205818865 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205818866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205818867 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205811971 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205818945 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205811892 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205811893 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205811894 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205811895 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205818946 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205811972 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205818868 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205818869 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205818870 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205818871 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205811973 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205818947 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205811896 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205811897 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205811898 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205811899 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205818948 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205818952 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205818956 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205818880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205818881 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205818888 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205818889 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205811906 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205811907 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205811914 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205811915 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205811974 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205811978 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205811982 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205818872 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205818873 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205818874 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205818875 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205811983 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205811979 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205811975 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205811916 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205811917 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205811908 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205811909 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205818890 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205818891 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205818882 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205818883 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205818957 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205818953 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205818949 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205811900 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205811901 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205811902 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205811903 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205818950 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205818954 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205818958 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205818884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205818885 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205818892 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205818893 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205811910 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205811911 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205811918 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205811919 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205811976 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205811980 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205811984 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205818876 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205818877 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205818878 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205818879 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205811985 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205811981 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205811977 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205811920 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205811921 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205811912 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205811913 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205818894 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205818895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205818886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205818887 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205818959 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205818955 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205818951 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205811904 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205811905 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
10515233 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10515243 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
10515253 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10515254 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10515244 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
10515234 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10515257 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10515259 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10515261 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10515262 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10515260 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10515258 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10515245 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
10515235 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10515255 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10515256 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10515236 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10515246 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
202021860 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202022822 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202021873 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202021874 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202022823 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202021861 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202022824 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202021855 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202021875 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202021876 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202021856 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202022825 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202022826 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202021857 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202021877 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202021878 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202016269 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202022827 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202022828 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202021858 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
202021879 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
202021880 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
202021859 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
202022829 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202022830 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202021881 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
202016271 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
208102025 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
208102022 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
201902946 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
10267499 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-72WM/B-U(U) |  |  | GMV-144WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
201902941 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
10306471 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) | IOV072H6CDC712(A) |  |  | IOV144H6CDC725(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
10267474 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-168WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
10267477 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-192WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
10267480 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-216WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
201903106 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
201903110 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
208102035 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
208102030 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
206799464 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
213916468 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.35 | 19.95 | 178000 | 3.68 | 132000 | 2.39 | R-410A | 13.3333
213916469 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P192ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 18.25 | 204000 | 3.58 | 150000 | 2.31 | R-410A | 15.3333
213896319 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Ducted Indoor Units | 160000 | 11.3 | 19.2 | 178000 | 3.54 | 132000 | 2.6 | R-410A | 13.3333
213896321 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P192ZSKMU-A | Ducted Indoor Units | 184000 | 11 | 18.7 | 204000 | 3.48 | 150000 | 2.45 | R-410A | 15.3333
213896358 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Non-Ducted Indoor Units | 160000 | 11.4 | 20.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
213896323 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P216ZSKMU-A | Ducted Indoor Units | 206000 | 10.8 | 19.8 | 232000 | 3.51 | 164000 | 2.48 | R-410A | 17.1667
213916470 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P216ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 18.8 | 232000 | 3.53 | 164000 | 2.28 | R-410A | 17.1667
9956577 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP120C432Y |  |  | VEP240C432Y | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
10306451 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  |  | IOV240H3CDC741(A) | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
208102043 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP120C432Y |  |  | VEP240C432Y | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
8176008 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  |  | GMV-240WM/B-F(U) | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
208102033 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y |  |  | VEP192C432Y | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
208102038 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP096C432Y |  |  | VEP216C432Y | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
9956567 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y |  |  | VEP192C432Y | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
9956569 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP096C432Y |  |  | VEP216C432Y | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
8176006 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  |  | GMV-192WM/B-F(U) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
8176007 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  |  | GMV-216WM/B-F(U) | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
10306441 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV072H3CDC712(A) |  |  | IOV144H3CDC725(A) | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10306447 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  |  | IOV192H3CDC733(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10306449 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  |  | IOV216H3CDC737(A) | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
10306444 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) |  |  | IOV168H3CDC729(A) | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
9088667 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 | IOV072H3CDC712 |  |  | IOV144H3CDC724 | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
8176009 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) |  |  | GMV-168WM/B-F(U) | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
9956558 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
7793599 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-72WM/B-F(U) |  |  | GMV-144WM/B-F(U) | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
208102027 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y |  |  | VEP168C432Y | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
204442761 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
204442764 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM168HXVAJR |  |  | AM240JXVAJR | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204442749 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM168HXVAFR |  |  | AM240JXVAFR | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
208102017 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10267482 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-240WM/B-U(U) | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
204442795 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442796 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
204442803 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442804 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
204442801 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442762 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR |  |  |  | AM192HXVAJR | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
204442747 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAFR |  |  |  | AM192HXVAFR | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
208102097 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y | VER120C432Y |  |  | VER216C432Y | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
201866461 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y | VER120C432Y |  |  | VER216C432Y | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
10344560 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) | GMV-Q120WM/B-F(U) |  |  | GMV-Q216WM/B-F(U) | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
208102021 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
208102041 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
201903113 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
204442802 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
9133486 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC240KHP/220V | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
9133445 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC96KHP/220V |  |  | TVRF-OC192KHP/220V | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
9133448 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC216KHP/220V | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
204442810 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Non-Ducted Indoor Units | 206000 | 11 | 24.5 | 230000 | 3.82 | 150000 | 2.7 | R-410A | 17.1667
10341446 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-U(U) | GMV-Q120WM/B-U(U) |  |  | GMV-Q216WM/B-U(U) | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
201904248 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432G | VER120C432G |  |  | VER216C432G | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
208102095 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432G | VER120C432G |  |  | VER216C432G | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
208102031 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
208102036 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
201903109 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
201903105 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10267479 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-216WM/B-U(U) | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
10267470 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-72WM/B-U(U) |  |  | GMV-144WM/B-U(U) | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10267472 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-168WM/B-U(U) | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
10267476 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-192WM/B-U(U) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10306470 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) | IOV072H6CDC712(A) |  |  | IOV144H6CDC725(A) | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
201902944 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
201902938 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
208102024 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
8175950 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.95 | 152000 | 3.71 | 109000 | 2.21 | R-410A | 11.3333
8175951 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.6 | 23.65 | 152000 | 3.85 | 109000 | 2.28 | R-410A | 11.3333
8175952 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.05 | 20.45 | 178000 | 3.62 | 132000 | 2.33 | R-410A | 13.3333
8175953 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 13 | 23 | 178000 | 3.7 | 132000 | 2.33 | R-410A | 13.3333
8175954 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.95 | 22.8 | 204000 | 3.65 | 150000 | 2.25 | R-410A | 15.1667
8175955 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.7 | 22.75 | 232000 | 3.6 | 164000 | 2.22 | R-410A | 17.1667
8175956 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  |  | PUHY-P240YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.6 | 22.15 | 258000 | 3.59 | 182000 | 2.17 | R-410A | 19
8175965 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.95 | 152000 | 3.71 | 109000 | 2.21 | R-410A | 11.3333
8175966 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.6 | 23.65 | 152000 | 3.85 | 109000 | 2.28 | R-410A | 11.3333
8175967 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.05 | 20.45 | 178000 | 3.62 | 132000 | 2.33 | R-410A | 13.3333
8175968 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 13 | 23 | 178000 | 3.7 | 132000 | 2.33 | R-410A | 13.3333
8175969 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.95 | 22.8 | 204000 | 3.65 | 150000 | 2.25 | R-410A | 15.1667
8175970 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.7 | 22.75 | 232000 | 3.6 | 164000 | 2.22 | R-410A | 17.1667
8175971 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  |  | PUHY-P240TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.6 | 22.15 | 258000 | 3.59 | 182000 | 2.17 | R-410A | 19
8175980 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 21.75 | 152000 | 3.53 | 97000 | 2.11 | R-410A | 11.3333
8175981 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 23.9 | 152000 | 3.8 | 97000 | 2.18 | R-410A | 11.3333
8175983 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 22.35 | 178000 | 3.56 | 119000 | 2.28 | R-410A | 13.3333
8175984 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 23.7 | 204000 | 3.55 | 142000 | 2.18 | R-410A | 15.1667
8175985 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.2 | 232000 | 3.54 | 158000 | 2.14 | R-410A | 17.1667
8175986 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.65 | 258000 | 3.53 | 174000 | 2.1 | R-410A | 19
8175994 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 22 | 152000 | 3.53 | 97000 | 2.11 | R-410A | 11.3333
8175995 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 23.9 | 152000 | 3.8 | 97000 | 2.18 | R-410A | 11.3333
8175997 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 22.35 | 178000 | 3.56 | 119000 | 2.28 | R-410A | 13.3333
8175998 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 23.7 | 204000 | 3.55 | 142000 | 2.18 | R-410A | 15.1667
8175999 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.2 | 232000 | 3.54 | 158000 | 2.14 | R-410A | 17.1667
8176000 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.65 | 258000 | 3.53 | 174000 | 2.1 | R-410A | 19
8578648 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R144DZN1-(A) |  |  |  | MV5-R144DZN1-(A) | Non-Ducted Indoor Units | 136000 | 11 | 19.5 | 150000 | 3.4 | 102000 | 2.25 | R-410A | 11.3333
9133171 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DXN1 |  |  |  | MV5-2R145DXN1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9133172 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DXN1 |  |  |  | MV5-2R145DXN1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9133173 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DXN1 |  |  |  | MV5-2R168DXN1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9133174 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DXN1 |  |  |  | MV5-2R168DXN1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9133175 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DXN1 |  |  |  | MV5-2R192DXN1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9133176 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DXN1 |  |  |  | MV5-2R192DXN1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9133177 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DXN1 |  |  |  | MV5-2R216DXN1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9133178 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DXN1 |  |  |  | MV5-2R216DXN1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9133187 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DZN1 |  |  |  | MV5-2R145DZN1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9133188 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DZN1 |  |  |  | MV5-2R145DZN1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9133189 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DZN1 |  |  |  | MV5-2R168DZN1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9133190 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DZN1 |  |  |  | MV5-2R168DZN1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9133191 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DZN1 |  |  |  | MV5-2R192DZN1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9133192 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DZN1 |  |  |  | MV5-2R192DZN1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9133193 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DZN1 |  |  |  | MV5-2R216DZN1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9133194 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DZN1 |  |  |  | MV5-2R216DZN1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9133200 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DXN1 |  |  |  | MV5-2R145DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9133201 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DXN1 |  |  |  | MV5-2R168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9133202 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DXN1 |  |  |  | MV5-2R192DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9133203 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DXN1 |  |  |  | MV5-2R216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9133208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DZN1 |  |  |  | MV5-2R145DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9133209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DZN1 |  |  |  | MV5-2R168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9133210 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DZN1 |  |  |  | MV5-2R192DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9133211 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DZN1 |  |  |  | MV5-2R216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
10091387 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
10091388 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
9487697 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9487698 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9487699 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9487701 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9487702 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9487703 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9487704 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9487705 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9487706 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9487707 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9487708 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9487710 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9487711 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9487712 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9487713 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9487714 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9487715 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9487716 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9487717 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9487719 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487720 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9487721 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9487722 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487723 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9487752 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9487753 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9487754 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9487755 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9487756 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9487757 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9487758 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9487759 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9487760 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9487762 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9487763 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9487764 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9487765 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9487766 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9487767 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9487768 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9487769 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9487771 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9487772 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9487773 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487774 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9487775 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9487776 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487777 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
200084125 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
200084126 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
200084127 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
200084128 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
200084129 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
200084130 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
202516754 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202516755 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
202516756 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 |  |  |  | ARUN144DTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202516758 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
202516760 | 1/1/2027 | LG | HMSV-A-CB | ARUN168DTE4 |  |  |  | ARUN168DTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202516761 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202516762 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
202516764 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 |  |  |  | ARUM216BTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
202516765 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN144DTE4 |  |  | ARUN216DTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202516766 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN144DTE4 |  |  | ARUN216DTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 25.5 | 230000 | 3.73 | 150000 | 2.58 | R-410A | 17.1667
202516768 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN144DTE4 |  |  | ARUN240DTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 22 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202517446 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 |  |  |  | ARUN144DTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202517464 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB144BTE4 |  |  | ARUB216BTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202517465 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB144DTE4 |  |  | ARUB216DTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202517466 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN144BTE4 |  |  | ARUN216BTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202519357 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN121DTE4 |  |  | ARUN192DTE4 | Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202519358 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN121DTE4 |  |  | ARUN192DTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202519359 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN144DTE4 |  |  | ARUN240DTE4 | Ducted Indoor Units | 228000 | 11.6 | 20 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202524545 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
202524546 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202524547 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
202524549 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
202524550 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202524551 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 |  |  |  | ARUM216DTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
9550138 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Non-Ducted Indoor Units | 138000 | 13.9 | 26.4 | 154000 | 3.77 | 109000 | 2.65 | R-410A | 11.5
9550161 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Ducted Indoor Units | 138000 | 13 | 22.6 | 154000 | 3.65 | 109000 | 2.6 | R-410A | 11.5
9680960 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.45 | 24.5 | 154000 | 3.71 | 109000 | 2.62 | R-410A | 11.5
202534252 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 |  |  |  | ARUB144DTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534258 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 |  |  |  | ARUN144BTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534259 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 |  |  |  | ARUN144BTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534260 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 |  |  |  | ARUB144DTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534261 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 |  |  |  | ARUB144BTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534262 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 |  |  |  | ARUB144BTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534264 | 1/1/2027 | LG | HMSV-A-CB | ARUN168BTE4 |  |  |  | ARUN168BTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534266 | 1/1/2027 | LG | HMSR-A-CB | ARUB168DTE4 |  |  |  | ARUB168DTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534268 | 1/1/2027 | LG | HMSR-A-CB | ARUB168BTE4 |  |  |  | ARUB168BTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534269 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN121BTE4 |  |  | ARUN192BTE4 | Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534270 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB121DTE4 |  |  | ARUB192DTE4 | Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534271 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB121BTE4 |  |  | ARUB192BTE4 | Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534272 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB121DTE4 |  |  | ARUB192DTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534273 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB121BTE4 |  |  | ARUB192BTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534274 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN121BTE4 |  |  | ARUN192BTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534275 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB144BTE4 |  |  | ARUB216BTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 25.5 | 230000 | 3.73 | 150000 | 2.58 | R-410A | 17.1667
202534276 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB144DTE4 |  |  | ARUB216DTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 25.5 | 230000 | 3.73 | 150000 | 2.58 | R-410A | 17.1667
202534277 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN144BTE4 |  |  | ARUN216BTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 25.5 | 230000 | 3.73 | 150000 | 2.58 | R-410A | 17.1667
202534278 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN144BTE4 |  |  | ARUN240BTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 22 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534279 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB144BTE4 |  |  | ARUB240BTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 22 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534280 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB144DTE4 |  |  | ARUB240DTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 22 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534281 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB144DTE4 |  |  | ARUB240DTE4 | Ducted Indoor Units | 228000 | 11.6 | 20 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202534282 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB144BTE4 |  |  | ARUB240BTE4 | Ducted Indoor Units | 228000 | 11.6 | 20 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202534283 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN144BTE4 |  |  | ARUN240BTE4 | Ducted Indoor Units | 228000 | 11.6 | 20 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
203297470 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168TLMU-A |  |  |  | PURY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
203297473 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Ducted Indoor Units | 160000 | 12.1 | 18.5 | 178000 | 3.6 | 132000 | 2.52 | R-410A | 13.3333
203297474 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 18.2 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
203297475 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Ducted Indoor Units | 160000 | 11 | 19 | 178000 | 3.37 | 119000 | 2.21 | R-410A | 13.3333
203297476 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
203297478 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168YLMU-A |  |  |  | PURY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
203297481 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Ducted Indoor Units | 160000 | 12.1 | 18.5 | 178000 | 3.6 | 132000 | 2.52 | R-410A | 13.3333
203297482 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 18.2 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
203297483 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Ducted Indoor Units | 160000 | 11 | 19 | 178000 | 3.37 | 119000 | 2.21 | R-410A | 13.3333
203297484 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
203297487 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P96TKMU-A |  |  | PURY-P192TSKMU-A | Ducted Indoor Units | 182000 | 11.6 | 18.5 | 204000 | 3.62 | 150000 | 2.52 | R-410A | 15.1667
203297489 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 22.6 | 204000 | 3.51 | 142000 | 2.19 | R-410A | 15.1667
203297490 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
203297493 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P96YKMU-A |  |  | PURY-P192YSKMU-A | Ducted Indoor Units | 182000 | 11.6 | 18.5 | 204000 | 3.62 | 150000 | 2.52 | R-410A | 15.1667
203297495 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 22.6 | 204000 | 3.51 | 142000 | 2.19 | R-410A | 15.1667
203297496 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
203297501 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TKMU-A | PURY-P96TKMU-A |  |  | PURY-P216TSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 18.1 | 232000 | 3.52 | 164000 | 2.26 | R-410A | 17.1667
203297503 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 20.8 | 232000 | 3.5 | 158000 | 2.19 | R-410A | 17.1667
203297504 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
203297507 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YKMU-A | PURY-P96YKMU-A |  |  | PURY-P216YSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 18.1 | 232000 | 3.52 | 164000 | 2.26 | R-410A | 17.1667
203297509 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 20.8 | 232000 | 3.5 | 158000 | 2.19 | R-410A | 17.1667
203297510 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
203297516 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TKMU-A | PURY-P120TKMU-A |  |  | PURY-P240TSKMU-A | Non-Ducted Indoor Units | 228000 | 10.9 | 18.1 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
203297517 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 18.6 | 258000 | 3.43 | 174000 | 2.14 | R-410A | 19
203297520 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YKMU-A | PURY-P120YKMU-A |  |  | PURY-P240YSKMU-A | Non-Ducted Indoor Units | 228000 | 10.9 | 18.1 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
203297521 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 18.6 | 258000 | 3.43 | 174000 | 2.14 | R-410A | 19
203301902 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Non-Ducted Indoor Units | 136000 | 14.4 | 19.5 | 152000 | 3.62 | 109000 | 2.28 | R-410A | 11.3333
203301903 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
203301904 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
203301906 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
203301907 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
203381177 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A |  |  |  | PURY-P144TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.2 | 19 | 152000 | 3.31 | 109000 | 2.18 | R-410A | 11.3333
203381179 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 21.55 | 152000 | 3.52 | 97000 | 2.1 | R-410A | 11.3333
203381181 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.65 | 152000 | 3.79 | 97000 | 2.17 | R-410A | 11.3333
203381182 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A |  |  |  | PURY-P144YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.2 | 19 | 152000 | 3.31 | 109000 | 2.18 | R-410A | 11.3333
203381184 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 21.55 | 152000 | 3.52 | 97000 | 2.1 | R-410A | 11.3333
203381186 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.2 | 18.65 | 152000 | 3.56 | 109000 | 2.33 | R-410A | 11.3333
203381188 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.65 | 152000 | 3.79 | 97000 | 2.17 | R-410A | 11.3333
203381192 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.5 | 18.35 | 178000 | 3.54 | 132000 | 2.36 | R-410A | 13.3333
203381194 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 21.35 | 178000 | 3.55 | 119000 | 2.27 | R-410A | 13.3333
203381197 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.5 | 18.35 | 178000 | 3.54 | 132000 | 2.36 | R-410A | 13.3333
203381199 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 21.35 | 178000 | 3.55 | 119000 | 2.27 | R-410A | 13.3333
203381201 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P96TKMU-A |  |  | PURY-P192TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 18 | 204000 | 3.53 | 150000 | 2.34 | R-410A | 15.1667
203381203 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 22.8 | 204000 | 3.54 | 142000 | 2.17 | R-410A | 15.1667
203381205 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P96YKMU-A |  |  | PURY-P192YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 18 | 204000 | 3.53 | 150000 | 2.34 | R-410A | 15.1667
203381207 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 22.8 | 204000 | 3.54 | 142000 | 2.17 | R-410A | 15.1667
203381212 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 21.5 | 232000 | 3.53 | 158000 | 2.14 | R-410A | 17.1667
203381216 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 21.5 | 232000 | 3.53 | 158000 | 2.14 | R-410A | 17.1667
203381221 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.2 | 258000 | 3.52 | 174000 | 2.09 | R-410A | 19
203381225 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.2 | 258000 | 3.52 | 174000 | 2.09 | R-410A | 19
200084155 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
200084156 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
200084157 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
200084158 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
200084159 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
200084160 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
201847125 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201847126 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847127 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201847128 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847129 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201847130 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847131 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201847132 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847133 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G |  |  | VPA216H4M-2G | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847134 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G |  |  | VPA216H4M-2G | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847135 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y |  |  | VPA216H4M-2Y | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847136 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y |  |  | VPA216H4M-2Y | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847137 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G |  |  | VPA240H4M-2G | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847138 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G |  |  | VPA240H4M-2G | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201847139 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y |  |  | VPA240H4M-2Y | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847140 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y |  |  | VPA240H4M-2Y | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201847185 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201847186 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847187 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201847188 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847189 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201847190 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847191 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201847192 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847193 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y |  |  | VRA216H4M-2Y | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847194 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y |  |  | VRA216H4M-2Y | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847195 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G |  |  | VRA216H4M-2G | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847196 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G |  |  | VRA216H4M-2G | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847197 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y |  |  | VRA240H4M-2Y | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847198 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y |  |  | VRA240H4M-2Y | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201847199 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G |  |  | VRA240H4M-2G | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847200 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G |  |  | VRA240H4M-2G | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201856724 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC144DXN1-(A) | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856725 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC144DXN1-(A) | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856726 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856727 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC168DXN1-(A) | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856728 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856729 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC192DXN1-(A) | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856730 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856731 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC216DXN1-(A) | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201856732 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) |  |  | MV5-RC240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856748 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC144DZN1-(A) | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856749 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC144DZN1-(A) | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856750 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856751 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC168DZN1-(A) | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856752 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856753 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC192DZN1-(A) | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856754 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856755 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC216DZN1-(A) | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201856756 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) |  |  | MV5-RC240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856772 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC144DXN1-(A) | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856773 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC144DXN1-(A) | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856774 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856775 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC168DXN1-(A) | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856776 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856777 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC192DXN1-(A) | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856778 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856780 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC120DXN1-(A) |  |  | MV5-XC240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856794 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC144DZN1-(A) | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856795 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC144DZN1-(A) | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856796 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856797 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC168DZN1-(A) | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856798 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856799 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC192DZN1-(A) | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856800 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856802 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC120DZN1-(A) |  |  | MV5-XC240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y | VRA072L4M-2Y |  |  | VRA144L4M-2Y | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862861 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y | VRA072L4M-2Y |  |  | VRA144L4M-2Y | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA072L4M-2Y |  |  | VRA168L4M-2Y | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862863 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA072L4M-2Y |  |  | VRA168L4M-2Y | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862864 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y |  |  | VRA192L4M-2Y | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862865 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y |  |  | VRA192L4M-2Y | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862866 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y |  |  | VRA216L4M-2Y | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862867 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y |  |  | VRA216L4M-2Y | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201862868 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y |  |  | VRA240L4M-2Y | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G | VRA072L4M-2G |  |  | VRA144L4M-2G | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862885 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G | VRA072L4M-2G |  |  | VRA144L4M-2G | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA072L4M-2G |  |  | VRA168L4M-2G | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862887 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA072L4M-2G |  |  | VRA168L4M-2G | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862888 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G |  |  | VRA192L4M-2G | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862889 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G |  |  | VRA192L4M-2G | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862890 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G |  |  | VRA216L4M-2G | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862891 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G |  |  | VRA216L4M-2G | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201862892 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G |  |  | VRA240L4M-2G | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862908 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y | VPA072L4M-2Y |  |  | VPA144L4M-2Y | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862909 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y | VPA072L4M-2Y |  |  | VPA144L4M-2Y | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862910 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA072L4M-2Y |  |  | VPA168L4M-2Y | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862911 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA072L4M-2Y |  |  | VPA168L4M-2Y | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862912 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y |  |  | VPA192L4M-2Y | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862913 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y |  |  | VPA192L4M-2Y | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862914 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y |  |  | VPA216L4M-2Y | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862916 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA120L4M-2Y |  |  | VPA240L4M-2Y | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862930 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G | VPA072L4M-2G |  |  | VPA144L4M-2G | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862931 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G | VPA072L4M-2G |  |  | VPA144L4M-2G | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862932 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA072L4M-2G |  |  | VPA168L4M-2G | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862933 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA072L4M-2G |  |  | VPA168L4M-2G | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862934 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G |  |  | VPA192L4M-2G | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862935 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G |  |  | VPA192L4M-2G | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862936 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G |  |  | VPA216L4M-2G | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862938 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA120L4M-2G |  |  | VPA240L4M-2G | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201863369 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863370 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863371 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863372 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201863375 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863376 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863377 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863378 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201863381 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863382 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863383 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863384 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201863387 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863388 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863389 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863390 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201874029 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 109000 | 2.32 | R-410A | 11.3333
201874030 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
201874031 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 108000 | 2.32 | R-410A | 11.3333
201874032 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
201874033 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
201874034 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
201874068 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  |  | PUHY-P240TSKMU-A | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
201874069 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  |  | PUHY-P240TSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
201874073 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  |  | PUHY-P240YSKMU-A | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
201874074 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  |  | PUHY-P240YSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
201874078 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 204000 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
201874080 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
201874081 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
201874083 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
201874084 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
201874085 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 20400 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
201874087 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Ducted Indoor Units | 136000 | 12.8 | 19.3 | 152000 | 3.79 | 108000 | 2.56 | R-410A | 11.3333
201874088 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
201874089 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
205281465 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
208685681 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
208685682 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
208685683 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
208685684 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
208685712 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
208685713 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
208758282 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
208758283 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
208758284 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
208758285 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
208758286 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
208758287 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
210691228 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA |  |  |  | AVWT-144FHFSHA | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
210691229 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA |  |  |  | AVWT-144FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
210691231 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FHFSHA |  |  |  | AVWT-168FHFSHA | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
210691232 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FHFSHA |  |  |  | AVWT-168FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 22.45 | 170000 | 3.29 | 115000 | 2.16 | R-410A | 13.3333
210691234 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FHFSHA |  |  |  | AVWT-192FHFSHA | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
210691235 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FHFSHA |  |  |  | AVWT-192FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
210691236 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
210691237 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
210691238 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
210691239 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
210691240 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
210691241 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
212924820 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Non-Ducted Indoor Units | 144000 | 12.2 | 20 | 162000 | 4.1 | 105000 | 2.45 | R-410A | 12
212924827 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Non-Ducted Indoor Units | 144000 | 12.2 | 20 | 162000 | 4.1 | 105000 | 2.45 | R-410A | 12
212928533 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Ducted Indoor Units | 144000 | 12.5 | 18.5 | 162000 | 3.72 | 105000 | 2.45 | R-410A | 12
212928534 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Ducted Indoor Units | 192000 | 11.5 | 19 | 206000 | 3.6 | 140000 | 2.37 | R-410A | 16
212928535 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Non-Ducted Indoor Units | 192000 | 11.8 | 19.5 | 206000 | 3.94 | 140000 | 2.4 | R-410A | 16
212928538 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Ducted Indoor Units | 144000 | 12.5 | 18.5 | 162000 | 3.72 | 105000 | 2.45 | R-410A | 12
212928539 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Ducted Indoor Units | 192000 | 11.5 | 19 | 206000 | 3.6 | 140000 | 2.37 | R-410A | 16
212928540 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Non-Ducted Indoor Units | 192000 | 11.8 | 19.5 | 206000 | 3.94 | 140000 | 2.4 | R-410A | 16
212928543 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 12.35 | 19.25 | 162000 | 3.91 | 105000 | 2.45 | R-410A | 12
212928544 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 192000 | 11.65 | 19.25 | 206000 | 3.77 | 140000 | 2.38 | R-410A | 16
212928546 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 12.35 | 19.25 | 162000 | 3.91 | 105000 | 2.45 | R-410A | 12
212928547 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 192000 | 11.65 | 19.25 | 206000 | 3.77 | 140000 | 2.38 | R-410A | 16
213686153 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
213686154 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
213686155 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
213686156 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
213686157 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
213686158 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
206453529 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
206453530 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 |  |  |  | ARUM216BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
206453532 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
206453533 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 |  |  |  | ARUM216DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
206453551 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
205281467 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
206453546 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
206453548 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
206453549 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
10103111 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Non-Ducted Indoor Units | 138000 | 11.8 | 22.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
10103113 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.2 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
10103114 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Non-Ducted Indoor Units | 206000 | 12.2 | 22 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
10103115 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Non-Ducted Indoor Units | 228000 | 11.6 | 21.1 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
10103138 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Ducted Indoor Units | 138000 | 11.3 | 18.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
10103140 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Ducted Indoor Units | 184000 | 12.6 | 19.7 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
10103141 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Ducted Indoor Units | 206000 | 11.6 | 19.6 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
10103142 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Ducted Indoor Units | 228000 | 11.4 | 18.6 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
10103152 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
10103154 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.55 | 20.95 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
10103155 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.9 | 20.8 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
10103156 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.5 | 19.85 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
10206679 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206680 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206682 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206683 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206693 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206694 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206696 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206697 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206707 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206708 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206710 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206711 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206721 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206722 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206724 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206725 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206735 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206736 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206738 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206739 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206749 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206750 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206752 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206753 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206763 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206764 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206765 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206766 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206777 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206778 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206779 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206780 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206791 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206792 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206793 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206794 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206805 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206806 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206807 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206808 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206819 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206820 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206821 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206822 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206833 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206834 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206835 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206836 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10207513 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207514 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207515 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207516 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207517 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207527 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207528 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207529 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207530 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207531 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207541 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207542 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207543 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207544 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207545 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207555 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207556 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207557 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207558 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207559 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207569 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207570 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207571 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207572 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207573 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207583 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207584 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207585 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207586 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207587 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10208207 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
10208212 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
10208472 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
10208477 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
9363453 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9363454 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9363455 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9363456 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9363457 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9363458 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9363460 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9363461 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9363462 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9363463 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9363464 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9363465 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9363466 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9363468 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9363469 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9363470 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9363471 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9363472 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9363473 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9363475 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9363476 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9363477 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9363478 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9363479 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9302730 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9302731 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9302732 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9302733 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9302734 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9302735 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9302736 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9302737 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9302738 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9302739 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9302740 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9302741 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9302742 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9302743 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9302744 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9302745 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9302746 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9302747 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9302748 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9302749 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9302750 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9302751 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9302752 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9302753 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9990032 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
9990034 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
9990035 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
9990036 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
9990049 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
9990051 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
9990052 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
9990053 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* |  |  | RXYQ240TAYD* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
9990063 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
9990064 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
9990067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
9990068 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
9990069 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
9990070 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
9990071 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
9990072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* |  |  | RXYQ240TAYD* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
9990093 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
9990094 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
9990097 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
9990098 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
9990099 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
9990100 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
9990101 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
9990102 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
9990302 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990303 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
9990304 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
9990305 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990306 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
10323537 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323538 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323540 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323541 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323553 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323554 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323556 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323557 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323569 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323570 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323572 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323573 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323585 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323586 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323588 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323589 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323601 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323602 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323604 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323605 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323617 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323618 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323620 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323621 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323633 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323634 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323635 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323636 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323649 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323650 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323651 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323652 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323665 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323666 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323667 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323668 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323681 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323682 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323683 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323684 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323697 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323698 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323699 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323700 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323713 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323714 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323715 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323716 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323731 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323732 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323733 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323734 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323735 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323747 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323748 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323749 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323750 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323751 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323763 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323764 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323765 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323766 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323767 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323780 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323781 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323782 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323783 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323784 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323796 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323797 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323798 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323799 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323800 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323812 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323813 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323814 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323815 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323816 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10340642 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/A-F(U) | GMV-Y96WM/A-F(U) |  |  | GMV-Y192WM/A-F(U) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10611537 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
10611538 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A) | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
10611539 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
10611540 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A) | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611541 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611542 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611543 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611544 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611551 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
10611552 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A) | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
10611553 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
10611554 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A) | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611555 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611556 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611557 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611558 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611572 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
10611573 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A) | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
10611574 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
10611575 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A) | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611576 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611577 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611578 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611579 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611596 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
10611597 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A) | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
10611598 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
10611599 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A) | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611600 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611601 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611602 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611603 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611620 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.69 | 126000 | 2.42 | R-410A | 13.3333
10611621 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 22.15 | 206000 | 3.67 | 144000 | 2.35 | R-410A | 15.3333
10611622 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.25 | 20.65 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10611623 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 20.2 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10611635 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.69 | 126000 | 2.42 | R-410A | 13.3333
10611636 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 22.15 | 206000 | 3.67 | 144000 | 2.35 | R-410A | 15.3333
10611637 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.25 | 20.65 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10611638 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 20.2 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10612354 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.25 | 22.8 | 180000 | 3.69 | 126000 | 2.42 | R-410A | 13.3333
10612355 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 22.65 | 206000 | 3.67 | 144000 | 2.35 | R-410A | 15.3333
10612356 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 20.85 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10612357 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.05 | 20.55 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10612366 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.25 | 22.8 | 180000 | 3.69 | 126000 | 2.42 | R-410A | 13.3333
10612367 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 22.65 | 206000 | 3.67 | 144000 | 2.35 | R-410A | 15.3333
10612368 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 20.85 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10612369 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.05 | 20.55 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10612400 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
10612401 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
10612402 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
10612403 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
10612404 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
10612405 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
10612406 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
10612407 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
10612408 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
10612409 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
10612410 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
10612411 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
10612412 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
10612413 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
10612414 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
10612453 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
10612454 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
10612455 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
10612456 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
10612457 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
10612458 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.85 | 22.85 | 154000 | 3.67 | 109000 | 2.59 | R-410A | 11.5
10612459 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
10612460 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
10612463 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
10612464 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
10612465 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
10612466 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
10612467 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
10612468 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
10612469 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
10612470 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
10612471 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
10612472 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
10612473 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
10612474 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
10612475 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
10612476 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
10612477 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
10612478 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
10612479 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
10612480 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
10612481 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
10612482 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
10612483 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
10612484 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
10612563 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
10612564 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
10612565 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
10612566 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
10612567 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
10612568 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Non-Ducted Indoor Units | 138000 | 13.5 | 25.7 | 154000 | 3.77 | 109000 | 2.65 | R-410A | 11.5
10612569 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Ducted Indoor Units | 138000 | 12.2 | 20 | 154000 | 3.57 | 109000 | 2.54 | R-410A | 11.5
10612570 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
10612572 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
10612574 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
10612575 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
10612576 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
10612577 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
10612578 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
10612579 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
10612580 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
10612581 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
10612582 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
10612583 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
10612584 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
10612585 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
10612586 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
10612587 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
10612588 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
10612589 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
10612590 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
10612591 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
10612592 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
10612593 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
10612594 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
10612596 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
10612663 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
10612664 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
10612707 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
9133436 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V | TVRF-OC72KHP/220V |  |  | TVRF-OC144KHP/220V | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
9133438 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V | TVRF-OC72KHP/220V |  |  | TVRF-OC144KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 21.6 | 154000 | 3.5 | 100000 | 2.3 | R-410A | 11.5
8657018 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144ZKMU-A |  |  |  | PUHY-P144ZKMU-A | Non-Ducted Indoor Units | 136000 | 13.1 | 23.9 | 152000 | 3.73 | 109000 | 2.22 | R-410A | 11.3333
8657020 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P72ZKMU-A |  |  | PUHY-P168ZSKMU-A | Non-Ducted Indoor Units | 160000 | 13.3 | 24.8 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
8657022 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A |  |  | PUHY-P192ZSKMU-A | Non-Ducted Indoor Units | 182000 | 13.2 | 23.7 | 204000 | 3.68 | 150000 | 2.17 | R-410A | 15.1667
8657024 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P216ZSKMU-A | Non-Ducted Indoor Units | 206000 | 12.7 | 23.2 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
9121962 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9121963 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9121964 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H196DXN1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9121965 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H196DXN1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9121966 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 |  |  | MV5-H216DXN1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9121967 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 |  |  | MV5-H216DXN1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9121968 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 |  |  | MV5-H240DXN1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9121969 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 |  |  | MV5-H240DXN1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9121983 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9121984 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9121985 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H196DZN1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9121986 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H196DZN1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9121987 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 |  |  | MV5-H216DZN1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9121988 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 |  |  | MV5-H216DZN1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9121989 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 |  |  | MV5-H240DZN1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9121990 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 |  |  | MV5-H240DZN1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9122292 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9122293 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H196DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9122294 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 |  |  | MV5-H216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9122295 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 |  |  | MV5-H240DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9122308 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9122309 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H196DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9122310 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 |  |  | MV5-H216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9122311 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 |  |  | MV5-H240DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9122950 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Non-Ducted Indoor Units | 138000 | 12.5 | 26.6 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
9122951 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 24 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
9122952 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.5 | 26.9 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
9122953 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Non-Ducted Indoor Units | 184000 | 12 | 26 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
9122954 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.9 | 24.9 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
9122955 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 24 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
9122956 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Non-Ducted Indoor Units | 230000 | 11 | 23.5 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9122977 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Ducted Indoor Units | 138000 | 12 | 23 | 154000 | 3.6 | 109000 | 2.54 | R-410A | 11.5
9122978 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Non-Ducted Indoor Units | 138000 | 12.5 | 26.6 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
9122979 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Ducted Indoor Units | 138000 | 12 | 23 | 154000 | 3.6 | 109000 | 2.54 | R-410A | 11.5
9122980 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Ducted Indoor Units | 160000 | 11 | 22 | 180000 | 3.3 | 132000 | 2.4 | R-410A | 13.3333
9122981 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 24 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
9122982 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Ducted Indoor Units | 160000 | 11 | 22 | 180000 | 3.3 | 132000 | 2.4 | R-410A | 13.3333
9122983 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Ducted Indoor Units | 184000 | 12.2 | 24 | 206000 | 3.75 | 150000 | 2.5 | R-410A | 15.3333
9122984 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.5 | 26.9 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
9122985 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Ducted Indoor Units | 184000 | 12.2 | 24 | 206000 | 3.75 | 150000 | 2.5 | R-410A | 15.3333
9122986 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Ducted Indoor Units | 184000 | 12 | 23.5 | 206000 | 3.65 | 150000 | 2.45 | R-410A | 15.3333
9122987 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Non-Ducted Indoor Units | 184000 | 12 | 26 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
9122988 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Ducted Indoor Units | 184000 | 12 | 23.5 | 206000 | 3.65 | 150000 | 2.45 | R-410A | 15.3333
9122989 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Ducted Indoor Units | 206000 | 11.8 | 23.5 | 232000 | 3.8 | 164000 | 2.48 | R-410A | 17.1667
9122990 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.9 | 24.9 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
9122991 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Ducted Indoor Units | 206000 | 11.8 | 23.5 | 232000 | 3.8 | 164000 | 2.48 | R-410A | 17.1667
9122992 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Ducted Indoor Units | 230000 | 11.9 | 23 | 256000 | 3.6 | 182000 | 2.5 | R-410A | 19.1667
9122993 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 24 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
9122994 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Ducted Indoor Units | 230000 | 11.9 | 23 | 256000 | 3.6 | 182000 | 2.5 | R-410A | 19.1667
9122995 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Ducted Indoor Units | 230000 | 11 | 22.5 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9122996 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Non-Ducted Indoor Units | 230000 | 11 | 23.5 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9122997 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Ducted Indoor Units | 230000 | 11 | 22.5 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9123037 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.25 | 24.8 | 154000 | 3.67 | 109000 | 2.57 | R-410A | 11.5
9123038 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.25 | 24.8 | 154000 | 3.67 | 109000 | 2.57 | R-410A | 11.5
9123039 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 23 | 180000 | 3.37 | 132000 | 2.4 | R-410A | 13.3333
9123040 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 23 | 180000 | 3.37 | 132000 | 2.4 | R-410A | 13.3333
9123041 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.35 | 25.45 | 206000 | 3.72 | 150000 | 2.5 | R-410A | 15.3333
9123042 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.35 | 25.45 | 206000 | 3.72 | 150000 | 2.5 | R-410A | 15.3333
9123043 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12 | 24.75 | 206000 | 3.62 | 150000 | 2.45 | R-410A | 15.3333
9123044 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12 | 24.75 | 206000 | 3.62 | 150000 | 2.45 | R-410A | 15.3333
9123045 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.85 | 24.2 | 232000 | 3.68 | 164000 | 2.47 | R-410A | 17.1667
9123046 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.85 | 24.2 | 232000 | 3.68 | 164000 | 2.47 | R-410A | 17.1667
9123047 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.9 | 23.5 | 256000 | 3.6 | 182000 | 2.51 | R-410A | 19.1667
9123048 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.9 | 23.5 | 256000 | 3.6 | 182000 | 2.51 | R-410A | 19.1667
9123049 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 23 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9123050 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 23 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
8578650 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R144DZN1-(A) |  |  |  | MV5-R144DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 10.8 | 19.5 | 150000 | 3.37 | 102000 | 2.25 | R-410A | 11.3333
8578651 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X144DZN1-(A) |  |  |  | MV5-X144DZN1-(A) | Non-Ducted Indoor Units | 136000 | 10.9 | 19.5 | 150000 | 3.4 | 102000 | 2.28 | R-410A | 11.3333
8656998 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144ZKMU-A |  |  |  | PURY-P144ZKMU-A | Non-Ducted Indoor Units | 136000 | 12.8 | 21.9 | 152000 | 3.57 | 97000 | 2.13 | R-410A | 11.3333
8657000 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A | PURY-P72ZKMU-A |  |  | PURY-P168ZSKMU-A | Non-Ducted Indoor Units | 160000 | 12.4 | 21 | 178000 | 3.6 | 119000 | 2.13 | R-410A | 13.3333
8657002 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A | PURY-P96ZKMU-A |  |  | PURY-P192ZSKMU-A | Non-Ducted Indoor Units | 182000 | 11.8 | 21.2 | 204000 | 3.48 | 142000 | 2.1 | R-410A | 15.1667
9045754 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045756 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045778 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045780 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045802 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045804 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9060358 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060360 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060361 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060362 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060364 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060365 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060374 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060376 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060377 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060378 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060380 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060381 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060390 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060392 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060393 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060394 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060396 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060397 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060406 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060407 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060408 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060409 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060414 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060415 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060416 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060417 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060422 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060423 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060424 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060425 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9085402 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
9085403 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 4 | 109000 | 2.85 | R-410A | 11.5
9085404 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
9085405 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Ducted Indoor Units | 160000 | 11.2 | 21 | 180000 | 3.7 | 132000 | 2.7 | R-410A | 13.3333
9085406 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
9085407 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Ducted Indoor Units | 184000 | 12.7 | 23 | 206000 | 4.1 | 150000 | 2.95 | R-410A | 15.3333
9085408 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
9085409 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Ducted Indoor Units | 184000 | 12.3 | 22.6 | 206000 | 3.92 | 150000 | 2.8 | R-410A | 15.3333
9085410 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
9085411 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Ducted Indoor Units | 206000 | 12.5 | 22.5 | 232000 | 4 | 164000 | 2.92 | R-410A | 17.1667
9085412 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
9085413 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Ducted Indoor Units | 230000 | 12.4 | 22.2 | 256000 | 4 | 182000 | 2.95 | R-410A | 19.1667
9085414 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
9085415 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Ducted Indoor Units | 230000 | 12.3 | 21.8 | 256000 | 3.95 | 182000 | 2.9 | R-410A | 19.1667
9085441 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12 | 23.85 | 154000 | 4.06 | 109000 | 2.79 | R-410A | 11.5
9085442 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 22.4 | 180000 | 3.72 | 132000 | 2.59 | R-410A | 13.3333
9085443 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.75 | 24.25 | 206000 | 4.07 | 150000 | 2.85 | R-410A | 15.3333
9085444 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.45 | 23.85 | 206000 | 3.93 | 150000 | 2.74 | R-410A | 15.3333
9085445 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.25 | 23.55 | 232000 | 3.95 | 164000 | 2.83 | R-410A | 17.1667
9085446 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.2 | 23.15 | 256000 | 3.87 | 182000 | 2.8 | R-410A | 19.1667
9085447 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.95 | 22.7 | 256000 | 3.82 | 182000 | 2.76 | R-410A | 19.1667
8578653 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X144DZN1-(A) |  |  |  | MV5-X144DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 10.75 | 19.5 | 150000 | 3.4 | 102000 | 2.28 | R-410A | 11.3333
8577925 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R144DXN1-(A) |  |  |  | MV5-R144DXN1-(A) | Non-Ducted Indoor Units | 136000 | 11 | 19.5 | 150000 | 3.4 | 102000 | 2.25 | R-410A | 11.3333
8578410 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R144DXN1-(A) |  |  |  | MV5-R144DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 10.8 | 19.5 | 150000 | 3.37 | 102000 | 2.25 | R-410A | 11.3333
8578615 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X144DXN1-(A) |  |  |  | MV5-X144DXN1-(A) | Non-Ducted Indoor Units | 136000 | 10.9 | 19.5 | 150000 | 3.4 | 102000 | 2.28 | R-410A | 11.3333
8578639 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X144DXN1-(A) |  |  |  | MV5-X144DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 10.75 | 19.5 | 150000 | 3.37 | 102000 | 2.28 | R-410A | 11.3333
8989554 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
8989555 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
8989556 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
8989557 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
8989558 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
8989559 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
8989569 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 4 | 109000 | 2.85 | R-410A | 11.5
8989570 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Ducted Indoor Units | 160000 | 11.2 | 21 | 180000 | 3.7 | 132000 | 2.7 | R-410A | 13.3333
8989571 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Ducted Indoor Units | 184000 | 12.7 | 23 | 206000 | 4.1 | 150000 | 2.95 | R-410A | 15.3333
8989572 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Ducted Indoor Units | 184000 | 12.3 | 22.6 | 206000 | 3.92 | 150000 | 2.8 | R-410A | 15.3333
8989573 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Ducted Indoor Units | 206000 | 12.5 | 22.5 | 232000 | 4 | 164000 | 2.92 | R-410A | 17.1667
8989574 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Ducted Indoor Units | 230000 | 12.4 | 22.2 | 256000 | 4 | 182000 | 2.95 | R-410A | 19.1667
8989575 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
8989610 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12 | 23.85 | 154000 | 4.06 | 109000 | 2.79 | R-410A | 11.5
8989611 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 22.4 | 180000 | 3.72 | 132000 | 2.59 | R-410A | 13.3333
8989612 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.75 | 24.25 | 206000 | 4.07 | 150000 | 2.85 | R-410A | 15.3333
8989613 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.45 | 23.85 | 206000 | 3.93 | 150000 | 2.74 | R-410A | 15.3333
8989614 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.25 | 23.55 | 232000 | 3.95 | 164000 | 2.83 | R-410A | 17.1667
8989615 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.2 | 23.15 | 256000 | 3.87 | 182000 | 2.8 | R-410A | 19.1667
8989616 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Ducted Indoor Units | 230000 | 12.3 | 21.8 | 256000 | 3.95 | 182000 | 2.9 | R-410A | 19.1667
8989622 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.95 | 22.7 | 256000 | 3.82 | 182000 | 2.76 | R-410A | 19.1667
7041885 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU |  |  |  | RXYQ144TTJU | Ducted Indoor Units | 138000 | 11.5 | 21 | 154000 | 3.72 | 96000 | 2.2 | R-410A | 11.5
7041886 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN |  |  |  | RXYQ144TYDN | Ducted Indoor Units | 138000 | 11.5 | 21 | 154000 | 3.72 | 96000 | 2.2 | R-410A | 11.5
7041887 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU |  |  |  | RXYQ144TTJU | Non-Ducted Indoor Units | 138000 | 12.3 | 24.1 | 154000 | 4.1 | 96000 | 2.33 | R-410A | 11.5
7041888 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN |  |  |  | RXYQ144TYDN | Non-Ducted Indoor Units | 138000 | 12.3 | 24.1 | 154000 | 4.1 | 96000 | 2.33 | R-410A | 11.5
7041893 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU | RXYQ120TTJU |  |  | RXYQ192TTJU | Ducted Indoor Units | 184000 | 12.3 | 20.7 | 206000 | 3.6 | 134000 | 2.4 | R-410A | 15.3333
7041894 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN | RXYQ120TYDN |  |  | RXYQ192TYDN | Ducted Indoor Units | 184000 | 12.3 | 20.7 | 206000 | 3.6 | 134000 | 2.4 | R-410A | 15.3333
7041895 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU | RXYQ120TTJU |  |  | RXYQ192TTJU | Non-Ducted Indoor Units | 184000 | 11.9 | 22.2 | 206000 | 3.8 | 134000 | 2.27 | R-410A | 15.3333
7041896 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN | RXYQ120TYDN |  |  | RXYQ192TYDN | Non-Ducted Indoor Units | 184000 | 11.9 | 22.2 | 206000 | 3.8 | 134000 | 2.27 | R-410A | 15.3333
7041913 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU |  |  | RXYQ216TTJU | Ducted Indoor Units | 206000 | 11.7 | 20 | 230000 | 3.65 | 158000 | 2.48 | R-410A | 17.1667
7041914 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN |  |  | RXYQ216TYDN | Ducted Indoor Units | 206000 | 11.7 | 20 | 230000 | 3.65 | 158000 | 2.48 | R-410A | 17.1667
7041915 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU |  |  | RXYQ216TTJU | Non-Ducted Indoor Units | 206000 | 11.6 | 20.5 | 230000 | 3.83 | 158000 | 2.62 | R-410A | 17.1667
7041916 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN |  |  | RXYQ216TYDN | Non-Ducted Indoor Units | 206000 | 11.6 | 20.5 | 230000 | 3.83 | 158000 | 2.62 | R-410A | 17.1667
7042715 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU |  |  |  | RXYQ144TTJU | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.9 | 22.55 | 154000 | 3.91 | 96000 | 2.26 | R-410A | 11.5
7042716 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN |  |  |  | RXYQ144TYDN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.9 | 22.55 | 154000 | 3.91 | 96000 | 2.26 | R-410A | 11.5
7042719 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU | RXYQ120TTJU |  |  | RXYQ192TTJU | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 21.45 | 206000 | 3.7 | 134000 | 2.33 | R-410A | 15.3333
7042720 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN | RXYQ120TYDN |  |  | RXYQ192TYDN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 21.45 | 206000 | 3.7 | 134000 | 2.33 | R-410A | 15.3333
7042721 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU |  |  | RXYQ216TTJU | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.25 | 230000 | 3.74 | 158000 | 2.55 | R-410A | 17.1667
7042722 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN |  |  | RXYQ216TYDN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.25 | 230000 | 3.74 | 158000 | 2.55 | R-410A | 17.1667
7064754 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU |  |  | RXYQ240TTJU | Ducted Indoor Units | 228000 | 11.6 | 18.4 | 256000 | 3.55 | 172000 | 2.43 | R-410A | 19
7064755 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN |  |  | RXYQ240TYDN | Ducted Indoor Units | 228000 | 11.6 | 18.4 | 256000 | 3.55 | 172000 | 2.43 | R-410A | 19
7064756 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU |  |  | RXYQ240TTJU | Non-Ducted Indoor Units | 228000 | 11.5 | 20.8 | 256000 | 3.63 | 172000 | 2.62 | R-410A | 19
7064757 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN |  |  | RXYQ240TYDN | Non-Ducted Indoor Units | 228000 | 11.5 | 20.8 | 256000 | 3.63 | 172000 | 2.62 | R-410A | 19
7064759 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU |  |  | RXYQ240TTJU | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.55 | 19.6 | 256000 | 3.59 | 172000 | 2.52 | R-410A | 19
7064760 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN |  |  | RXYQ240TYDN | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.55 | 19.6 | 256000 | 3.59 | 172000 | 2.52 | R-410A | 19
7159062 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-144ME2U9 |  |  |  | U-144ME2U9 | Non-Ducted Indoor Units | 138000 | 10.9 | 23.4 | 154000 | 3.41 | 100000 | 2.45 | R-410A | 11.5
7159374 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-96ME2U9 | U-96ME2U9 |  |  | WU-192ME2U9 | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.25 | 134000 | 2.39 | R-410A | 15.3333
7490342 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-U |  |  |  | PUHY-P144TKMU-U | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
7490343 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-U |  |  |  | PUHY-P144TKMU-U | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 109000 | 2.32 | R-410A | 11.3333
7490344 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-U |  |  |  | PUHY-P144YKMU-U | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
7490345 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-U |  |  |  | PUHY-P144YKMU-U | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 108000 | 2.32 | R-410A | 11.3333
7490347 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P144YSKMU-U | Non-Ducted Indoor Units | 136000 | 13.2 | 20.3 | 152000 | 3.95 | 109000 | 2.13 | R-410A | 11.3333
7490349 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P144YSKMU-U | Ducted Indoor Units | 136000 | 12.8 | 19.3 | 152000 | 3.79 | 108000 | 2.56 | R-410A | 11.3333
7490351 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-U | PUHY-P72TKMU-U |  |  | PUHY-P168TSKMU-U | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
7490353 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-U | PUHY-P72TKMU-U |  |  | PUHY-P168TSKMU-U | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
7490355 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P168YSKMU-U | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
7490356 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P168YSKMU-U | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
7490358 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P72TKMU-U |  |  | PUHY-P192TSKMU-U | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
7490360 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P72TKMU-U |  |  | PUHY-P192TSKMU-U | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 204000 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
7490362 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P192YSKMU-U | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
7490363 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P192YSKMU-U | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 20400 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
7490365 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P96TKMU-U |  |  | PUHY-P216TSKMU-U | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
7490367 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P96TKMU-U |  |  | PUHY-P216TSKMU-U | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
7490369 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P96YKMU-U |  |  | PUHY-P216YSKMU-U | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
7490370 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P96YKMU-U |  |  | PUHY-P216YSKMU-U | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
7490374 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U |  |  | PUHY-P240TSKMU-U | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
7490377 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U |  |  | PUHY-P240YSKMU-U | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
7490430 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-U |  |  |  | PURY-P144TKMU-U | Ducted Indoor Units | 136000 | 11.7 | 18 | 152000 | 3.41 | 109000 | 2.32 | R-410A | 11.3333
7490432 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-U |  |  |  | PURY-P144YKMU-U | Ducted Indoor Units | 136000 | 11.7 | 18 | 152000 | 3.41 | 109000 | 2.32 | R-410A | 11.3333
7490434 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-U | PURY-P72YKMU-U |  |  | PURY-P144YSKMU-U | Ducted Indoor Units | 136000 | 12 | 18.8 | 152000 | 3.54 | 109000 | 2.41 | R-410A | 11.3333
7490435 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-U | PURY-P72YKMU-U |  |  | PURY-P144YSKMU-U | Non-Ducted Indoor Units | 136000 | 14.4 | 20.6 | 152000 | 3.65 | 109000 | 2.3 | R-410A | 11.3333
7490436 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U | PURY-P72TKMU-U |  |  | PURY-P168TSKMU-U | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
7490437 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U | PURY-P72TKMU-U |  |  | PURY-P168TSKMU-U | Non-Ducted Indoor Units | 160000 | 12.9 | 19.1 | 178000 | 3.52 | 132000 | 2.22 | R-410A | 13.3333
7490438 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U | PURY-P72YKMU-U |  |  | PURY-P168YSKMU-U | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
7490439 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U | PURY-P72YKMU-U |  |  | PURY-P168YSKMU-U | Non-Ducted Indoor Units | 160000 | 12.9 | 19.1 | 178000 | 3.52 | 132000 | 2.22 | R-410A | 13.3333
7490440 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U | PURY-P96TKMU-U |  |  | PURY-P192TSKMU-U | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
7490441 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U | PURY-P96TKMU-U |  |  | PURY-P192TSKMU-U | Non-Ducted Indoor Units | 182000 | 11.9 | 18.2 | 204000 | 3.47 | 150000 | 2.18 | R-410A | 15.1667
7490442 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U | PURY-P96YKMU-U |  |  | PURY-P192YSKMU-U | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
7490444 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U | PURY-P96YKMU-U |  |  | PURY-P192YSKMU-U | Non-Ducted Indoor Units | 182000 | 11.9 | 18.2 | 204000 | 3.47 | 150000 | 2.18 | R-410A | 15.1667
7490445 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-U | PURY-P96TKMU-U |  |  | PURY-P216TSKMU-U | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
7490446 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-U | PURY-P96TKMU-U |  |  | PURY-P216TSKMU-U | Non-Ducted Indoor Units | 206000 | 11.3 | 18.3 | 232000 | 3.43 | 164000 | 2.16 | R-410A | 17.1667
7490447 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-U | PURY-P96YKMU-U |  |  | PURY-P216YSKMU-U | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
7490448 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-U | PURY-P96YKMU-U |  |  | PURY-P216YSKMU-U | Non-Ducted Indoor Units | 206000 | 11.3 | 18.3 | 232000 | 3.43 | 164000 | 2.16 | R-410A | 17.1667
7490451 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-U | PURY-P120TKMU-U |  |  | PURY-P240TSKMU-U | Non-Ducted Indoor Units | 228000 | 10.9 | 18.5 | 258000 | 3.42 | 182000 | 2.15 | R-410A | 19
7490453 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-U | PURY-P120YKMU-U |  |  | PURY-P240YSKMU-U | Non-Ducted Indoor Units | 228000 | 10.9 | 18.5 | 258000 | 3.42 | 182000 | 2.15 | R-410A | 19
7505345 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ144PBTJ |  |  |  | REYQ144PBTJ | Non-Ducted Indoor Units | 138000 | 11.2 | 18.9 | 154000 | 3.6 | 104000 | 2.55 | R-410A | 11.5
7505347 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Non-Ducted Indoor Units | 138000 | 13.8 | 22.5 | 154000 | 3.8 | 104000 | 2.55 | R-410A | 11.5
7505348 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Ducted Indoor Units | 138000 | 13.7 | 20 | 154000 | 3.6 | 104000 | 2.4 | R-410A | 11.5
7505349 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Non-Ducted Indoor Units | 160000 | 12 | 20.3 | 180000 | 3.7 | 122000 | 2.5 | R-410A | 13.3333
7505350 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Ducted Indoor Units | 160000 | 11.5 | 19.4 | 180000 | 3.5 | 122000 | 2.35 | R-410A | 13.3333
7505351 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Non-Ducted Indoor Units | 160000 | 12 | 20.3 | 180000 | 3.7 | 122000 | 2.5 | R-410A | 13.3333
7505352 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Ducted Indoor Units | 160000 | 11.5 | 19.4 | 180000 | 3.5 | 122000 | 2.35 | R-410A | 13.3333
7505353 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBTJ | REMQ96PBTJ |  |  | REYQ192PBTJ | Non-Ducted Indoor Units | 184000 | 11.2 | 18.7 | 206000 | 3.4 | 138000 | 2.5 | R-410A | 15.3333
7505354 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBYD | REMQ96PBYD |  |  | REYQ192PBYD | Non-Ducted Indoor Units | 184000 | 11.2 | 18.7 | 206000 | 3.4 | 138000 | 2.5 | R-410A | 15.3333
7505410 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.75 | 21.25 | 154000 | 3.7 | 104000 | 2.47 | R-410A | 11.5
7505411 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.75 | 19.85 | 180000 | 3.6 | 122000 | 2.42 | R-410A | 13.3333
7505412 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.75 | 19.85 | 180000 | 3.6 | 122000 | 2.42 | R-410A | 13.3333
7628554 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU |  |  |  | REYQ168TTJU | Non-Ducted Indoor Units | 156000 | 11.7 | 22 | 176000 | 3.77 | 128000 | 2.32 | R-410A | 13
7628557 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN |  |  |  | REYQ168TYDN | Non-Ducted Indoor Units | 156000 | 11.7 | 22 | 176000 | 3.77 | 128000 | 2.32 | R-410A | 13
7628559 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU | REYQ120TTJU |  |  | REYQ192TTJU | Non-Ducted Indoor Units | 180000 | 12.5 | 22.9 | 200000 | 3.84 | 146000 | 2.55 | R-410A | 15
7628561 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN | REYQ120TYDN |  |  | REYQ192TYDN | Non-Ducted Indoor Units | 180000 | 12.5 | 22.9 | 200000 | 3.84 | 146000 | 2.55 | R-410A | 15
7628563 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU | REYQ120TTJU |  |  | REYQ216TTJU | Non-Ducted Indoor Units | 200000 | 12.5 | 22.9 | 226000 | 3.73 | 160000 | 2.45 | R-410A | 16.6667
7628566 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN | REYQ120TYDN |  |  | REYQ216TYDN | Non-Ducted Indoor Units | 200000 | 12.5 | 22.9 | 226000 | 3.73 | 160000 | 2.45 | R-410A | 16.6667
7628567 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU |  |  | REYQ240TTJU | Non-Ducted Indoor Units | 222000 | 12.2 | 21.9 | 250000 | 3.67 | 178000 | 2.48 | R-410A | 18.5
7628570 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN |  |  | REYQ240TYDN | Non-Ducted Indoor Units | 222000 | 12.2 | 21.9 | 250000 | 3.67 | 178000 | 2.48 | R-410A | 18.5
7628626 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU |  |  |  | REYQ168TTJU | Ducted Indoor Units | 156000 | 11.3 | 20.8 | 176000 | 3.33 | 128000 | 2.15 | R-410A | 13
7628627 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN |  |  |  | REYQ168TYDN | Ducted Indoor Units | 156000 | 11.3 | 20.8 | 176000 | 3.33 | 128000 | 2.15 | R-410A | 13
7628630 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU | REYQ120TTJU |  |  | REYQ192TTJU | Ducted Indoor Units | 180000 | 12.6 | 21.1 | 200000 | 3.67 | 146000 | 2.38 | R-410A | 15
7628632 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN | REYQ120TYDN |  |  | REYQ192TYDN | Ducted Indoor Units | 180000 | 12.6 | 21.1 | 200000 | 3.67 | 146000 | 2.38 | R-410A | 15
7628634 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU | REYQ120TTJU |  |  | REYQ216TTJU | Ducted Indoor Units | 200000 | 12.4 | 20.8 | 226000 | 3.67 | 160000 | 2.28 | R-410A | 16.6667
7628636 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN | REYQ120TYDN |  |  | REYQ216TYDN | Ducted Indoor Units | 200000 | 12.4 | 20.8 | 226000 | 3.67 | 160000 | 2.28 | R-410A | 16.6667
7628639 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU |  |  | REYQ240TTJU | Ducted Indoor Units | 222000 | 11.6 | 19.8 | 250000 | 3.55 | 178000 | 2.31 | R-410A | 18.5
7628640 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN |  |  | REYQ240TYDN | Ducted Indoor Units | 222000 | 11.6 | 19.8 | 250000 | 3.55 | 178000 | 2.31 | R-410A | 18.5
7629591 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU |  |  |  | REYQ168TTJU | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.5 | 21.4 | 176000 | 3.55 | 128000 | 2.23 | R-410A | 13
7629594 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN |  |  |  | REYQ168TYDN | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.5 | 21.4 | 176000 | 3.55 | 128000 | 2.23 | R-410A | 13
7629595 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU | REYQ120TTJU |  |  | REYQ192TTJU | Mixed Ducted and Non-Ducted Indoor Units | 180000 | 12.55 | 22 | 200000 | 3.75 | 146000 | 2.46 | R-410A | 15
7629598 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN | REYQ120TYDN |  |  | REYQ192TYDN | Mixed Ducted and Non-Ducted Indoor Units | 180000 | 12.55 | 22 | 200000 | 3.75 | 146000 | 2.46 | R-410A | 15
7629601 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU | REYQ120TTJU |  |  | REYQ216TTJU | Mixed Ducted and Non-Ducted Indoor Units | 200000 | 12.45 | 21.85 | 226000 | 3.7 | 160000 | 2.36 | R-410A | 16.6667
7629603 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN | REYQ120TYDN |  |  | REYQ216TYDN | Mixed Ducted and Non-Ducted Indoor Units | 200000 | 12.45 | 21.85 | 226000 | 3.7 | 160000 | 2.36 | R-410A | 16.6667
7629606 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU |  |  | REYQ240TTJU | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 11.9 | 20.85 | 250000 | 3.61 | 178000 | 2.39 | R-410A | 18.5
7629608 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN |  |  | REYQ240TYDN | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 11.9 | 20.85 | 250000 | 3.61 | 178000 | 2.39 | R-410A | 18.5
7850825 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850827 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850829 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
7850831 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850833 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850845 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850847 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850849 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
7850851 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850853 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7987132 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987133 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987134 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987135 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987137 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S |  |  | TVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987139 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987141 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987152 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987153 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987154 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987155 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987157 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S |  |  | TVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987159 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987161 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987178 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987179 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987180 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987181 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987185 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987187 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987198 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987199 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987200 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987201 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987205 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987207 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987224 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987225 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987226 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987227 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987229 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S |  |  | HVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987231 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987233 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987244 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987245 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987246 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987247 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987249 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S |  |  | HVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987251 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987253 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987270 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987271 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987272 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987273 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987277 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987279 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987290 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987291 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987292 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987293 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987297 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987299 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987316 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987317 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987318 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987319 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987321 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S |  |  | YVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987323 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987325 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987336 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987337 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987338 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987339 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987341 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S |  |  | YVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987343 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987345 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987362 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987363 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987364 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987365 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987369 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987371 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987382 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987383 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987384 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987385 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987389 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987391 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7990693 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990694 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990695 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S |  |  | TVAHP192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990697 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990698 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990707 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990708 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990709 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S |  |  | TVAHR192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990710 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990711 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990720 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990721 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990723 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990724 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990734 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990735 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990737 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990738 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.8 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990747 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990748 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990749 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S |  |  | HVAHP192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990750 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990751 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990760 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990761 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990762 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S |  |  | HVAHR192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990764 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990765 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990774 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990775 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990777 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990778 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990787 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990788 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990790 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990791 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.8 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990802 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990803 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S |  |  | YVAHP192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990804 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990805 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990814 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990815 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990816 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S |  |  | YVAHR192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990817 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990818 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990827 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990828 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990830 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990831 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990840 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990841 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990843 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990844 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.8 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
8033331 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P144YSKMU-* | Non-Ducted Indoor Units | 136000 | 13.2 | 20.3 | 152000 | 3.95 | 109000 | 2.13 | R-410A | 11.3333
8033332 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P144YSKMU-* | Ducted Indoor Units | 136000 | 12.8 | 19.3 | 152000 | 3.79 | 108000 | 2.56 | R-410A | 11.3333
8033333 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-* | PUHY-P72TKMU-* |  |  | PUHY-P168TSKMU-* | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
8033334 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-* | PUHY-P72TKMU-* |  |  | PUHY-P168TSKMU-* | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
8033335 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P168YSKMU-* | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
8033336 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P168YSKMU-* | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
8033337 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P72TKMU-* |  |  | PUHY-P192TSKMU-* | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
8033338 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P72TKMU-* |  |  | PUHY-P192TSKMU-* | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 204000 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
8033339 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P192YSKMU-* | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
8033340 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P192YSKMU-* | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 20400 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
8033341 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P96TKMU-* |  |  | PUHY-P216TSKMU-* | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
8033342 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P96TKMU-* |  |  | PUHY-P216TSKMU-* | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
8033343 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P96YKMU-* |  |  | PUHY-P216YSKMU-* | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
8033344 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P96YKMU-* |  |  | PUHY-P216YSKMU-* | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
8033346 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* |  |  | PUHY-P240TSKMU-* | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
8033348 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* |  |  | PUHY-P240YSKMU-* | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
8033369 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-* | PURY-P72YKMU-* |  |  | PURY-P144YSKMU-* | Ducted Indoor Units | 136000 | 12 | 18.8 | 152000 | 3.54 | 109000 | 2.41 | R-410A | 11.3333
8033370 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-* | PURY-P72YKMU-* |  |  | PURY-P144YSKMU-* | Non-Ducted Indoor Units | 136000 | 14.4 | 20.6 | 152000 | 3.62 | 109000 | 2.28 | R-410A | 11.3333
8033371 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-* | PURY-P72TKMU-* |  |  | PURY-P168TSKMU-* | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
8033372 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-* | PURY-P72TKMU-* |  |  | PURY-P168TSKMU-* | Non-Ducted Indoor Units | 160000 | 12.9 | 19.1 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
8033373 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-* | PURY-P72YKMU-* |  |  | PURY-P168YSKMU-* | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
8033374 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-* | PURY-P72YKMU-* |  |  | PURY-P168YSKMU-* | Non-Ducted Indoor Units | 160000 | 12.9 | 19.1 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
8033375 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-* | PURY-P96TKMU-* |  |  | PURY-P192TSKMU-* | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
8033376 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-* | PURY-P96TKMU-* |  |  | PURY-P192TSKMU-* | Non-Ducted Indoor Units | 182000 | 11.9 | 18.2 | 204000 | 3.45 | 150000 | 2.17 | R-410A | 15.1667
8033377 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-* | PURY-P96YKMU-* |  |  | PURY-P192YSKMU-* | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
8033378 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-* | PURY-P96YKMU-* |  |  | PURY-P192YSKMU-* | Non-Ducted Indoor Units | 182000 | 11.9 | 18.2 | 204000 | 3.45 | 150000 | 2.17 | R-410A | 15.1667
8033379 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-* | PURY-P96TKMU-* |  |  | PURY-P216TSKMU-* | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
8033380 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-* | PURY-P96TKMU-* |  |  | PURY-P216TSKMU-* | Non-Ducted Indoor Units | 206000 | 11.3 | 18.3 | 232000 | 3.41 | 164000 | 2.15 | R-410A | 17.1667
8033381 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-* | PURY-P96YKMU-* |  |  | PURY-P216YSKMU-* | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
8033382 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-* | PURY-P96YKMU-* |  |  | PURY-P216YSKMU-* | Non-Ducted Indoor Units | 206000 | 11.3 | 18.3 | 232000 | 3.41 | 164000 | 2.15 | R-410A | 17.1667
8033384 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-* | PURY-P120TKMU-* |  |  | PURY-P240TSKMU-* | Non-Ducted Indoor Units | 228000 | 10.9 | 18.5 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
8033386 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-* | PURY-P120YKMU-* |  |  | PURY-P240YSKMU-* | Non-Ducted Indoor Units | 228000 | 10.9 | 18.5 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
8175484 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
8175485 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
8175486 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
8175487 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
8175488 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
8175489 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
8175490 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
8175491 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
8175492 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
8175493 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
8175494 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
8175495 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
8175496 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  |  | PUHY-P240YSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
8175514 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
8175515 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
8175516 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
8175517 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
8175518 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
8175519 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
8175520 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
8175521 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
8175522 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
8175523 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
8175524 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
8175525 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
8175526 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  |  | PUHY-P240TSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
8175897 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Ducted Indoor Units | 136000 | 12.2 | 19.7 | 152000 | 3.38 | 97000 | 2.07 | R-410A | 11.3333
8175898 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
8175899 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Ducted Indoor Units | 136000 | 12.3 | 21.2 | 152000 | 3.58 | 97000 | 2.08 | R-410A | 11.3333
8175900 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
8175902 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P168YLMU-A |  |  |  | PURY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
8175903 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Ducted Indoor Units | 160000 | 11 | 19.9 | 178000 | 3.39 | 119000 | 2.23 | R-410A | 13.3333
8175904 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
8175905 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 23.5 | 204000 | 3.53 | 142000 | 2.21 | R-410A | 15.1667
8175906 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
8175907 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 21.5 | 232000 | 3.52 | 158000 | 2.2 | R-410A | 17.1667
8175908 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
8175909 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 19 | 258000 | 3.45 | 174000 | 2.15 | R-410A | 19
8175925 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Ducted Indoor Units | 136000 | 12.2 | 19.7 | 152000 | 3.38 | 97000 | 2.07 | R-410A | 11.3333
8175926 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
8175927 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Ducted Indoor Units | 136000 | 12.3 | 21.2 | 152000 | 3.58 | 97000 | 2.08 | R-410A | 11.3333
8175928 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
8175930 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P168TLMU-A |  |  |  | PURY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
8175931 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Ducted Indoor Units | 160000 | 11 | 19.9 | 178000 | 3.39 | 119000 | 2.23 | R-410A | 13.3333
8175932 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
8175933 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 23.5 | 204000 | 3.53 | 142000 | 2.21 | R-410A | 15.1667
8175934 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
8175935 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 21.5 | 232000 | 3.52 | 158000 | 2.2 | R-410A | 17.1667
8175936 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
8175937 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 19 | 258000 | 3.45 | 174000 | 2.15 | R-410A | 19
4677066 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ144PBTJ |  |  |  | RXYQ144PBTJ | Non-Ducted Indoor Units | 138000 | 11.3 | 20.5 | 154000 | 3.6 | 100000 | 2.55 | R-410A | 11.5
4677068 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ144PBTJ |  |  |  | RXYQ144PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.3 | 19.05 | 154000 | 3.5 | 100000 | 2.5 | R-410A | 11.5
4677069 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ |  |  | RXYQ168PBTJ | Non-Ducted Indoor Units | 160000 | 12.4 | 22 | 180000 | 3.95 | 118000 | 2.65 | R-410A | 13.3333
4677070 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ |  |  | RXYQ168PBTJ | Ducted Indoor Units | 160000 | 12.1 | 20.2 | 180000 | 3.7 | 118000 | 2.45 | R-410A | 13.3333
4677071 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ |  |  | RXYQ168PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.25 | 21.1 | 180000 | 3.82 | 118000 | 2.55 | R-410A | 13.3333
4677072 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ |  |  | RXYQ192PBTJ | Non-Ducted Indoor Units | 184000 | 11.7 | 19.9 | 206000 | 3.7 | 134000 | 2.55 | R-410A | 15.3333
4677073 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ |  |  | RXYQ192PBTJ | Ducted Indoor Units | 184000 | 11.8 | 19.1 | 206000 | 3.55 | 134000 | 2.45 | R-410A | 15.3333
4677074 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ |  |  | RXYQ192PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.75 | 19.5 | 206000 | 3.62 | 134000 | 2.5 | R-410A | 15.3333
4677075 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ | RXYQ120PBTJ |  |  | RXYQ216PBTJ | Non-Ducted Indoor Units | 206000 | 11.6 | 19.2 | 230000 | 3.8 | 150000 | 2.6 | R-410A | 17.1667
4677076 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ | RXYQ120PBTJ |  |  | RXYQ216PBTJ | Ducted Indoor Units | 206000 | 11.7 | 19.5 | 230000 | 3.6 | 150000 | 2.45 | R-410A | 17.1667
4677077 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ | RXYQ120PBTJ |  |  | RXYQ216PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 19.35 | 230000 | 3.7 | 150000 | 2.52 | R-410A | 17.1667
4677078 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ120PBTJ | RXYQ120PBTJ |  |  | RXYQ240PBTJ | Non-Ducted Indoor Units | 228000 | 11.5 | 18.2 | 256000 | 3.6 | 168000 | 2.55 | R-410A | 19
4677099 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD |  |  | RXYQ144PBYD | Non-Ducted Indoor Units | 138000 | 14 | 21.5 | 154000 | 3.9 | 100000 | 2.55 | R-410A | 11.5
4677100 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD |  |  | RXYQ144PBYD | Ducted Indoor Units | 138000 | 12.7 | 22.1 | 154000 | 3.7 | 100000 | 2.45 | R-410A | 11.5
4677101 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD |  |  | RXYQ144PBYD | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.8 | 154000 | 3.8 | 100000 | 2.5 | R-410A | 11.5
4677102 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD |  |  | RXYQ168PBYD | Non-Ducted Indoor Units | 160000 | 12.4 | 22 | 180000 | 3.95 | 118000 | 2.65 | R-410A | 13.3333
4677103 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD |  |  | RXYQ168PBYD | Ducted Indoor Units | 160000 | 12.1 | 20.2 | 180000 | 3.7 | 118000 | 2.45 | R-410A | 13.3333
4677104 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD |  |  | RXYQ168PBYD | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.25 | 21.1 | 180000 | 3.82 | 118000 | 2.55 | R-410A | 13.3333
4677105 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD |  |  | RXYQ192PBYD | Non-Ducted Indoor Units | 184000 | 11.7 | 19.9 | 206000 | 3.7 | 134000 | 2.55 | R-410A | 15.3333
4677106 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD |  |  | RXYQ192PBYD | Ducted Indoor Units | 184000 | 11.8 | 19.1 | 206000 | 3.55 | 134000 | 2.45 | R-410A | 15.3333
4677107 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD |  |  | RXYQ192PBYD | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.75 | 19.5 | 206000 | 3.62 | 134000 | 2.5 | R-410A | 15.3333
4677108 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD | RXYQ120PBYD |  |  | RXYQ216PBYD | Non-Ducted Indoor Units | 206000 | 11.6 | 19.2 | 230000 | 3.8 | 150000 | 2.6 | R-410A | 17.1667
4677109 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD | RXYQ120PBYD |  |  | RXYQ216PBYD | Ducted Indoor Units | 206000 | 11.7 | 19.5 | 230000 | 3.6 | 150000 | 2.45 | R-410A | 17.1667
4677110 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD | RXYQ120PBYD |  |  | RXYQ216PBYD | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 19.35 | 230000 | 3.7 | 150000 | 2.52 | R-410A | 17.1667
4677111 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ120PBYD | RXYQ120PBYD |  |  | RXYQ240PBYD | Non-Ducted Indoor Units | 228000 | 11.5 | 18.2 | 256000 | 3.6 | 168000 | 2.55 | R-410A | 19
4677126 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ144PBTJ |  |  |  | REYQ144PBTJ | Non-Ducted Indoor Units | 138000 | 11.2 | 18.9 | 154000 | 3.6 | 104000 | 2.55 | R-410A | 11.5
4677129 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Non-Ducted Indoor Units | 160000 | 12 | 20.3 | 180000 | 3.7 | 122000 | 2.5 | R-410A | 13.3333
4677130 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Ducted Indoor Units | 160000 | 11.5 | 19.4 | 180000 | 3.5 | 122000 | 2.35 | R-410A | 13.3333
4677131 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.75 | 19.85 | 180000 | 3.6 | 122000 | 2.42 | R-410A | 13.3333
4677132 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBTJ | REMQ96PBTJ |  |  | REYQ192PBTJ | Non-Ducted Indoor Units | 184000 | 11.2 | 18.7 | 206000 | 3.4 | 138000 | 2.5 | R-410A | 15.3333
4677150 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Non-Ducted Indoor Units | 138000 | 13.8 | 22.5 | 154000 | 3.8 | 104000 | 2.55 | R-410A | 11.5
4677151 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Ducted Indoor Units | 138000 | 13.7 | 20 | 154000 | 3.6 | 104000 | 2.4 | R-410A | 11.5
4677152 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.75 | 21.25 | 154000 | 3.7 | 104000 | 2.47 | R-410A | 11.5
4677153 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Non-Ducted Indoor Units | 160000 | 12 | 20.3 | 180000 | 3.7 | 122000 | 2.5 | R-410A | 13.3333
4677154 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Ducted Indoor Units | 160000 | 11.5 | 19.4 | 180000 | 3.5 | 122000 | 2.35 | R-410A | 13.3333
4677155 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.75 | 19.85 | 180000 | 3.6 | 122000 | 2.42 | R-410A | 13.3333
4677156 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBYD | REMQ96PBYD |  |  | REYQ192PBYD | Non-Ducted Indoor Units | 184000 | 11.2 | 18.7 | 206000 | 3.4 | 138000 | 2.5 | R-410A | 15.3333
4679538 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BT3 |  |  |  | ARUB144BT3 | Ducted Indoor Units | 138000 | 11.6 | 19.1 | 154000 | 3.45 | 100000 | 2.46 | R-410A | 11.5
4679539 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BT3 |  |  |  | ARUB144BT3 | Non-Ducted Indoor Units | 138000 | 11.8 | 18.9 | 154000 | 3.67 | 100000 | 2.65 | R-410A | 11.5
4679540 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DT3 |  |  |  | ARUB144DT3 | Ducted Indoor Units | 138000 | 11.6 | 19.1 | 154000 | 3.45 | 100000 | 2.46 | R-410A | 11.5
4679541 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DT3 |  |  |  | ARUB144DT3 | Non-Ducted Indoor Units | 138000 | 11.8 | 18.9 | 154000 | 3.67 | 100000 | 2.65 | R-410A | 11.5
4679542 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB096BT3 |  |  | ARUB168BT3 | Ducted Indoor Units | 160000 | 11.7 | 19.5 | 180000 | 3.33 | 118000 | 2.47 | R-410A | 13.3333
4679543 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB096BT3 |  |  | ARUB168BT3 | Non-Ducted Indoor Units | 160000 | 12.7 | 22.1 | 180000 | 3.77 | 118000 | 2.66 | R-410A | 13.3333
4679544 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB096DT3 |  |  | ARUB168DT3 | Ducted Indoor Units | 160000 | 11.7 | 19.5 | 180000 | 3.33 | 118000 | 2.47 | R-410A | 13.3333
4679545 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB096DT3 |  |  | ARUB168DT3 | Non-Ducted Indoor Units | 160000 | 12.7 | 22.1 | 180000 | 3.77 | 118000 | 2.66 | R-410A | 13.3333
4679546 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB121BT3 |  |  | ARUB192BT3 | Ducted Indoor Units | 184000 | 11.4 | 18.5 | 206000 | 3.32 | 134000 | 2.46 | R-410A | 15.3333
4679547 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB121BT3 |  |  | ARUB192BT3 | Non-Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679548 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB121DT3 |  |  | ARUB192DT3 | Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679549 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB121DT3 |  |  | ARUB192DT3 | Non-Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679550 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB144BT3 |  |  | ARUB216BT3 | Ducted Indoor Units | 206000 | 11 | 19.7 | 230000 | 3.41 | 150000 | 2.44 | R-410A | 17.1667
4679551 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB144BT3 |  |  | ARUB216BT3 | Non-Ducted Indoor Units | 206000 | 11.5 | 19.3 | 230000 | 3.71 | 150000 | 2.58 | R-410A | 17.1667
4679552 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB144DT3 |  |  | ARUB216DT3 | Ducted Indoor Units | 206000 | 11 | 19.7 | 230000 | 3.41 | 150000 | 2.44 | R-410A | 17.1667
4679553 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB144DT3 |  |  | ARUB216DT3 | Non-Ducted Indoor Units | 206000 | 11.5 | 19.3 | 230000 | 3.71 | 150000 | 2.37 | R-410A | 17.1667
4679555 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BT3 | ARUB144BT3 |  |  | ARUB240BT3 | Non-Ducted Indoor Units | 228000 | 11.9 | 18.3 | 256000 | 3.54 | 168000 | 2.57 | R-410A | 19
4679557 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DT3 | ARUB144DT3 |  |  | ARUB240DT3 | Non-Ducted Indoor Units | 228000 | 11.9 | 18.3 | 256000 | 3.54 | 168000 | 2.57 | R-410A | 19
4679582 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BT3 |  |  |  | ARUN144BT3 | Ducted Indoor Units | 138000 | 11.6 | 19.1 | 154000 | 3.45 | 100000 | 2.46 | R-410A | 11.5
4679583 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BT3 |  |  |  | ARUN144BT3 | Non-Ducted Indoor Units | 138000 | 11.8 | 18.9 | 154000 | 3.67 | 100000 | 2.65 | R-410A | 11.5
4679584 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DT3 |  |  |  | ARUN144DT3 | Ducted Indoor Units | 138000 | 11.6 | 19.1 | 154000 | 3.45 | 100000 | 2.46 | R-410A | 11.5
4679585 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DT3 |  |  |  | ARUN144DT3 | Non-Ducted Indoor Units | 138000 | 11.8 | 18.9 | 154000 | 3.67 | 100000 | 2.65 | R-410A | 11.5
4679586 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN096BT3 |  |  | ARUN168BT3 | Ducted Indoor Units | 160000 | 11.7 | 19.5 | 180000 | 3.33 | 118000 | 2.47 | R-410A | 13.3333
4679587 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN096BT3 |  |  | ARUN168BT3 | Non-Ducted Indoor Units | 160000 | 12.7 | 20 | 180000 | 3.77 | 118000 | 2.66 | R-410A | 13.3333
4679588 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN096DT3 |  |  | ARUN168DT3 | Ducted Indoor Units | 160000 | 11.7 | 19.5 | 180000 | 3.33 | 118000 | 2.47 | R-410A | 13.3333
4679589 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN096DT3 |  |  | ARUN168DT3 | Non-Ducted Indoor Units | 160000 | 12.7 | 22.1 | 180000 | 3.77 | 118000 | 2.66 | R-410A | 13.3333
4679590 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN121BT3 |  |  | ARUN192BT3 | Ducted Indoor Units | 184000 | 11.4 | 18.5 | 206000 | 3.32 | 134000 | 2.46 | R-410A | 15.3333
4679591 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN121BT3 |  |  | ARUN192BT3 | Non-Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679592 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN121DT3 |  |  | ARUN192DT3 | Ducted Indoor Units | 184000 | 11.4 | 18.5 | 206000 | 3.32 | 134000 | 2.46 | R-410A | 15.3333
4679593 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN121DT3 |  |  | ARUN192DT3 | Non-Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679594 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN144BT3 |  |  | ARUN216BT3 | Ducted Indoor Units | 206000 | 11 | 19.7 | 230000 | 3.41 | 150000 | 2.44 | R-410A | 17.1667
4679595 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN144BT3 |  |  | ARUN216BT3 | Non-Ducted Indoor Units | 206000 | 11.5 | 19.3 | 230000 | 3.71 | 150000 | 2.58 | R-410A | 17.1667
4679596 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN144DT3 |  |  | ARUN216DT3 | Ducted Indoor Units | 206000 | 11 | 19.7 | 230000 | 3.41 | 150000 | 2.44 | R-410A | 17.1667
4679597 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN144DT3 |  |  | ARUN216DT3 | Non-Ducted Indoor Units | 206000 | 11.5 | 19.3 | 230000 | 3.71 | 150000 | 2.58 | R-410A | 17.1667
4679599 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BT3 | ARUN144BT3 |  |  | ARUN240BT3 | Non-Ducted Indoor Units | 228000 | 11.9 | 18.3 | 256000 | 3.54 | 168000 | 2.57 | R-410A | 19
4679601 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DT3 | ARUN144DT3 |  |  | ARUN240DT3 | Non-Ducted Indoor Units | 228000 | 11.9 | 18.3 | 256000 | 3.54 | 168000 | 2.57 | R-410A | 19
5012629 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT9UL | MMY-MAP0724HT9UL |  |  | MMY-AP1444HT9UL | Non-Ducted Indoor Units | 138000 | 10.9 | 20.9 | 162000 | 3.4 | 82000 | 2.25 | R-410A | 11.5
5194490 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT6UL | MMY-MAP0724HT6UL |  |  | MMY-AP1444HT6UL | Non-Ducted Indoor Units | 138000 | 10.9 | 20.4 | 162000 | 3.4 | 82000 | 2.25 | R-410A | 11.5
5198217 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV | AOUA72RLBV |  |  | AOUA144RLBVG | Non-Ducted Indoor Units | 138000 | 12.4 | 19.5 | 154000 | 3.68 | 107000 | 2.36 | R-410A | 11.5
5198220 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA72RLBV |  |  | AOUA168RLBVG | Non-Ducted Indoor Units | 160000 | 11.6 | 19.5 | 180000 | 3.6 | 118000 | 2.47 | R-410A | 13.3333
5198222 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA72RLBV |  |  | AOUA168RLBVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 18.3 | 180000 | 3.57 | 118000 | 2.34 | R-410A | 13.3333
5198223 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA96RLBV |  |  | AOUA192RLBVG | Non-Ducted Indoor Units | 174000 | 11.4 | 19.6 | 196000 | 3.55 | 128000 | 2.53 | R-410A | 14.5
5198225 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA96RLBV |  |  | AOUA192RLBVG | Mixed Ducted and Non-Ducted Indoor Units | 174000 | 11.25 | 18.45 | 196000 | 3.49 | 128000 | 2.41 | R-410A | 14.5
5198226 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV | AOUA72RLBV | AOUA72RLBV |  | AOUA216RLBVG | Non-Ducted Indoor Units | 206000 | 12 | 20.2 | 230000 | 3.72 | 160000 | 2.38 | R-410A | 17.1667
5198228 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV | AOUA72RLBV | AOUA72RLBV |  | AOUA216RLBVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12 | 18.7 | 230000 | 3.66 | 160000 | 2.32 | R-410A | 17.1667
5198229 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA72RLBV | AOUA72RLBV |  | AOUA240RLBVG | Non-Ducted Indoor Units | 228000 | 11.3 | 19.6 | 258000 | 3.53 | 166000 | 2.24 | R-410A | 19
5198231 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA72RLBV | AOUA72RLBV |  | AOUA240RLBVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.6 | 18.4 | 258000 | 3.55 | 166000 | 2.22 | R-410A | 19
5358528 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 108000 | 2.32 | R-410A | 11.3333
5358529 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
5358530 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 11.7 | 19.75 | 152000 | 3.64 | 108000 | 2.27 | R-410A | 11.3333
5358531 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Ducted Indoor Units | 136000 | 12.8 | 19.3 | 152000 | 3.79 | 108000 | 2.56 | R-410A | 11.3333
5358532 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Non-Ducted Indoor Units | 136000 | 13.2 | 20.3 | 152000 | 3.95 | 109000 | 2.13 | R-410A | 11.3333
5358533 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13 | 19.8 | 152000 | 3.87 | 108000 | 2.34 | R-410A | 11.3333
5358534 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
5358535 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
5358536 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.75 | 19.65 | 178000 | 3.8 | 132000 | 2.39 | R-410A | 13.3333
5358537 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 20400 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
5358538 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
5358539 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.45 | 19 | 112000 | 3.62 | 150000 | 2.31 | R-410A | 15.1667
5358540 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
5358541 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
5358542 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.3 | 18.75 | 232000 | 3.6 | 164000 | 2.28 | R-410A | 17.1667
5358543 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  |  | PUHY-P240YSKMU-A | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
5358545 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  |  | PUHY-P240YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.05 | 18.35 | 258000 | 3.54 | 182000 | 2.23 | R-410A | 19
5358570 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 109000 | 2.32 | R-410A | 11.3333
5358571 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
5358572 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 11.7 | 19.75 | 152000 | 3.64 | 109000 | 2.27 | R-410A | 11.3333
5358573 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
5358574 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
5358575 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.75 | 19.65 | 178000 | 3.8 | 132000 | 2.39 | R-410A | 13.3333
5358576 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 204000 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
5358577 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
5358578 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.45 | 19 | 204000 | 3.62 | 150000 | 2.31 | R-410A | 15.1667
5358579 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
5358580 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
5358581 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.3 | 18.75 | 232000 | 3.6 | 164000 | 2.28 | R-410A | 17.1667
5358582 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  |  | PUHY-P240TSKMU-A | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
5358584 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  |  | PUHY-P240TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.05 | 18.35 | 258000 | 3.54 | 182000 | 2.23 | R-410A | 19
5358609 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A |  |  |  | PURY-P144YKMU-A | Ducted Indoor Units | 136000 | 11.7 | 18 | 152000 | 3.41 | 109000 | 2.32 | R-410A | 11.3333
5358611 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A |  |  |  | PURY-P144YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.2 | 19.45 | 152000 | 3.33 | 109000 | 2.19 | R-410A | 11.3333
5358612 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Ducted Indoor Units | 136000 | 12 | 18.8 | 152000 | 3.54 | 109000 | 2.41 | R-410A | 11.3333
5358613 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Non-Ducted Indoor Units | 136000 | 14.4 | 19.5 | 152000 | 3.62 | 109000 | 2.28 | R-410A | 11.3333
5358614 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.2 | 19.7 | 152000 | 3.58 | 109000 | 2.34 | R-410A | 11.3333
5358615 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
5358616 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 18.2 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
5358617 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.5 | 19.25 | 178000 | 3.56 | 132000 | 2.37 | R-410A | 13.3333
5358618 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P96YKMU-A |  |  | PURY-P192YSKMU-A | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
5358620 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P96YKMU-A |  |  | PURY-P192YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 18.75 | 204000 | 3.54 | 150000 | 2.35 | R-410A | 15.1667
5358621 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A | PURY-P96YKMU-A |  |  | PURY-P216YSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
5358623 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A | PURY-P96YKMU-A |  |  | PURY-P216YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 18.5 | 232000 | 3.47 | 164000 | 2.21 | R-410A | 17.1667
5358625 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A | PURY-P120YKMU-A |  |  | PURY-P240YSKMU-A | Non-Ducted Indoor Units | 228000 | 10.9 | 18.1 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
5358626 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A | PURY-P120YKMU-A |  |  | PURY-P240YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 18.15 | 258000 | 3.39 | 182000 | 2.13 | R-410A | 19
5358639 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A |  |  |  | PURY-P144TKMU-A | Ducted Indoor Units | 136000 | 11.7 | 18 | 152000 | 3.41 | 109000 | 2.32 | R-410A | 11.3333
5358641 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A |  |  |  | PURY-P144TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.2 | 19.45 | 152000 | 3.33 | 109000 | 2.19 | R-410A | 11.3333
5358642 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
5358643 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 18.2 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
5358644 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.5 | 19.25 | 178000 | 3.56 | 132000 | 2.37 | R-410A | 13.3333
5358645 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P96TKMU-A |  |  | PURY-P192TSKMU-A | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
5358647 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P96TKMU-A |  |  | PURY-P192TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 18.75 | 204000 | 3.54 | 150000 | 2.35 | R-410A | 15.1667
5358648 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A | PURY-P96TKMU-A |  |  | PURY-P216TSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
5358650 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A | PURY-P96TKMU-A |  |  | PURY-P216TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 18.5 | 232000 | 3.47 | 164000 | 2.21 | R-410A | 17.1667
5358652 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A | PURY-P120TKMU-A |  |  | PURY-P240TSKMU-A | Non-Ducted Indoor Units | 228000 | 10.9 | 18.1 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
5358653 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A | PURY-P120TKMU-A |  |  | PURY-P240TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 18.15 | 258000 | 3.39 | 182000 | 2.13 | R-410A | 19
5733045 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM096FXVAFH |  |  | AM168FXVAFH | Ducted Indoor Units | 160000 | 11.4 | 20.8 | 180000 | 3.46 | 118000 | 2.43 | R-410A | 13.3333
5733046 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM096FXVAJH |  |  | AM168FXVAJH | Ducted Indoor Units | 160000 | 11.3 | 20.5 | 180000 | 3.44 | 118000 | 2.43 | R-410A | 13.3333
5733047 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM096FXVAFH |  |  | AM168FXVAFH | Non-Ducted Indoor Units | 160000 | 12.1 | 25.9 | 180000 | 3.94 | 118000 | 2.65 | R-410A | 13.3333
5733048 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM096FXVAJH |  |  | AM168FXVAJH | Non-Ducted Indoor Units | 160000 | 12.1 | 25.3 | 180000 | 3.94 | 118000 | 2.65 | R-410A | 13.3333
5733049 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM096FXVAFR |  |  | AM168FXVAFR | Ducted Indoor Units | 160000 | 11.4 | 20.8 | 180000 | 3.46 | 118000 | 2.43 | R-410A | 13.3333
5733050 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM096FXVAJR |  |  | AM168FXVAJR | Ducted Indoor Units | 160000 | 11.3 | 20.5 | 180000 | 3.44 | 118000 | 2.43 | R-410A | 13.3333
5733051 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM096FXVAFR |  |  | AM168FXVAFR | Non-Ducted Indoor Units | 160000 | 12.1 | 25.9 | 180000 | 3.94 | 118000 | 2.65 | R-410A | 13.3333
5733052 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM096FXVAJR |  |  | AM168FXVAJR | Non-Ducted Indoor Units | 160000 | 12.1 | 25.3 | 180000 | 3.94 | 118000 | 2.65 | R-410A | 13.3333
5733053 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM120FXVAFH |  |  | AM192FXVAFH | Ducted Indoor Units | 184000 | 10.9 | 21.5 | 206000 | 3.34 | 134000 | 2.42 | R-410A | 15.3333
5733054 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM120FXVAJH |  |  | AM192FXVAJH | Ducted Indoor Units | 184000 | 10.9 | 21.5 | 206000 | 3.34 | 134000 | 2.42 | R-410A | 15.3333
5733055 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM120FXVAFH |  |  | AM192FXVAFH | Non-Ducted Indoor Units | 184000 | 11.4 | 24.1 | 206000 | 3.83 | 134000 | 2.59 | R-410A | 15.3333
5733056 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM120FXVAJH |  |  | AM192FXVAJH | Non-Ducted Indoor Units | 184000 | 11.2 | 24.2 | 206000 | 3.83 | 134000 | 2.59 | R-410A | 15.3333
5733057 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM120FXVAFR |  |  | AM192FXVAFR | Ducted Indoor Units | 184000 | 10.9 | 21.5 | 206000 | 3.34 | 134000 | 2.42 | R-410A | 15.3333
5733058 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM120FXVAJR |  |  | AM192FXVAJR | Ducted Indoor Units | 184000 | 10.9 | 21.5 | 206000 | 3.34 | 134000 | 2.42 | R-410A | 15.3333
5733059 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM120FXVAFR |  |  | AM192FXVAFR | Non-Ducted Indoor Units | 184000 | 11.4 | 24.1 | 206000 | 3.83 | 134000 | 2.59 | R-410A | 15.3333
5733060 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM120FXVAJR |  |  | AM192FXVAJR | Non-Ducted Indoor Units | 184000 | 11.2 | 24.2 | 206000 | 3.83 | 134000 | 2.59 | R-410A | 15.3333
5733063 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM144FXVAFH |  |  | AM216FXVAFH | Non-Ducted Indoor Units | 206000 | 10.8 | 22.4 | 230000 | 3.63 | 150000 | 2.52 | R-410A | 17.1667
5733064 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM144FXVAJH |  |  | AM216FXVAJH | Non-Ducted Indoor Units | 206000 | 10.8 | 22.4 | 230000 | 3.63 | 150000 | 2.52 | R-410A | 17.1667
5733067 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM144FXVAFR |  |  | AM216FXVAFR | Non-Ducted Indoor Units | 206000 | 10.8 | 22.4 | 230000 | 3.63 | 150000 | 2.52 | R-410A | 17.1667
5733068 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM144FXVAJR |  |  | AM216FXVAJR | Non-Ducted Indoor Units | 206000 | 10.8 | 22.4 | 230000 | 3.63 | 150000 | 2.52 | R-410A | 17.1667
5733071 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH | AM120FXVAFH |  |  | AM240FXVAFH | Non-Ducted Indoor Units | 228000 | 11.1 | 21.8 | 258000 | 3.65 | 168000 | 2.54 | R-410A | 19
5733072 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH | AM120FXVAJH |  |  | AM240FXVAJH | Non-Ducted Indoor Units | 228000 | 10.7 | 22.1 | 258000 | 3.65 | 168000 | 2.54 | R-410A | 19
5733075 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR | AM120FXVAFR |  |  | AM240FXVAFR | Non-Ducted Indoor Units | 228000 | 11.1 | 21.8 | 258000 | 3.65 | 168000 | 2.54 | R-410A | 19
5733076 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR | AM120FXVAJR |  |  | AM240FXVAJR | Non-Ducted Indoor Units | 228000 | 10.7 | 22.1 | 258000 | 3.65 | 168000 | 2.54 | R-410A | 19
5924245 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT9UL | MMY-MAP0724HT9UL |  |  | MMY-AP1444HT9UL | Mixed Ducted and Non-Ducted Indoor Units | 140000 | 10.8 | 18.85 | 162000 | 3.32 | 87000 | 2.35 | R-410A | 11.6667
5924246 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT6UL | MMY-MAP0724HT6UL |  |  | MMY-AP1444HT6UL | Mixed Ducted and Non-Ducted Indoor Units | 140000 | 10.8 | 18.5 | 162000 | 3.32 | 87000 | 2.35 | R-410A | 11.6667
6334550 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT9UL | MMY-MAP0724FT9UL |  |  | MMY-AP1684FT9UL | Non-Ducted Indoor Units | 160000 | 11.7 | 19.4 | 180000 | 3.27 | 110000 | 2.16 | R-410A | 13.3333
6334551 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT9UL | MMY-MAP0964FT9UL |  |  | MMY-AP1924FT9UL | Non-Ducted Indoor Units | 184000 | 11.4 | 18.9 | 206000 | 3.25 | 126000 | 2.12 | R-410A | 15.3333
6334570 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT9UL | MMY-MAP0724FT9UL |  |  | MMY-AP1444FT9UL | Non-Ducted Indoor Units | 138000 | 11.3 | 20.4 | 154000 | 3.44 | 96000 | 2.19 | R-410A | 11.5
6334577 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT6UL | MMY-MAP0724FT6UL |  |  | MMY-AP1444FT6UL | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.44 | 96000 | 2.19 | R-410A | 11.5
6334578 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT6UL | MMY-MAP0724FT6UL |  |  | MMY-AP1684FT6UL | Non-Ducted Indoor Units | 160000 | 11.7 | 19 | 180000 | 3.27 | 110000 | 2.16 | R-410A | 13.3333
6334579 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT6UL | MMY-MAP0964FT6UL |  |  | MMY-AP1924FT6UL | Non-Ducted Indoor Units | 184000 | 11.4 | 18.5 | 206000 | 3.25 | 126000 | 2.12 | R-410A | 15.3333
6334587 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT9UL | MMY-MAP0724FT9UL |  |  | MMY-AP1444FT9UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.1 | 18.35 | 152000 | 3.32 | 96000 | 2.19 | R-410A | 11.5
6687546 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
6687548 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687550 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
6687552 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6687554 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
201874092 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
201874093 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
201874095 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
201874097 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
201874099 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
201874142 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
201874143 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
201874145 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
201874146 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
201874156 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
201874158 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
201874159 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
201874160 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
201874162 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
201874163 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
201874167 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
201874169 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
201977973 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
201977974 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
201978073 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
201978074 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
201978075 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Non-Ducted Indoor Units | 136000 | 13.2 | 20.3 | 152000 | 3.95 | 109000 | 2.13 | R-410A | 11.3333
201978076 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
201978077 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
201978078 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
201978079 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
201992875 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Non-Ducted Indoor Units | 138000 | 11.5 | 22.2 | 154000 | 3.84 | 109000 | 2.2 | R-410A | 11.5
202016259 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Non-Ducted Indoor Units | 206000 | 11.8 | 21.7 | 232000 | 3.84 | 164000 | 2.35 | R-410A | 17.1667
202016261 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 256000 | 3.77 | 182000 | 2.39 | R-410A | 19
202021854 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.4 | 21.9 | 206000 | 3.91 | 150000 | 2.52 | R-410A | 15.3333
202021884 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Ducted Indoor Units | 138000 | 10.8 | 18.2 | 154000 | 3.46 | 109000 | 2.14 | R-410A | 11.5
202021886 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Ducted Indoor Units | 184000 | 11.8 | 19.2 | 206000 | 3.72 | 150000 | 2.39 | R-410A | 15.3333
202021887 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Ducted Indoor Units | 206000 | 11.3 | 19.1 | 232000 | 3.58 | 164000 | 2.22 | R-410A | 17.1667
202021888 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Ducted Indoor Units | 228000 | 10.7 | 18.1 | 256000 | 3.46 | 182000 | 2.18 | R-410A | 19
202022802 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.2 | 154000 | 3.65 | 109000 | 2.17 | R-410A | 11.5
202022804 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 20.55 | 206000 | 3.81 | 150000 | 2.45 | R-410A | 15.3333
202022805 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.55 | 20.4 | 232000 | 3.71 | 164000 | 2.28 | R-410A | 17.1667
202022806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 19.45 | 256000 | 3.61 | 182000 | 2.28 | R-410A | 19
202095830 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095834 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095835 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095836 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095837 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095838 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095839 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095842 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095843 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095845 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202606778 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606779 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606780 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606781 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606782 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606783 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606784 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606785 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606786 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606787 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606788 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606789 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606796 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606797 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606798 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606799 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606800 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606802 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606803 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606804 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606805 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606806 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606807 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606814 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S |  |  | TVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606815 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S |  |  | HVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606816 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S |  |  | YVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606820 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S |  |  | TVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606821 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S |  |  | HVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606822 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S |  |  | YVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606832 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606833 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606834 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606835 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606836 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606837 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606838 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606839 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606840 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606841 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606842 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606843 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606844 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606845 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606846 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606847 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606848 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606849 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606850 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606851 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606852 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606853 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606854 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606855 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202607401 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607402 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607403 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607404 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607405 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607406 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607407 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607408 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607409 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607410 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607411 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607412 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607413 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607414 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607415 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607416 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607417 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607418 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607419 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607420 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607421 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607422 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607423 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607424 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607425 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607426 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607427 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607428 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607429 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607430 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607431 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607432 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607433 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607434 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607435 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607436 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607475 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607476 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607477 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607478 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607479 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607480 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607481 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607482 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607483 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607484 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607485 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607486 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607493 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607494 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607495 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607496 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607497 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607498 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607499 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607500 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607501 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607502 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607503 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607504 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607505 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607506 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607507 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607508 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607509 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607510 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607511 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607512 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607513 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607514 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607515 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607516 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607517 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607518 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607519 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607520 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607521 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607522 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607523 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607524 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607525 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607526 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607527 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607528 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607529 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607530 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607531 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607532 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607533 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607534 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607565 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607566 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607567 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607568 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607569 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607570 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607571 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607572 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607573 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607574 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607575 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607576 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607577 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607578 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607579 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607580 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607581 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607582 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607583 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607584 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607585 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607586 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607587 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607588 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607622 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607623 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607624 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607625 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607626 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607627 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607628 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607629 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607630 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607631 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607632 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607633 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608010 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608011 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608012 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608013 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608014 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608015 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608016 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608017 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608018 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608019 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608020 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608021 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608040 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608041 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608042 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608043 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608044 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608045 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608046 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608047 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608048 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608049 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608051 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608070 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608071 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608072 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608073 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608074 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608075 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608076 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608077 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608078 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608079 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608080 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608081 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608094 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608095 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608096 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608097 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608098 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608099 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608100 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608101 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608102 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608103 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608104 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608105 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608124 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608125 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608126 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608127 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608128 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608129 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608130 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608131 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608132 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608133 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608134 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608135 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
203906663 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906664 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906665 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906666 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906667 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906668 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906669 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906670 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906671 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906672 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906673 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906674 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906675 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906676 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906677 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906678 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906679 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906680 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906681 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906682 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906684 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906685 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906686 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906687 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906688 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906689 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906690 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906691 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906693 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906694 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906695 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906696 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906697 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906698 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906699 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906732 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906733 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906734 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906735 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906736 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906737 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906738 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906740 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906741 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906742 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906743 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906744 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906745 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906746 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906747 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906748 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906749 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906750 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906751 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906752 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906754 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906755 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906756 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906757 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906758 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906759 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906760 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906761 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906762 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906763 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906770 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906771 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906773 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906774 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906775 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906776 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906777 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906778 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906779 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906780 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906781 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906782 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906783 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906784 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906785 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906786 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906787 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906788 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906789 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906790 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906792 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906793 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906794 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906795 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906808 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906809 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906811 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906812 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906813 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906814 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906815 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906817 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906818 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906819 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906820 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203993992 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993994 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993996 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993999 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203994001 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203994003 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
204268354 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268356 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268360 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268362 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S | TVAHR120B52S |  |  | TVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268379 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268380 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268382 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268383 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S | HVAHR120B52S |  |  | HVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268395 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268396 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268398 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268399 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S | YVAHR120B52S |  |  | YVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268411 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268412 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268413 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S |  |  |  | TVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268414 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268427 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268428 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268429 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S |  |  |  | HVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268430 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268445 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268447 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268449 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S |  |  |  | YVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268451 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268474 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268476 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268478 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268480 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S | TVAHP120B52S |  |  | TVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268502 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268504 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268509 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268511 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S | HVAHP120B52S |  |  | HVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268535 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268536 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268540 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268542 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S | YVAHP120B52S |  |  | YVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268561 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268563 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268565 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S |  |  |  | TVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268567 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268583 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268584 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268585 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S |  |  |  | HVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268586 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268599 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268600 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268601 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S |  |  |  | YVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268602 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204269027 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269028 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269029 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S |  |  |  | TVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269030 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269031 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S | TVAHR120B52S |  |  | TVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269043 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269044 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269045 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S |  |  |  | HVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269046 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269047 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S | HVAHR120B52S |  |  | HVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269059 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269060 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269061 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S |  |  |  | YVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269062 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269063 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S | YVAHR120B52S |  |  | YVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269075 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269076 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269077 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S |  |  |  | TVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269078 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269079 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S | TVAHP120B52S |  |  | TVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269091 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269092 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269093 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S |  |  |  | HVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269094 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269095 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S | HVAHP120B52S |  |  | HVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269107 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269108 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269109 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S |  |  |  | YVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269110 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269111 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S | YVAHP120B52S |  |  | YVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204442746 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
204442793 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442794 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204572224 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572239 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572254 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572269 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572284 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572285 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572286 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572287 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572292 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572293 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572294 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572295 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572300 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572301 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572302 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572303 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572308 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572309 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572310 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572311 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572314 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
204572317 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
205000507 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000513 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
205000527 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000528 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000529 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205281447 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
205281450 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
205281453 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
8657017 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144ZKMU-A |  |  |  | PUHY-P144ZKMU-A | Ducted Indoor Units | 136000 | 11.7 | 20.7 | 152000 | 3.46 | 109000 | 2.32 | R-410A | 11.3333
8657003 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120ZKMU-A | PURY-P96ZKMU-A |  |  | PURY-P216ZSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 19.5 | 232000 | 3.34 | 158000 | 2.19 | R-410A | 17.1667
8657001 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A | PURY-P96ZKMU-A |  |  | PURY-P192ZSKMU-A | Ducted Indoor Units | 182000 | 11.2 | 19.9 | 204000 | 3.39 | 142000 | 2.19 | R-410A | 15.1667
8656999 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A | PURY-P72ZKMU-A |  |  | PURY-P168ZSKMU-A | Ducted Indoor Units | 160000 | 11.1 | 19.9 | 178000 | 3.31 | 119000 | 2.13 | R-410A | 13.3333
8657025 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P240ZSKMU-A | Ducted Indoor Units | 228000 | 11.9 | 20.4 | 258000 | 3.45 | 182000 | 2.42 | R-410A | 19
8657023 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P216ZSKMU-A | Ducted Indoor Units | 206000 | 11.8 | 20.7 | 232000 | 3.51 | 164000 | 2.48 | R-410A | 17.1667
8657021 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A |  |  | PUHY-P192ZSKMU-A | Ducted Indoor Units | 182000 | 12 | 20.7 | 204000 | 3.48 | 150000 | 2.45 | R-410A | 15.1667
8657019 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P72ZKMU-A |  |  | PUHY-P168ZSKMU-A | Ducted Indoor Units | 160000 | 11.9 | 21.2 | 178000 | 3.54 | 132000 | 2.6 | R-410A | 13.3333
206453550 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
206453547 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
206453535 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
206453536 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 |  |  |  | ARUM216CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
205281466 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202566102 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
202566103 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202566104 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
202566106 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
202566107 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202566108 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 |  |  |  | ARUM216CTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
202534322 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 |  |  |  | ARUB144CTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534323 | 1/1/2027 | LG | HMSR-A-CB | ARUB168CTE4 |  |  |  | ARUB168CTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534324 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 | ARUB121CTE4 |  |  | ARUB192CTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534325 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 | ARUB144CTE4 |  |  | ARUB216CTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 20 | 230000 | 3.72 | 150000 | 2.58 | R-410A | 17.1667
202534326 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 | ARUB144CTE4 |  |  | ARUB240CTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 20.2 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534334 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 |  |  |  | ARUB144CTE4 | Ducted Indoor Units | 138000 | 11.8 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534336 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 | ARUB121CTE4 |  |  | ARUB192CTE4 | Ducted Indoor Units | 184000 | 12.5 | 21 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534337 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 | ARUB144CTE4 |  |  | ARUB216CTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202534338 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 | ARUB144CTE4 |  |  | ARUB240CTE4 | Ducted Indoor Units | 228000 | 11.6 | 18 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202534346 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 |  |  |  | ARUN144CTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534347 | 1/1/2027 | LG | HMSV-A-CB | ARUN168CTE4 |  |  |  | ARUN168CTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534348 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 | ARUN121CTE4 |  |  | ARUN192CTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534349 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 | ARUN144CTE4 |  |  | ARUN216CTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 21 | 230000 | 3.72 | 150000 | 2.58 | R-410A | 17.1667
202534350 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 | ARUN144CTE4 |  |  | ARUN240CTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 20.2 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534358 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 |  |  |  | ARUN144CTE4 | Ducted Indoor Units | 138000 | 11.8 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534360 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 | ARUN121CTE4 |  |  | ARUN192CTE4 | Ducted Indoor Units | 184000 | 12.5 | 21 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534361 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 | ARUN144CTE4 |  |  | ARUN216CTE4 | Ducted Indoor Units | 206000 | 12 | 20 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202534362 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 | ARUN144CTE4 |  |  | ARUN240CTE4 | Ducted Indoor Units | 228000 | 11.6 | 18 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
9505334 | 1/1/2027 | INNOVAIR | HMSV-A-CB | V5BV-72WMBC | V5BV-96WMBC |  |  | V5BV-168WMBC | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
201874091 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
9088676 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 | IOV096H3CDC713 |  |  | IOV192H3CDC732 | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
9088678 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 | IOV120H3CDC714 |  |  | IOV216H3CDC736 | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
9088686 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC714 | IOV120H3CDC714 |  |  | IOV240H3CDC734 | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
9088670 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 | IOV096H3CDC713 |  |  | IOV168H3CDC728 | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
9119338 | 1/1/2027 | LG | HMSV-A-CB | ARUN144QTE4 |  |  |  | ARUN144QTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
9119339 | 1/1/2027 | LG | HMSV-A-CB | ARUN144QTE4 |  |  |  | ARUN144QTE4 | Non-Ducted Indoor Units | 138000 | 12.4 | 27 | 152000 | 3.8 | 98000 | 2.69 | R-410A | 11.5
202534368 | 1/1/2027 | LG | HMSV-A-CB | ARUN168QTE4 |  |  |  | ARUN168QTE4 | Non-Ducted Indoor Units | 160000 | 11.8 | 22.5 | 180000 | 3.6 | 117000 | 2.51 | R-410A | 13.3333
10567396 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-168U8S1B |  |  |  | AVWT-168U8S1B | Non-Ducted Indoor Units | 160000 | 12.25 | 27.15 | 170000 | 3.68 | 105000 | 2.5 | R-410A | 13.3333
10567400 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-168U8S1B |  |  |  | AVWT-168U8S1B | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.57 | 24.72 | 170000 | 3.45 | 105000 | 2.35 | R-410A | 13.3333
10594387 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B |  |  |  | AVWT-144U8S1B | Ducted Indoor Units | 144000 | 10.8 | 21.3 | 154000 | 3.25 | 96000 | 2.3 | R-410A | 12
10594388 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B |  |  |  | AVWT-144U8S1B | Non-Ducted Indoor Units | 144000 | 12.1 | 27.2 | 154000 | 3.64 | 96000 | 2.45 | R-410A | 12
10594389 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120U8STB | AVWT-072U8SNB |  |  | AVWT-192U8SZB | Non-Ducted Indoor Units | 184000 | 12.1 | 27.5 | 206000 | 3.75 | 136000 | 2.53 | R-410A | 15.3333
10594390 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-072U8SNB |  |  | AVWT-216U8SZB | Non-Ducted Indoor Units | 208000 | 11.35 | 25.2 | 230000 | 3.6 | 150000 | 2.4 | R-410A | 17.3333
10594391 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-96U8STB |  |  | AVWT-240U8SZB | Non-Ducted Indoor Units | 230000 | 11.3 | 24.95 | 256000 | 3.66 | 164000 | 2.42 | R-410A | 19.1667
10594398 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120U8STB | AVWT-072U8SNB |  |  | AVWT-192U8SZB | Ducted Indoor Units | 184000 | 11.9 | 24.1 | 206000 | 3.28 | 136000 | 2.32 | R-410A | 15.3333
10594399 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-072U8SNB |  |  | AVWT-216U8SZB | Ducted Indoor Units | 208000 | 11.35 | 22.8 | 230000 | 3.25 | 150000 | 2.27 | R-410A | 17.3333
10594400 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-96U8STB |  |  | AVWT-240U8SZB | Ducted Indoor Units | 230000 | 11.45 | 23.75 | 256000 | 3.25 | 164000 | 2.32 | R-410A | 19.1667
10594407 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B |  |  |  | AVWT-144U8S1B | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 11.45 | 24.25 | 154000 | 3.44 | 96000 | 2.37 | R-410A | 12
209842413 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842423 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209863189 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209842432 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209863198 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209842442 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842443 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209863199 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209842433 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209863178 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209842194 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842204 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842205 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209842195 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209863179 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209842462 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842452 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209863208 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209863209 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209842453 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842463 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209863188 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209842412 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842422 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
207827292 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM432BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207826725 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH | AM216BXVGFH |  |  | AM432BXVGFH | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826729 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH | AM216BXVGFH |  |  | AM432BXVGFH | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207827296 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM432BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207826733 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH | AM216BXVGJH |  |  | AM432BXVGJH | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826737 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH | AM216BXVGJH |  |  | AM432BXVGJH | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207827277 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM432BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207826251 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR | AM216BXVGFR |  |  | AM432BXVGFR | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826256 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR | AM216BXVGFR |  |  | AM432BXVGFR | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207827300 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM432BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207826741 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR | AM216BXVGJR |  |  | AM432BXVGJR | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR | AM216BXVGJR |  |  | AM432BXVGJR | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
208931871 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.45 | 20.1 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931873 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 19.8 | 308000 | 3.38 | 210000 | 2.16 | R-410A | 23
208931883 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 11 | 20.15 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931885 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 10.8 | 20.2 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931875 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.9 | 19.8 | 320000 | 3.38 | 214000 | 2.16 | R-410A | 24.8333
208931877 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.9 | 19.8 | 338000 | 3.38 | 224000 | 2.16 | R-410A | 26.6667
208931879 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 19.8 | 346000 | 3.38 | 232000 | 2.16 | R-410A | 28.6667
208931881 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.8 | 354000 | 3.38 | 240000 | 2.16 | R-410A | 30.5
208931905 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 11 | 20.15 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931907 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 10.8 | 20.2 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931893 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.45 | 20.1 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931895 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 19.8 | 308000 | 3.38 | 210000 | 2.16 | R-410A | 23
208931897 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.9 | 19.8 | 320000 | 3.38 | 214000 | 2.16 | R-410A | 24.8333
208931899 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.9 | 19.8 | 338000 | 3.38 | 224000 | 2.16 | R-410A | 26.6667
208931901 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 19.8 | 346000 | 3.38 | 232000 | 2.16 | R-410A | 28.6667
208931903 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.8 | 354000 | 3.38 | 240000 | 2.16 | R-410A | 30.5
206799490 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
10267498 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903135 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102065 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102045 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
208102046 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
205000514 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR | AM192HXVAFR |  |  | AM360JXVAFR | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
205000550 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR | AM192HXVAJR |  |  | AM360JXVAJR | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
204442808 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH | AM216KXVGJH |  |  | AM408KXVGJH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
9989804 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ120TATJ* | REYQ120TATJ* |  | REYQ360TATJ* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 376000 | 3.52 | 258000 | 2.28 | R-410A | 28.5
9989800 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ144TATJ* |  |  | REYQ264TATJ* | Non-Ducted Indoor Units | 252000 | 11.6 | 21.6 | 274000 | 3.55 | 196000 | 2.33 | R-410A | 21
9989855 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ144TATJ* |  |  | REYQ264TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.1 | 274000 | 3.37 | 196000 | 2.2 | R-410A | 21
9989863 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ120TATJ* | REYQ120TATJ* |  | REYQ360TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.2 | 376000 | 3.39 | 258000 | 2.16 | R-410A | 28.5
9989864 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ120TAYD* | REYQ120TAYD* |  | REYQ360TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.2 | 376000 | 3.39 | 258000 | 2.16 | R-410A | 28.5
9989856 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ144TAYD* |  |  | REYQ264TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.1 | 274000 | 3.37 | 196000 | 2.2 | R-410A | 21
9989814 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ120TAYD* | REYQ120TAYD* |  | REYQ360TAYD* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 376000 | 3.52 | 258000 | 2.28 | R-410A | 28.5
9989810 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ144TAYD* |  |  | REYQ264TAYD* | Non-Ducted Indoor Units | 252000 | 11.6 | 21.6 | 274000 | 3.55 | 196000 | 2.33 | R-410A | 21
9989801 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ144TATJ* |  |  | REYQ288TATJ* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 288000 | 3.51 | 210000 | 2.41 | R-410A | 22.8333
9989802 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ168TATJ* |  |  | REYQ312TATJ* | Non-Ducted Indoor Units | 296000 | 11 | 20.2 | 306000 | 3.57 | 230000 | 2.35 | R-410A | 24.6667
9989857 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ144TATJ* |  |  | REYQ288TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 19.45 | 288000 | 3.35 | 210000 | 2.27 | R-410A | 22.8333
9989859 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ168TATJ* |  |  | REYQ312TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.5 | 19.1 | 306000 | 3.38 | 230000 | 2.22 | R-410A | 24.6667
9989860 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ168TAYD* |  |  | REYQ312TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.5 | 19.1 | 306000 | 3.38 | 230000 | 2.22 | R-410A | 24.6667
9989858 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ144TAYD* |  |  | REYQ288TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 19.45 | 288000 | 3.35 | 210000 | 2.27 | R-410A | 22.8333
9989811 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ144TAYD* |  |  | REYQ288TAYD* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 288000 | 3.51 | 210000 | 2.41 | R-410A | 22.8333
9989812 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ168TAYD* |  |  | REYQ312TAYD* | Non-Ducted Indoor Units | 296000 | 11 | 20.2 | 306000 | 3.57 | 230000 | 2.35 | R-410A | 24.6667
9989803 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TATJ* | REYQ168TATJ* |  |  | REYQ336TATJ* | Non-Ducted Indoor Units | 320000 | 10.3 | 19 | 316000 | 3.53 | 244000 | 2.18 | R-410A | 26.6667
9989861 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TATJ* | REYQ168TATJ* |  |  | REYQ336TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.95 | 18.15 | 316000 | 3.36 | 244000 | 2.11 | R-410A | 26.6667
9989862 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYD* | REYQ168TAYD* |  |  | REYQ336TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.95 | 18.15 | 316000 | 3.36 | 244000 | 2.11 | R-410A | 26.6667
9989813 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYD* | REYQ168TAYD* |  |  | REYQ336TAYD* | Non-Ducted Indoor Units | 320000 | 10.3 | 19 | 316000 | 3.53 | 244000 | 2.18 | R-410A | 26.6667
9990314 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
9990315 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
212511135 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
212511127 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
212511128 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
212512508 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
212512502 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
212512492 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
212512486 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
212512511 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
212511111 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
212511112 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
212511115 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
212511116 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
212511131 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1686FT6P-UL |  |  | MMY-AP336S6FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
212511119 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
212511120 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
212511123 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
212511124 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
212512494 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
212512498 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
212512503 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
212512509 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
212511129 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
212511130 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
212511137 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
212511117 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
212511118 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
212511113 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
212511114 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
212512512 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
212512487 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
212512493 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
212512499 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
212512495 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
212511125 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
212511126 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
212511121 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
212511122 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
212511133 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1686FT9P-UL |  |  | MMY-AP336S6FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
206799492 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204723118 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
207591096 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
202073626 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.1 | 19.9 | 274000 | 3.29 | 186000 | 2.24 | R-410A | 20.6667
201850318 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850201 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201994790 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201830311 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1* | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201830337 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1* | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850344 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850228 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201994832 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
202073639 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.1 | 19.9 | 274000 | 3.29 | 186000 | 2.24 | R-410A | 20.6667
207591122 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
204723144 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
206799488 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
6691445 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
6691446 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
204442724 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM144FXVAFH | AM192HXVAFH |  | AM408JXVAFH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442739 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM144FXVAJH | AM192HXVAJH |  | AM408JXVAJH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
206799485 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204442720 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442735 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
206799487 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
206799486 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
208102048 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10032811 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-264WM/B-F(U) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10255984 | 1/1/2027 | INNOVAIR | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10257465 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10306453 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV264H3CDC745(A) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10306455 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV288H3CDC749(A) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10257462 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10035095 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-288WM/B-F(U) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
208102053 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
7850866 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
7850867 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
7850876 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
7850877 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
204442722 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH | AM168HXVAFH |  |  | AM336JXVAFH | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
205000548 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH | AM192HXVAFH |  |  | AM360JXVAFH | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
205000549 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH | AM192HXVAJH |  |  | AM360JXVAJH | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
204442737 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH | AM168HXVAJH |  |  | AM336JXVAJH | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
204442782 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
206799489 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
206799491 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204442790 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442809 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH | AM216KXVGJH |  |  | AM432KXVGJH | Non-Ducted Indoor Units | 416000 | 9.8 | 21 | 460000 | 3.3 | 300000 | 2.4 | R-410A | 34.6667
212511022 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
212511023 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
212512506 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
212512488 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
212512531 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
212512532 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
212512533 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 436000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
212511032 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
212511033 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
212511034 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
212511151 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 436000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
212511152 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 436000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
212511013 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
212511014 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
212511015 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
212511016 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
212511017 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
212511018 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
212511019 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
212511020 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
212511021 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
212511155 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 436000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
212511156 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 436000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
212511035 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
212511036 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
212512534 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 436000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
212512535 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
212512490 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
212512496 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
212512500 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
212511164 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4566HT6P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 488000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
212512507 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
212511059 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
212511060 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
212511070 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
212511050 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
212511051 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
212511052 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
212511153 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 436000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
212511154 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 436000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
212511139 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
212511140 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
212512513 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 436000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
212512510 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
212512489 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
212512485 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
212511166 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4566HT9P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 488000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
212512491 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
212512501 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
212512497 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
212512517 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
212512514 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 436000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
212511145 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
212511146 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
212511157 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 436000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
212511158 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 436000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
212511053 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
212511054 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
212511055 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
212511056 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
212511057 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
212511058 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
207591034 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
207591035 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
207591036 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
207591037 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
204723056 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
204723057 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
204723058 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
204723059 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201830249 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201830250 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201830251 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201830252 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850139 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850140 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850141 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850142 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201994686 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201994687 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201994689 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201994691 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850256 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850257 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850258 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850259 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
202073595 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.25 | 18.76 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
202073596 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 9.9 | 17.92 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
207591066 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
207591067 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
207591068 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
207591069 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
204723088 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
204723089 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
204723090 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
204723091 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201830281 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201830282 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201830283 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201830284 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201994739 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201994741 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201994742 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201994744 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850171 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850172 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850173 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850174 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850288 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850289 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850290 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850291 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
202073611 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.25 | 18.76 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
202073612 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 9.9 | 17.92 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
202897168 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202897169 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202918881 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202918882 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202918883 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202897242 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202897243 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202918878 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202918879 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202918880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202897206 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202897207 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202897208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202897209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202918989 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202918990 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202918991 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202897244 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202897245 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202918986 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202918987 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202918988 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202897210 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202897211 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202897170 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202897171 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202918887 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202918888 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202918889 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202918899 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202918900 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202918901 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202897246 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202897254 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202897174 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202897175 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202897255 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202897247 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202897224 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202897225 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202918896 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202918897 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202918898 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202918884 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202918885 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202918886 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202897212 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202897213 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202897214 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202897215 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202918995 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202918996 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202918997 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202919007 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202919008 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202919009 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202897226 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202897227 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202897248 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202897256 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202897257 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202897249 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202897228 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202897229 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202919004 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202919005 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202919006 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202918992 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202918993 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202918994 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202897216 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202897217 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202897172 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202897173 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202918893 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202918894 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202918895 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202918906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB168H4M-3Y |  |  | VPB360H4M-3Y | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202918907 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB168H4M-3Y |  |  | VPB360H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202897250 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202897302 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X168DXN1 |  |  | MV6-X360DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202897259 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X168DXN1 |  |  | MV6-X360DXN1 | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897271 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X168DZN1 |  |  | MV6-X360DZN1 | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897303 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X168DZN1 |  |  | MV6-X360DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202897251 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202918903 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB168H4M-3G |  |  | VPB360H4M-3G | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202918904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB168H4M-3G |  |  | VPB360H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202918890 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202918891 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202918892 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202897218 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202897219 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202897220 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202897221 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202919014 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB168H4M-3Y |  |  | VRB360H4M-3Y | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202919015 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB168H4M-3Y |  |  | VRB360H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202919001 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202919002 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202919003 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202897252 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202897304 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R168DXN1 |  |  | MV6-R360DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202897273 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R168DXN1 |  |  | MV6-R360DXN1 | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897275 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R168DZN1 |  |  | MV6-R360DZN1 | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897305 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R168DZN1 |  |  | MV6-R360DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202897253 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202918998 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202918999 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202919000 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202919011 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB168H4M-3G |  |  | VRB360H4M-3G | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202919012 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB168H4M-3G |  |  | VRB360H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202897222 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202897223 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
213916640 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916641 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916642 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P312YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893584 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893585 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893592 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893593 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893600 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P312YSNU-A | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893608 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893609 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916643 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916644 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P360YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893614 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P360YSNU-A | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893618 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P144YNU-A |  | PUHY-P384YSNU-A | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893622 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P408YSNU-A | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893626 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P432YSNU-A | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213916601 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916602 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916603 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P312TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893581 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893596 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P312TSNU-A | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893588 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893589 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893604 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893605 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916604 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916605 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P360TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893612 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P360TSNU-A | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893620 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P144TNU-A | PUHY-P144TNU-A |  | PUHY-P408TSNU-A | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893616 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P144TNU-A |  | PUHY-P384TSNU-A | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893624 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P144TNU-A | PUHY-P144TNU-A |  | PUHY-P432TSNU-A | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213916619 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916620 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916621 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893478 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893479 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893486 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893487 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893494 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893495 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893502 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893503 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916622 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916623 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893520 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP144YNU-A | PUHY-EP144YNU-A |  | PUHY-EP408YSNU-A | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893510 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893511 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893516 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP144YNU-A |  | PUHY-EP384YSNU-A | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893838 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP144YNU-A | PUHY-EP144YNU-A |  | PUHY-EP432YSNU-A | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893474 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893475 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893482 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893483 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893490 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893491 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213916580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916581 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916582 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916583 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893498 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893499 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893518 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP144TNU-A | PUHY-EP144TNU-A |  | PUHY-EP408TSNU-A | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893514 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP144TNU-A |  | PUHY-EP384TSNU-A | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893506 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893507 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213916584 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893836 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP144TNU-A | PUHY-EP144TNU-A |  | PUHY-EP432TSNU-A | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916823 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916827 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916831 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3124BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893716 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893717 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893720 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893721 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893724 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3124BN40AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893728 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893729 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916835 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916839 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3604BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893731 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3604BN40AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893733 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1444AN40AN |  | TUHYP3844BN40AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893735 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1444AN40AN | TUHYP1444AN40AN |  | TUHYP4084BN40AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893737 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1444AN40AN | TUHYP1444AN40AN |  | TUHYP4324BN40AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213916821 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916829 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3123BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916825 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213893714 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893715 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893718 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893719 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893722 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3123BN40AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893726 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893727 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916833 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916837 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3603BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893734 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1443AN40AN | TUHYP1443AN40AN |  | TUHYP4083BN40AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893732 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1443AN40AN |  | TUHYP3843BN40AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893730 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3603BN40AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893736 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1443AN40AN | TUHYP1443AN40AN |  | TUHYP4323BN40AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213916742 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916746 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916750 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893666 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893667 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893658 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893659 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893662 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893663 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893670 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893671 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916754 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916758 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893674 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893675 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893677 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1444AN40AN |  | TUHYE3844BN40AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893679 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1444AN40AN | TUHYE1444AN40AN |  | TUHYE4084BN40AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893841 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1444AN40AN | TUHYE1444AN40AN |  | TUHYE4324BN40AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893656 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893657 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893664 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893665 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893660 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893661 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213916744 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916740 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916748 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916752 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893668 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893669 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893672 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893673 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893678 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1443AN40AN | TUHYE1443AN40AN |  | TUHYE4083BN40AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893676 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1443AN40AN |  | TUHYE3843BN40AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213916756 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893840 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1443AN40AN | TUHYE1443AN40AN |  | TUHYE4323BN40AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
203364252 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ144XATJ* |  |  | REYQ264XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203364256 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* | REYQ120XATJ* |  | REYQ360XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
203334944 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ144XATJ* |  |  | REYQ264XATJ* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334948 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* | REYQ120XATJ* |  | REYQ360XATJ* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203334945 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ144XATJ* |  |  | REYQ288XATJ* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334946 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ168XATJ* |  |  | REYQ312XATJ* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203364253 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ144XATJ* |  |  | REYQ288XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364254 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ168XATJ* |  |  | REYQ312XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203364255 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* | REYQ168XATJ* |  |  | REYQ336XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203334947 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* | REYQ168XATJ* |  |  | REYQ336XATJ* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
203334961 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ144XAYD* |  |  | REYQ264XAYD* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334965 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* | REYQ120XAYD* |  | REYQ360XAYD* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203364269 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ144XAYD* |  |  | REYQ264XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203364273 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* | REYQ120XAYD* |  | REYQ360XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
203364270 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ144XAYD* |  |  | REYQ288XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364271 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ168XAYD* |  |  | REYQ312XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203334962 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ144XAYD* |  |  | REYQ288XAYD* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334963 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ168XAYD* |  |  | REYQ312XAYD* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203334964 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* | REYQ168XAYD* |  |  | REYQ336XAYD* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
203364272 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* | REYQ168XAYD* |  |  | REYQ336XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203364286 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ144XAYC* |  |  | REYQ264XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203364290 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* | REYQ120XAYC* |  | REYQ360XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
203334978 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ144XAYC* |  |  | REYQ264XAYC* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334982 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* | REYQ120XAYC* |  | REYQ360XAYC* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203334979 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ144XAYC* |  |  | REYQ288XAYC* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334980 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ168XAYC* |  |  | REYQ312XAYC* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203364287 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ144XAYC* |  |  | REYQ288XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364288 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ168XAYC* |  |  | REYQ312XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203364289 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* | REYQ168XAYC* |  |  | REYQ336XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203334981 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* | REYQ168XAYC* |  |  | REYQ336XAYC* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
205234703 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ144XATJ* |  |  | RXYQ264XATJ* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
205234707 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* | RXYQ120XATJ* |  | RXYQ360XATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
205234843 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ144XATJ* |  |  | RXYQ264XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
205234847 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* | RXYQ120XATJ* |  | RXYQ360XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
205234857 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* | RXYQ120XAYD* |  | RXYQ360XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
205234853 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ144XAYD* |  |  | RXYQ264XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
205234777 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* | RXYQ120XAYD* |  | RXYQ360XAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
205234773 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ144XAYD* |  |  | RXYQ264XAYD* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
205234710 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ120XAYC* |  | RXYQ360XAYC* | Non-Ducted Indoor Units | 342000 | 10.5 | 19.1 | 384000 | 3.62 | 270000 | 2.28 | R-410A | 28.5
205234711 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ144XAYC* |  | RXYQ384XAYC* | Non-Ducted Indoor Units | 352000 | 9.6 | 18.3 | 398000 | 3.26 | 280000 | 2.24 | R-410A | 29.3333
205234788 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ144XAYC* |  |  | RXYQ264XAYC* | Non-Ducted Indoor Units | 252000 | 10.8 | 20.1 | 282000 | 3.71 | 200000 | 2.27 | R-410A | 21
205234868 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ144XAYC* |  |  | RXYQ264XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.2 | 18.3 | 282000 | 3.47 | 200000 | 2.18 | R-410A | 21
205234872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ120XAYC* |  | RXYQ360XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.1 | 384000 | 3.42 | 270000 | 2.19 | R-410A | 28.5
205234869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* | RXYQ144XAYC* |  |  | RXYQ288XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 18.6 | 306000 | 3.34 | 216000 | 2.16 | R-410A | 22.8333
205234789 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* | RXYQ144XAYC* |  |  | RXYQ288XAYC* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.1 | 306000 | 3.48 | 216000 | 2.24 | R-410A | 22.8333
205234791 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168XAYC* | RXYQ168XAYC* |  |  | RXYQ336XAYC* | Non-Ducted Indoor Units | 308000 | 9.8 | 18.9 | 338000 | 3.6 | 228000 | 2.11 | R-410A | 25.6667
205234871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168XAYC* | RXYQ168XAYC* |  |  | RXYQ336XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 308000 | 9.65 | 17.8 | 338000 | 3.4 | 228000 | 2.08 | R-410A | 25.6667
205234844 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
205234845 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ168XATJ* |  |  | RXYQ312XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
205234796 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
205234704 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
205234705 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ168XATJ* |  |  | RXYQ312XATJ* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
205234854 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
205234855 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ168XAYD* |  |  | RXYQ312XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
205234806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
205234774 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
205234775 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ168XAYD* |  |  | RXYQ312XAYD* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
205811998 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205818960 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205818964 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205818968 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205818972 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205818976 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205818977 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205818978 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205818920 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205818921 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205818904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205818905 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205818912 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205818913 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205812002 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205812003 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205812004 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205818896 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205818897 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205811946 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205811947 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205811930 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205811931 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205811938 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205811939 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205811922 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205811923 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205811986 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205811990 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205811994 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205811995 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205811991 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205811987 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205811924 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205811925 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205811940 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205811941 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205811932 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205811933 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205811948 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205811949 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205818898 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205818899 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205812005 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205812006 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205812007 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205818914 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205818915 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205818906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205818907 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205818922 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205818923 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205818979 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205818980 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205818981 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205818973 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205818969 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205818965 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205818961 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205811999 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205812000 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205818962 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205818966 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205818970 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205818974 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205818982 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205818983 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205818984 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205818924 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205818925 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205818908 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205818909 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205818916 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205818917 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205812008 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205812009 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205812010 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205818900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205818901 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205811950 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205811951 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205811934 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205811935 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205811942 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205811943 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205811926 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205811927 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205811988 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205811992 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205811996 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205811997 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205811993 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205811989 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205811928 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205811929 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205811944 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205811945 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205811936 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205811937 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205811952 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205811953 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205818902 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205818903 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205812011 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205812012 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205812013 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205818918 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205818919 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205818910 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205818911 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205818926 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205818927 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205818985 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205818986 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205818987 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205818975 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205818971 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205818967 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205818963 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205812001 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
201903117 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
201903119 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
10267485 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10267486 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
10267488 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10267489 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
10267492 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
201903122 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
201903123 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
201903127 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102050 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
208102051 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
208102055 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
213916472 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.05 | 18.6 | 280000 | 3.54 | 200000 | 2.34 | R-410A | 21
213916473 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.85 | 18.5 | 308000 | 3.54 | 216000 | 2.37 | R-410A | 23
213916474 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.5 | 17.4 | 334000 | 3.52 | 236000 | 2.32 | R-410A | 24.8333
213896325 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Ducted Indoor Units | 252000 | 11.3 | 19 | 280000 | 3.47 | 200000 | 2.52 | R-410A | 21
213896327 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Ducted Indoor Units | 276000 | 11.1 | 18.1 | 308000 | 3.49 | 216000 | 2.53 | R-410A | 23
213896329 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Ducted Indoor Units | 298000 | 11 | 17.3 | 334000 | 3.46 | 236000 | 2.43 | R-410A | 24.8333
213896359 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Non-Ducted Indoor Units | 252000 | 10.8 | 18.2 | 280000 | 3.62 | 200000 | 2.16 | R-410A | 21
213896365 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Non-Ducted Indoor Units | 276000 | 10.6 | 18.9 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 23
213896366 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Non-Ducted Indoor Units | 298000 | 10 | 17.5 | 334000 | 3.59 | 236000 | 2.22 | R-410A | 24.8333
213896360 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Non-Ducted Indoor Units | 320000 | 10.1 | 17.9 | 360000 | 3.42 | 268000 | 2.13 | R-410A | 26.6667
213896331 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Ducted Indoor Units | 320000 | 10.9 | 17.4 | 360000 | 3.42 | 268000 | 2.38 | R-410A | 26.6667
213916475 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 17.65 | 360000 | 3.42 | 268000 | 2.25 | R-410A | 26.6667
213916476 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P360ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 17.1 | 386000 | 3.36 | 284000 | 2.18 | R-410A | 28.6667
213896333 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P360ZSKMU-A | Ducted Indoor Units | 344000 | 10.8 | 16.8 | 386000 | 3.32 | 284000 | 2.32 | R-410A | 28.6667
204442753 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR | AM168HXVAFR |  |  | AM336JXVAFR | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
9964029 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-360WM/B-F(U) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10257470 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP120C432Y | VEP120C432Y |  | VEP360C432Y | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102067 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP120C432Y | VEP120C432Y |  | VEP360C432Y | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102057 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102052 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10035096 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-312WM/B-F(U) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10257463 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10035094 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-288WM/B-F(U) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10324126 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  | IOV312H3CDC753(A) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10257466 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10306454 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV288H3CDC749(A) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10306452 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV264H3CDC745(A) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10257464 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10032555 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-264WM/B-F(U) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
208102047 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
204442751 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442766 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442770 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM144FXVAJR | AM192HXVAJR |  | AM408JXVAJR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442755 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM144FXVAFR | AM192HXVAFR |  | AM408JXVAFR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
208102044 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
204442812 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR | AM216KXVGJR |  |  | AM408KXVGJR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442768 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR | AM168HXVAJR |  |  | AM336JXVAJR | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
10306460 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  | IOV360H3CDC761(A) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102066 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102064 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903132 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903134 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10267496 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10267497 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
204442798 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442806 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442813 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR | AM216KXVGJR |  |  | AM432KXVGJR | Non-Ducted Indoor Units | 416000 | 9.8 | 21 | 460000 | 3.3 | 300000 | 2.4 | R-410A | 34.6667
208102056 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102054 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102059 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G | VEP120C432G |  | VEP336C432G | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
208102049 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
201903128 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G | VEP120C432G |  | VEP336C432G | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
201903124 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
201903126 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
201903120 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10267493 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-336WM/B-U(U) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
10267490 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10267491 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10267487 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10267484 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
201903116 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10306458 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  | IOV336H3CDC758(A) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
10324127 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  | IOV312H3CDC753(A) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10035097 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-312WM/B-F(U) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10035098 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-336WM/B-F(U) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
208102058 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102062 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP120C432Y | VEP120C432Y |  | VEP336C432Y | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
8175957 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 13 | 22.55 | 280000 | 3.67 | 200000 | 2.27 | R-410A | 21
8175958 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 12.75 | 22.2 | 308000 | 3.58 | 216000 | 2.3 | R-410A | 22.8333
8175959 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 12.7 | 21.85 | 334000 | 3.55 | 236000 | 2.26 | R-410A | 24.6667
8175960 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 12.5 | 21.85 | 360000 | 3.47 | 268000 | 2.19 | R-410A | 26.6667
8175961 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  | PUHY-P360YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 12.45 | 21.4 | 386000 | 3.46 | 284000 | 2.12 | R-410A | 28.5
8175972 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 13 | 22.55 | 280000 | 3.67 | 200000 | 2.27 | R-410A | 21
8175973 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 12.75 | 22.2 | 308000 | 3.58 | 216000 | 2.3 | R-410A | 22.8333
8175974 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 12.7 | 21.85 | 334000 | 3.55 | 236000 | 2.26 | R-410A | 24.6667
8175975 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 12.5 | 21.85 | 360000 | 3.47 | 268000 | 2.19 | R-410A | 26.6667
8175976 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  | PUHY-P360TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 12.45 | 21.4 | 386000 | 3.46 | 284000 | 2.12 | R-410A | 28.5
9122299 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9302773 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9363503 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
10091389 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
10091390 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
10091391 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DXN1 |  |  |  | MV5-2R288DXN1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
10091392 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DXN1 |  |  |  | MV5-2R288DXN1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
200084131 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
200084132 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
200084133 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
200084134 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
200084137 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
200084138 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
200084139 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
200084140 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
200084141 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
200084142 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
200084135 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
200084136 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
202516769 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
202516770 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202516771 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 | ARUN144DTE4 |  |  | ARUN264DTE4 | Ducted Indoor Units | 250000 | 11.4 | 21.4 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202516772 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 | ARUN144DTE4 |  |  | ARUN264DTE4 | Non-Ducted Indoor Units | 250000 | 11.9 | 21.8 | 280000 | 3.6 | 182000 | 2.49 | R-410A | 20.8333
202517448 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN121DTE4 | ARUN144DTE4 |  | ARUN360DTE4 | Ducted Indoor Units | 342000 | 11 | 21.2 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202517467 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 | ARUB144BTE4 |  |  | ARUB264BTE4 | Ducted Indoor Units | 250000 | 11.4 | 21.4 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202517468 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 | ARUN144BTE4 |  |  | ARUN264BTE4 | Ducted Indoor Units | 250000 | 11.4 | 21.4 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202517490 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 | ARUB144DTE4 |  |  | ARUB264DTE4 | Ducted Indoor Units | 250000 | 11.4 | 21.4 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202519360 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202519361 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202519362 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 | ARUN144DTE4 |  |  | ARUN288DTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202519363 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 | ARUN144DTE4 |  |  | ARUN288DTE4 | Non-Ducted Indoor Units | 274000 | 11.9 | 21.4 | 306000 | 3.55 | 198000 | 2.47 | R-410A | 22.8333
202519364 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202519365 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202519367 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 | ARUN168DTE4 |  |  | ARUN313DTE4 | Non-Ducted Indoor Units | 296000 | 11.3 | 22 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202519368 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM121BTE5 |  |  | ARUM336BTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202519369 | 1/1/2027 | LG | HMSV-A-CB | ARUN168DTE4 | ARUN168DTE4 |  |  | ARUN337DTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20.5 | 360000 | 3.52 | 234000 | 2.34 | R-410A | 26.6667
202519371 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202519372 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN121DTE4 | ARUN144DTE4 |  | ARUN360DTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 22.8 | 386000 | 3.51 | 248000 | 2.4 | R-410A | 28.5
202519374 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM168BTE5 |  |  | ARUM384BTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202519375 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN384DTE4 | Ducted Indoor Units | 366000 | 10.8 | 20.9 | 410000 | 3.4 | 266000 | 2.38 | R-410A | 30.5
202519376 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN384DTE4 | Non-Ducted Indoor Units | 366000 | 9.9 | 21 | 410000 | 3.4 | 266000 | 2.4 | R-410A | 30.5
202519378 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
202519379 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN408DTE4 | Ducted Indoor Units | 390000 | 10.6 | 20.5 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202519380 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN408DTE4 | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202519382 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM121BTE5 | ARUM121BTE5 |  | ARUM432BTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
202524555 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202524556 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
202524557 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202524558 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202524559 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202524560 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202524561 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM121DTE5 |  |  | ARUM336DTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202524563 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202524565 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM168DTE5 |  |  | ARUM384DTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202524567 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
202524569 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM121DTE5 | ARUM121DTE5 |  | ARUM432DTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
202534243 | 1/1/2027 | LG | HMSV-A-CB | ARUN145DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN432DTE4 | Ducted Indoor Units | 410000 | 10.4 | 19.8 | 460000 | 3.3 | 298000 | 2.25 | R-410A | 34.1667
202534244 | 1/1/2027 | LG | HMSV-A-CB | ARUN145DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN432DTE4 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.5 | 460000 | 3.3 | 298000 | 2.3 | R-410A | 34.1667
202534284 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 | ARUB144DTE4 |  |  | ARUB264DTE4 | Non-Ducted Indoor Units | 250000 | 11.9 | 21.8 | 280000 | 3.6 | 182000 | 2.49 | R-410A | 20.8333
202534285 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 | ARUB144BTE4 |  |  | ARUB264BTE4 | Non-Ducted Indoor Units | 250000 | 11.9 | 21.8 | 280000 | 3.6 | 182000 | 2.49 | R-410A | 20.8333
202534287 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 | ARUN144BTE4 |  |  | ARUN288BTE4 | Non-Ducted Indoor Units | 274000 | 11.9 | 21.4 | 306000 | 3.55 | 198000 | 2.47 | R-410A | 22.8333
202534288 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 | ARUB144BTE4 |  |  | ARUB288BTE4 | Non-Ducted Indoor Units | 274000 | 11.9 | 21.4 | 306000 | 3.55 | 198000 | 2.47 | R-410A | 22.8333
202534289 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 | ARUB144DTE4 |  |  | ARUB288DTE4 | Non-Ducted Indoor Units | 274000 | 11.9 | 21.4 | 306000 | 3.55 | 198000 | 2.47 | R-410A | 22.8333
202534290 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 | ARUB144DTE4 |  |  | ARUB288DTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534291 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 | ARUB144BTE4 |  |  | ARUB288BTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534292 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 | ARUN144BTE4 |  |  | ARUN288BTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534293 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN121BTE4 | ARUN144BTE4 |  | ARUN360BTE4 | Ducted Indoor Units | 342000 | 11 | 21.2 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202534294 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB121BTE4 | ARUB144BTE4 |  | ARUB360BTE4 | Ducted Indoor Units | 342000 | 11 | 21.2 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202534295 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB121DTE4 | ARUB144DTE4 |  | ARUB360DTE4 | Ducted Indoor Units | 342000 | 11 | 21.2 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202534296 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB121DTE4 | ARUB144DTE4 |  | ARUB360DTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 22.8 | 386000 | 3.51 | 248000 | 2.4 | R-410A | 28.5
202534297 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB121BTE4 | ARUB144BTE4 |  | ARUB360BTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 22.8 | 386000 | 3.51 | 248000 | 2.4 | R-410A | 28.5
202534298 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN121BTE4 | ARUN144BTE4 |  | ARUN360BTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 22.8 | 386000 | 3.51 | 248000 | 2.4 | R-410A | 28.5
202534299 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN384BTE4 | Ducted Indoor Units | 366000 | 10.8 | 20.9 | 410000 | 3.4 | 266000 | 2.38 | R-410A | 30.5
202534300 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN384BTE4 | Non-Ducted Indoor Units | 366000 | 9.9 | 21 | 410000 | 3.4 | 266000 | 2.4 | R-410A | 30.5
202534301 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB145DTE4 | ARUB145DTE4 |  | ARUB384DTE4 | Ducted Indoor Units | 366000 | 10.8 | 20.9 | 410000 | 3.4 | 266000 | 2.38 | R-410A | 30.5
202534302 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB145DTE4 | ARUB145DTE4 |  | ARUB384DTE4 | Non-Ducted Indoor Units | 366000 | 9.9 | 21 | 410000 | 3.4 | 266000 | 2.4 | R-410A | 30.5
202534303 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB384BTE4 | Ducted Indoor Units | 366000 | 10.8 | 20.9 | 410000 | 3.4 | 266000 | 2.38 | R-410A | 30.5
202534304 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB384BTE4 | Non-Ducted Indoor Units | 366000 | 9.9 | 21 | 410000 | 3.4 | 266000 | 2.4 | R-410A | 30.5
202534305 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN408BTE4 | Ducted Indoor Units | 390000 | 10.6 | 20.5 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534306 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN408BTE4 | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534307 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 | ARUB145DTE4 | ARUB145DTE4 |  | ARUB408DTE4 | Ducted Indoor Units | 390000 | 10.6 | 20.5 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534308 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 | ARUB145DTE4 | ARUB145DTE4 |  | ARUB408DTE4 | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534309 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB408BTE4 | Ducted Indoor Units | 390000 | 10.6 | 20.5 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534310 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB408BTE4 | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534311 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 | ARUB168DTE4 |  |  | ARUB313DTE4 | Non-Ducted Indoor Units | 296000 | 11.3 | 22 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534312 | 1/1/2027 | LG | HMSR-A-CB | ARUB168DTE4 | ARUB168DTE4 |  |  | ARUB337DTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20.5 | 360000 | 3.52 | 234000 | 2.34 | R-410A | 26.6667
202534313 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 | ARUB168BTE4 |  |  | ARUB313BTE4 | Non-Ducted Indoor Units | 296000 | 11.3 | 22 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534314 | 1/1/2027 | LG | HMSR-A-CB | ARUB168BTE4 | ARUB168BTE4 |  |  | ARUB337BTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20.5 | 360000 | 3.52 | 234000 | 2.34 | R-410A | 26.6667
202534315 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 | ARUN168BTE4 |  |  | ARUN313BTE4 | Non-Ducted Indoor Units | 296000 | 11.3 | 22 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534316 | 1/1/2027 | LG | HMSV-A-CB | ARUN168BTE4 | ARUN168BTE4 |  |  | ARUN337BTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20.5 | 360000 | 3.52 | 234000 | 2.34 | R-410A | 26.6667
203297525 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A | PURY-P120TKMU-A |  |  | PURY-P264TSKMU-A | Ducted Indoor Units | 250000 | 11 | 17.3 | 280000 | 3.38 | 200000 | 2.35 | R-410A | 20.8333
203297529 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A | PURY-P120YKMU-A |  |  | PURY-P264YSKMU-A | Ducted Indoor Units | 250000 | 11 | 17.3 | 280000 | 3.38 | 200000 | 2.35 | R-410A | 20.8333
203297535 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A | PURY-P144TKMU-A |  |  | PURY-P288TSKMU-A | Ducted Indoor Units | 274000 | 11.2 | 17.2 | 304000 | 3.39 | 216000 | 2.35 | R-410A | 22.8333
203297539 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A | PURY-P144YKMU-A |  |  | PURY-P288YSKMU-A | Ducted Indoor Units | 274000 | 11.2 | 17.2 | 304000 | 3.39 | 216000 | 2.35 | R-410A | 22.8333
203376929 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203376933 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203376937 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203376941 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378290 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203378291 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203378292 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378293 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378353 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378354 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378419 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203378420 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203378449 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378450 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378451 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203378452 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203381097 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381098 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381141 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203381142 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203381228 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A | PURY-P120TKMU-A |  |  | PURY-P264TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11 | 17.65 | 280000 | 3.3 | 200000 | 2.21 | R-410A | 20.8333
203381232 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A | PURY-P120YKMU-A |  |  | PURY-P264YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11 | 17.65 | 280000 | 3.3 | 200000 | 2.21 | R-410A | 20.8333
203381237 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A | PURY-P144TKMU-A |  |  | PURY-P288TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.25 | 17.7 | 304000 | 3.3 | 216000 | 2.2 | R-410A | 22.8333
203381241 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A | PURY-P144YKMU-A |  |  | PURY-P288YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.25 | 17.7 | 304000 | 3.3 | 216000 | 2.2 | R-410A | 22.8333
203381300 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381301 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381344 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203381346 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
200084161 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
200084162 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
200084163 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
200084164 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
200084165 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
200084166 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
200084167 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
200084168 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
200084169 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
200084170 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
200084171 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
200084172 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
201847149 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201847150 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847151 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201847152 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847153 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G | VPA096H4M-2G |  | VPA336H4M-2G | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847154 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G | VPA096H4M-2G |  | VPA336H4M-2G | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201847155 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y | VPA096H4M-2Y |  | VPA336H4M-2Y | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847156 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y | VPA096H4M-2Y |  | VPA336H4M-2Y | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201847209 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201847210 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847211 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201847212 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847213 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y | VRA096H4M-2Y |  | VRA336H4M-2Y | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847214 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y | VRA096H4M-2Y |  | VRA336H4M-2Y | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201847215 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G | VRA096H4M-2G |  | VRA336H4M-2G | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847216 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G | VRA096H4M-2G |  | VRA336H4M-2G | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201856734 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC264DXN1-(A) | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856735 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC264DXN1-(A) | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856736 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC288DXN1-(A) | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856737 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC288DXN1-(A) | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856738 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856739 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC312DXN1-(A) | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201856740 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201856741 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC336DXN1-(A) | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201856758 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC264DZN1-(A) | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856759 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC264DZN1-(A) | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856760 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC288DZN1-(A) | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856761 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC288DZN1-(A) | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856762 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856763 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC312DZN1-(A) | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201856764 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201856765 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC336DZN1-(A) | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201856782 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC264DXN1-(A) | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856783 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC264DXN1-(A) | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856784 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC288DXN1-(A) | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856785 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC288DXN1-(A) | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856786 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  | MV5-XC312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856804 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC264DZN1-(A) | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856805 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC264DZN1-(A) | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856806 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC288DZN1-(A) | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856807 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC288DZN1-(A) | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856808 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  | MV5-XC312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862870 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA264L4M-2Y | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862871 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA264L4M-2Y | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862872 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA288L4M-2Y | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862873 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA288L4M-2Y | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862874 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA096L4M-2Y |  | VRA312L4M-2Y | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862875 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA096L4M-2Y |  | VRA312L4M-2Y | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201862876 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y | VRA096L4M-2Y |  | VRA336L4M-2Y | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201862877 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y | VRA096L4M-2Y |  | VRA336L4M-2Y | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201862894 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA264L4M-2G | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA264L4M-2G | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862896 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA288L4M-2G | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862897 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA288L4M-2G | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862898 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA096L4M-2G |  | VRA312L4M-2G | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862899 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA096L4M-2G |  | VRA312L4M-2G | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201862900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G | VRA096L4M-2G |  | VRA336L4M-2G | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201862901 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G | VRA096L4M-2G |  | VRA336L4M-2G | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201862918 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA264L4M-2Y | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862919 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA264L4M-2Y | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862920 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA288L4M-2Y | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862921 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA288L4M-2Y | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862922 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA096L4M-2Y |  | VPA312L4M-2Y | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862940 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA264L4M-2G | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862941 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA264L4M-2G | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862942 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA288L4M-2G | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862943 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA288L4M-2G | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862944 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA096L4M-2G |  | VPA312L4M-2G | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201863373 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863374 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A)* | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863379 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863380 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A)* | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863385 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863386 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A)* | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863391 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863392 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A)* | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201874070 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
201874071 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
201874072 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  | PUHY-P360TSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
201874075 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
201874076 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
201874077 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  | PUHY-P360YSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
201874079 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Ducted Indoor Units | 252000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 21
201874082 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
201874086 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Ducted Indoor Units | 250000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 20.8333
201874090 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
206799477 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799478 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799479 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799480 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799481 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799482 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799483 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799484 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
202534373 | 1/1/2027 | LG | HMSR-A-CB | ARUB145BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB432BTE4 | Ducted Indoor Units | 410000 | 10.4 | 19.8 | 460000 | 3.3 | 298000 | 2.25 | R-410A | 34.1667
202534374 | 1/1/2027 | LG | HMSR-A-CB | ARUB145BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB432BTE4 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.5 | 460000 | 3.3 | 298000 | 2.3 | R-410A | 34.1667
205281471 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
205281473 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
205281474 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
205281479 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
205281480 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
205281481 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
208685685 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
208685686 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
208685687 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
208685689 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH |  |  | AVWT-288FFFH | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
208685690 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH |  |  | AVWT-288FFFH | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
208685692 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-168FFFH |  |  | AVWT-312FFFH | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
208685704 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-408FFFH | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
208685705 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-408FFFH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
208685707 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-432FFFH | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
208685708 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-432FFFH | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
208685710 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-168FFFH |  | AVWT-456FFFH | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
208758288 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
208758289 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
208758290 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
208758292 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB |  |  | CHV6-288URB | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
208758293 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB |  |  | CHV6-288URB | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
208758295 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-168URB |  |  | CHV6-312URB | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
208758307 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB | CHV6-144URB |  | CHV6-408URB | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
208758308 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB | CHV6-144URB |  | CHV6-408URB | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
208758310 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-144URB |  | CHV6-432URB | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
208758311 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-144URB |  | CHV6-432URB | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
208758313 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-168URB |  | CHV6-456URB | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
210691242 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
210691243 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
210691244 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
210691246 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA |  |  | AVWT-288FHFSHA | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
210691247 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA |  |  | AVWT-288FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
210691249 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-168FHFSHA |  |  | AVWT-312FHFSHA | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
210691261 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-408FHFSHA | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
210691262 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-408FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
210691264 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-432FHFSHA | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
210691265 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-432FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
210691267 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-168FHFSHA |  | AVWT-456FHFSHA | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
212928536 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Ducted Indoor Units | 240000 | 11.4 | 18.7 | 258000 | 3.5 | 162000 | 2.36 | R-410A | 20
212928537 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Non-Ducted Indoor Units | 240000 | 11.8 | 19 | 258000 | 3.8 | 162000 | 2.38 | R-410A | 20
212928541 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Ducted Indoor Units | 240000 | 11.4 | 18.7 | 258000 | 3.5 | 162000 | 2.36 | R-410A | 20
212928542 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Non-Ducted Indoor Units | 240000 | 11.8 | 19 | 258000 | 3.8 | 162000 | 2.38 | R-410A | 20
212928545 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 240000 | 11.6 | 18.85 | 258000 | 3.65 | 162000 | 2.37 | R-410A | 20
212928548 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 240000 | 11.6 | 18.85 | 258000 | 3.65 | 162000 | 2.37 | R-410A | 20
213686159 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
213686160 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
213686161 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
213686163 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH |  |  | AVWT-288FLFSH | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
213686164 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH |  |  | AVWT-288FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
213686166 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-168FLFSH |  |  | AVWT-312FLFSH | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
213686178 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-408FLFSH | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
213686179 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-408FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
213686181 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-432FLFSH | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
213686182 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-432FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
213686184 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-168FLFSH |  | AVWT-456FLFSH | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
206453552 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
206453553 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM121BTE5 |  |  | ARUM336BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
206453554 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453555 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453556 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453557 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM168BTE5 |  |  | ARUM384BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453558 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
206453559 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM121BTE5 | ARUM121BTE5 |  | ARUM432BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
206453560 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
206453561 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453562 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453563 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM121DTE5 |  |  | ARUM336DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
206453564 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453565 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM168DTE5 |  |  | ARUM384DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453566 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
206453567 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM121DTE5 | ARUM121DTE5 |  | ARUM432DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
10103116 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ144TAYC* |  |  | REYQ264TAYC* | Non-Ducted Indoor Units | 252000 | 11.2 | 20.5 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
10103117 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ144TAYC* |  |  | REYQ288TAYC* | Non-Ducted Indoor Units | 274000 | 11 | 20.3 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
10103118 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ168TAYC* |  |  | REYQ312TAYC* | Non-Ducted Indoor Units | 296000 | 10.1 | 19.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
10103119 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYC* | REYQ168TAYC* |  |  | REYQ336TAYC* | Non-Ducted Indoor Units | 320000 | 9.8 | 19 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
10103120 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* | REYQ120TAYC* |  | REYQ360TAYC* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 384000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
10103157 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ144TAYC* |  |  | REYQ264TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 18.75 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
10103158 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ144TAYC* |  |  | REYQ288TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 18.85 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
10103159 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ168TAYC* |  |  | REYQ312TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.9 | 18.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
10103160 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYC* | REYQ168TAYC* |  |  | REYQ336TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 17.9 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
10103161 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* | REYQ120TAYC* |  | REYQ360TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.65 | 18.6 | 384000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
10206684 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206712 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206726 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206740 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206754 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206768 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206769 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206770 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206771 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206773 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S | TVAHP144B32S |  | TVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206782 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206783 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206784 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206785 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206787 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S | HVAHP144B32S |  | HVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206796 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206797 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206798 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206799 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S | YVAHP144B32S |  | YVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206810 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206811 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206812 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206813 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206815 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S | TVAHP144B42S |  | TVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206824 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206825 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206826 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206827 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206829 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S | HVAHP144B42S |  | HVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206838 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206839 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206840 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206841 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206843 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S | YVAHP144B42S |  | YVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10207486 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S | TVAHP120B32S |  | TVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207488 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S | HVAHP120B32S |  | HVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207490 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S | YVAHP120B32S |  | YVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207492 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S | TVAHP120B42S |  | TVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207494 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S | HVAHP120B42S |  | HVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207496 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S | YVAHP120B42S |  | YVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207518 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207519 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207520 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207521 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207532 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207533 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207534 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207535 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207546 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207547 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207548 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207549 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207560 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207561 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207562 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207563 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207574 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207575 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207576 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207577 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207588 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207589 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207590 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207591 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10208208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
10208209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DZN1 |  |  |  | MV5-2R288DZN1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
10208213 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
10208214 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DZN1 |  |  |  | MV5-2R288DZN1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
10208473 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
10208474 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DXN1 |  |  |  | MV5-2R288DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
10208478 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
10208479 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DZN1 |  |  |  | MV5-2R288DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
9363504 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9363505 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9363506 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9363507 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9363483 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA144HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA264HDS5-1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9363486 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA144HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA264HDS6-1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9363494 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9363496 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9363497 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9363498 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9363499 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9363500 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9363501 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9302774 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9302775 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9302776 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9302777 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9302756 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA144HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA264HDS5-1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9302759 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA144HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA264HDS6-1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9302766 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9302767 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9302768 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9302769 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9302770 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9302771 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9302772 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9990037 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ144TATJ* |  |  | RXYQ264TATJ* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
9990038 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
9990039 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ168TATJ* |  |  | RXYQ312TATJ* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
9990041 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* | RXYQ120TATJ* |  | RXYQ360TATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
9990054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ144TAYD* |  |  | RXYQ264TAYD* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
9990055 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
9990056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ168TAYD* |  |  | RXYQ312TAYD* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
9990058 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* | RXYQ120TAYD* |  | RXYQ360TAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
9990075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
9990076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
9990103 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ144TATJ* |  |  | RXYQ264TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
9990104 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ144TAYD* |  |  | RXYQ264TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
9990105 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
9990106 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
9990107 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ168TATJ* |  |  | RXYQ312TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
9990108 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ168TAYD* |  |  | RXYQ312TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
9990111 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* | RXYQ120TATJ* |  | RXYQ360TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
9990112 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* | RXYQ120TAYD* |  | RXYQ360TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
9990307 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
9990308 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
10323542 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323547 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S | TVAHR120B32S |  | TVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323558 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323563 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S | HVAHR120B32S |  | HVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323574 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323579 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S | YVAHR120B32S |  | YVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323590 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323595 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S | TVAHR120B42S |  | TVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323606 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323611 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S | HVAHR120B42S |  | HVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323622 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323627 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S | YVAHR120B42S |  | YVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323638 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323639 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323640 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323641 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323645 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S | TVAHR144B32S |  | TVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323654 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323655 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323656 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323657 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323661 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S | HVAHR144B32S |  | HVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323670 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323671 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323672 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323673 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323677 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S | YVAHR144B32S |  | YVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323686 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323687 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323688 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323689 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323693 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S | TVAHR144B42S |  | TVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323702 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323703 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323704 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323705 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323709 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S | HVAHR144B42S |  | HVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323718 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323719 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323720 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323721 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323725 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S | YVAHR144B42S |  | YVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323736 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323737 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323738 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323739 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323752 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323753 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323754 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323755 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323768 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323769 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323770 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323771 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323785 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323786 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323787 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323788 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323801 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323802 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323803 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323804 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323817 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323818 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323819 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323820 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10611545 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
10611546 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A) | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611547 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611548 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611559 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
10611560 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A) | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611561 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611562 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611584 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
10611585 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A) | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611586 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611587 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611608 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
10611609 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A) | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611610 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611611 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611628 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.65 | 20.65 | 320000 | 3.31 | 218000 | 2.22 | R-410A | 24.8333
10611629 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 19.3 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10611643 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.65 | 20.65 | 320000 | 3.31 | 218000 | 2.22 | R-410A | 24.8333
10611644 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 19.3 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10612360 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.8 | 21 | 320000 | 3.31 | 218000 | 2.22 | R-410A | 24.8333
10612361 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.65 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10612372 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.8 | 21 | 320000 | 3.31 | 218000 | 2.22 | R-410A | 24.8333
10612373 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.65 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10612415 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
10612416 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
10612417 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
10612418 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
10612419 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
10612420 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
10612421 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
10612422 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
10612423 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
10612424 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
10612425 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
10612426 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
10612427 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
10612428 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
10612429 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
10612430 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
10612431 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
10612432 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
10612433 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
10612434 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
10612435 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
10612436 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
10612487 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
10612488 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
10612489 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
10612490 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
10612491 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
10612492 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
10612493 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
10612494 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
10612495 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
10612496 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
10612497 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
10612498 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
10612499 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
10612500 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
10612501 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
10612502 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
10612503 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
10612504 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
10612505 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
10612506 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
10612507 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
10612510 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
10612511 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
10612512 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
10612513 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
10612514 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
10612515 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
10612516 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
10612517 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 434000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
10612518 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 434000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
10612521 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
10612598 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
10612599 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
10612600 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
10612601 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
10612602 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
10612603 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
10612604 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
10612605 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
10612606 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
10612607 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
10612608 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
10612609 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
10612610 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
10612611 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
10612612 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
10612613 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
10612614 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
10612615 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
10612616 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
10612617 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
10612618 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
10612619 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1686FT6P-UL |  |  | MMY-AP336S6FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
10612621 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1686FT9P-UL |  |  | MMY-AP336S6FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
10612623 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
10612625 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
10612627 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
10612628 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
10612629 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
10612630 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
10612635 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
10612636 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 435000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
10612637 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
10612638 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 435000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
10612639 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
10612640 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 435000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
10612641 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
10612642 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 435000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
10612647 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
10612648 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
10612649 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
10612650 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
10612656 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4566HT6P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 485000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
10612658 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4566HT9P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 485000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
10612665 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
10612666 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 434000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
10612667 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 434000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
10612668 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
8657028 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P264ZSKMU-A | Non-Ducted Indoor Units | 252000 | 12.9 | 23.5 | 280000 | 3.62 | 200000 | 2.16 | R-410A | 21
8657030 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P288ZSKMU-A | Non-Ducted Indoor Units | 274000 | 12.8 | 23.5 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
8657032 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P312ZSKMU-A | Non-Ducted Indoor Units | 296000 | 12.7 | 22.7 | 334000 | 3.59 | 236000 | 2.22 | R-410A | 24.6667
8657034 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A |  | PUHY-P336ZSKMU-A | Non-Ducted Indoor Units | 320000 | 12.5 | 22.6 | 360000 | 3.42 | 268000 | 2.13 | R-410A | 26.6667
9121946 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H144DXN1 | MV5-H120DXN1 |  |  | MV5-H264DXN1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9121957 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H144DZN1 | MV5-H120DZN1 |  |  | MV5-H264DZN1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9121971 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9121972 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9121973 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9121974 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9121992 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9121993 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9121994 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9121995 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9122298 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9122314 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9122315 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9122957 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Non-Ducted Indoor Units | 252000 | 11.2 | 23.8 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
9122958 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.4 | 23.5 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
9122959 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 23 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
9122960 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.6 | 22.7 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
9122961 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Non-Ducted Indoor Units | 320000 | 11 | 24.6 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
9122962 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1686FT6P-UL |  |  | MMY-AP336S6FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.4 | 22.5 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
9122963 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Non-Ducted Indoor Units | 342000 | 10 | 24 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
9122998 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Ducted Indoor Units | 252000 | 11.4 | 22.5 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
9122999 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Non-Ducted Indoor Units | 252000 | 11.2 | 23.8 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
9123000 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Ducted Indoor Units | 252000 | 11.4 | 22.5 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
9123001 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Ducted Indoor Units | 276000 | 11.5 | 22 | 308000 | 3.5 | 216000 | 2.4 | R-410A | 23
9123002 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.4 | 23.5 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
9123003 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Ducted Indoor Units | 276000 | 11.5 | 22 | 308000 | 3.5 | 216000 | 2.4 | R-410A | 23
9123004 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Ducted Indoor Units | 276000 | 10.3 | 21.5 | 308000 | 3.4 | 216000 | 2.35 | R-410A | 23
9123005 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 23 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
9123006 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Ducted Indoor Units | 276000 | 10.3 | 21.5 | 308000 | 3.4 | 216000 | 2.35 | R-410A | 23
9123007 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Ducted Indoor Units | 298000 | 10.5 | 21.5 | 334000 | 3.32 | 236000 | 2.35 | R-410A | 24.8333
9123008 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.6 | 22.7 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
9123009 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Ducted Indoor Units | 298000 | 10.5 | 21.5 | 334000 | 3.32 | 236000 | 2.35 | R-410A | 24.8333
9123010 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Ducted Indoor Units | 320000 | 10.7 | 22.5 | 360000 | 3.35 | 268000 | 2.4 | R-410A | 26.6667
9123011 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Non-Ducted Indoor Units | 320000 | 11 | 24.6 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
9123012 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Ducted Indoor Units | 320000 | 10.7 | 22.5 | 360000 | 3.35 | 268000 | 2.4 | R-410A | 26.6667
9123014 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1686FT9P-UL |  |  | MMY-AP336S6FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.4 | 22.5 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
9123016 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Ducted Indoor Units | 342000 | 10 | 22 | 386000 | 3.4 | 284000 | 2.3 | R-410A | 28.5
9123017 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Non-Ducted Indoor Units | 342000 | 10 | 24 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
9123018 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Ducted Indoor Units | 342000 | 10 | 22 | 386000 | 3.4 | 284000 | 2.3 | R-410A | 28.5
9123019 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.3 | 294000 | 2.2 | R-410A | 30.5
9123021 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.3 | 294000 | 2.2 | R-410A | 30.5
9123022 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP4086FT6P-UL | Ducted Indoor Units | 390000 | 9.9 | 21 | 435000 | 3.3 | 310000 | 2.31 | R-410A | 32.5
9123024 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP4086FT9P-UL | Ducted Indoor Units | 390000 | 9.9 | 21 | 435000 | 3.3 | 310000 | 2.31 | R-410A | 32.5
9123025 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  | MMY-AP4326FT6P-UL | Ducted Indoor Units | 410000 | 9.7 | 20.5 | 460000 | 3.25 | 328000 | 2.3 | R-410A | 34.1667
9123027 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  | MMY-AP4326FT9P-UL | Ducted Indoor Units | 410000 | 9.7 | 20.5 | 460000 | 3.25 | 328000 | 2.3 | R-410A | 34.1667
9123051 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.3 | 23.15 | 282000 | 3.45 | 200000 | 2.42 | R-410A | 21
9123052 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.3 | 23.15 | 282000 | 3.45 | 200000 | 2.42 | R-410A | 21
9123053 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.45 | 22.75 | 308000 | 3.47 | 216000 | 2.45 | R-410A | 23
9123054 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.45 | 22.75 | 308000 | 3.47 | 216000 | 2.45 | R-410A | 23
9123055 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.45 | 22.25 | 308000 | 3.37 | 216000 | 2.35 | R-410A | 23
9123056 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.45 | 22.25 | 308000 | 3.37 | 216000 | 2.35 | R-410A | 23
9123057 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 22.1 | 334000 | 3.31 | 236000 | 2.37 | R-410A | 24.8333
9123058 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 22.1 | 334000 | 3.31 | 236000 | 2.37 | R-410A | 24.8333
9123059 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.85 | 23.55 | 360000 | 3.37 | 268000 | 2.4 | R-410A | 26.6667
9123060 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.85 | 23.55 | 360000 | 3.37 | 268000 | 2.4 | R-410A | 26.6667
9123063 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10 | 23 | 386000 | 3.35 | 284000 | 2.32 | R-410A | 28.5
9123064 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10 | 23 | 386000 | 3.35 | 284000 | 2.32 | R-410A | 28.5
9123065 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10 | 22.45 | 410000 | 3.27 | 294000 | 2.27 | R-410A | 30.5
9123066 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10 | 22.45 | 410000 | 3.27 | 294000 | 2.27 | R-410A | 30.5
9123067 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP4086FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.9 | 21.75 | 434000 | 3.26 | 310000 | 2.33 | R-410A | 32.5
9123068 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP4086FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.9 | 21.75 | 434000 | 3.26 | 310000 | 2.33 | R-410A | 32.5
9045762 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045764 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045786 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045788 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045812 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9056984 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9056985 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9056996 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9056997 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9057008 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9057009 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9085416 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
9085417 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Ducted Indoor Units | 252000 | 12.2 | 21.6 | 282000 | 3.95 | 200000 | 2.92 | R-410A | 21
9085418 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
9085419 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Ducted Indoor Units | 276000 | 11.5 | 21.2 | 308000 | 3.85 | 216000 | 2.92 | R-410A | 23
9085420 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
9085421 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Ducted Indoor Units | 276000 | 11.4 | 20.8 | 308000 | 3.8 | 216000 | 2.83 | R-410A | 23
9085422 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
9085423 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Ducted Indoor Units | 298000 | 11 | 20.9 | 334000 | 3.7 | 236000 | 2.75 | R-410A | 24.8333
9085424 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
9085425 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Ducted Indoor Units | 320000 | 10.6 | 20.7 | 360000 | 3.52 | 268000 | 2.6 | R-410A | 26.6667
9085426 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 386000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
9085427 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Ducted Indoor Units | 342000 | 12 | 21.4 | 386000 | 3.7 | 284000 | 2.75 | R-410A | 28.5
9085428 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
9085429 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Ducted Indoor Units | 366000 | 11.2 | 20.8 | 410000 | 3.58 | 294000 | 2.66 | R-410A | 30.5
9085430 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
9085431 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Ducted Indoor Units | 390000 | 11.2 | 20.6 | 435000 | 3.4 | 310000 | 2.6 | R-410A | 32.5
9085432 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
9085433 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Ducted Indoor Units | 390000 | 10.8 | 20.2 | 435000 | 3.35 | 310000 | 2.58 | R-410A | 32.5
9085434 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
9085435 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Ducted Indoor Units | 410000 | 10.4 | 20 | 460000 | 3.35 | 328000 | 2.55 | R-410A | 34.1667
9085437 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4566HT9P-UL | Ducted Indoor Units | 435000 | 10 | 19.8 | 490000 | 3.28 | 350000 | 2.52 | R-410A | 36.25
9085448 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.8 | 22.2 | 282000 | 3.8 | 200000 | 2.79 | R-410A | 21
9085449 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 21.85 | 308000 | 3.72 | 216000 | 2.78 | R-410A | 23
9085450 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.15 | 21.5 | 308000 | 3.65 | 216000 | 2.7 | R-410A | 23
9085451 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21.5 | 334000 | 3.56 | 236000 | 2.67 | R-410A | 24.8333
9085452 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 21.35 | 360000 | 3.43 | 268000 | 2.53 | R-410A | 26.6667
9085453 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.8 | 21.9 | 386000 | 3.61 | 284000 | 2.66 | R-410A | 28.5
9085454 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.9 | 21.3 | 410000 | 3.49 | 294000 | 2.6 | R-410A | 30.5
9085455 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.8 | 21 | 434000 | 3.39 | 310000 | 2.55 | R-410A | 32.5
9085456 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.5 | 20.6 | 434000 | 3.32 | 310000 | 2.53 | R-410A | 32.5
9085457 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.2 | 20.65 | 460000 | 3.31 | 328000 | 2.51 | R-410A | 34.1667
8989560 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
8989561 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
8989562 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
8989563 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
8989564 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
8989565 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 386000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
8989576 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Ducted Indoor Units | 252000 | 12.2 | 21.6 | 282000 | 3.95 | 200000 | 2.92 | R-410A | 21
8989577 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Ducted Indoor Units | 276000 | 11.5 | 21.2 | 308000 | 3.85 | 216000 | 2.92 | R-410A | 23
8989578 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Ducted Indoor Units | 276000 | 11.4 | 20.8 | 308000 | 3.8 | 216000 | 2.83 | R-410A | 23
8989579 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Ducted Indoor Units | 298000 | 11 | 20.9 | 334000 | 3.7 | 236000 | 2.75 | R-410A | 24.8333
8989580 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Ducted Indoor Units | 320000 | 10.6 | 20.7 | 360000 | 3.52 | 268000 | 2.6 | R-410A | 26.6667
8989617 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.8 | 22.2 | 282000 | 3.8 | 200000 | 2.79 | R-410A | 21
8989618 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 21.85 | 308000 | 3.72 | 216000 | 2.78 | R-410A | 23
8989619 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.15 | 21.5 | 308000 | 3.65 | 216000 | 2.7 | R-410A | 23
8989620 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21.5 | 334000 | 3.56 | 236000 | 2.67 | R-410A | 24.8333
8989621 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 21.35 | 360000 | 3.43 | 268000 | 2.53 | R-410A | 26.6667
8989623 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Ducted Indoor Units | 342000 | 12 | 21.4 | 386000 | 3.7 | 284000 | 2.75 | R-410A | 28.5
8989624 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
8989625 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
8989626 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
8989627 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
8989629 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.8 | 21.9 | 386000 | 3.61 | 284000 | 2.66 | R-410A | 28.5
8989630 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Ducted Indoor Units | 366000 | 11.2 | 20.8 | 410000 | 3.58 | 294000 | 2.66 | R-410A | 30.5
8989631 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Ducted Indoor Units | 390000 | 11.2 | 20.6 | 435000 | 3.4 | 310000 | 2.6 | R-410A | 32.5
8989632 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Ducted Indoor Units | 390000 | 10.8 | 20.2 | 435000 | 3.35 | 310000 | 2.58 | R-410A | 32.5
8989633 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Ducted Indoor Units | 410000 | 10.4 | 20 | 460000 | 3.35 | 328000 | 2.55 | R-410A | 34.1667
8989634 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4566HT6P-UL | Ducted Indoor Units | 435000 | 10 | 19.8 | 490000 | 3.28 | 350000 | 2.52 | R-410A | 36.25
8989635 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.9 | 21.3 | 410000 | 3.49 | 294000 | 2.6 | R-410A | 30.5
8989636 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.8 | 21 | 434000 | 3.39 | 310000 | 2.55 | R-410A | 32.5
8989637 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.5 | 20.6 | 434000 | 3.32 | 310000 | 2.53 | R-410A | 32.5
8989638 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.2 | 20.65 | 460000 | 3.31 | 328000 | 2.51 | R-410A | 34.1667
8715619 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715620 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715625 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715626 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715631 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715632 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715637 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715638 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715643 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715644 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715649 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715650 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715655 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715656 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715657 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP120B31S |  | YVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715658 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP120B41S |  | YVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715661 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715662 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715663 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR120B31S |  | YVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715664 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR120B41S |  | YVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715667 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715668 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715669 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP120B31S |  | HVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715670 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP120B41S |  | HVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715673 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715674 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715675 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR120B31S |  | HVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715676 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR120B41S |  | HVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715679 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715680 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715681 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP120B31S |  | TVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715682 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP120B41S |  | TVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715685 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715686 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715687 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR120B31S |  | TVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715688 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR120B41S |  | TVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715691 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715692 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715693 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP120B31S |  | YVAHP360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715694 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP120B41S |  | YVAHP360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715697 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715698 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715699 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR120B31S |  | YVAHR360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715700 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR120B41S |  | YVAHR360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715703 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715704 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715705 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP120B31S |  | HVAHP360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715706 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP120B41S |  | HVAHP360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715709 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715710 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715711 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR120B31S |  | HVAHR360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715712 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR120B41S |  | HVAHR360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715715 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715716 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715717 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP120B31S |  | TVAHP360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715718 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP120B41S |  | TVAHP360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715721 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715722 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715723 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR120B31S |  | TVAHR360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715724 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR120B41S |  | TVAHR360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
7041897 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ144TTJU |  |  | RXYQ288TTJU | Ducted Indoor Units | 274000 | 10.5 | 19.3 | 308000 | 3.31 | 200000 | 2.13 | R-410A | 22.8333
7041898 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ144TYDN |  |  | RXYQ288TYDN | Ducted Indoor Units | 274000 | 10.5 | 19.3 | 308000 | 3.31 | 200000 | 2.13 | R-410A | 22.8333
7041899 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ144TTJU |  |  | RXYQ288TTJU | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
7041900 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ144TYDN |  |  | RXYQ288TYDN | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
7042723 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ144TTJU |  |  | RXYQ288TTJU | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 19.7 | 308000 | 3.28 | 200000 | 2.1 | R-410A | 22.8333
7042724 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ144TYDN |  |  | RXYQ288TYDN | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 19.7 | 308000 | 3.28 | 200000 | 2.1 | R-410A | 22.8333
7064658 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ168TTJU |  |  | RXYQ312TTJU | Ducted Indoor Units | 296000 | 9.8 | 18.8 | 334000 | 3.26 | 206000 | 2.2 | R-410A | 24.6667
7064659 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ168TYDN |  |  | RXYQ312TYDN | Ducted Indoor Units | 296000 | 9.8 | 18.8 | 334000 | 3.26 | 206000 | 2.2 | R-410A | 24.6667
7064660 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ168TTJU |  |  | RXYQ312TTJU | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
7064661 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ168TYDN |  |  | RXYQ312TYDN | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
7064662 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU | RXYQ120TTJU |  | RXYQ360TTJU | Ducted Indoor Units | 342000 | 10.9 | 18.5 | 384000 | 3.25 | 250000 | 2.41 | R-410A | 28.5
7064663 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN | RXYQ120TYDN |  | RXYQ360TYDN | Ducted Indoor Units | 342000 | 10.9 | 18.5 | 384000 | 3.25 | 250000 | 2.41 | R-410A | 28.5
7064664 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU | RXYQ120TTJU |  | RXYQ360TTJU | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 384000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
7064665 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN | RXYQ120TYDN |  | RXYQ360TYDN | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 384000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
7064666 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU | RXYQ168TTJU |  | RXYQ384TTJU | Ducted Indoor Units | 364000 | 10 | 18.5 | 410000 | 3.26 | 274000 | 2.28 | R-410A | 30.3333
7064667 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN | RXYQ168TYDN |  | RXYQ384TYDN | Ducted Indoor Units | 364000 | 10 | 18.5 | 410000 | 3.26 | 274000 | 2.28 | R-410A | 30.3333
7064672 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ168TTJU |  |  | RXYQ312TTJU | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.8 | 19.35 | 334000 | 3.28 | 206000 | 2.26 | R-410A | 24.6667
7064673 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ168TYDN |  |  | RXYQ312TYDN | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.8 | 19.35 | 334000 | 3.28 | 206000 | 2.26 | R-410A | 24.6667
7064674 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU | RXYQ120TTJU |  | RXYQ360TTJU | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.6 | 18.95 | 384000 | 3.35 | 250000 | 2.44 | R-410A | 28.5
7064675 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN | RXYQ120TYDN |  | RXYQ360TYDN | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.6 | 18.95 | 384000 | 3.35 | 250000 | 2.44 | R-410A | 28.5
7064676 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU | RXYQ168TTJU |  | RXYQ384TTJU | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.75 | 19.45 | 410000 | 3.28 | 274000 | 2.28 | R-410A | 30.3333
7064677 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN | RXYQ168TYDN |  | RXYQ384TYDN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.75 | 19.45 | 410000 | 3.28 | 274000 | 2.28 | R-410A | 30.3333
7064758 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ144TYDN |  |  | RXYQ264TYDN | Non-Ducted Indoor Units | 250000 | 10.9 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 20.8333
7064761 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ144TTJU |  |  | RXYQ264TTJU | Ducted Indoor Units | 250000 | 10.5 | 19.3 | 282000 | 3.35 | 186000 | 2.3 | R-410A | 20.8333
7064762 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ144TYDN |  |  | RXYQ264TYDN | Ducted Indoor Units | 250000 | 10.5 | 19.3 | 282000 | 3.35 | 186000 | 2.3 | R-410A | 20.8333
7064763 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ144TTJU |  |  | RXYQ264TTJU | Non-Ducted Indoor Units | 250000 | 10.9 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 20.8333
7064764 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ144TTJU |  |  | RXYQ264TTJU | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.7 | 19.8 | 282000 | 3.34 | 186000 | 2.36 | R-410A | 20.8333
7064765 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ144TYDN |  |  | RXYQ264TYDN | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.7 | 19.8 | 282000 | 3.34 | 186000 | 2.36 | R-410A | 20.8333
7089785 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM120FXVAFH | AM144FXVAFH |  | AM336FXVAFH | Non-Ducted Indoor Units | 320000 | 10.2 | 20.5 | 360000 | 3.27 | 234000 | 2.39 | R-410A | 26.6667
7089786 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM120FXVAJH | AM144FXVAJH |  | AM336FXVAJH | Non-Ducted Indoor Units | 320000 | 10.2 | 20.5 | 360000 | 3.27 | 234000 | 2.39 | R-410A | 26.6667
7133818 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM120FXVAFR | AM144FXVAFR |  | AM336FXVAFR | Non-Ducted Indoor Units | 320000 | 10.2 | 20.5 | 360000 | 3.27 | 234000 | 2.39 | R-410A | 26.6667
7133819 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM120FXVAJR | AM144FXVAJR |  | AM336FXVAJR | Non-Ducted Indoor Units | 320000 | 10.2 | 20.5 | 360000 | 3.27 | 234000 | 2.39 | R-410A | 26.6667
7490379 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P72TKMU-U | PUHY-P72TKMU-U |  | PUHY-P264TSKMU-U | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
7490381 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P72TKMU-U | PUHY-P72TKMU-U |  | PUHY-P264TSKMU-U | Ducted Indoor Units | 252000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 21
7490382 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P72YKMU-U | PUHY-P72YKMU-U |  | PUHY-P264YSKMU-U | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
7490384 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P72YKMU-U | PUHY-P72YKMU-U |  | PUHY-P264YSKMU-U | Ducted Indoor Units | 250000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 20.8333
7490385 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P96TKMU-U | PUHY-P72TKMU-U |  | PUHY-P288TSKMU-U | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
7490387 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P96TKMU-U | PUHY-P72TKMU-U |  | PUHY-P288TSKMU-U | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
7490388 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P96YKMU-U | PUHY-P72YKMU-U |  | PUHY-P288YSKMU-U | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
7490390 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P96YKMU-U | PUHY-P72YKMU-U |  | PUHY-P288YSKMU-U | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
7490392 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P72TKMU-U |  | PUHY-P312TSKMU-U | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
7490394 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P72TKMU-U |  | PUHY-P312TSKMU-U | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
7490395 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P72YKMU-U |  | PUHY-P312YSKMU-U | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
7490397 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P72YKMU-U |  | PUHY-P312YSKMU-U | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
7490399 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P96TKMU-U |  | PUHY-P336TSKMU-U | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
7490400 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P96TKMU-U |  | PUHY-P336TSKMU-U | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
7490402 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P96YKMU-U |  | PUHY-P336YSKMU-U | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
7490404 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P96YKMU-U |  | PUHY-P336YSKMU-U | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
7490406 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P120TKMU-U |  | PUHY-P360TSKMU-U | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
7490412 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P120YKMU-U |  | PUHY-P360YSKMU-U | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
7490454 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-U | PURY-P120TKMU-U |  |  | PURY-P264TSKMU-U | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
7490455 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-U | PURY-P120TKMU-U |  |  | PURY-P264TSKMU-U | Non-Ducted Indoor Units | 250000 | 11 | 18.4 | 280000 | 3.25 | 200000 | 2.08 | R-410A | 20.8333
7490457 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-U | PURY-P120YKMU-U |  |  | PURY-P264YSKMU-U | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
7490458 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-U | PURY-P120YKMU-U |  |  | PURY-P264YSKMU-U | Non-Ducted Indoor Units | 250000 | 11 | 18.4 | 280000 | 3.25 | 200000 | 2.08 | R-410A | 20.8333
7490459 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-U | PURY-P144TKMU-U |  |  | PURY-P288TSKMU-U | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
7490461 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-U | PURY-P144YKMU-U |  |  | PURY-P288YSKMU-U | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
7505375 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Non-Ducted Indoor Units | 274000 | 10.7 | 19 | 308000 | 3.35 | 208000 | 2.4 | R-410A | 22.8333
7505376 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Ducted Indoor Units | 274000 | 10.7 | 17.5 | 308000 | 3.4 | 208000 | 2.35 | R-410A | 22.8333
7505377 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Non-Ducted Indoor Units | 274000 | 10.7 | 19 | 308000 | 3.35 | 208000 | 2.4 | R-410A | 22.8333
7505378 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Ducted Indoor Units | 274000 | 10.7 | 17.5 | 308000 | 3.4 | 208000 | 2.35 | R-410A | 22.8333
7505399 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ96PBTJ |  | REYQ264PBTJ | Non-Ducted Indoor Units | 250000 | 10.8 | 18.7 | 282000 | 3.4 | 190000 | 2.4 | R-410A | 20.8333
7505400 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ96PBTJ |  | REYQ264PBTJ | Ducted Indoor Units | 250000 | 11.3 | 18.1 | 282000 | 3.3 | 190000 | 2.3 | R-410A | 20.8333
7505401 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ96PBYD |  | REYQ264PBYD | Non-Ducted Indoor Units | 250000 | 10.8 | 18.7 | 282000 | 3.4 | 190000 | 2.4 | R-410A | 20.8333
7505402 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ96PBYD |  | REYQ264PBYD | Ducted Indoor Units | 250000 | 11.3 | 18.1 | 282000 | 3.3 | 190000 | 2.3 | R-410A | 20.8333
7505419 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ96PBTJ |  | REYQ264PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.05 | 18.4 | 282000 | 3.35 | 190000 | 2.35 | R-410A | 20.8333
7505420 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ96PBYD |  | REYQ264PBYD | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.05 | 18.4 | 282000 | 3.35 | 190000 | 2.35 | R-410A | 20.8333
7505421 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.7 | 18.25 | 308000 | 3.37 | 208000 | 2.37 | R-410A | 22.8333
7505422 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.7 | 18.25 | 308000 | 3.37 | 208000 | 2.37 | R-410A | 22.8333
7505424 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ312PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.25 | 16.55 | 334000 | 3.28 | 224000 | 2.25 | R-410A | 24.6667
7505425 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ312PBYD | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.25 | 16.55 | 334000 | 3.28 | 224000 | 2.25 | R-410A | 24.6667
7628337 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ144TTJU |  |  | REYQ264TTJU | Ducted Indoor Units | 246000 | 10.5 | 19.6 | 276000 | 3.38 | 196000 | 2.26 | R-410A | 20.5
7628340 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ144TYDN |  |  | REYQ264TYDN | Ducted Indoor Units | 246000 | 10.5 | 19.6 | 276000 | 3.38 | 196000 | 2.26 | R-410A | 20.5
7628572 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ144TTJU |  |  | REYQ264TTJU | Non-Ducted Indoor Units | 246000 | 11.8 | 21.6 | 276000 | 3.55 | 196000 | 2.42 | R-410A | 20.5
7628574 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ144TYDN |  |  | REYQ264TYDN | Non-Ducted Indoor Units | 246000 | 11.8 | 21.6 | 276000 | 3.55 | 196000 | 2.42 | R-410A | 20.5
7628576 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ144TTJU |  |  | REYQ288TTJU | Non-Ducted Indoor Units | 268000 | 11.8 | 21.4 | 300000 | 3.51 | 210000 | 2.41 | R-410A | 22.3333
7628579 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ144TYDN |  |  | REYQ288TYDN | Non-Ducted Indoor Units | 268000 | 11.8 | 21.4 | 300000 | 3.51 | 210000 | 2.41 | R-410A | 22.3333
7628581 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ168TTJU |  |  | REYQ312TTJU | Non-Ducted Indoor Units | 290000 | 11.3 | 20.2 | 326000 | 3.56 | 230000 | 2.41 | R-410A | 24.1667
7628585 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU | REYQ168TTJU |  |  | REYQ336TTJU | Non-Ducted Indoor Units | 312000 | 10.7 | 19 | 352000 | 3.52 | 262000 | 2.18 | R-410A | 26
7628588 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN | REYQ168TYDN |  |  | REYQ336TYDN | Non-Ducted Indoor Units | 312000 | 10.7 | 19 | 352000 | 3.52 | 262000 | 2.18 | R-410A | 26
7628589 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU | REYQ120TTJU |  | REYQ360TTJU | Non-Ducted Indoor Units | 334000 | 10.8 | 19.6 | 376000 | 3.51 | 264000 | 2.42 | R-410A | 27.8333
7628592 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN | REYQ120TYDN |  | REYQ360TYDN | Non-Ducted Indoor Units | 334000 | 10.8 | 19.6 | 376000 | 3.51 | 264000 | 2.42 | R-410A | 27.8333
7628644 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ144TTJU |  |  | REYQ288TTJU | Ducted Indoor Units | 268000 | 10.9 | 19.6 | 300000 | 3.26 | 210000 | 2.24 | R-410A | 22.3333
7628647 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ144TYDN |  |  | REYQ288TYDN | Ducted Indoor Units | 268000 | 10.9 | 19.6 | 300000 | 3.26 | 210000 | 2.24 | R-410A | 22.3333
7628657 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU | REYQ120TTJU |  | REYQ360TTJU | Ducted Indoor Units | 334000 | 11 | 20.1 | 376000 | 3.31 | 264000 | 2.17 | R-410A | 27.8333
7628659 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN | REYQ120TYDN |  | REYQ360TYDN | Ducted Indoor Units | 334000 | 11 | 20.1 | 376000 | 3.31 | 264000 | 2.17 | R-410A | 27.8333
7629610 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ144TTJU |  |  | REYQ264TTJU | Mixed Ducted and Non-Ducted Indoor Units | 246000 | 11.15 | 20.6 | 276000 | 3.46 | 196000 | 2.34 | R-410A | 20.5
7629612 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ144TYDN |  |  | REYQ264TYDN | Mixed Ducted and Non-Ducted Indoor Units | 246000 | 11.15 | 20.6 | 276000 | 3.46 | 196000 | 2.34 | R-410A | 20.5
7629614 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ144TTJU |  |  | REYQ288TTJU | Mixed Ducted and Non-Ducted Indoor Units | 268000 | 11.35 | 20.5 | 300000 | 3.38 | 210000 | 2.32 | R-410A | 22.3333
7629617 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ144TYDN |  |  | REYQ288TYDN | Mixed Ducted and Non-Ducted Indoor Units | 268000 | 11.35 | 20.5 | 300000 | 3.38 | 210000 | 2.32 | R-410A | 22.3333
7629619 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ168TTJU |  |  | REYQ312TTJU | Mixed Ducted and Non-Ducted Indoor Units | 290000 | 10.95 | 19.6 | 326000 | 3.39 | 230000 | 2.32 | R-410A | 24.1667
7629622 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU | REYQ168TTJU |  |  | REYQ336TTJU | Mixed Ducted and Non-Ducted Indoor Units | 312000 | 10.35 | 18.6 | 352000 | 3.36 | 262000 | 2.12 | R-410A | 26
7629623 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN | REYQ168TYDN |  |  | REYQ336TYDN | Mixed Ducted and Non-Ducted Indoor Units | 312000 | 10.35 | 18.6 | 352000 | 3.36 | 262000 | 2.12 | R-410A | 26
7629626 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU | REYQ120TTJU |  | REYQ360TTJU | Mixed Ducted and Non-Ducted Indoor Units | 334000 | 10.9 | 19.85 | 376000 | 3.41 | 264000 | 2.29 | R-410A | 27.8333
7629628 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN | REYQ120TYDN |  | REYQ360TYDN | Mixed Ducted and Non-Ducted Indoor Units | 334000 | 10.9 | 19.85 | 376000 | 3.41 | 264000 | 2.29 | R-410A | 27.8333
7783690 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ168TYDN |  |  | REYQ312TYDN | Non-Ducted Indoor Units | 290000 | 11.3 | 20.2 | 326000 | 3.56 | 230000 | 2.41 | R-410A | 24.1667
7783693 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ168TYDN |  |  | REYQ312TYDN | Mixed Ducted and Non-Ducted Indoor Units | 290000 | 10.95 | 19.6 | 326000 | 3.39 | 230000 | 2.32 | R-410A | 24.1667
7850835 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
7850837 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
7850855 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
7850857 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
7987142 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987143 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987144 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987145 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987146 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987147 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987148 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987149 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987151 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987162 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987163 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987164 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987165 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987166 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987167 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987168 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987169 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987171 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987188 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987189 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987191 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S |  | TVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987194 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987195 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987197 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987208 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987209 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987211 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S |  | TVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987214 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987215 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987217 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987234 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987235 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987236 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987237 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987238 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987239 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987240 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987241 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987243 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987254 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987255 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987256 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987257 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987258 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987259 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987260 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987261 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987263 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987280 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987281 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987283 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S |  | HVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987286 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987287 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987289 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987300 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987301 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987303 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S |  | HVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987306 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987307 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987309 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987326 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987327 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987328 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987329 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987330 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987331 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987332 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987333 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987335 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987346 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987347 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987348 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987349 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987350 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987351 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987352 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987353 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987355 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987372 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987373 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987375 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S |  | YVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987378 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987379 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987381 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987392 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987393 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987395 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S |  | YVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987398 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987399 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987401 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7990699 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990700 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990701 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990702 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990703 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990712 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990713 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990714 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990715 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990716 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990725 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990726 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S |  | TVAHP288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990728 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990730 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990739 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990740 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S |  | TVAHR288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990742 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990743 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990752 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990753 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990754 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990755 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990756 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990766 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990767 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990768 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990769 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990770 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990779 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990780 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S |  | HVAHP288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990782 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990783 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990792 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990793 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S |  | HVAHR288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990796 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990797 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990806 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990807 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990808 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990809 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990819 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990820 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990821 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990822 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990823 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990832 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990833 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S |  | YVAHP288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990835 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990836 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990845 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990846 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S |  | YVAHR288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990848 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990849 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
8033349 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P72TKMU-* | PUHY-P72TKMU-* |  | PUHY-P264TSKMU-* | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
8033350 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P72TKMU-* | PUHY-P72TKMU-* |  | PUHY-P264TSKMU-* | Ducted Indoor Units | 252000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 21
8033351 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P72YKMU-* | PUHY-P72YKMU-* |  | PUHY-P264YSKMU-* | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
8033352 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P72YKMU-* | PUHY-P72YKMU-* |  | PUHY-P264YSKMU-* | Ducted Indoor Units | 250000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 20.8333
8033353 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P96TKMU-* | PUHY-P72TKMU-* |  | PUHY-P288TSKMU-* | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
8033354 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P96TKMU-* | PUHY-P72TKMU-* |  | PUHY-P288TSKMU-* | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
8033355 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P96YKMU-* | PUHY-P72YKMU-* |  | PUHY-P288YSKMU-* | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
8033356 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P96YKMU-* | PUHY-P72YKMU-* |  | PUHY-P288YSKMU-* | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
8033357 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P72TKMU-* |  | PUHY-P312TSKMU-* | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
8033358 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P72TKMU-* |  | PUHY-P312TSKMU-* | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
8033359 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P72YKMU-* |  | PUHY-P312YSKMU-* | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
8033360 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P72YKMU-* |  | PUHY-P312YSKMU-* | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
8033361 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P96TKMU-* |  | PUHY-P336TSKMU-* | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
8033362 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P96TKMU-* |  | PUHY-P336TSKMU-* | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
8033363 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P96YKMU-* |  | PUHY-P336YSKMU-* | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
8033364 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P96YKMU-* |  | PUHY-P336YSKMU-* | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
8033365 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P120TKMU-* |  | PUHY-P360TSKMU-* | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
8033368 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P120YKMU-* |  | PUHY-P360YSKMU-* | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
8033387 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-* | PURY-P120TKMU-* |  |  | PURY-P264TSKMU-* | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
8033389 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-* | PURY-P120YKMU-* |  |  | PURY-P264YSKMU-* | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
8033391 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-* | PURY-P144TKMU-* |  |  | PURY-P288TSKMU-* | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
8033393 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-* | PURY-P144YKMU-* |  |  | PURY-P288YSKMU-* | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
8175498 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
8175499 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
8175500 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
8175501 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
8175502 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
8175503 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Non-Ducted Indoor Units | 296000 | 13.4 | 23.4 | 334000 | 3.66 | 236000 | 2.22 | R-410A | 24.6667
8175504 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
8175505 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Non-Ducted Indoor Units | 320000 | 13.2 | 23.4 | 360000 | 3.52 | 268000 | 2.13 | R-410A | 26.6667
8175506 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  | PUHY-P360YSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
8175528 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
8175529 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
8175530 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
8175531 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
8175532 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
8175533 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Non-Ducted Indoor Units | 296000 | 13.4 | 23.4 | 334000 | 3.66 | 236000 | 2.22 | R-410A | 24.6667
8175534 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
8175535 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Non-Ducted Indoor Units | 320000 | 13.2 | 23.4 | 360000 | 3.52 | 268000 | 2.13 | R-410A | 26.6667
8175536 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  | PUHY-P360TSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
4677081 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ72PBTJ | RXYQ120PBTJ |  | RXYQ264PBTJ | Non-Ducted Indoor Units | 250000 | 11.3 | 20.8 | 282000 | 3.5 | 184000 | 2.45 | R-410A | 20.8333
4677082 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ72PBTJ | RXYQ120PBTJ |  | RXYQ264PBTJ | Ducted Indoor Units | 250000 | 11.7 | 19.1 | 282000 | 3.5 | 184000 | 2.3 | R-410A | 20.8333
4677083 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ72PBTJ | RXYQ120PBTJ |  | RXYQ264PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.5 | 19.95 | 282000 | 3.5 | 184000 | 2.37 | R-410A | 20.8333
4677084 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ | RXYQ120PBTJ |  | RXYQ288PBTJ | Non-Ducted Indoor Units | 274000 | 11.5 | 19.6 | 308000 | 3.5 | 200000 | 2.45 | R-410A | 22.8333
4677085 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ | RXYQ120PBTJ |  | RXYQ288PBTJ | Ducted Indoor Units | 274000 | 10.5 | 18.8 | 308000 | 3.45 | 200000 | 2.45 | R-410A | 22.8333
4677086 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ | RXYQ120PBTJ |  | RXYQ288PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11 | 19.2 | 308000 | 3.47 | 200000 | 2.45 | R-410A | 22.8333
4677087 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ | RXYQ120PBTJ |  | RXYQ312PBTJ | Non-Ducted Indoor Units | 296000 | 10.7 | 18.2 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677088 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ | RXYQ120PBTJ |  | RXYQ312PBTJ | Ducted Indoor Units | 296000 | 11.5 | 17 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677089 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ | RXYQ120PBTJ |  | RXYQ312PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.1 | 17.6 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677114 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD | RXYQ120PBYD |  | RXYQ264PBYD | Non-Ducted Indoor Units | 250000 | 11.3 | 20.8 | 282000 | 3.5 | 184000 | 2.45 | R-410A | 20.8333
4677115 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD | RXYQ120PBYD |  | RXYQ264PBYD | Ducted Indoor Units | 250000 | 11.7 | 19.1 | 282000 | 3.5 | 184000 | 2.3 | R-410A | 20.8333
4677116 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD | RXYQ120PBYD |  | RXYQ264PBYD | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.5 | 19.95 | 282000 | 3.5 | 184000 | 2.37 | R-410A | 20.8333
4677117 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD | RXYQ120PBYD |  | RXYQ288PBYD | Non-Ducted Indoor Units | 274000 | 11.5 | 19.6 | 308000 | 3.5 | 200000 | 2.45 | R-410A | 22.8333
4677118 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD | RXYQ120PBYD |  | RXYQ288PBYD | Ducted Indoor Units | 274000 | 10.5 | 18.8 | 308000 | 3.45 | 200000 | 2.45 | R-410A | 22.8333
4677119 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD | RXYQ120PBYD |  | RXYQ288PBYD | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11 | 19.2 | 308000 | 3.47 | 200000 | 2.45 | R-410A | 22.8333
4677120 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD | RXYQ120PBYD |  | RXYQ312PBYD | Non-Ducted Indoor Units | 296000 | 10.7 | 18.2 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677121 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD | RXYQ120PBYD |  | RXYQ312PBYD | Ducted Indoor Units | 296000 | 11.5 | 17 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677122 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD | RXYQ120PBYD |  | RXYQ312PBYD | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.1 | 17.6 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677141 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ72PBTJ | REMQ120PBTJ |  | REYQ264PBTJ | Non-Ducted Indoor Units | 250000 | 10.8 | 18.7 | 282000 | 3.4 | 190000 | 2.4 | R-410A | 20.8333
4677142 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ72PBTJ | REMQ120PBTJ |  | REYQ264PBTJ | Ducted Indoor Units | 250000 | 11.3 | 18.1 | 282000 | 3.3 | 190000 | 2.3 | R-410A | 20.8333
4677143 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ72PBTJ | REMQ120PBTJ |  | REYQ264PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.05 | 18.4 | 282000 | 3.35 | 190000 | 2.35 | R-410A | 20.8333
4677144 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Non-Ducted Indoor Units | 274000 | 10.7 | 19 | 308000 | 3.35 | 208000 | 2.4 | R-410A | 22.8333
4677145 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Ducted Indoor Units | 274000 | 10.7 | 17.5 | 308000 | 3.4 | 208000 | 2.35 | R-410A | 22.8333
4677146 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.7 | 18.25 | 308000 | 3.37 | 208000 | 2.37 | R-410A | 22.8333
4677149 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ312PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.25 | 16.55 | 334000 | 3.28 | 224000 | 2.25 | R-410A | 24.6667
4677165 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD | REMQ120PBYD |  | REYQ264PBYD | Non-Ducted Indoor Units | 250000 | 10.8 | 18.7 | 282000 | 3.4 | 190000 | 2.4 | R-410A | 20.8333
4677166 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD | REMQ120PBYD |  | REYQ264PBYD | Ducted Indoor Units | 250000 | 11.3 | 18.1 | 282000 | 3.3 | 190000 | 2.3 | R-410A | 20.8333
4677167 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD | REMQ120PBYD |  | REYQ264PBYD | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.05 | 18.4 | 282000 | 3.35 | 190000 | 2.35 | R-410A | 20.8333
4677168 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Non-Ducted Indoor Units | 274000 | 10.7 | 19 | 308000 | 3.35 | 208000 | 2.4 | R-410A | 22.8333
4677169 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Ducted Indoor Units | 274000 | 10.7 | 17.5 | 308000 | 3.4 | 208000 | 2.35 | R-410A | 22.8333
4677170 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.7 | 18.25 | 308000 | 3.37 | 208000 | 2.37 | R-410A | 22.8333
4677173 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ312PBYD | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.25 | 16.55 | 334000 | 3.28 | 224000 | 2.25 | R-410A | 24.6667
4679558 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BT3 | ARUB144BT3 |  |  | ARUB264BT3 | Ducted Indoor Units | 250000 | 11.2 | 17 | 282000 | 3.28 | 184000 | 2.35 | R-410A | 20.8333
4679559 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BT3 | ARUB144BT3 |  |  | ARUB264BT3 | Non-Ducted Indoor Units | 250000 | 11.6 | 18.1 | 282000 | 3.51 | 184000 | 2.45 | R-410A | 20.8333
4679560 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DT3 | ARUB144DT3 |  |  | ARUB264DT3 | Ducted Indoor Units | 250000 | 11.2 | 17 | 282000 | 3.28 | 184000 | 2.35 | R-410A | 20.8333
4679561 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DT3 | ARUB144DT3 |  |  | ARUB264DT3 | Non-Ducted Indoor Units | 250000 | 11.6 | 18.1 | 282000 | 3.51 | 184000 | 2.45 | R-410A | 20.8333
4679562 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BT3 | ARUB144BT3 |  |  | ARUB288BT3 | Ducted Indoor Units | 274000 | 10.9 | 17 | 308000 | 3.26 | 200000 | 2.34 | R-410A | 22.8333
4679563 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BT3 | ARUB144BT3 |  |  | ARUB288BT3 | Non-Ducted Indoor Units | 274000 | 11.5 | 17.8 | 308000 | 3.48 | 200000 | 2.4 | R-410A | 22.8333
4679564 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DT3 | ARUB144DT3 |  |  | ARUB288DT3 | Ducted Indoor Units | 274000 | 10.9 | 17 | 308000 | 3.26 | 200000 | 2.34 | R-410A | 22.8333
4679565 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DT3 | ARUB144DT3 |  |  | ARUB288DT3 | Non-Ducted Indoor Units | 274000 | 11.5 | 17.8 | 308000 | 3.48 | 200000 | 2.4 | R-410A | 22.8333
4679566 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB096BT3 | ARUB144BT3 |  | ARUB312BT3 | Ducted Indoor Units | 296000 | 11.3 | 18 | 334000 | 3.25 | 222000 | 2.36 | R-410A | 24.6667
4679567 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB096BT3 | ARUB144BT3 |  | ARUB312BT3 | Non-Ducted Indoor Units | 296000 | 11.8 | 18.2 | 334000 | 3.46 | 222000 | 2.36 | R-410A | 24.6667
4679568 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB096DT3 | ARUB144DT3 |  | ARUB312DT3 | Ducted Indoor Units | 296000 | 11.3 | 18 | 334000 | 3.25 | 222000 | 2.36 | R-410A | 24.6667
4679569 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB096DT3 | ARUB144DT3 |  | ARUB312DT3 | Non-Ducted Indoor Units | 296000 | 11.8 | 18.2 | 334000 | 3.46 | 222000 | 2.36 | R-410A | 24.6667
4679602 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BT3 | ARUN144BT3 |  |  | ARUN264BT3 | Ducted Indoor Units | 250000 | 11.2 | 17 | 282000 | 3.28 | 184000 | 2.35 | R-410A | 20.8333
4679603 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BT3 | ARUN144BT3 |  |  | ARUN264BT3 | Non-Ducted Indoor Units | 250000 | 11.6 | 18.1 | 282000 | 3.51 | 184000 | 2.45 | R-410A | 20.8333
4679604 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DT3 | ARUN144DT3 |  |  | ARUN264DT3 | Ducted Indoor Units | 250000 | 11.2 | 17 | 282000 | 3.28 | 184000 | 2.35 | R-410A | 20.8333
4679605 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DT3 | ARUN144DT3 |  |  | ARUN264DT3 | Non-Ducted Indoor Units | 250000 | 11.6 | 18.1 | 282000 | 3.51 | 184000 | 2.45 | R-410A | 20.8333
4679606 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BT3 | ARUN144BT3 |  |  | ARUN288BT3 | Ducted Indoor Units | 274000 | 10.9 | 17 | 308000 | 3.26 | 200000 | 2.34 | R-410A | 22.8333
4679607 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BT3 | ARUN144BT3 |  |  | ARUN288BT3 | Non-Ducted Indoor Units | 274000 | 11.5 | 17.8 | 308000 | 3.48 | 200000 | 2.4 | R-410A | 22.8333
4679608 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DT3 | ARUN144DT3 |  |  | ARUN288DT3 | Ducted Indoor Units | 274000 | 10.9 | 17 | 308000 | 3.26 | 200000 | 2.34 | R-410A | 22.8333
4679609 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DT3 | ARUN144DT3 |  |  | ARUN288DT3 | Non-Ducted Indoor Units | 274000 | 11.8 | 18.2 | 308000 | 3.46 | 200000 | 2.4 | R-410A | 22.8333
4679610 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN096BT3 | ARUN144BT3 |  | ARUN312BT3 | Ducted Indoor Units | 296000 | 11.3 | 18 | 334000 | 3.25 | 222000 | 2.36 | R-410A | 24.6667
4679611 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN096BT3 | ARUN144BT3 |  | ARUN312BT3 | Non-Ducted Indoor Units | 296000 | 11.5 | 18 | 334000 | 3.44 | 222000 | 2.36 | R-410A | 24.6667
4679612 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN096DT3 | ARUN144DT3 |  | ARUN312DT3 | Ducted Indoor Units | 296000 | 11.3 | 18 | 334000 | 3.25 | 222000 | 2.36 | R-410A | 24.6667
4679613 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN096DT3 | ARUN144DT3 |  | ARUN312DT3 | Non-Ducted Indoor Units | 296000 | 11.8 | 18.2 | 334000 | 3.46 | 222000 | 2.36 | R-410A | 24.6667
5358546 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Ducted Indoor Units | 250000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 20.8333
5358547 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
5358548 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 12.5 | 18.85 | 280000 | 3.64 | 200000 | 2.34 | R-410A | 20.8333
5358549 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
5358550 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
5358551 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 12.4 | 18.85 | 308000 | 3.63 | 216000 | 2.37 | R-410A | 22.8333
5358552 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
5358553 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
5358554 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 12.1 | 18.25 | 334000 | 3.49 | 236000 | 2.32 | R-410A | 24.6667
5358555 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
5358556 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
5358557 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.95 | 18 | 360000 | 3.43 | 268000 | 2.25 | R-410A | 26.6667
5358558 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  | PUHY-P360YSKMU-A | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
5358560 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  | PUHY-P360YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.75 | 17.5 | 386000 | 3.3 | 284000 | 2.18 | R-410A | 28.5
5358585 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Ducted Indoor Units | 252000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 21
5358586 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
5358587 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12.5 | 18.85 | 280000 | 3.64 | 200000 | 2.34 | R-410A | 21
5358588 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
5358589 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
5358590 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 12.4 | 18.85 | 308000 | 3.63 | 216000 | 2.37 | R-410A | 22.8333
5358591 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
5358592 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
5358593 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 12.1 | 18.25 | 334000 | 3.49 | 236000 | 2.32 | R-410A | 24.6667
5358594 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
5358595 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
5358596 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.95 | 18 | 360000 | 3.43 | 268000 | 2.25 | R-410A | 26.6667
5358597 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  | PUHY-P360TSKMU-A | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
5358599 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  | PUHY-P360TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.75 | 17.5 | 386000 | 3.3 | 284000 | 2.18 | R-410A | 28.5
5358627 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A | PURY-P120YKMU-A |  |  | PURY-P264YSKMU-A | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
5358629 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A | PURY-P120YKMU-A |  |  | PURY-P264YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11 | 18.05 | 280000 | 3.31 | 200000 | 2.21 | R-410A | 20.8333
5358630 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A | PURY-P144YKMU-A |  |  | PURY-P288YSKMU-A | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
5358632 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A | PURY-P144YKMU-A |  |  | PURY-P288YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.25 | 18.1 | 304000 | 3.31 | 216000 | 2.2 | R-410A | 22.8333
5358654 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A | PURY-P120TKMU-A |  |  | PURY-P264TSKMU-A | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
5358656 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A | PURY-P120TKMU-A |  |  | PURY-P264TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11 | 18.05 | 280000 | 3.31 | 200000 | 2.21 | R-410A | 20.8333
5358657 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A | PURY-P144TKMU-A |  |  | PURY-P288TSKMU-A | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
5358659 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A | PURY-P144TKMU-A |  |  | PURY-P288TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.25 | 18.1 | 304000 | 3.31 | 216000 | 2.2 | R-410A | 22.8333
5733077 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH | AM144FXVAFH |  |  | AM264FXVAFH | Ducted Indoor Units | 252000 | 10.1 | 18.6 | 282000 | 3.25 | 184000 | 2.26 | R-410A | 21
5733078 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH | AM144FXVAJH |  |  | AM264FXVAJH | Ducted Indoor Units | 252000 | 10.1 | 18.5 | 282000 | 3.25 | 184000 | 2.26 | R-410A | 21
5733079 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH | AM144FXVAFH |  |  | AM264FXVAFH | Non-Ducted Indoor Units | 252000 | 10.5 | 21.5 | 282000 | 3.45 | 184000 | 2.41 | R-410A | 21
5733080 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH | AM144FXVAJH |  |  | AM264FXVAJH | Non-Ducted Indoor Units | 252000 | 10.1 | 21.5 | 282000 | 3.45 | 184000 | 2.41 | R-410A | 21
5733081 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR | AM144FXVAFR |  |  | AM264FXVAFR | Ducted Indoor Units | 252000 | 10.1 | 18.6 | 282000 | 3.25 | 184000 | 2.26 | R-410A | 21
5733082 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR | AM144FXVAJR |  |  | AM264FXVAJR | Ducted Indoor Units | 252000 | 10.1 | 18.5 | 282000 | 3.25 | 184000 | 2.26 | R-410A | 21
5733083 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR | AM144FXVAFR |  |  | AM264FXVAFR | Non-Ducted Indoor Units | 252000 | 10.5 | 21.5 | 282000 | 3.45 | 184000 | 2.41 | R-410A | 21
5733084 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR | AM144FXVAJR |  |  | AM264FXVAJR | Non-Ducted Indoor Units | 252000 | 10.1 | 21.5 | 282000 | 3.45 | 184000 | 2.41 | R-410A | 21
5733085 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288FXVAFH | Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.25 | 200000 | 2.12 | R-410A | 23
5733086 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288FXVAJH | Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.25 | 200000 | 2.12 | R-410A | 23
5733088 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288FXVAJH | Non-Ducted Indoor Units | 276000 | 9.9 | 21 | 308000 | 3.26 | 200000 | 2.29 | R-410A | 23
5733089 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288FXVAFR | Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.25 | 200000 | 2.12 | R-410A | 23
5733090 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288FXVAJR | Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.25 | 200000 | 2.12 | R-410A | 23
5733092 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288FXVAJR | Non-Ducted Indoor Units | 276000 | 9.9 | 21 | 308000 | 3.26 | 200000 | 2.29 | R-410A | 23
5733095 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM096FXVAFH | AM144FXVAFH |  | AM312FXVAFH | Non-Ducted Indoor Units | 298000 | 10.5 | 21.2 | 334000 | 3.38 | 218000 | 2.54 | R-410A | 24.8333
5733096 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM096FXVAJH | AM144FXVAJH |  | AM312FXVAJH | Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.38 | 218000 | 2.51 | R-410A | 24.8333
5733099 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM096FXVAFR | AM144FXVAFR |  | AM312FXVAFR | Non-Ducted Indoor Units | 298000 | 10.5 | 21.2 | 334000 | 3.38 | 218000 | 2.54 | R-410A | 24.8333
5733100 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM096FXVAJR | AM144FXVAJR |  | AM312FXVAJR | Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.38 | 218000 | 2.51 | R-410A | 24.8333
6495707 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN096DTE4 | ARUN144DTE4 |  | ARUN312DTE4 | Ducted Indoor Units | 296000 | 11.3 | 19.5 | 334000 | 3.3 | 222000 | 2.37 | R-410A | 24.6667
6495708 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN096BTE4 | ARUN144BTE4 |  | ARUN312BTE4 | Ducted Indoor Units | 296000 | 11.3 | 19.5 | 334000 | 3.3 | 222000 | 2.37 | R-410A | 24.6667
6495709 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB096DTE4 | ARUB144DTE4 |  | ARUB312DTE4 | Ducted Indoor Units | 296000 | 11.3 | 19.5 | 334000 | 3.3 | 222000 | 2.37 | R-410A | 24.6667
6495710 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB096BTE4 | ARUB144BTE4 |  | ARUB312BTE4 | Ducted Indoor Units | 296000 | 11.3 | 19.5 | 334000 | 3.3 | 222000 | 2.37 | R-410A | 24.6667
6495711 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB096BTE4 | ARUB144BTE4 |  | ARUB312BTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.55 | 222000 | 2.4 | R-410A | 24.6667
6495712 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB096DTE4 | ARUB144DTE4 |  | ARUB312DTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.55 | 222000 | 2.4 | R-410A | 24.6667
6495713 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN096DTE4 | ARUN144DTE4 |  | ARUN312DTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.55 | 222000 | 2.4 | R-410A | 24.6667
6495714 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN096BTE4 | ARUN144DTE4 |  | ARUN312BTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.55 | 222000 | 2.4 | R-410A | 24.6667
6495715 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN096DTE4 | ARUN144DTE4 |  | ARUN336DTE4 | Non-Ducted Indoor Units | 320000 | 10.8 | 20 | 360000 | 3.51 | 234000 | 2.42 | R-410A | 26.6667
6495716 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN096BTE4 | ARUN144BTE4 |  | ARUN336BTE4 | Non-Ducted Indoor Units | 320000 | 10.8 | 20 | 360000 | 3.51 | 234000 | 2.42 | R-410A | 26.6667
6495717 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB096BTE4 | ARUB144BTE4 |  | ARUB336BTE4 | Non-Ducted Indoor Units | 320000 | 10.8 | 20 | 360000 | 3.51 | 234000 | 2.42 | R-410A | 26.6667
6495718 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB096DTE4 | ARUB144DTE4 |  | ARUB336DTE4 | Non-Ducted Indoor Units | 320000 | 10.8 | 20 | 360000 | 3.51 | 234000 | 2.42 | R-410A | 26.6667
6495719 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB096DTE4 | ARUB144DTE4 |  | ARUB336DTE4 | Ducted Indoor Units | 320000 | 11.1 | 19 | 360000 | 3.27 | 234000 | 2.38 | R-410A | 26.6667
6495720 | 1/1/2027 | LG | HMSR-A-CB | ARUN096BTE4 | ARUB096BTE4 | ARUB144BTE4 |  | ARUB336BTE4 | Ducted Indoor Units | 320000 | 11.1 | 19 | 360000 | 3.27 | 234000 | 2.38 | R-410A | 26.6667
6495721 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN096BTE4 | ARUN144BTE4 |  | ARUN336BTE4 | Ducted Indoor Units | 320000 | 11.1 | 19 | 360000 | 3.27 | 234000 | 2.38 | R-410A | 26.6667
6495722 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN096DTE4 | ARUN144DTE4 |  | ARUN336DTE4 | Ducted Indoor Units | 320000 | 11.1 | 19 | 360000 | 3.27 | 234000 | 2.38 | R-410A | 26.6667
6687556 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
6687558 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
201874094 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
201874096 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
201874098 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
201874100 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
201874157 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
201874161 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
201874168 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
201874170 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
201874786 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Non-Ducted Indoor Units | 282000 | 13.4 | 22.1 | 316000 | 3.66 | 236000 | 2.22 | R-410A | 23.5
201874787 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Non-Ducted Indoor Units | 304000 | 13.2 | 20.9 | 342000 | 3.52 | 268000 | 2.13 | R-410A | 25.3333
201874789 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Non-Ducted Indoor Units | 282000 | 13.4 | 22.1 | 316000 | 3.66 | 236000 | 2.22 | R-410A | 23.5
201874790 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Non-Ducted Indoor Units | 304000 | 13.2 | 20.9 | 342000 | 3.52 | 268000 | 2.13 | R-410A | 25.3333
201978080 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
201978081 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
201978082 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
201978083 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
201978084 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
201978085 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
201978086 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
201978087 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
201981536 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
201981537 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
201981538 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  | PUHY-P360YSKMU-A | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
201982846 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
201982847 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
201982848 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  | PUHY-P360TSKMU-A | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
201992870 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ144TAYC* |  | RXYQ384TAYC* | Non-Ducted Indoor Units | 352000 | 9.6 | 18.3 | 398000 | 3.26 | 280000 | 2.24 | R-410A | 29.3333
201992876 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ144TAYC* |  |  | RXYQ264TAYC* | Non-Ducted Indoor Units | 252000 | 10.8 | 20.1 | 282000 | 3.71 | 200000 | 2.27 | R-410A | 21
201992877 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* | RXYQ144TAYC* |  |  | RXYQ288TAYC* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.1 | 306000 | 3.48 | 216000 | 2.24 | R-410A | 22.8333
202016263 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168TAYC* | RXYQ168TAYC* |  |  | RXYQ336TAYC* | Non-Ducted Indoor Units | 308000 | 9.8 | 18.9 | 338000 | 3.6 | 228000 | 2.11 | R-410A | 25.6667
202016265 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ120TAYC* |  | RXYQ360TAYC* | Non-Ducted Indoor Units | 342000 | 10.5 | 19.1 | 384000 | 3.62 | 270000 | 2.28 | R-410A | 28.5
202022807 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ144TAYC* |  |  | RXYQ264TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.2 | 18.3 | 282000 | 3.47 | 200000 | 2.18 | R-410A | 21
202022808 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* | RXYQ144TAYC* |  |  | RXYQ288TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 18.6 | 306000 | 3.34 | 216000 | 2.16 | R-410A | 22.8333
202022810 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168TAYC* | RXYQ168TAYC* |  |  | RXYQ336TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 308000 | 9.65 | 17.8 | 338000 | 3.4 | 228000 | 2.08 | R-410A | 25.6667
202022811 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ120TAYC* |  | RXYQ360TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.1 | 384000 | 3.42 | 270000 | 2.19 | R-410A | 28.5
202095846 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095847 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202095848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202095850 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095851 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202095852 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202606862 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606863 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606864 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606865 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606866 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606867 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606868 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606869 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606870 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606871 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606872 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606873 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606874 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606875 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606876 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606877 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S |  | TVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606878 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S |  | HVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606879 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S |  | YVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606880 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606881 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606882 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606883 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S |  | TVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606884 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S |  | HVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606885 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S |  | YVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202607634 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607635 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607636 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607637 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607638 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607639 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607640 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607641 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607642 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607643 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607644 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607645 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607646 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607647 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607648 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607649 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607650 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607651 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607652 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607653 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607654 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607655 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607656 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607657 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607658 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607659 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607660 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607661 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607662 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607663 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607664 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607665 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607666 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607667 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607668 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607669 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607670 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607671 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607672 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607676 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607677 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607678 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607682 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607683 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607684 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607685 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607686 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607687 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607688 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607689 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607690 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607691 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607693 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607694 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607695 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607696 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607697 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607698 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607699 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607712 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607713 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607714 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607718 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607719 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607720 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607724 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607725 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607726 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607730 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607731 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607732 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607736 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607737 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607738 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607739 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607740 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607741 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607742 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607743 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607744 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607745 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607746 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607747 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607760 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607761 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607762 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607763 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607764 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607765 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607766 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607767 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607768 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607769 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607770 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607771 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607772 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607773 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607774 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607775 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607776 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607777 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607778 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607779 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607780 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607781 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607782 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607783 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607784 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607785 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607786 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607787 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607788 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607789 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607790 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607791 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607792 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607793 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607794 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607795 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607796 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607797 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607798 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607799 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607800 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607802 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607803 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607804 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607805 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607806 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607807 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607808 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607809 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607811 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607812 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607813 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607814 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607815 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607816 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607817 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607818 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607819 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607832 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607833 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607834 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607835 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607836 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607837 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607838 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607839 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607840 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607841 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607842 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607843 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607856 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP120B31S |  | TVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607857 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP120B31S |  | HVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607858 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP120B31S |  | YVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607859 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP120B41S |  | TVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607860 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP120B41S |  | HVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607861 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP120B41S |  | YVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607862 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR120B31S |  | TVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607863 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR120B31S |  | HVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607864 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR120B31S |  | YVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607865 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR120B41S |  | TVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607866 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR120B41S |  | HVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607867 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR120B41S |  | YVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202608148 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608149 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608150 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608151 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608152 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608153 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608154 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608155 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608156 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608157 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608158 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608159 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608172 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608173 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608174 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608175 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608176 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608177 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608178 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608179 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608180 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608181 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608182 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608183 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608184 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608185 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608186 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608187 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608188 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608189 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608202 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608203 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608204 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608205 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608206 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608207 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608208 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608209 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608210 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608211 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608212 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608213 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608238 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608239 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608240 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608241 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608242 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608243 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608244 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608245 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608246 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608247 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608248 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608249 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
203906821 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906822 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906823 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906824 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906825 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906826 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906827 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906828 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906829 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906830 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906831 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906832 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906833 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906835 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906836 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906837 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906838 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906839 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906840 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906841 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906842 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906843 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906844 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906845 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906846 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906847 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906848 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906849 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906850 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906851 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906852 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906854 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906855 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906856 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906857 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906858 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906859 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906860 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906861 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906862 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906863 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906864 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906878 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906879 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906880 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906881 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906882 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906883 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906884 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906885 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906887 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906888 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906889 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906890 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906903 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906904 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906905 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906906 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906907 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906909 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906910 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906911 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906912 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906913 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906914 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906915 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203994166 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994167 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994168 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994169 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994170 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994171 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994694 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994695 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994696 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994697 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994699 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
204268364 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268371 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S | TVAHR120B52S |  | TVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268384 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268389 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S | HVAHR120B52S |  | HVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268400 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268405 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S | YVAHR120B52S |  | YVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268416 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268417 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S |  |  | TVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268418 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S | TVAHR144B52S |  |  | TVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268419 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268423 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S | TVAHR144B52S |  | TVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268432 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268433 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S |  |  | HVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268434 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S | HVAHR144B52S |  |  | HVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268435 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268439 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S | HVAHR144B52S |  | HVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268456 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268458 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S |  |  | YVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268460 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S | YVAHR144B52S |  |  | YVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268462 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268470 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S | YVAHR144B52S |  | YVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268481 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268489 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S | TVAHP120B52S |  | TVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268513 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268525 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S | HVAHP120B52S |  | HVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268545 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268553 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S | YVAHP120B52S |  | YVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268569 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268570 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S |  |  | TVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268572 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S | TVAHP144B52S |  |  | TVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268574 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268579 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S | TVAHP144B52S |  | TVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268588 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268589 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S |  |  | HVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268590 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S | HVAHP144B52S |  |  | HVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268591 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268595 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S | HVAHP144B52S |  | HVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268604 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268606 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S |  |  | YVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268607 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S | YVAHP144B52S |  |  | YVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268609 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268616 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S | YVAHP144B52S |  | YVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204269032 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269033 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S |  |  | TVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269034 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S | TVAHR144B52S |  |  | TVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269035 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269048 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269049 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S |  |  | HVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S | HVAHR144B52S |  |  | HVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269051 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269064 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269065 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S |  |  | YVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269066 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S | YVAHR144B52S |  |  | YVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269067 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269080 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269081 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S |  |  | TVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269082 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S | TVAHP144B52S |  |  | TVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269083 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269096 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269097 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S |  |  | HVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269098 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S | HVAHP144B52S |  |  | HVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269099 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269112 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269113 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S |  |  | YVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269114 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S | YVAHP144B52S |  |  | YVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269115 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204442719 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442721 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM168HXVAFH |  |  | AM312JXVAFH | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204442723 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAFH | AM192HXVAFH |  |  | AM384JXVAFH | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442734 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442736 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM168HXVAJH |  |  | AM312JXVAJH | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204442738 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH | AM192HXVAJH |  |  | AM384JXVAJH | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442750 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442752 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM168HXVAFR |  |  | AM312JXVAFR | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204442754 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAFR | AM192HXVAFR |  |  | AM384JXVAFR | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442765 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442767 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM168HXVAJR |  |  | AM312JXVAJR | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204442769 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR | AM192HXVAJR |  |  | AM384JXVAJR | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442781 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204442789 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204442797 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204442805 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204572228 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572229 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572243 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572244 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572258 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572259 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572273 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572274 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572288 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572289 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204572296 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572297 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204572304 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572305 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204572312 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572313 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
8657035 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P360ZSKMU-A | Ducted Indoor Units | 342000 | 11.4 | 19.8 | 386000 | 3.32 | 284000 | 2.32 | R-410A | 28.5
8657033 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A |  | PUHY-P336ZSKMU-A | Ducted Indoor Units | 320000 | 11.6 | 20 | 360000 | 3.42 | 268000 | 2.38 | R-410A | 26.6667
8657031 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P312ZSKMU-A | Ducted Indoor Units | 296000 | 11.9 | 20 | 334000 | 3.46 | 236000 | 2.43 | R-410A | 24.6667
8657029 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P288ZSKMU-A | Ducted Indoor Units | 274000 | 11.8 | 20.1 | 308000 | 3.49 | 216000 | 2.53 | R-410A | 22.8333
8657027 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P264ZSKMU-A | Ducted Indoor Units | 252000 | 11.9 | 20.7 | 280000 | 3.47 | 200000 | 2.52 | R-410A | 21
206453568 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
206453569 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453570 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453571 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM121CTE5 |  |  | ARUM336CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
206453572 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453573 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM168CTE5 |  |  | ARUM384CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453574 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
206453575 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM121CTE5 | ARUM121CTE5 |  | ARUM432CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
205281487 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
205281488 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
205281489 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202566112 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202566113 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
202566114 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202566115 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202566116 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202566117 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202566118 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM121CTE5 |  |  | ARUM336CTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202566120 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202566122 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM168CTE5 |  |  | ARUM384CTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202566124 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
202566126 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM121CTE5 | ARUM121CTE5 |  | ARUM432CTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
202534327 | 1/1/2027 | LG | HMSR-A-CB | ARUB121CTE4 | ARUB144CTE4 |  |  | ARUB264CTE4 | Non-Ducted Indoor Units | 250000 | 11.6 | 20.5 | 280000 | 3.54 | 182000 | 2.49 | R-410A | 20.8333
202534328 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 | ARUB144CTE4 |  |  | ARUB288CTE4 | Non-Ducted Indoor Units | 274000 | 11.6 | 20.5 | 306000 | 3.5 | 198000 | 2.47 | R-410A | 22.8333
202534329 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 | ARUB168CTE4 |  |  | ARUB313CTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534330 | 1/1/2027 | LG | HMSR-A-CB | ARUB168CTE4 | ARUB168CTE4 |  |  | ARUB337CTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20 | 360000 | 3.51 | 234000 | 2.34 | R-410A | 26.6667
202534331 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 | ARUB121CTE4 | ARUB144CTE4 |  | ARUB360CTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 19.5 | 386000 | 3.5 | 248000 | 2.4 | R-410A | 28.5
202534339 | 1/1/2027 | LG | HMSR-A-CB | ARUB121CTE4 | ARUB144CTE4 |  |  | ARUB264CTE4 | Ducted Indoor Units | 250000 | 11.4 | 19.5 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202534340 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 | ARUB144CTE4 |  |  | ARUB288CTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534343 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 | ARUB121CTE4 | ARUB144CTE4 |  | ARUB360CTE4 | Ducted Indoor Units | 342000 | 11 | 20 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202534351 | 1/1/2027 | LG | HMSV-A-CB | ARUN121CTE4 | ARUN144CTE4 |  |  | ARUN264CTE4 | Non-Ducted Indoor Units | 250000 | 11.6 | 20.5 | 280000 | 3.54 | 182000 | 2.49 | R-410A | 20.8333
202534352 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 | ARUN144CTE4 |  |  | ARUN288CTE4 | Non-Ducted Indoor Units | 274000 | 11.6 | 20.5 | 306000 | 3.5 | 198000 | 2.47 | R-410A | 22.8333
202534353 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 | ARUN168CTE4 |  |  | ARUN313CTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534354 | 1/1/2027 | LG | HMSV-A-CB | ARUN168CTE4 | ARUN168CTE4 |  |  | ARUN337CTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20 | 360000 | 3.51 | 234000 | 2.34 | R-410A | 26.6667
202534355 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 | ARUN121CTE4 | ARUN144CTE4 |  | ARUN360CTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 19.5 | 386000 | 3.5 | 248000 | 2.4 | R-410A | 28.5
202534363 | 1/1/2027 | LG | HMSV-A-CB | ARUN121CTE4 | ARUN144CTE4 |  |  | ARUN264CTE4 | Ducted Indoor Units | 250000 | 11.4 | 19.5 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202534364 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 | ARUN144CTE4 |  |  | ARUN288CTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534367 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 | ARUN121CTE4 | ARUN144CTE4 |  | ARUN360CTE4 | Ducted Indoor Units | 342000 | 11 | 20 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202584338 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 | ARUN144BTE4 |  |  | ARUN264BTE4 | Non-Ducted Indoor Units | 250000 | 11.9 | 21.8 | 280000 | 3.6 | 182000 | 2.49 | R-410A | 20.8333
10225961 | 1/1/2027 | INNOVAIR | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
202616839 | 1/1/2027 | LG | HMSV-A-CB | ARUN145BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN432BTE4 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.5 | 460000 | 3.3 | 298000 | 2.3 | R-410A | 34.1667
202616840 | 1/1/2027 | LG | HMSV-A-CB | ARUN145BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN432BTE4 | Ducted Indoor Units | 410000 | 10.4 | 19.8 | 460000 | 3.3 | 298000 | 2.25 | R-410A | 34.1667
10594392 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-120U8STB |  |  | AVWT-264U8SZB | Non-Ducted Indoor Units | 258000 | 11.05 | 24.1 | 282000 | 3.69 | 180000 | 2.39 | R-410A | 21.5
10594393 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B |  |  | AVWT-288U8SZB | Non-Ducted Indoor Units | 276000 | 10.7 | 23.35 | 300000 | 3.59 | 192000 | 2.3 | R-410A | 23
10594394 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-168U8S1B | AVWT-144U8S1B |  |  | AVWT-312U8SZB | Non-Ducted Indoor Units | 298000 | 10.45 | 21.2 | 316000 | 3.57 | 202000 | 2.22 | R-410A | 24.8333
10594395 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-168U8S1B | AVWT-168U8S1B |  |  | AVWT-336U8SZB | Non-Ducted Indoor Units | 320000 | 10.25 | 20.6 | 324000 | 3.57 | 210000 | 2.24 | R-410A | 26.6667
10594396 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B | AVWT-072U8SNB |  | AVWT-360U8SZB | Non-Ducted Indoor Units | 346000 | 10.65 | 21.15 | 372000 | 3.55 | 244000 | 2.33 | R-410A | 28.8333
10594397 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B | AVWT-96U8STB |  | AVWT-384U8SZB | Non-Ducted Indoor Units | 370000 | 10.5 | 21.55 | 400000 | 3.47 | 260000 | 2.33 | R-410A | 30.8333
10594401 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-120U8STB |  |  | AVWT-264U8SZB | Ducted Indoor Units | 258000 | 11.55 | 24.3 | 282000 | 3.31 | 180000 | 2.25 | R-410A | 21.5
10595368 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B | AVWT-120U8STB |  | AVWT-408U8SZB | Ducted Indoor Units | 390000 | 11.25 | 22.9 | 435000 | 3.36 | 278000 | 2.34 | R-410A | 32.5
10595370 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B | AVWT-120U8STB |  | AVWT-408U8SZB | Non-Ducted Indoor Units | 390000 | 10.15 | 22.2 | 435000 | 3.59 | 278000 | 2.31 | R-410A | 32.5

## Commercial Water Loop HP
AHRI Certified Reference Number | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage | Tax Credit (IRA) Eligibility
206570649 | Water Loop | 7 SERIES | NVV/NVH036C1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
216687114 | Water Loop | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216687119 | Water Loop | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216687732 | Water Loop | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | No
216687737 | Water Loop | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | No
207337513 | Water Loop | GEOSTAR | 103J036**1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | No
207337514 | Water Loop | GEOSTAR | 103J036**1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | No
215400201 | Water Loop | DAIKIN | WSSV036K3*B*C |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
215400204 | Water Loop | DAIKIN | WSSV042E1*B*T |  | 43000 | 18.36 | 47600 | 5.43 | 3.5833 | No
215400205 | Water Loop | DAIKIN | WSSV042F3*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215400208 | Water Loop | DAIKIN | WSSV042E1*B*C |  | 43000 | 18.36 | 47600 | 5.43 | 3.5833 | No
215400209 | Water Loop | DAIKIN | WSSV042F3*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215400212 | Water Loop | DAIKIN | WSSV048E1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400213 | Water Loop | DAIKIN | WSSV048F3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400216 | Water Loop | DAIKIN | WSSV048E1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400217 | Water Loop | DAIKIN | WSSV048F3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400220 | Water Loop | DAIKIN | WSSV060E1*B*T |  | 64000 | 17.4 | 78000 | 5.3 | 5.3333 | No
215400221 | Water Loop | DAIKIN | WSSV060F3*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215400222 | Water Loop | DAIKIN | WSSV060E1*B*C |  | 64000 | 17.4 | 78000 | 5.3 | 5.3333 | No
215400223 | Water Loop | DAIKIN | WSSV060F3*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215402546 | Water Loop | DAIKIN | WSSV007E1*B*T |  | 7100 | 17.99 | 8100 | 5.49 | 0.59167 | No
215402548 | Water Loop | DAIKIN | WSSV009E1*B*T |  | 9200 | 17.49 | 11000 | 4.98 | 0.76667 | No
215402550 | Water Loop | DAIKIN | WSSV024E1*B*T |  | 24400 | 18.37 | 28000 | 5.79 | 2.0333 | No
215402551 | Water Loop | DAIKIN | WSSV024F3*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215402554 | Water Loop | DAIKIN | WSSV024E1*B*C |  | 24400 | 18.37 | 28000 | 5.79 | 2.0333 | No
215402555 | Water Loop | DAIKIN | WSSV024F3*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215402558 | Water Loop | DAIKIN | WSSV030E1*B*T |  | 29200 | 19.17 | 34500 | 5.67 | 2.4333 | No
215402559 | Water Loop | DAIKIN | WSSV030F3*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215402562 | Water Loop | DAIKIN | WSSV030E1*B*C |  | 29200 | 19.17 | 34500 | 5.67 | 2.4333 | No
215402563 | Water Loop | DAIKIN | WSSV030F3*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215402566 | Water Loop | DAIKIN | WSSV036E1*B*T |  | 39000 | 19.02 | 44100 | 5.35 | 3.25 | No
215402567 | Water Loop | DAIKIN | WSSV036F3*B*T |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
215402570 | Water Loop | DAIKIN | WSSV036E1*B*C |  | 39000 | 19.02 | 44100 | 5.35 | 3.25 | No
215402571 | Water Loop | DAIKIN | WSSV036F3*B*C |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
214595646 | Water Loop | AAON, Inc. | M2-006-2-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
214595648 | Water Loop | AAON, Inc. | M2-006-3-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
214595650 | Water Loop | AAON, Inc. | M2-006-4-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
5220675 | Water Loop | DAIKIN | WGSV/WGSH030B*E |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220676 | Water Loop | DAIKIN | WGSV/WGSH030B*F |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220677 | Water Loop | DAIKIN | WGSV/WGSH030B*J |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220678 | Water Loop | DAIKIN | WGSV/WGSH030B*K |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220681 | Water Loop | DAIKIN | WGSV/WGSH036B*E |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
215268781 | Water Loop | WaterFurnace | V5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268782 | Water Loop | WaterFurnace | V5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268783 | Water Loop | WaterFurnace | V5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268784 | Water Loop | WaterFurnace | V5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
202330563 | Water Loop | AAON, Inc. | M2-006-2-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
202330567 | Water Loop | AAON, Inc. | M2-006-3-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
202330571 | Water Loop | AAON, Inc. | M2-006-4-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
215851795 | Water Loop | DAIKIN | WSTV024J1*C/S*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
215851796 | Water Loop | DAIKIN | WSTV024K3*C/S*C |  | 24300 | 17.06 | 28000 | 5.64 | 2.025 | No
215851809 | Water Loop | DAIKIN | WSTV036J1*C/S*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
215851810 | Water Loop | DAIKIN | WSTV036K3*C/S*C |  | 38100 | 17.89 | 41100 | 5.03 | 3.175 | No
215851818 | Water Loop | DAIKIN | WSTV048K3*C/S*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
215851820 | Water Loop | DAIKIN | WSTV048L3*C/S*C |  | 50800 | 17.09 | 58500 | 5.35 | 4.2333 | No
215852846 | Water Loop | DAIKIN | WSTH024E1*C/S*C |  | 24500 | 17.53 | 26100 | 5.29 | 2.0417 | No
215852847 | Water Loop | DAIKIN | WSTH024F3*C/S*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
215852850 | Water Loop | DAIKIN | WSTH030E1*C/S*C |  | 31400 | 17.12 | 34900 | 5.36 | 2.6167 | No
215852854 | Water Loop | DAIKIN | WSTH036E1*C/S*C |  | 38000 | 18.43 | 42900 | 5.36 | 3.1667 | No
215852855 | Water Loop | DAIKIN | WSTH036F3*C/S*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
9910449 | Water Loop | GEOCOMFORT | GZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
9910450 | Water Loop | HYDRON MODULE | HZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
9910451 | Water Loop | TETCO | TZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
9910452 | Water Loop | GEOCOMFORT | GZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
9910453 | Water Loop | HYDRON MODULE | HZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
9910454 | Water Loop | TETCO | TZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
214772074 | Water Loop | TRANE | EXVK0097 |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214772075 | Water Loop | TRANE | EXVK0127 |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214772077 | Water Loop | TRANE | EXVK0187 |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214772078 | Water Loop | TRANE | EXVK024B |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
216128491 | Water Loop | GEOSTAR | G5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
216411470 | Water Loop | ClimateMaster | SJ/PN036A | SAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
215746915 | Water Loop | TRANE | GSK036A3 |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746916 | Water Loop | TRANE | GSK048A3 |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746918 | Water Loop | TRANE | GSK060A3 |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746919 | Water Loop | TRANE | GSK072A3 |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746920 | Water Loop | TRANE | GSK090A3 |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
215746922 | Water Loop | TRANE | GSK120A3 |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
215746923 | Water Loop | TRANE | GSK036A4 |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746924 | Water Loop | TRANE | GSK036AW |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746925 | Water Loop | TRANE | GSK048A4 |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746926 | Water Loop | TRANE | GSK048AW |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746927 | Water Loop | TRANE | GSK060A4 |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746928 | Water Loop | TRANE | GSK060AW |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746929 | Water Loop | TRANE | GSK072A4 |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746930 | Water Loop | TRANE | GSK072AW |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746931 | Water Loop | TRANE | GSK090A4 |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
215746932 | Water Loop | TRANE | GSK090AW |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
215746935 | Water Loop | TRANE | GSK120A4 |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
215746936 | Water Loop | TRANE | GSK120AW |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
215748227 | Water Loop | ClimateMaster | SMT(S,M)24A*Q |  | 25000 | 17.6 | 28000 | 5.1 | 2.0833 | No
215748230 | Water Loop | ClimateMaster | SMT(S,M)30A*Q |  | 30000 | 17 | 35500 | 5.3 | 2.5 | No
4218842 | Water Loop | DAIKIN | WVFC1030*E***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
4218843 | Water Loop | DAIKIN | WVFC1030*F***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
4218844 | Water Loop | DAIKIN | WVFC1030*J***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
205767467 | Water Loop | ClimateMaster | QEV/H/D1860 |  | 48000 | 17.3 | 60000 | 5.5 | 4 | Yes
205767473 | Water Loop | ClimateMaster | TEV/H/D026B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
205767474 | Water Loop | ClimateMaster | TEV/H/D038B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
214067548 | Water Loop | GeoSmart Energy | GBV/GBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067549 | Water Loop | GeoSmart Energy | GBV/GBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067551 | Water Loop | GeoSmart Energy | GBV/GBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067552 | Water Loop | GeoSmart Energy | GBV/GBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067557 | Water Loop | GeoSmart Energy | GBV/GBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214067558 | Water Loop | GeoSmart Energy | GBV/GBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067559 | Water Loop | GeoSmart Energy | GBV/GBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067560 | Water Loop | GeoSmart Energy | GBV/GBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214067561 | Water Loop | GeoSmart Energy | GBV/GBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067562 | Water Loop | GeoSmart Energy | GBV/GBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067564 | Water Loop | GeoSmart Energy | GBV/GBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067565 | Water Loop | GeoSmart Energy | GBV/GBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067567 | Water Loop | GeoSmart Energy | GBV/GBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067568 | Water Loop | GeoSmart Energy | GBV/GBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067569 | Water Loop | GeoSmart Energy | GBV/GBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067570 | Water Loop | GeoSmart Energy | GBV/GBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067571 | Water Loop | GeoSmart Energy | GBV/GBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067572 | Water Loop | GeoSmart Energy | GBV/GBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067574 | Water Loop | GeoSmart Energy | GBV/GBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067575 | Water Loop | GeoSmart Energy | GBV/GBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067577 | Water Loop | GeoSmart Energy | GBV/GBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067578 | Water Loop | GeoSmart Energy | GBV/GBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
207200614 | Water Loop | GeoSmart Energy | VI036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
214796344 | Water Loop | WaterFurnace | W5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214796345 | Water Loop | WaterFurnace | W5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
214810493 | Water Loop | GEOSTAR | G5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214810494 | Water Loop | GEOSTAR | G5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
202921908 | Water Loop | BOSCH | EP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921909 | Water Loop | BOSCH | EP036-3VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921910 | Water Loop | BOSCH | EP036-4VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921911 | Water Loop | BOSCH-GEO | BP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921957 | Water Loop | FHP | EP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921958 | Water Loop | FHP | EP036-3VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921959 | Water Loop | FHP | EP036-4VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921960 | Water Loop | BOSCH | BP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922716 | Water Loop | CARRIER | 50PSV036***3/CA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922719 | Water Loop | CARRIER | 50PSV036***5/EA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922722 | Water Loop | CARRIER | 50PSV036***6/FA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922725 | Water Loop | CARRIER | GB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922728 | Water Loop | BRYANT | GB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922731 | Water Loop | HEIL | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922734 | Water Loop | ARCOAIRE | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922737 | Water Loop | KEEPRITE | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922740 | Water Loop | TEMPSTAR | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922742 | Water Loop | COMFORTMAKER | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922745 | Water Loop | DAY & NIGHT | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
203113888 | Water Loop | GEOSTAR | 103J036**1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
201907628 | Water Loop | WaterFurnace | URD038*4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907629 | Water Loop | WaterFurnace | URD038*4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907630 | Water Loop | WaterFurnace | URD038*4*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907631 | Water Loop | WaterFurnace | URD049*4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
201907632 | Water Loop | WaterFurnace | URD049*4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
201907633 | Water Loop | WaterFurnace | URD049*4*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349409 | Water Loop | WaterFurnace | NBV/NBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
213711981 | Water Loop | DAIKIN | WSSH048E1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
213711982 | Water Loop | DAIKIN | WSSH048E1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
213711984 | Water Loop | DAIKIN | WSSH060E1*B*T |  | 60872 | 17.4 | 78027 | 5.72 | 5.0727 | No
215837673 | Water Loop | DAIKIN | WSMH024F3*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837675 | Water Loop | DAIKIN | WSMH024J1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837676 | Water Loop | DAIKIN | WSMH024K3*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837681 | Water Loop | DAIKIN | WSMH024F3*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837683 | Water Loop | DAIKIN | WSMH024J1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837685 | Water Loop | DAIKIN | WSMH024K3*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837698 | Water Loop | DAIKIN | WSMH030F3*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754443 | Water Loop | DAIKIN | WSSV042F1*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217754446 | Water Loop | DAIKIN | WSSV042F1*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217754449 | Water Loop | DAIKIN | WSSV048F1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217754453 | Water Loop | DAIKIN | WSSV048F1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217754457 | Water Loop | DAIKIN | WSSV060F1*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217754461 | Water Loop | DAIKIN | WSSV060F1*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217754553 | Water Loop | DAIKIN | WSMH030F1*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754554 | Water Loop | DAIKIN | WSMH030K1*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
216625463 | Water Loop | GEOSTAR | G5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625464 | Water Loop | GEOSTAR | G5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625465 | Water Loop | GEOSTAR | G5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625466 | Water Loop | GEOSTAR | G5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625467 | Water Loop | GEOSTAR | G5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625468 | Water Loop | GEOSTAR | G5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625469 | Water Loop | GEOSTAR | G5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625470 | Water Loop | GEOSTAR | G5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625645 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625646 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625647 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625648 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625649 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625650 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625651 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625652 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625653 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625654 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625655 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625656 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625657 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625658 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625659 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625660 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625661 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625662 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625663 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625664 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625665 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625666 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625667 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625668 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625669 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625670 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625671 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625672 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625673 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625674 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625675 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625676 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625677 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625678 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625679 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625680 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625681 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625682 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625683 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625694 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625695 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215399790 | Water Loop | DAIKIN | WSMV024J1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399791 | Water Loop | DAIKIN | WSMV024K3*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399794 | Water Loop | DAIKIN | WSMV024J1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399795 | Water Loop | DAIKIN | WSMV024K3*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399815 | Water Loop | DAIKIN | WSMV036K3*C/S*T |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
215399819 | Water Loop | DAIKIN | WSMV036K3*C/S*C |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
207338127 | Water Loop | GEOSTAR | 141/142C036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
207348654 | Water Loop | WaterFurnace | URS036*0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348655 | Water Loop | WaterFurnace | URS036*0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348656 | Water Loop | WaterFurnace | URS036*0*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348657 | Water Loop | WaterFurnace | URS036*3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348658 | Water Loop | WaterFurnace | URS036*3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348659 | Water Loop | WaterFurnace | URS036*3*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348660 | Water Loop | WaterFurnace | URS036*4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348661 | Water Loop | WaterFurnace | URS036*4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348662 | Water Loop | WaterFurnace | URS036*4*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
217752718 | Water Loop | DAIKIN | WSSV060K1*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217752724 | Water Loop | DAIKIN | WSTH024K1*B*C |  | 24500 | 17 | 26100 | 5.14 | 2.0417 | No
217752728 | Water Loop | DAIKIN | WSTH036K1*B*C |  | 38000 | 17.88 | 42900 | 5.2 | 3.1667 | No
217752730 | Water Loop | DAIKIN | WSTH042K1*B*C |  | 44000 | 17.07 | 50300 | 4.97 | 3.6667 | No
217752744 | Water Loop | DAIKIN | WSTV024K1*B*C |  | 24300 | 17.06 | 28000 | 5.64 | 2.025 | No
215285739 | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215285740 | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | Yes
215285741 | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | Yes
215852858 | Water Loop | DAIKIN | WSTH042E1*C/S*C |  | 44000 | 17.59 | 50300 | 5.12 | 3.6667 | No
215852859 | Water Loop | DAIKIN | WSTH042F3*C/S*C |  | 44000 | 17.24 | 50300 | 5.02 | 3.6667 | No
9063207 | Water Loop | DAIKIN | WVFC1030*K***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
215852868 | Water Loop | DAIKIN | WSTV024E1*C/S*C |  | 24300 | 17.59 | 28000 | 5.81 | 2.025 | No
215852869 | Water Loop | DAIKIN | WSTV024F3*C/S*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
215852874 | Water Loop | DAIKIN | WSTV036E1*C/S*C |  | 38100 | 18.45 | 41100 | 5.18 | 3.175 | No
215852875 | Water Loop | DAIKIN | WSTV036F3*C/S*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
215852878 | Water Loop | DAIKIN | WSTV042E1*C/S*C |  | 43500 | 17.3 | 50000 | 5.06 | 3.625 | No
215852882 | Water Loop | DAIKIN | WSTV048E1*C/S*C |  | 50800 | 17.62 | 58500 | 5.52 | 4.2333 | No
215852883 | Water Loop | DAIKIN | WSTV048F3*C/S*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
215852884 | Water Loop | DAIKIN | WSTV060E1*C/S*C |  | 60500 | 17.3 | 74700 | 5.5 | 5.0417 | No
5699505 | Water Loop | TRANE | VSVE0421 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699525 | Water Loop | TRANE | VSVE0422 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699526 | Water Loop | TRANE | VSVE0424 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699628 | Water Loop | TRANE | VSHE0241 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699631 | Water Loop | TRANE | VSHE0242 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699633 | Water Loop | TRANE | VSHE0244 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699639 | Water Loop | TRANE | VSHE0421 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
5699644 | Water Loop | TRANE | VSHE0422 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
5699650 | Water Loop | TRANE | VSHE0424 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
6501973 | Water Loop | GEOSTAR | GBV/GBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501974 | Water Loop | GEOSTAR | GBV/GBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501975 | Water Loop | GEOSTAR | GBV/GBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6502006 | Water Loop | GEOSTAR | GBV/GBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
206346951 | Water Loop | DAIKIN | WVFC*030*E***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
206346952 | Water Loop | DAIKIN | WVFC*030*F***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
206346953 | Water Loop | DAIKIN | WVFC*030*J***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
207335398 | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335399 | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335407 | Water Loop | GeoSmart Energy | GS030**1*(0,3)*J |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | Yes
207335408 | Water Loop | GeoSmart Energy | GS030**1*(1,4)*J |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335409 | Water Loop | GeoSmart Energy | GS036**1*(0,3)*K |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207335514 | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207335573 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335575 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207335580 | Water Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335581 | Water Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335585 | Water Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335586 | Water Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
209156974 | Water Loop | AE Air | WSS6006*6* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
209156993 | Water Loop | AE Air | WSS6006*7* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
7499543 | Water Loop | FHP | LM024-1CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499546 | Water Loop | FHP | LM024-2CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499547 | Water Loop | FHP | LM024-3CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499548 | Water Loop | FHP | LM024-4CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499550 | Water Loop | FHP | LM036-1VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499552 | Water Loop | FHP | LM036-2VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499553 | Water Loop | FHP | LM036-3VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499554 | Water Loop | FHP | LM036-4VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
5599272 | Water Loop | BOSCH-GEO | SM036-1CF/HZ/VT |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
217037822 | Water Loop | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037827 | Water Loop | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
7167540 | Water Loop | CARRIER | 50PTD/H/V024***4/DA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167541 | Water Loop | CARRIER | 50PTD/H/V024***6/FA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167542 | Water Loop | CARRIER | 50PTD/H/V036***3/CA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167543 | Water Loop | CARRIER | 50PTD/H/V036***5/EA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167544 | Water Loop | CARRIER | 50PTD/H/V036***4/DA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167545 | Water Loop | CARRIER | 50PTD/H/V036***6/FA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
216621313 | Water Loop | GEOSTAR | G5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216621314 | Water Loop | GEOSTAR | G5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216621315 | Water Loop | GEOSTAR | G5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216621316 | Water Loop | GEOSTAR | G5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216621333 | Water Loop | GEOSTAR | G5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621334 | Water Loop | GEOSTAR | G5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621335 | Water Loop | GEOSTAR | G5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621336 | Water Loop | GEOSTAR | G5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621337 | Water Loop | GEOSTAR | G5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621338 | Water Loop | GEOSTAR | G5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621339 | Water Loop | GEOSTAR | G5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621340 | Water Loop | GEOSTAR | G5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621341 | Water Loop | GEOSTAR | G5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621342 | Water Loop | GEOSTAR | G5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
217967018 | Water Loop | TRANE | VSHK024A |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217967019 | Water Loop | TRANE | VSVK024A |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967021 | Water Loop | TRANE | VSVK033A |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967022 | Water Loop | TRANE | VSHK042A |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967023 | Water Loop | TRANE | VSVK042A |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
217967025 | Water Loop | TRANE | VSVK050A |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
217967028 | Water Loop | TRANE | VSHK024B |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217967029 | Water Loop | TRANE | VSVK024B |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967031 | Water Loop | TRANE | VSVK033B |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967032 | Water Loop | TRANE | VSHK042B |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967033 | Water Loop | TRANE | VSVK042B |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
217967035 | Water Loop | TRANE | VSVK050B |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
7519727 | Water Loop | GEOCOMFORT | GVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
7519748 | Water Loop | HYDRON MODULE | HVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
7519756 | Water Loop | TETCO | TVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
7519769 | Water Loop | GEOCOMFORT | GVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519770 | Water Loop | HYDRON MODULE | HVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519771 | Water Loop | TETCO | TVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519772 | Water Loop | GEOCOMFORT | GVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519773 | Water Loop | HYDRON MODULE | HVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519774 | Water Loop | TETCO | TVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519775 | Water Loop | GEOCOMFORT | GVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519776 | Water Loop | HYDRON MODULE | HVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519777 | Water Loop | TETCO | TVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7520238 | Water Loop | GEOCOMFORT | GVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520239 | Water Loop | HYDRON MODULE | HVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520240 | Water Loop | TETCO | TVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520241 | Water Loop | GEOCOMFORT | GVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520242 | Water Loop | HYDRON MODULE | HVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520243 | Water Loop | TETCO | TVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520244 | Water Loop | TETCO | TVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520245 | Water Loop | HYDRON MODULE | HVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520246 | Water Loop | GEOCOMFORT | GVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520247 | Water Loop | HYDRON MODULE | HVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520248 | Water Loop | TETCO | TVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520249 | Water Loop | GEOCOMFORT | GVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7523956 | Water Loop | GEOCOMFORT | GVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
7523957 | Water Loop | HYDRON MODULE | HVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
7523958 | Water Loop | TETCO | TVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
7523959 | Water Loop | GEOCOMFORT | GVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
7523960 | Water Loop | HYDRON MODULE | HVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
7523961 | Water Loop | TETCO | TVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
7411100 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411231 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411380 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411778 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411949 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6674620 | Water Loop | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674621 | Water Loop | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674622 | Water Loop | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674623 | Water Loop | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6676515 | Water Loop | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676516 | Water Loop | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676518 | Water Loop | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676519 | Water Loop | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
203238019 | Water Loop | BOSCH-GEO | BP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203253412 | Water Loop | BOSCH | BP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254606 | Water Loop | CARRIER | GB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203254607 | Water Loop | BRYANT | GB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254608 | Water Loop | ARCOAIRE | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
213154474 | Water Loop | GeoSmart Energy | GT038**1*1********L |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
213154475 | Water Loop | GeoSmart Energy | GT049**1*1********L |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
211594132 | Water Loop | TRANE | EXHG018A |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
211594133 | Water Loop | TRANE | EXHG024A |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594134 | Water Loop | TRANE | EXHG030A |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594135 | Water Loop | TRANE | EXHG036A |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594136 | Water Loop | TRANE | EXHG042A |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594137 | Water Loop | TRANE | EXHG048A |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594138 | Water Loop | TRANE | EXHG060A |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594139 | Water Loop | TRANE | EXHG070A |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
211594213 | Water Loop | TRANE | DXHG036A |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594214 | Water Loop | TRANE | DXHG048A |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594215 | Water Loop | TRANE | DXHG060A |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
211594216 | Water Loop | TRANE | DXHG070A |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
215415909 | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215415910 | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215415911 | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | Yes
215415912 | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | Yes
215415913 | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | Yes
215415914 | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | Yes
963510 | Water Loop | WaterFurnace | NLV/NXV095T*3 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
963511 | Water Loop | WaterFurnace | NLV/NXV095T*4 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
963512 | Water Loop | WaterFurnace | NLV/NXV095T*5 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
10298936 | Water Loop | WaterFurnace | UVV/UVH036**0*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
10298937 | Water Loop | WaterFurnace | UVV/UVH036**3*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
10298938 | Water Loop | WaterFurnace | UVV/UVH036**4*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
207349387 | Water Loop | WaterFurnace | NBV/NBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349388 | Water Loop | WaterFurnace | NBV/NBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349389 | Water Loop | WaterFurnace | NBV/NBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349390 | Water Loop | WaterFurnace | NBV/NBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349391 | Water Loop | WaterFurnace | NBV/NBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349392 | Water Loop | WaterFurnace | NBV/NBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349393 | Water Loop | WaterFurnace | NBV/NBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349394 | Water Loop | WaterFurnace | NBV/NBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349395 | Water Loop | WaterFurnace | NBV/NBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349396 | Water Loop | WaterFurnace | NBV/NBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349397 | Water Loop | WaterFurnace | NBV/NBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349398 | Water Loop | WaterFurnace | NBV/NBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349399 | Water Loop | WaterFurnace | NBV/NBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349400 | Water Loop | WaterFurnace | NBV/NBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
206347035 | Water Loop | DAIKIN | WCCH*015*J***14* |  | 15600 | 17.6 | 17200 | 5.6 | 1.3 | No
206347037 | Water Loop | DAIKIN | WCCH*015*E***14* |  | 16000 | 17.6 | 18100 | 5.6 | 1.3333 | No
206347960 | Water Loop | HYDROTECH | WSS6006*6* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
203383899 | Water Loop | FHP | EP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383900 | Water Loop | FHP | EP042-3HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383901 | Water Loop | FHP | EP042-4HZ*******B |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
215837818 | Water Loop | DAIKIN | WSSH024F3*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837820 | Water Loop | DAIKIN | WSSH024J1*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837821 | Water Loop | DAIKIN | WSSH024K3*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837827 | Water Loop | DAIKIN | WSSH030F3*C/S*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837828 | Water Loop | DAIKIN | WSSH030J1*C/S*T |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
215837829 | Water Loop | DAIKIN | WSSH030K3*C/S*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837835 | Water Loop | DAIKIN | WSSH030F3*C/S*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837836 | Water Loop | DAIKIN | WSSH030J1*C/S*C |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
215837837 | Water Loop | DAIKIN | WSSH030K3*C/S*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837843 | Water Loop | DAIKIN | WSSH036F3*C/S*T |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
215837844 | Water Loop | DAIKIN | WSSH036J1*C/S*T |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
215837845 | Water Loop | DAIKIN | WSSH036K3*C/S*T |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
215837851 | Water Loop | DAIKIN | WSSH036F3*C/S*C |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
215837853 | Water Loop | DAIKIN | WSSH036J1*C/S*C |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
215837854 | Water Loop | DAIKIN | WSSH036K3*C/S*C |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
217754575 | Water Loop | DAIKIN | WSMH042E1*C/S*T |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
217754581 | Water Loop | DAIKIN | WSMH042E1*C/S*C |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
214771931 | Water Loop | TRANE | EXVK009A |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214771932 | Water Loop | TRANE | EXVK012A |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
216014181 | Water Loop | RHEEM | RPVV/H/D036D |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
216054107 | Water Loop | WaterFurnace | W5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
216625808 | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625809 | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625810 | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625811 | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625812 | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625813 | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625814 | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625815 | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625816 | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625817 | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625828 | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625829 | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625830 | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625831 | Water Loop | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625832 | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625833 | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625834 | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625835 | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625836 | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625837 | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216759817 | Water Loop | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216759822 | Water Loop | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
214772079 | Water Loop | TRANE | EXVK0244 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772080 | Water Loop | TRANE | EXVK0247 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772081 | Water Loop | TRANE | EXVK030B |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772082 | Water Loop | TRANE | EXVK0304 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772083 | Water Loop | TRANE | EXVK0307 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772084 | Water Loop | TRANE | EXVK036B |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772085 | Water Loop | TRANE | EXVK0364 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772086 | Water Loop | TRANE | EXVK0367 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772087 | Water Loop | TRANE | EXVK042B |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772088 | Water Loop | TRANE | EXVK0424 |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772089 | Water Loop | TRANE | EXVK048B |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772090 | Water Loop | TRANE | EXVK0484 |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772091 | Water Loop | TRANE | EXVK060B |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772092 | Water Loop | TRANE | EXVK0604 |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772093 | Water Loop | TRANE | EXVK070B |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772094 | Water Loop | TRANE | EXVK0704 |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772095 | Water Loop | TRANE | DXVK024A |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772096 | Water Loop | TRANE | DXVK036A |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772097 | Water Loop | TRANE | DXVK048A |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772098 | Water Loop | TRANE | DXVK060A |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772120 | Water Loop | TRANE | EXHK0097 |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214772121 | Water Loop | TRANE | EXHK0127 |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214772123 | Water Loop | TRANE | EXHK0187 |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214772124 | Water Loop | TRANE | EXHK024B |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772125 | Water Loop | TRANE | EXHK0244 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772126 | Water Loop | TRANE | EXHK0247 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772127 | Water Loop | TRANE | EXHK030B |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772128 | Water Loop | TRANE | EXHK0304 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772129 | Water Loop | TRANE | EXHK0307 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772130 | Water Loop | TRANE | EXHK036B |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772131 | Water Loop | TRANE | EXHK0364 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772132 | Water Loop | TRANE | EXHK0367 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772133 | Water Loop | TRANE | EXHK042B |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772134 | Water Loop | TRANE | EXHK0424 |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
208106952 | Water Loop | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
208106953 | Water Loop | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
4947178 | Water Loop | TRANE | VSVE0241 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
4947179 | Water Loop | TRANE | VSVE0242 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
4947180 | Water Loop | TRANE | VSVE0244 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
5220663 | Water Loop | DAIKIN | WGSV/WGSH015B*E |  | 15300 | 18.1 | 19100 | 5.9 | 1.275 | No
211594245 | Water Loop | TRANE | EXHG0187 |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
211594246 | Water Loop | TRANE | EXHG024B |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594247 | Water Loop | TRANE | EXHG0244 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594248 | Water Loop | TRANE | EXHG0247 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594249 | Water Loop | TRANE | EXHG030B |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594250 | Water Loop | TRANE | EXHG0304 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594251 | Water Loop | TRANE | EXHG0307 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594252 | Water Loop | TRANE | EXHG036B |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594253 | Water Loop | TRANE | EXHG0364 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594254 | Water Loop | TRANE | EXHG0367 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594255 | Water Loop | TRANE | EXHG042B |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594256 | Water Loop | TRANE | EXHG0424 |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594257 | Water Loop | TRANE | EXHG048B |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594258 | Water Loop | TRANE | EXHG0484 |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594259 | Water Loop | TRANE | EXHG060B |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594260 | Water Loop | TRANE | EXHG0604 |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594261 | Water Loop | TRANE | EXHG070B |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
211594262 | Water Loop | TRANE | EXHG0704 |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
211594266 | Water Loop | TRANE | DXHG036B |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594267 | Water Loop | TRANE | DXHG0364 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594268 | Water Loop | TRANE | DXHG0367 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594269 | Water Loop | TRANE | DXHG048B |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594270 | Water Loop | TRANE | DXHG0484 |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594271 | Water Loop | TRANE | DXHG060B |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
211594272 | Water Loop | TRANE | DXHG0604 |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
211594273 | Water Loop | TRANE | DXHG070B |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
211594274 | Water Loop | TRANE | DXHG0704 |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
8964157 | Water Loop | BRYANT | GC036C/H/V******1*X1 + UI |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
8964158 | Water Loop | CARRIER | GC036C/H/V******1**1 + UI |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
202211042 | Water Loop | WaterFurnace | URD038*0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211043 | Water Loop | WaterFurnace | URD038*0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211044 | Water Loop | WaterFurnace | URD038*0*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211045 | Water Loop | WaterFurnace | URD038*3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211046 | Water Loop | WaterFurnace | URD038*3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211047 | Water Loop | WaterFurnace | URD038*3*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211048 | Water Loop | WaterFurnace | URD049*0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211049 | Water Loop | WaterFurnace | URD049*0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211050 | Water Loop | WaterFurnace | URD049*0*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211051 | Water Loop | WaterFurnace | URD049*3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211052 | Water Loop | WaterFurnace | URD049*3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211053 | Water Loop | WaterFurnace | URD049*3*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202262237 | Water Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
7412057 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7412253 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7412381 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7414142 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414232 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414335 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414470 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414553 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414651 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414828 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414896 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415098 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415209 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7415301 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415373 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415878 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416559 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416782 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416889 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417060 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417146 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417329 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417419 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417586 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417698 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417776 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417867 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417918 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417992 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418047 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418154 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418360 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418435 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418635 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418715 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418887 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418965 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501900 | Water Loop | GEOSTAR | GBV/GBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501901 | Water Loop | GEOSTAR | GBV/GBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501903 | Water Loop | GEOSTAR | GBV/GBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501904 | Water Loop | GEOSTAR | GBV/GBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501906 | Water Loop | GEOSTAR | GBV/GBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501907 | Water Loop | GEOSTAR | GBV/GBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501909 | Water Loop | GEOSTAR | GBV/GBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501910 | Water Loop | GEOSTAR | GBV/GBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501918 | Water Loop | GEOSTAR | GBV/GBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501919 | Water Loop | GEOSTAR | GBV/GBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501920 | Water Loop | GEOSTAR | GBV/GBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501921 | Water Loop | GEOSTAR | GBV/GBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501922 | Water Loop | GEOSTAR | GBV/GBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501923 | Water Loop | GEOSTAR | GBV/GBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501924 | Water Loop | GEOSTAR | GBV/GBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501925 | Water Loop | GEOSTAR | GBV/GBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501926 | Water Loop | GEOSTAR | GBV/GBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501927 | Water Loop | GEOSTAR | GBV/GBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501928 | Water Loop | GEOSTAR | GBV/GBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501929 | Water Loop | GEOSTAR | GBV/GBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501931 | Water Loop | GEOSTAR | GBV/GBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501932 | Water Loop | GEOSTAR | GBV/GBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501934 | Water Loop | GEOSTAR | GBV/GBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501935 | Water Loop | GEOSTAR | GBV/GBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501937 | Water Loop | GEOSTAR | GBV/GBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501938 | Water Loop | GEOSTAR | GBV/GBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501940 | Water Loop | GEOSTAR | GBV/GBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501941 | Water Loop | GEOSTAR | GBV/GBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501942 | Water Loop | GEOSTAR | GBV/GBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501943 | Water Loop | GEOSTAR | GBV/GBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501944 | Water Loop | GEOSTAR | GBV/GBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501945 | Water Loop | GEOSTAR | GBV/GBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501946 | Water Loop | GEOSTAR | GBV/GBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501947 | Water Loop | GEOSTAR | GBV/GBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501948 | Water Loop | GEOSTAR | GBV/GBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501949 | Water Loop | GEOSTAR | GBV/GBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501951 | Water Loop | GEOSTAR | GBV/GBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501952 | Water Loop | GEOSTAR | GBV/GBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
207177466 | Water Loop | TRANE | EXVG018A |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
207177467 | Water Loop | TRANE | EXVG0187 |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
207177468 | Water Loop | TRANE | EXVG024A |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177469 | Water Loop | TRANE | EXVG024B |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177470 | Water Loop | TRANE | EXVG0244 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177471 | Water Loop | TRANE | EXVG0247 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177472 | Water Loop | TRANE | EXVG030A |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177473 | Water Loop | TRANE | EXVG030B |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177474 | Water Loop | TRANE | EXVG0304 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177475 | Water Loop | TRANE | EXVG0307 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177476 | Water Loop | TRANE | EXVG036A |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177477 | Water Loop | TRANE | EXVG036B |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177478 | Water Loop | TRANE | EXVG0364 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177479 | Water Loop | TRANE | EXVG0367 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177480 | Water Loop | TRANE | EXVG042A |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177481 | Water Loop | TRANE | EXVG042B |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177482 | Water Loop | TRANE | EXVG0424 |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177483 | Water Loop | TRANE | EXVG048A |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177484 | Water Loop | TRANE | EXVG048B |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177485 | Water Loop | TRANE | EXVG0484 |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177486 | Water Loop | TRANE | EXVG060A |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177487 | Water Loop | TRANE | EXVG060B |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177488 | Water Loop | TRANE | EXVG0604 |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177489 | Water Loop | TRANE | EXVG070A |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177490 | Water Loop | TRANE | EXVG070B |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177491 | Water Loop | TRANE | EXVG0704 |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177496 | Water Loop | TRANE | DXVG036A |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177497 | Water Loop | TRANE | DXVG036B |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177498 | Water Loop | TRANE | DXVG0364 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177499 | Water Loop | TRANE | DXVG0367 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177500 | Water Loop | TRANE | DXVG048A |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207177501 | Water Loop | TRANE | DXVG048B |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207177502 | Water Loop | TRANE | DXVG0484 |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207177503 | Water Loop | TRANE | DXVG060A |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177504 | Water Loop | TRANE | DXVG060B |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177505 | Water Loop | TRANE | DXVG0604 |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177506 | Water Loop | TRANE | DXVG070A |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
207177507 | Water Loop | TRANE | DXVG070B |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
207177508 | Water Loop | TRANE | DXVG0704 |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
216625696 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625697 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625698 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625699 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625700 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625701 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625702 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625703 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216739926 | Water Loop | DAIKIN | WSNH036E1*C/S*C |  | 35200 | 17.4 | 42500 | 5.3 | 2.9333 | No
216739927 | Water Loop | DAIKIN | WSNH036F3*C/S*C |  | 35200 | 17.1 | 42500 | 5.2 | 2.9333 | No
216739928 | Water Loop | DAIKIN | WSNH036J1*C/S*C |  | 35200 | 17.1 | 42500 | 5.2 | 2.9333 | No
216739949 | Water Loop | DAIKIN | WSNV024E1*C/S*C |  | 23900 | 17 | 27100 | 5.2 | 1.9917 | No
216739961 | Water Loop | DAIKIN | WSNV036E1*C/S*C |  | 36700 | 18.2 | 39400 | 5.1 | 3.0583 | No
216739962 | Water Loop | DAIKIN | WSNV036F3*C/S*C |  | 36700 | 17.8 | 39400 | 5 | 3.0583 | No
216739963 | Water Loop | DAIKIN | WSNV036J1*C/S*C |  | 36700 | 17.8 | 39400 | 5 | 3.0583 | No
216739964 | Water Loop | DAIKIN | WSNV036K3*C/S*C |  | 36700 | 17.6 | 39400 | 5 | 3.0583 | No
216739969 | Water Loop | DAIKIN | WSNV042E1*C/S*C |  | 43300 | 17.1 | 49900 | 5 | 3.6083 | No
9111998 | Water Loop | BOSCH | SM036-1VT/CF*-*****B |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | No
9113183 | Water Loop | BOSCH | SM036-1VT/CF*-*****B |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | Yes
217754631 | Water Loop | DAIKIN | WSMV024F1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754632 | Water Loop | DAIKIN | WSMV024K1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754635 | Water Loop | DAIKIN | WSMV024F1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754636 | Water Loop | DAIKIN | WSMV024K1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754655 | Water Loop | DAIKIN | WSMV036F1*C/S*T |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
217754656 | Water Loop | DAIKIN | WSMV036K1*C/S*T |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
217754659 | Water Loop | DAIKIN | WSMV036F1*C/S*C |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
217754660 | Water Loop | DAIKIN | WSMV036K1*C/S*C |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
217903418 | Water Loop | WaterFurnace | V5R036*S0**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903419 | Water Loop | WaterFurnace | V5R036*S0**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903420 | Water Loop | WaterFurnace | V5R036*S0**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903430 | Water Loop | WaterFurnace | V5R036*S3**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903431 | Water Loop | WaterFurnace | V5R036*S3**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903432 | Water Loop | WaterFurnace | V5R036*S3**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903433 | Water Loop | WaterFurnace | V5R036*S4**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903434 | Water Loop | WaterFurnace | V5R036*S4**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903435 | Water Loop | WaterFurnace | V5R036*S4**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903454 | Water Loop | WaterFurnace | V5R036*D4**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903455 | Water Loop | WaterFurnace | V5R036*D4**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903456 | Water Loop | WaterFurnace | V5R036*D4**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
215399772 | Water Loop | DAIKIN | WSMV015A1*C/S*T |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215399776 | Water Loop | DAIKIN | WSMV015A1*C/S*C |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
217735426 | Water Loop | DAIKIN | WSSH024J1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
9035993 | Water Loop | GEOCOMFORT | GZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
9035994 | Water Loop | HYDRON MODULE | HZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
9035995 | Water Loop | TETCO | TZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
9035996 | Water Loop | GEOCOMFORT | GZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035997 | Water Loop | HYDRON MODULE | HZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035998 | Water Loop | TETCO | TZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035999 | Water Loop | GEOCOMFORT | GZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036000 | Water Loop | HYDRON MODULE | HZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036001 | Water Loop | TETCO | TZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036002 | Water Loop | GEOCOMFORT | GZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036003 | Water Loop | HYDRON MODULE | HZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036004 | Water Loop | TETCO | TZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036975 | Water Loop | GEOCOMFORT | GZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9036998 | Water Loop | HYDRON MODULE | HZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9037017 | Water Loop | TETCO | TZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9037062 | Water Loop | GEOCOMFORT | GZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037081 | Water Loop | HYDRON MODULE | HZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037097 | Water Loop | TETCO | TZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037137 | Water Loop | GEOCOMFORT | GZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037158 | Water Loop | HYDRON MODULE | HZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037175 | Water Loop | TETCO | TZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037215 | Water Loop | GEOCOMFORT | GZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037240 | Water Loop | HYDRON MODULE | HZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037275 | Water Loop | TETCO | TZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
217752748 | Water Loop | DAIKIN | WSTV036K1*B*C |  | 38100 | 17.89 | 41100 | 5.03 | 3.175 | No
217752752 | Water Loop | DAIKIN | WSTV048K1*B*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
217752753 | Water Loop | DAIKIN | WSTV048L1*B*C |  | 50800 | 17.09 | 58500 | 5.35 | 4.2333 | No
217754377 | Water Loop | DAIKIN | WSSH024F1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217754380 | Water Loop | DAIKIN | WSSH024F1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217754383 | Water Loop | DAIKIN | WSSH030F1*B*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
9910660 | Water Loop | GEOCOMFORT | GZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910661 | Water Loop | HYDRON MODULE | HZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910662 | Water Loop | TETCO | TZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910663 | Water Loop | GEOCOMFORT | GZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910664 | Water Loop | HYDRON MODULE | HZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910665 | Water Loop | TETCO | TZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910666 | Water Loop | GEOCOMFORT | GZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910667 | Water Loop | HYDRON MODULE | HZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910668 | Water Loop | TETCO | TZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
215268667 | Water Loop | WaterFurnace | V5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268668 | Water Loop | WaterFurnace | V5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
5220682 | Water Loop | DAIKIN | WGSV/WGSH036B*F |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220683 | Water Loop | DAIKIN | WGSV/WGSH036B*J |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220684 | Water Loop | DAIKIN | WGSV/WGSH036B*K |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220686 | Water Loop | DAIKIN | WGSV/WGSH042B*E |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220687 | Water Loop | DAIKIN | WGSV/WGSH042B*F |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220688 | Water Loop | DAIKIN | WGSV/WGSH042B*K |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220690 | Water Loop | DAIKIN | WGSV/WGSH048B*E |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220691 | Water Loop | DAIKIN | WGSV/WGSH048B*F |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220693 | Water Loop | DAIKIN | WGSV/WGSH048B*K |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220700 | Water Loop | DAIKIN | WGSV/WGSH060B*E |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
5220701 | Water Loop | DAIKIN | WGSV/WGSH060B*F |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
5220702 | Water Loop | DAIKIN | WGSV/WGSH060B*K |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
5220980 | Water Loop | DAIKIN | WGTV/WGTH038B*E |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220981 | Water Loop | DAIKIN | WGTV/WGTH038B*F |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220982 | Water Loop | DAIKIN | WGTV/WGTH038B*K |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220983 | Water Loop | DAIKIN | WGTV/WGTH044B*E |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220984 | Water Loop | DAIKIN | WGTV/WGTH044B*F |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220985 | Water Loop | DAIKIN | WGTV/WGTH044B*K |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220990 | Water Loop | DAIKIN | WGTV/WGTH064B*E |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
5220991 | Water Loop | DAIKIN | WGTV/WGTH064B*F |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
5220992 | Water Loop | DAIKIN | WGTV/WGTH064B*K |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
9910558 | Water Loop | HYDRON MODULE | HZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910559 | Water Loop | TETCO | TZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910584 | Water Loop | GEOCOMFORT | GZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910585 | Water Loop | HYDRON MODULE | HZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910586 | Water Loop | TETCO | TZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910587 | Water Loop | GEOCOMFORT | GZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910588 | Water Loop | HYDRON MODULE | HZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910589 | Water Loop | TETCO | TZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910590 | Water Loop | GEOCOMFORT | GZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910591 | Water Loop | HYDRON MODULE | HZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910592 | Water Loop | TETCO | TZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910593 | Water Loop | GEOCOMFORT | GZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910594 | Water Loop | HYDRON MODULE | HZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910595 | Water Loop | TETCO | TZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
216625542 | Water Loop | GEOSTAR | G5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625543 | Water Loop | GEOSTAR | G5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625636 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625637 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625638 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625639 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
217037792 | Water Loop | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037797 | Water Loop | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037802 | Water Loop | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037807 | Water Loop | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037812 | Water Loop | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037817 | Water Loop | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
5296014 | Water Loop | WaterFurnace | NBV/NBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296015 | Water Loop | WaterFurnace | NBV/NBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296225 | Water Loop | WaterFurnace | NBV/NBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296226 | Water Loop | WaterFurnace | NBV/NBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296227 | Water Loop | WaterFurnace | NBV/NBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296228 | Water Loop | WaterFurnace | NBV/NBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296229 | Water Loop | WaterFurnace | NBV/NBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296230 | Water Loop | WaterFurnace | NBV/NBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
215851767 | Water Loop | DAIKIN | WSTH036J1*C/S*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
215851769 | Water Loop | DAIKIN | WSTH036K3*C/S*C |  | 38000 | 17.88 | 42900 | 5.2 | 3.1667 | No
215851773 | Water Loop | DAIKIN | WSTH042K3*C/S*C |  | 44000 | 17.07 | 50300 | 4.97 | 3.6667 | No
213710594 | Water Loop | DAIKIN | WSSH007A1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
213710599 | Water Loop | DAIKIN | WSSH007J1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
216739975 | Water Loop | DAIKIN | WSNV048E1*C/S*C |  | 49300 | 17.2 | 55800 | 5.2 | 4.1083 | No
200083642 | Water Loop | COMFORT-AIRE | HZV/H/D036B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
200083643 | Water Loop | CENTURY | HZV/H/D036B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
200083644 | Water Loop | COMFORT-AIRE | HZV/H/D024B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
200083645 | Water Loop | CENTURY | HZV/H/D024B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
216772568 | Water Loop | Enertech | EVS018* |  | 21300 | 20.5 | 23700 | 6.3 | 1.775 | Yes
216772569 | Water Loop | Enertech | EVT024* |  | 24650 | 17.5 | 29100 | 5.6 | 2.0542 | No
216772586 | Water Loop | Enertech | EVS015* |  | 15775 | 19.9 | 17700 | 6.4 | 1.3146 | Yes
216772594 | Water Loop | Enertech | EZS018* |  | 19725 | 18 | 21900 | 5.5 | 1.6438 | Yes
215400162 | Water Loop | DAIKIN | WSSV007A1*B*T |  | 7100 | 17.99 | 8100 | 5.49 | 0.59167 | No
215400166 | Water Loop | DAIKIN | WSSV009A1*B*T |  | 9200 | 17.49 | 11000 | 4.98 | 0.76667 | No
215400172 | Water Loop | DAIKIN | WSSV015E1*B*T |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215400174 | Water Loop | DAIKIN | WSSV015E1*B*C |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215400176 | Water Loop | DAIKIN | WSSV019E1*B*T |  | 19700 | 17.98 | 23500 | 5.33 | 1.6417 | No
215400178 | Water Loop | DAIKIN | WSSV019E1*B*C |  | 19700 | 17.98 | 23500 | 5.33 | 1.6417 | No
215400180 | Water Loop | DAIKIN | WSSV024J1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400181 | Water Loop | DAIKIN | WSSV024K3*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400184 | Water Loop | DAIKIN | WSSV024J1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400185 | Water Loop | DAIKIN | WSSV024K3*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400188 | Water Loop | DAIKIN | WSSV030J1*B*T |  | 29200 | 18.02 | 34500 | 5.67 | 2.4333 | No
215400189 | Water Loop | DAIKIN | WSSV030K3*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215400192 | Water Loop | DAIKIN | WSSV030J1*B*C |  | 29200 | 18.02 | 34500 | 5.67 | 2.4333 | No
215400193 | Water Loop | DAIKIN | WSSV030K3*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215400196 | Water Loop | DAIKIN | WSSV036J1*B*T |  | 39000 | 17.94 | 44100 | 5.35 | 3.25 | No
215400197 | Water Loop | DAIKIN | WSSV036K3*B*T |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
215400200 | Water Loop | DAIKIN | WSSV036J1*B*C |  | 39000 | 17.94 | 44100 | 5.35 | 3.25 | No
217897465 | Water Loop | CENTURY | MJN036A | MAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
217897466 | Water Loop | COMFORT-AIRE | MJN036A | MAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
215399856 | Water Loop | DAIKIN | WSSV015A1*B*T |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215399857 | Water Loop | DAIKIN | WSSV015J1*B*T |  | 16100 | 18.01 | 18600 | 5.72 | 1.3417 | No
215399860 | Water Loop | DAIKIN | WSSV015A1*B*C |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215399861 | Water Loop | DAIKIN | WSSV015J1*B*C |  | 16100 | 18.01 | 18600 | 5.72 | 1.3417 | No
215399864 | Water Loop | DAIKIN | WSSV019J1*B*T |  | 19600 | 17.18 | 23500 | 5.23 | 1.6333 | No
215399866 | Water Loop | DAIKIN | WSSV019J1*B*C |  | 19600 | 17.18 | 23500 | 5.23 | 1.6333 | No
215399868 | Water Loop | DAIKIN | WSSV042J1*B*T |  | 42570 | 18.17 | 47124 | 5.38 | 3.5475 | No
215399869 | Water Loop | DAIKIN | WSSV042K3*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215399872 | Water Loop | DAIKIN | WSSV042J1*B*C |  | 42570 | 18.17 | 47124 | 5.38 | 3.5475 | No
215399873 | Water Loop | DAIKIN | WSSV042K3*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215399876 | Water Loop | DAIKIN | WSSV048K3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399877 | Water Loop | DAIKIN | WSSV048L3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399880 | Water Loop | DAIKIN | WSSV048K3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399881 | Water Loop | DAIKIN | WSSV048L3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399884 | Water Loop | DAIKIN | WSSV060K3*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215399886 | Water Loop | DAIKIN | WSSV060K3*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
214771934 | Water Loop | TRANE | EXVK018A |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214771935 | Water Loop | TRANE | EXVK024A |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214771936 | Water Loop | TRANE | EXVK030A |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214771937 | Water Loop | TRANE | EXVK036A |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214771938 | Water Loop | TRANE | EXVK042A |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214771939 | Water Loop | TRANE | EXVK048A |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
207335590 | Water Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335591 | Water Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
205782239 | Water Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205782243 | Water Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205788279 | Water Loop | Johnson Controls | JSH/V/D024C*K B |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | No
205788280 | Water Loop | SKYMARK | JSH/V/D024C*K C |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | No
205788283 | Water Loop | Johnson Controls | JSH/V/D036C B |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | No
205788284 | Water Loop | SKYMARK | JSH/V/D036C C |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | No
205788285 | Water Loop | Johnson Controls | JSH/V/D036C*K B |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | No
205788286 | Water Loop | SKYMARK | JSH/V/D036C*K C |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | No
205788287 | Water Loop | Johnson Controls | JSH/V/D042C B |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | No
205788288 | Water Loop | SKYMARK | JSH/V/D042C C |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | No
205788289 | Water Loop | Johnson Controls | JSH/V/D042C*K B |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
205788290 | Water Loop | SKYMARK | JSH/V/D042C*K C |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
205996643 | Water Loop | Johnson Controls | JEV/H/D026B B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | No
205996644 | Water Loop | Johnson Controls | JEV/H/D038B B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | No
207348707 | Water Loop | WaterFurnace | URD038*0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348708 | Water Loop | WaterFurnace | URD038*0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348709 | Water Loop | WaterFurnace | URD038*0*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348710 | Water Loop | WaterFurnace | URD038*3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348711 | Water Loop | WaterFurnace | URD038*3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348712 | Water Loop | WaterFurnace | URD038*3*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348713 | Water Loop | WaterFurnace | URD038*4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348714 | Water Loop | WaterFurnace | URD038*4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348715 | Water Loop | WaterFurnace | URD038*4*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348716 | Water Loop | WaterFurnace | URD049*0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348717 | Water Loop | WaterFurnace | URD049*0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348718 | Water Loop | WaterFurnace | URD049*0*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348719 | Water Loop | WaterFurnace | URD049*3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348720 | Water Loop | WaterFurnace | URD049*3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348721 | Water Loop | WaterFurnace | URD049*3*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348722 | Water Loop | WaterFurnace | URD049*4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348723 | Water Loop | WaterFurnace | URD049*4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348724 | Water Loop | WaterFurnace | URD049*4*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067584 | Water Loop | GeoSmart Energy | GBV/GBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067585 | Water Loop | GeoSmart Energy | GBV/GBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067586 | Water Loop | GeoSmart Energy | GBV/GBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067587 | Water Loop | GeoSmart Energy | GBV/GBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
215837859 | Water Loop | DAIKIN | WSSH042F3*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837860 | Water Loop | DAIKIN | WSSH042J1*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837862 | Water Loop | DAIKIN | WSSH042K3*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837867 | Water Loop | DAIKIN | WSSH042F3*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837869 | Water Loop | DAIKIN | WSSH042J1*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837870 | Water Loop | DAIKIN | WSSH042K3*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837877 | Water Loop | DAIKIN | WSSH048F3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837879 | Water Loop | DAIKIN | WSSH048K3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837880 | Water Loop | DAIKIN | WSSH048L3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837886 | Water Loop | DAIKIN | WSSH048F3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837887 | Water Loop | DAIKIN | WSSH048K3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837889 | Water Loop | DAIKIN | WSSH048L3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837895 | Water Loop | DAIKIN | WSSH060F3*C/S*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837896 | Water Loop | DAIKIN | WSSH060K3*C/S*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837904 | Water Loop | DAIKIN | WSSH060F3*C/S*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837905 | Water Loop | DAIKIN | WSSH060K3*C/S*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837913 | Water Loop | DAIKIN | WSSH070F3*C/S*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837914 | Water Loop | DAIKIN | WSSH070K3*C/S*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837922 | Water Loop | DAIKIN | WSSH070F3*C/S*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837923 | Water Loop | DAIKIN | WSSH070K3*C/S*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215851754 | Water Loop | DAIKIN | WSTH024J1*C/S*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
215851756 | Water Loop | DAIKIN | WSTH024K3*C/S*C |  | 24500 | 17 | 26100 | 5.14 | 2.0417 | No
201907610 | Water Loop | WaterFurnace | URS036*0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907611 | Water Loop | WaterFurnace | URS036*0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907612 | Water Loop | WaterFurnace | URS036*0*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907613 | Water Loop | WaterFurnace | URS036*3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907614 | Water Loop | WaterFurnace | URS036*3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907615 | Water Loop | WaterFurnace | URS036*3*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907616 | Water Loop | WaterFurnace | URS036*4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907617 | Water Loop | WaterFurnace | URS036*4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907618 | Water Loop | WaterFurnace | URS036*4*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214823446 | Water Loop | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
217903468 | Water Loop | WaterFurnace | V5R036*D0**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903469 | Water Loop | WaterFurnace | V5R036*D0**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903470 | Water Loop | WaterFurnace | V5R036*D0**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903471 | Water Loop | WaterFurnace | V5R036*D3**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903472 | Water Loop | WaterFurnace | V5R036*D3**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903473 | Water Loop | WaterFurnace | V5R036*D3**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
211127895 | Water Loop | WaterFurnace | NVV/NVH036D1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
211127898 | Water Loop | GEOSTAR | 141/142D036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
215400094 | Water Loop | DAIKIN | WSMV024E1*C/S*T |  | 24700 | 18.03 | 28600 | 5.25 | 2.0583 | No
215400095 | Water Loop | DAIKIN | WSMV024F3*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215400098 | Water Loop | DAIKIN | WSMV024E1*C/S*C |  | 24700 | 18.03 | 28600 | 5.25 | 2.0583 | No
215400099 | Water Loop | DAIKIN | WSMV024F3*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
213502571 | Water Loop | DAIKIN | WSCH042E1*C/S*T |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
213502572 | Water Loop | DAIKIN | WSCH042E1*C/S*C |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
217754473 | Water Loop | DAIKIN | WSTH024E1*B*C |  | 24500 | 17.53 | 26100 | 5.29 | 2.0417 | No
217754474 | Water Loop | DAIKIN | WSTH024F1*B*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
217754477 | Water Loop | DAIKIN | WSTH030E1*B*C |  | 31400 | 17.12 | 34900 | 5.36 | 2.6167 | No
217754481 | Water Loop | DAIKIN | WSTH036E1*B*C |  | 38000 | 18.43 | 42900 | 5.36 | 3.1667 | No
217754482 | Water Loop | DAIKIN | WSTH036F1*B*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
217754485 | Water Loop | DAIKIN | WSTH042E1*B*C |  | 44000 | 17.59 | 50300 | 5.12 | 3.6667 | No
217754486 | Water Loop | DAIKIN | WSTH042F1*B*C |  | 44000 | 17.24 | 50300 | 5.02 | 3.6667 | No
217754489 | Water Loop | DAIKIN | WSTH048E1*B*C |  | 48200 | 17.34 | 56900 | 5.08 | 4.0167 | No
213154467 | Water Loop | GeoSmart Energy | GS030**1*1********L |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
213154468 | Water Loop | GeoSmart Energy | GS036**1*1********L |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
213154469 | Water Loop | GeoSmart Energy | GS042**1*1********L |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
205129920 | Water Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205129921 | Water Loop | GEOSTAR | 103J036**1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
216625471 | Water Loop | GEOSTAR | G5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625472 | Water Loop | GEOSTAR | G5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625473 | Water Loop | GEOSTAR | G5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625474 | Water Loop | GEOSTAR | G5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625475 | Water Loop | GEOSTAR | G5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625476 | Water Loop | GEOSTAR | G5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625477 | Water Loop | GEOSTAR | G5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625478 | Water Loop | GEOSTAR | G5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625479 | Water Loop | GEOSTAR | G5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625480 | Water Loop | GEOSTAR | G5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625481 | Water Loop | GEOSTAR | G5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625482 | Water Loop | GEOSTAR | G5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625483 | Water Loop | GEOSTAR | G5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625484 | Water Loop | GEOSTAR | G5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625485 | Water Loop | GEOSTAR | G5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625486 | Water Loop | GEOSTAR | G5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625487 | Water Loop | GEOSTAR | G5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625488 | Water Loop | GEOSTAR | G5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625489 | Water Loop | GEOSTAR | G5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625490 | Water Loop | GEOSTAR | G5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625491 | Water Loop | GEOSTAR | G5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625492 | Water Loop | GEOSTAR | G5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625493 | Water Loop | GEOSTAR | G5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625494 | Water Loop | GEOSTAR | G5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625495 | Water Loop | GEOSTAR | G5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625496 | Water Loop | GEOSTAR | G5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625497 | Water Loop | GEOSTAR | G5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625498 | Water Loop | GEOSTAR | G5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625499 | Water Loop | GEOSTAR | G5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625500 | Water Loop | GEOSTAR | G5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625501 | Water Loop | GEOSTAR | G5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625502 | Water Loop | GEOSTAR | G5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625503 | Water Loop | GEOSTAR | G5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625504 | Water Loop | GEOSTAR | G5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
9910752 | Water Loop | GEOCOMFORT | GZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910753 | Water Loop | HYDRON MODULE | HZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910754 | Water Loop | TETCO | TZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910755 | Water Loop | GEOCOMFORT | GZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910756 | Water Loop | HYDRON MODULE | HZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910757 | Water Loop | TETCO | TZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910758 | Water Loop | GEOCOMFORT | GZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910759 | Water Loop | HYDRON MODULE | HZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910760 | Water Loop | TETCO | TZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
203495469 | Water Loop | GEOSTAR | 101/102J049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
215866231 | Water Loop | ClimateMaster | SMT24A*L |  | 25000 | 17.6 | 28000 | 5.1 | 2.0833 | No
215866538 | Water Loop | DAIKIN | WSTH048E1*C/S*C |  | 48200 | 17.34 | 56900 | 5.08 | 4.0167 | No
206194171 | Water Loop | Johnson Controls | JSH/V/D030C*K B |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
206194172 | Water Loop | SKYMARK | JSH/V/D030C*K C |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
206194173 | Water Loop | Johnson Controls | JSH/V/D048C*K B |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | No
206194174 | Water Loop | SKYMARK | JSH/V/D048C*K C |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | No
206194175 | Water Loop | Johnson Controls | JSH/V/D060C*K B |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | No
206194176 | Water Loop | SKYMARK | JSH/V/D060C*K C |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | No
215837701 | Water Loop | DAIKIN | WSMH030K3*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
215837707 | Water Loop | DAIKIN | WSMH030F3*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
215837709 | Water Loop | DAIKIN | WSMH030K3*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
7421327 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421397 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421438 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421969 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421970 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7422309 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
217967038 | Water Loop | TRANE | VSHK0244 |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217967039 | Water Loop | TRANE | VSVK0244 |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967041 | Water Loop | TRANE | VSVK0334 |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967042 | Water Loop | TRANE | VSHK0424 |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967043 | Water Loop | TRANE | VSVK0424 |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
217967045 | Water Loop | TRANE | VSVK0504 |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
205767605 | Water Loop | ClimateMaster | VEV/H/D1860 |  | 48000 | 17.3 | 60000 | 5.5 | 4 | Yes
205767606 | Water Loop | ClimateMaster | VEV/H/D0930 |  | 24000 | 19.3 | 30000 | 6.6 | 2 | Yes
8735903 | Water Loop | GEOCOMFORT | GVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735904 | Water Loop | HYDRON MODULE | HVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735905 | Water Loop | TETCO | TVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735906 | Water Loop | GEOCOMFORT | GVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735907 | Water Loop | HYDRON MODULE | HVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735908 | Water Loop | TETCO | TVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735909 | Water Loop | GEOCOMFORT | GVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735910 | Water Loop | HYDRON MODULE | HVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735911 | Water Loop | TETCO | TVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
202835053 | Water Loop | BOSCH | SM036-1HZ*-*****C |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
202836307 | Water Loop | BOSCH | SM036-1VT*-*****C |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | Yes
206342120 | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206342121 | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206342122 | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206345837 | Water Loop | HYDROTECH | WSS6006*7* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
206346927 | Water Loop | DAIKIN | WVFC*030*K***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
217735427 | Water Loop | DAIKIN | WSSH024J1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217735428 | Water Loop | DAIKIN | WSSH030J1*B*T |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
217735429 | Water Loop | DAIKIN | WSSH030J1*B*C |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
217735430 | Water Loop | DAIKIN | WSSH036J1*B*T |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
217735431 | Water Loop | DAIKIN | WSSH036J1*B*C |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
217735432 | Water Loop | DAIKIN | WSSH042J1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217735433 | Water Loop | DAIKIN | WSSH042J1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217735434 | Water Loop | DAIKIN | WSTH024J1*B*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
217735438 | Water Loop | DAIKIN | WSTH036J1*B*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
217735440 | Water Loop | DAIKIN | WSTV024J1*B*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
217735444 | Water Loop | DAIKIN | WSTV036J1*B*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
205767514 | Water Loop | ClimateMaster | TSH/V/D024C*K |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | Yes
205767516 | Water Loop | ClimateMaster | TSH/V/D030C*K |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
205767517 | Water Loop | ClimateMaster | TSH/V/D036C |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | Yes
205767518 | Water Loop | ClimateMaster | TSH/V/D036C*K |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | Yes
205767519 | Water Loop | ClimateMaster | TSH/V/D042C |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | Yes
205767520 | Water Loop | ClimateMaster | TSH/V/D042C*K |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
205767521 | Water Loop | ClimateMaster | TSH/V/D048C*K |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | Yes
205767523 | Water Loop | ClimateMaster | TSH/V/D060C*K |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | Yes
215415919 | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | No
215415920 | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | No
215415921 | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | No
215415922 | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | No
215415923 | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | No
215415924 | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | No
8740368 | Water Loop | GEOCOMFORT | GVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
8740369 | Water Loop | HYDRON MODULE | HVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
8740370 | Water Loop | TETCO | TVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
8740371 | Water Loop | GEOCOMFORT | GVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740372 | Water Loop | HYDRON MODULE | HVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740373 | Water Loop | TETCO | TVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740374 | Water Loop | GEOCOMFORT | GVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740375 | Water Loop | HYDRON MODULE | HVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740376 | Water Loop | TETCO | TVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
215400080 | Water Loop | DAIKIN | WSMV015E1*C/S*T |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215400082 | Water Loop | DAIKIN | WSMV015E1*C/S*C |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
7499702 | Water Loop | BOSCH | SM036-1CF/HZ/VT |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
5317193 | Water Loop | WaterFurnace | NBV/NBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317194 | Water Loop | WaterFurnace | NBV/NBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317195 | Water Loop | WaterFurnace | NBV/NBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317196 | Water Loop | WaterFurnace | NBV/NBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317197 | Water Loop | WaterFurnace | NBV/NBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317198 | Water Loop | WaterFurnace | NBV/NBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317199 | Water Loop | WaterFurnace | NBV/NBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317200 | Water Loop | WaterFurnace | NBV/NBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317201 | Water Loop | WaterFurnace | NBV/NBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317202 | Water Loop | WaterFurnace | NBV/NBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317203 | Water Loop | WaterFurnace | NBV/NBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317205 | Water Loop | WaterFurnace | NBV/NBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317206 | Water Loop | WaterFurnace | NBV/NBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317207 | Water Loop | WaterFurnace | NBV/NBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317332 | Water Loop | WaterFurnace | NBV/NBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
216625770 | Water Loop | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625771 | Water Loop | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625772 | Water Loop | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625773 | Water Loop | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625774 | Water Loop | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625775 | Water Loop | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625776 | Water Loop | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625777 | Water Loop | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625778 | Water Loop | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625779 | Water Loop | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625780 | Water Loop | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625781 | Water Loop | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625782 | Water Loop | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625783 | Water Loop | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625784 | Water Loop | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625785 | Water Loop | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625786 | Water Loop | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625787 | Water Loop | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625788 | Water Loop | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625789 | Water Loop | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625790 | Water Loop | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625791 | Water Loop | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625792 | Water Loop | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625793 | Water Loop | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625794 | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625795 | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625796 | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625797 | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625798 | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625799 | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625800 | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625801 | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625802 | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625803 | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625804 | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625805 | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625806 | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625807 | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268725 | Water Loop | WaterFurnace | V5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268734 | Water Loop | WaterFurnace | V5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
213711986 | Water Loop | DAIKIN | WSSH060E1*B*C |  | 60872 | 17.4 | 78027 | 5.72 | 5.0727 | No
213714593 | Water Loop | DAIKIN | WSSH070E1*B*T |  | 70700 | 17.29 | 83100 | 4.81 | 5.8917 | No
213714595 | Water Loop | DAIKIN | WSSH070E1*B*C |  | 70700 | 17.29 | 83100 | 4.81 | 5.8917 | No
214063753 | Water Loop | GeoSmart Energy | GBV/GBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063754 | Water Loop | GeoSmart Energy | GBV/GBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063756 | Water Loop | GeoSmart Energy | GBV/GBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063757 | Water Loop | GeoSmart Energy | GBV/GBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063762 | Water Loop | GeoSmart Energy | GBV/GBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214063763 | Water Loop | GeoSmart Energy | GBV/GBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063764 | Water Loop | GeoSmart Energy | GBV/GBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063765 | Water Loop | GeoSmart Energy | GBV/GBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214063766 | Water Loop | GeoSmart Energy | GBV/GBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063767 | Water Loop | GeoSmart Energy | GBV/GBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063769 | Water Loop | GeoSmart Energy | GBV/GBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063770 | Water Loop | GeoSmart Energy | GBV/GBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063772 | Water Loop | GeoSmart Energy | GBV/GBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063773 | Water Loop | GeoSmart Energy | GBV/GBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063774 | Water Loop | GeoSmart Energy | GBV/GBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063775 | Water Loop | GeoSmart Energy | GBV/GBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063776 | Water Loop | GeoSmart Energy | GBV/GBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063777 | Water Loop | GeoSmart Energy | GBV/GBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063778 | Water Loop | GeoSmart Energy | GBV/GBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214063779 | Water Loop | GeoSmart Energy | GBV/GBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214063780 | Water Loop | GeoSmart Energy | GBV/GBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214063781 | Water Loop | GeoSmart Energy | GBV/GBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
215837810 | Water Loop | DAIKIN | WSSH024F3*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837811 | Water Loop | DAIKIN | WSSH024J1*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837813 | Water Loop | DAIKIN | WSSH024K3*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
216439574 | Water Loop | GeoSmart Energy | S5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
214771940 | Water Loop | TRANE | EXVK060A |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214771941 | Water Loop | TRANE | EXVK070A |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214771953 | Water Loop | TRANE | EXHK009A |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214771954 | Water Loop | TRANE | EXHK012A |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214771956 | Water Loop | TRANE | EXHK018A |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214771957 | Water Loop | TRANE | EXHK024A |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214771958 | Water Loop | TRANE | EXHK030A |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214771959 | Water Loop | TRANE | EXHK036A |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214771960 | Water Loop | TRANE | EXHK042A |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214771961 | Water Loop | TRANE | EXHK048A |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214771962 | Water Loop | TRANE | EXHK060A |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214771963 | Water Loop | TRANE | EXHK070A |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
217754386 | Water Loop | DAIKIN | WSSH030F1*B*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217754389 | Water Loop | DAIKIN | WSSH036F1*B*T |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
217754392 | Water Loop | DAIKIN | WSSH036F1*B*C |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
217754395 | Water Loop | DAIKIN | WSSH042F1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217754398 | Water Loop | DAIKIN | WSSH042F1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217754401 | Water Loop | DAIKIN | WSSH048F1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217754405 | Water Loop | DAIKIN | WSSH048F1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217754409 | Water Loop | DAIKIN | WSSH060F1*B*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217754413 | Water Loop | DAIKIN | WSSH060F1*B*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217754417 | Water Loop | DAIKIN | WSSH070F1*B*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217754421 | Water Loop | DAIKIN | WSSH070F1*B*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217754425 | Water Loop | DAIKIN | WSSV024F1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217754428 | Water Loop | DAIKIN | WSSV024F1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217754431 | Water Loop | DAIKIN | WSSV030F1*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217754434 | Water Loop | DAIKIN | WSSV030F1*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217754437 | Water Loop | DAIKIN | WSSV036F1*B*T |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
217754440 | Water Loop | DAIKIN | WSSV036F1*B*C |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
215827093 | Water Loop | DAIKIN | WSLV072F1*C/S |  | 74000 | 17 | 87000 | 5.2 | 6.1667 | No
215827095 | Water Loop | DAIKIN | WSLV072K1*C/S |  | 74000 | 17 | 87000 | 5.2 | 6.1667 | No
215827097 | Water Loop | DAIKIN | WSLV072L1*C/S |  | 74000 | 17 | 87000 | 5.1 | 6.1667 | No
217752676 | Water Loop | DAIKIN | WSSH024K1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217752678 | Water Loop | DAIKIN | WSSH024K1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217752680 | Water Loop | DAIKIN | WSSH030K1*B*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217752682 | Water Loop | DAIKIN | WSSH030K1*B*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217752684 | Water Loop | DAIKIN | WSSH036K1*B*T |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
217752686 | Water Loop | DAIKIN | WSSH036K1*B*C |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
217752688 | Water Loop | DAIKIN | WSSH042K1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217752690 | Water Loop | DAIKIN | WSSH042K1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217752692 | Water Loop | DAIKIN | WSSH048K1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752693 | Water Loop | DAIKIN | WSSH048L1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752694 | Water Loop | DAIKIN | WSSH048K1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752695 | Water Loop | DAIKIN | WSSH048L1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752696 | Water Loop | DAIKIN | WSSH060K1*B*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217752698 | Water Loop | DAIKIN | WSSH060K1*B*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217752700 | Water Loop | DAIKIN | WSSH070K1*B*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217752702 | Water Loop | DAIKIN | WSSH070K1*B*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217752704 | Water Loop | DAIKIN | WSSV024K1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217752705 | Water Loop | DAIKIN | WSSV024K1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217752706 | Water Loop | DAIKIN | WSSV030K1*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217752707 | Water Loop | DAIKIN | WSSV030K1*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217752708 | Water Loop | DAIKIN | WSSV036K1*B*T |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
217752709 | Water Loop | DAIKIN | WSSV036K1*B*C |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
217752710 | Water Loop | DAIKIN | WSSV042K1*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217752711 | Water Loop | DAIKIN | WSSV042K1*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217752712 | Water Loop | DAIKIN | WSSV048K1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752713 | Water Loop | DAIKIN | WSSV048L1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752714 | Water Loop | DAIKIN | WSSV048K1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752715 | Water Loop | DAIKIN | WSSV048L1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752716 | Water Loop | DAIKIN | WSSV060K1*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
9910548 | Water Loop | GEOCOMFORT | GZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910549 | Water Loop | HYDRON MODULE | HZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910550 | Water Loop | TETCO | TZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910551 | Water Loop | GEOCOMFORT | GZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910552 | Water Loop | HYDRON MODULE | HZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910553 | Water Loop | TETCO | TZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910554 | Water Loop | GEOCOMFORT | GZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910555 | Water Loop | HYDRON MODULE | HZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910556 | Water Loop | TETCO | TZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910557 | Water Loop | GEOCOMFORT | GZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
206570652 | Water Loop | GEOSTAR | 141/142C036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
206598629 | Water Loop | GeoSmart Energy | VI036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
206598632 | Water Loop | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
5295984 | Water Loop | WaterFurnace | NBV/NBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295985 | Water Loop | WaterFurnace | NBV/NBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295986 | Water Loop | WaterFurnace | NBV/NBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295987 | Water Loop | WaterFurnace | NBV/NBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295988 | Water Loop | WaterFurnace | NBV/NBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295989 | Water Loop | WaterFurnace | NBV/NBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295990 | Water Loop | WaterFurnace | NBV/NBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295991 | Water Loop | WaterFurnace | NBV/NBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295992 | Water Loop | WaterFurnace | NBV/NBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295993 | Water Loop | WaterFurnace | NBV/NBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295994 | Water Loop | WaterFurnace | NBV/NBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295995 | Water Loop | WaterFurnace | NBV/NBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295996 | Water Loop | WaterFurnace | NBV/NBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5295997 | Water Loop | WaterFurnace | NBV/NBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5295998 | Water Loop | WaterFurnace | NBV/NBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5295999 | Water Loop | WaterFurnace | NBV/NBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296000 | Water Loop | WaterFurnace | NBV/NBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296001 | Water Loop | WaterFurnace | NBV/NBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296002 | Water Loop | WaterFurnace | NBV/NBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296003 | Water Loop | WaterFurnace | NBV/NBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296008 | Water Loop | WaterFurnace | NBV/NBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296009 | Water Loop | WaterFurnace | NBV/NBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296010 | Water Loop | WaterFurnace | NBV/NBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296011 | Water Loop | WaterFurnace | NBV/NBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296012 | Water Loop | WaterFurnace | NBV/NBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296013 | Water Loop | WaterFurnace | NBV/NBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067608 | Water Loop | GeoSmart Energy | GBV/GBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
213710602 | Water Loop | DAIKIN | WSSH009A1*B*T |  | 9100 | 18 | 11200 | 5.6 | 0.75833 | No
213710607 | Water Loop | DAIKIN | WSSH009J1*B*T |  | 9100 | 17 | 11200 | 5.4 | 0.75833 | No
213710618 | Water Loop | DAIKIN | WSSH015A1*B*T |  | 16100 | 19.7 | 18000 | 5.76 | 1.3417 | No
213710619 | Water Loop | DAIKIN | WSSH015A1*B*C |  | 16100 | 19.7 | 18000 | 5.76 | 1.3417 | No
213710626 | Water Loop | DAIKIN | WSSH015J1*B*T |  | 16100 | 18.2 | 18000 | 5.7 | 1.3417 | No
213710627 | Water Loop | DAIKIN | WSSH015J1*B*C |  | 16100 | 18.2 | 18000 | 5.7 | 1.3417 | No
213710636 | Water Loop | DAIKIN | WSSH019J1*B*T |  | 19900 | 17.7 | 23300 | 5.3 | 1.6583 | No
213710637 | Water Loop | DAIKIN | WSSH019J1*B*C |  | 19900 | 17.7 | 23300 | 5.3 | 1.6583 | No
213711957 | Water Loop | DAIKIN | WSSH007E1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
213711959 | Water Loop | DAIKIN | WSSH009E1*B*T |  | 9100 | 18 | 11200 | 5.6 | 0.75833 | No
213711963 | Water Loop | DAIKIN | WSSH015E1*B*T |  | 16100 | 19.95 | 18000 | 5.76 | 1.3417 | No
213711964 | Water Loop | DAIKIN | WSSH015E1*B*C |  | 16100 | 19.95 | 18000 | 5.76 | 1.3417 | No
213711966 | Water Loop | DAIKIN | WSSH019E1*B*T |  | 19900 | 18 | 23300 | 5.3 | 1.6583 | No
213711967 | Water Loop | DAIKIN | WSSH019E1*B*C |  | 19900 | 18 | 23300 | 5.3 | 1.6583 | No
213711969 | Water Loop | DAIKIN | WSSH024E1*B*T |  | 24500 | 18.1 | 28000 | 5.8 | 2.0417 | No
213711970 | Water Loop | DAIKIN | WSSH024E1*B*C |  | 24500 | 18.1 | 28000 | 5.8 | 2.0417 | No
213711972 | Water Loop | DAIKIN | WSSH030E1*B*T |  | 29500 | 19.3 | 34500 | 6 | 2.4583 | No
213711974 | Water Loop | DAIKIN | WSSH030E1*B*C |  | 29500 | 19.3 | 34500 | 6 | 2.4583 | No
213711975 | Water Loop | DAIKIN | WSSH036E1*B*T |  | 39000 | 19.3 | 44600 | 5.2 | 3.25 | No
213711976 | Water Loop | DAIKIN | WSSH036E1*B*C |  | 39000 | 19.3 | 44600 | 5.2 | 3.25 | No
213711978 | Water Loop | DAIKIN | WSSH042E1*B*T |  | 42600 | 18.4 | 47000 | 5.4 | 3.55 | No
213711979 | Water Loop | DAIKIN | WSSH042E1*B*C |  | 42600 | 18.4 | 47000 | 5.4 | 3.55 | No
217754501 | Water Loop | DAIKIN | WSTV024E1*B*C |  | 24300 | 17.59 | 28000 | 5.81 | 2.025 | No
217754502 | Water Loop | DAIKIN | WSTV024F1*B*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
217754509 | Water Loop | DAIKIN | WSTV036E1*B*C |  | 38100 | 18.45 | 41100 | 5.18 | 3.175 | No
217754510 | Water Loop | DAIKIN | WSTV036F1*B*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
217754513 | Water Loop | DAIKIN | WSTV042E1*B*C |  | 43500 | 17.3 | 50000 | 5.06 | 3.625 | No
217754517 | Water Loop | DAIKIN | WSTV048E1*B*C |  | 50800 | 17.62 | 58500 | 5.52 | 4.2333 | No
217754518 | Water Loop | DAIKIN | WSTV048F1*B*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
217754521 | Water Loop | DAIKIN | WSTV060E1*B*C |  | 60500 | 17.3 | 74700 | 5.5 | 5.0417 | No
217754537 | Water Loop | DAIKIN | WSMH024F1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754538 | Water Loop | DAIKIN | WSMH024K1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754541 | Water Loop | DAIKIN | WSMH024F1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754542 | Water Loop | DAIKIN | WSMH024K1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754549 | Water Loop | DAIKIN | WSMH030F1*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754550 | Water Loop | DAIKIN | WSMH030K1*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
216625640 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625641 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625642 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625643 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625644 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
214772135 | Water Loop | TRANE | EXHK048B |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772136 | Water Loop | TRANE | EXHK0484 |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772137 | Water Loop | TRANE | EXHK060B |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772138 | Water Loop | TRANE | EXHK0604 |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772139 | Water Loop | TRANE | EXHK070B |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772140 | Water Loop | TRANE | EXHK0704 |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772141 | Water Loop | TRANE | DXHK024A |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772142 | Water Loop | TRANE | DXHK036A |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772143 | Water Loop | TRANE | DXHK048A |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772144 | Water Loop | TRANE | DXHK060A |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772146 | Water Loop | TRANE | DXVK024B |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772147 | Water Loop | TRANE | DXVK0244 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772148 | Water Loop | TRANE | DXVK036B |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772149 | Water Loop | TRANE | DXVK0364 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772150 | Water Loop | TRANE | DXVK048B |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772151 | Water Loop | TRANE | DXVK0484 |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772152 | Water Loop | TRANE | DXVK060B |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772153 | Water Loop | TRANE | DXVK0604 |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772156 | Water Loop | TRANE | DXHK024B |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772157 | Water Loop | TRANE | DXHK0244 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772158 | Water Loop | TRANE | DXHK036B |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772159 | Water Loop | TRANE | DXHK0364 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772160 | Water Loop | TRANE | DXHK048B |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772161 | Water Loop | TRANE | DXHK0484 |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772162 | Water Loop | TRANE | DXHK060B |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772163 | Water Loop | TRANE | DXHK0604 |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772166 | Water Loop | TRANE | DXVK0247 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772167 | Water Loop | TRANE | DXVK0367 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772168 | Water Loop | TRANE | DXHK0247 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772169 | Water Loop | TRANE | DXHK0367 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
206199262 | Water Loop | RHEEM | RPVV/H/D026D |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
215400114 | Water Loop | DAIKIN | WSMV036E1*C/S*P |  | 37300 | 17.25 | 43000 | 5.02 | 3.1083 | No
215400118 | Water Loop | DAIKIN | WSMV036E1*C/S*T |  | 37200 | 17.68 | 43100 | 5.17 | 3.1 | No
215400119 | Water Loop | DAIKIN | WSMV036F3*C/S*T |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
215400122 | Water Loop | DAIKIN | WSMV036E1*C/S*C |  | 37200 | 17.68 | 43100 | 5.17 | 3.1 | No
215400123 | Water Loop | DAIKIN | WSMV036F3*C/S*C |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
215400130 | Water Loop | DAIKIN | WSMV042E1*C/S*T |  | 41200 | 17.13 | 49300 | 5.36 | 3.4333 | No
215400134 | Water Loop | DAIKIN | WSMV042E1*C/S*C |  | 41200 | 17.13 | 49300 | 5.36 | 3.4333 | No
207312172 | Water Loop | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207312173 | Water Loop | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207312225 | Water Loop | WaterFurnace | NSV/NSH030J1*(1,4) |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207312226 | Water Loop | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207312227 | Water Loop | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207312265 | Water Loop | WaterFurnace | NSV/NSH030J1*(0,3) |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | Yes
215268745 | Water Loop | WaterFurnace | V5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268746 | Water Loop | WaterFurnace | V5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268747 | Water Loop | WaterFurnace | V5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268748 | Water Loop | WaterFurnace | V5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268749 | Water Loop | WaterFurnace | V5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268750 | Water Loop | WaterFurnace | V5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268751 | Water Loop | WaterFurnace | V5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268752 | Water Loop | WaterFurnace | V5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268753 | Water Loop | WaterFurnace | V5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268754 | Water Loop | WaterFurnace | V5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268775 | Water Loop | WaterFurnace | V5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268776 | Water Loop | WaterFurnace | V5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268777 | Water Loop | WaterFurnace | V5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268778 | Water Loop | WaterFurnace | V5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268779 | Water Loop | WaterFurnace | V5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268780 | Water Loop | WaterFurnace | V5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
202443461 | Water Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
202443470 | Water Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
6501954 | Water Loop | GEOSTAR | GBV/GBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501955 | Water Loop | GEOSTAR | GBV/GBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501957 | Water Loop | GEOSTAR | GBV/GBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501958 | Water Loop | GEOSTAR | GBV/GBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501970 | Water Loop | GEOSTAR | GBV/GBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501971 | Water Loop | GEOSTAR | GBV/GBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501972 | Water Loop | GEOSTAR | GBV/GBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207200598 | Water Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207200605 | Water Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
217193306 | Water Loop | WaterFurnace | V7A(V/H)024*V0**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193307 | Water Loop | WaterFurnace | V7A(V/H)036*V0**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
217193552 | Water Loop | WaterFurnace | V7A(V/H)024*V3**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193553 | Water Loop | WaterFurnace | V7A(V/H)024*V4**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193554 | Water Loop | WaterFurnace | V7A(V/H)036*V3**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
217193555 | Water Loop | WaterFurnace | V7A(V/H)036*V4**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
205767615 | Water Loop | ClimateMaster | QEV/H/D0930 |  | 24000 | 19.3 | 30000 | 6.6 | 2 | Yes
215268669 | Water Loop | WaterFurnace | V5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268670 | Water Loop | WaterFurnace | V5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268682 | Water Loop | WaterFurnace | V5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268683 | Water Loop | WaterFurnace | V5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268684 | Water Loop | WaterFurnace | V5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268685 | Water Loop | WaterFurnace | V5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268686 | Water Loop | WaterFurnace | V5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268687 | Water Loop | WaterFurnace | V5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268688 | Water Loop | WaterFurnace | V5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268689 | Water Loop | WaterFurnace | V5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268690 | Water Loop | WaterFurnace | V5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268691 | Water Loop | WaterFurnace | V5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268692 | Water Loop | WaterFurnace | V5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268693 | Water Loop | WaterFurnace | V5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268694 | Water Loop | WaterFurnace | V5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268695 | Water Loop | WaterFurnace | V5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268696 | Water Loop | WaterFurnace | V5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268697 | Water Loop | WaterFurnace | V5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268698 | Water Loop | WaterFurnace | V5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268699 | Water Loop | WaterFurnace | V5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268700 | Water Loop | WaterFurnace | V5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268701 | Water Loop | WaterFurnace | V5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268713 | Water Loop | WaterFurnace | V5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268714 | Water Loop | WaterFurnace | V5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268715 | Water Loop | WaterFurnace | V5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268716 | Water Loop | WaterFurnace | V5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268717 | Water Loop | WaterFurnace | V5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268718 | Water Loop | WaterFurnace | V5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268719 | Water Loop | WaterFurnace | V5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268720 | Water Loop | WaterFurnace | V5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268721 | Water Loop | WaterFurnace | V5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268722 | Water Loop | WaterFurnace | V5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268723 | Water Loop | WaterFurnace | V5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268724 | Water Loop | WaterFurnace | V5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216759827 | Water Loop | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216759832 | Water Loop | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | No
213502523 | Water Loop | DAIKIN | WSMH015A1*C/S*T |  | 15500 | 17.8 | 19900 | 5.9 | 1.2917 | No
213502524 | Water Loop | DAIKIN | WSMH015A1*C/S*C |  | 15500 | 17.8 | 19900 | 5.9 | 1.2917 | No
213502529 | Water Loop | DAIKIN | WSMH015E1*C/S*T |  | 15500 | 17.8 | 20000 | 5.9 | 1.2917 | No
213502530 | Water Loop | DAIKIN | WSMH015E1*C/S*C |  | 15500 | 17.8 | 20000 | 5.9 | 1.2917 | No
213502535 | Water Loop | DAIKIN | WSMH015J1*C/S*T |  | 15400 | 17 | 20000 | 5.8 | 1.2833 | No
213502536 | Water Loop | DAIKIN | WSMH015J1*C/S*C |  | 15400 | 17 | 20000 | 5.8 | 1.2833 | No
213502541 | Water Loop | DAIKIN | WSMH019E1*C/S*T |  | 19700 | 17 | 24200 | 5.2 | 1.6417 | No
213502542 | Water Loop | DAIKIN | WSMH019E1*C/S*C |  | 19700 | 17 | 24200 | 5.2 | 1.6417 | No
213502547 | Water Loop | DAIKIN | WSMH019J1*C/S*T |  | 19700 | 17 | 24200 | 5.1 | 1.6417 | No
213502548 | Water Loop | DAIKIN | WSMH019J1*C/S*C |  | 19700 | 17 | 24200 | 5.1 | 1.6417 | No
213502553 | Water Loop | DAIKIN | WSMH024E1*C/S*T |  | 24800 | 17.5 | 30700 | 5.6 | 2.0667 | No
213502554 | Water Loop | DAIKIN | WSMH024E1*C/S*C |  | 24800 | 17.5 | 30700 | 5.6 | 2.0667 | No
213502559 | Water Loop | DAIKIN | WSMH030E1*C/S*T |  | 28300 | 17.6 | 35300 | 5.7 | 2.3583 | No
213502560 | Water Loop | DAIKIN | WSMH030E1*C/S*C |  | 28300 | 17.6 | 35300 | 5.7 | 2.3583 | No
213502565 | Water Loop | DAIKIN | WSMH036E1*C/S*T |  | 36500 | 17.2 | 48300 | 5.4 | 3.0417 | No
213502566 | Water Loop | DAIKIN | WSMH036E1*C/S*C |  | 36500 | 17.2 | 48300 | 5.4 | 3.0417 | No
203380966 | Water Loop | BOSCH | EP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203380967 | Water Loop | BOSCH | EP042-3HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203380968 | Water Loop | BOSCH | EP042-4HZ*******B |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
203383883 | Water Loop | CARRIER | 50PSH042***3/CA |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383884 | Water Loop | CARRIER | 50PSH042***5/EA |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383885 | Water Loop | CARRIER | 50PSH042***6/FA |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
7167538 | Water Loop | CARRIER | 50PTD/H/V024***3/CA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167539 | Water Loop | CARRIER | 50PTD/H/V024***5/EA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
214823447 | Water Loop | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
214823482 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214823484 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
207323903 | Water Loop | WaterFurnace | NSZ036J1* | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207323912 | Water Loop | WaterFurnace | NSZ036J1* | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207324064 | Water Loop | WaterFurnace | NVV/NVH036C1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
207335136 | Water Loop | GEOSTAR | 101/102J030**1*(1,4)***** |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335137 | Water Loop | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207335138 | Water Loop | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207335143 | Water Loop | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335144 | Water Loop | GEOSTAR | 101/102K049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335251 | Water Loop | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335253 | Water Loop | GEOSTAR | 161/162K049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
8560938 | Water Loop | GEOCOMFORT | GVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560939 | Water Loop | HYDRON MODULE | HVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560940 | Water Loop | TETCO | TVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560941 | Water Loop | GEOCOMFORT | GVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560942 | Water Loop | HYDRON MODULE | HVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560943 | Water Loop | TETCO | TVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560946 | Water Loop | GEOCOMFORT | GVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
8560947 | Water Loop | HYDRON MODULE | HVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
8560948 | Water Loop | TETCO | TVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
8560949 | Water Loop | GEOCOMFORT | GVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
8560950 | Water Loop | HYDRON MODULE | HVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
8560951 | Water Loop | TETCO | TVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
203254609 | Water Loop | HEIL | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254610 | Water Loop | KEEPRITE | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254611 | Water Loop | TEMPSTAR | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254612 | Water Loop | COMFORTMAKER | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254614 | Water Loop | DAY & NIGHT | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
206726680 | Water Loop | WaterFurnace | UVV/UVH024**0*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
206726691 | Water Loop | WaterFurnace | UVV/UVH024**3*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
206726692 | Water Loop | WaterFurnace | UVV/UVH024**4*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
206726812 | Water Loop | GEOCOMFORT | GBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726813 | Water Loop | GEOCOMFORT | GBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726814 | Water Loop | HYDRON MODULE | HBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726815 | Water Loop | HYDRON MODULE | HBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726816 | Water Loop | TETCO | TBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726817 | Water Loop | TETCO | TBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726818 | Water Loop | GEOCOMFORT | GBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726819 | Water Loop | GEOCOMFORT | GBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
206726820 | Water Loop | HYDRON MODULE | HBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726821 | Water Loop | HYDRON MODULE | HBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
206726822 | Water Loop | TETCO | TBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726823 | Water Loop | TETCO | TBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
10259035 | Water Loop | GEOCOMFORT | GZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259036 | Water Loop | HYDRON MODULE | HZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259037 | Water Loop | TETCO | TZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259038 | Water Loop | GEOCOMFORT | GZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259039 | Water Loop | HYDRON MODULE | HZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259040 | Water Loop | TETCO | TZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259054 | Water Loop | GEOCOMFORT | GZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259055 | Water Loop | HYDRON MODULE | HZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259056 | Water Loop | TETCO | TZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259057 | Water Loop | GEOCOMFORT | GZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
10259058 | Water Loop | HYDRON MODULE | HZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
10259059 | Water Loop | TETCO | TZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
207200617 | Water Loop | GeoSmart Energy | VI036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
207200624 | Water Loop | GeoSmart Energy | VI048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
6580833 | Water Loop | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
5696567 | Water Loop | 5 SERIES | NSV/NSH022G1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708463 | Water Loop | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708493 | Water Loop | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708550 | Water Loop | GEOSTAR | 101/102A022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708623 | Water Loop | GeoSmart Energy | GS022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
6581203 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5612204 | Water Loop | GeoSmart Energy | VI048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
5613676 | Water Loop | GEOSTAR | 141/142A048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
202607208 | Water Loop | WHALEN | VP-A-1004-*DD |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
205993162 | Water Loop | GEOCOMFORT | GBT024*2 | GAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
205993164 | Water Loop | HYDRON MODULE | HBT024*2 | HAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
205993166 | Water Loop | TETCO | TBT024*2 | TAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
10581119 | Water Loop | GEOSTAR | 107H038**1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
203466716 | Water Loop | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
203490410 | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
8560787 | Water Loop | 5 SERIES | NSV/NSH030H1*(0,3) |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5343143 | Water Loop | DAIKIN | WVFC1030*E***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
5343144 | Water Loop | DAIKIN | WVFC1030*F***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
5343145 | Water Loop | DAIKIN | WVFC1030*J***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
203362374 | Water Loop | WHALEN | VP-H-1004-*DD |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
8789598 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214855048 | Water Loop | WHALEN | CASH*018AD**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
214855049 | Water Loop | WHALEN | CASV*018AB**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
214855050 | Water Loop | WHALEN | CASV*018AD**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
207200563 | Water Loop | GeoSmart Energy | GS030**1*(0,3)*H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
207200564 | Water Loop | GeoSmart Energy | GS030**1*(1,4)*H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
206315256 | Water Loop | WHALEN | CASV*018AD**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
207334459 | Water Loop | WaterFurnace | NDP038H1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
205536348 | Water Loop | AAON, Inc. | WV-072-3-0-DCAC-C0-10-200-A |  | 81000 | 17 | 96200 | 5.4 | 6.75 | No
202443457 | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202443459 | Water Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202443460 | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214855069 | Water Loop | WHALEN | CASH*036AJ**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855070 | Water Loop | WHALEN | CASH*036AM**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855071 | Water Loop | WHALEN | CASV*036AB**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855072 | Water Loop | WHALEN | CASV*036AD**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855073 | Water Loop | WHALEN | CASV*036AJ**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855074 | Water Loop | WHALEN | CASV*036AM**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
205993156 | Water Loop | GEOCOMFORT | GBT024 | GAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
205993158 | Water Loop | HYDRON MODULE | HBT024 | HAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
205993160 | Water Loop | TETCO | TBT024 | TAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
204344184 | Water Loop | 7 SERIES | NVV/NVH036B1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
204452547 | Water Loop | GeoSmart Energy | VI036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
204457696 | Water Loop | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
204474784 | Water Loop | GEOSTAR | 141/142B036**1*(1,2) |  | 32000 | 18 | 50000 | 5.3 | 2.6667 | No
214855067 | Water Loop | WHALEN | CASH*036AB**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855068 | Water Loop | WHALEN | CASH*036AD**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330359 | Water Loop | AAON, Inc. | WV-016-1-H-ACAC-C0-10-200-A |  | 14000 | 17.5 | 18400 | 5.1 | 1.1667 | No
202330360 | Water Loop | AAON, Inc. | WV-016-A-H-ACAC-C0-10-200-A |  | 14000 | 17.5 | 18400 | 5.1 | 1.1667 | No
207178494 | Water Loop | GEOSTAR | 161/162J049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5295953 | Water Loop | TRANE | EXHF0361 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295954 | Water Loop | TRANE | EXHF0362 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295955 | Water Loop | TRANE | EXHF0367 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295956 | Water Loop | TRANE | EXHF0363 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
8105950 | Water Loop | TRANE | DXVF0241 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105955 | Water Loop | TRANE | DXVF0242 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105956 | Water Loop | TRANE | DXVF0243 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105960 | Water Loop | TRANE | DXVF0244 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
205993113 | Water Loop | GEOCOMFORT | GBS018 | GED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993114 | Water Loop | GEOCOMFORT | GBS018 | GAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993115 | Water Loop | HYDRON MODULE | HBS018 | HED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993116 | Water Loop | HYDRON MODULE | HBS018 | HAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993117 | Water Loop | TETCO | TBS018 | TED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993118 | Water Loop | TETCO | TBS018 | TAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993119 | Water Loop | GEOCOMFORT | GBS018*2 | GED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
202330748 | Water Loop | WHALEN | CASH*036AD**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330749 | Water Loop | WHALEN | CASV*036AD**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
203113882 | Water Loop | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
203113887 | Water Loop | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
8105926 | Water Loop | TRANE | DXHF0481 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105927 | Water Loop | TRANE | DXHF0482 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105928 | Water Loop | TRANE | DXHF0483 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105929 | Water Loop | TRANE | DXHF0484 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105930 | Water Loop | TRANE | DXHF0488 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105973 | Water Loop | TRANE | DXVF0481 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105974 | Water Loop | TRANE | DXVF0482 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105975 | Water Loop | TRANE | DXVF0483 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105976 | Water Loop | TRANE | DXVF0484 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105977 | Water Loop | TRANE | DXVF0488 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
202350095 | Water Loop | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202350096 | Water Loop | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
206315249 | Water Loop | WHALEN | CASH*015AB**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315250 | Water Loop | WHALEN | CASV*015AB**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315251 | Water Loop | WHALEN | CASH*015AD**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315252 | Water Loop | WHALEN | CASV*015AD**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315253 | Water Loop | WHALEN | CASH*018AB**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
206315254 | Water Loop | WHALEN | CASV*018AB**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
206315255 | Water Loop | WHALEN | CASH*018AD**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
204031802 | Water Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202330771 | Water Loop | WHALEN | CASH*036AJ**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330772 | Water Loop | WHALEN | CASV*036AJ**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330773 | Water Loop | WHALEN | CASH*036AM**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330774 | Water Loop | WHALEN | CASV*036AM**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330746 | Water Loop | WHALEN | CASH*036AB**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330747 | Water Loop | WHALEN | CASV*036AB**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
203363090 | Water Loop | WILLIAMS | EW010H1D*A |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
9063208 | Water Loop | DAIKIN | WVFC1030*K***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
8105965 | Water Loop | TRANE | DXVF0247 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105966 | Water Loop | TRANE | DXVF0248 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
5440741 | Water Loop | 7 SERIES | NVV/NVH048A1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
205993120 | Water Loop | GEOCOMFORT | GBS018*2 | GAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993121 | Water Loop | HYDRON MODULE | HBS018*2 | HED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993122 | Water Loop | HYDRON MODULE | HBS018*2 | HAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993123 | Water Loop | TETCO | TBS018*2 | TED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993124 | Water Loop | TETCO | TBS018*2 | TAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
214855043 | Water Loop | WHALEN | CASH*015AB**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855044 | Water Loop | WHALEN | CASH*015AD**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855045 | Water Loop | WHALEN | CASV*015AB**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855046 | Water Loop | WHALEN | CASV*015AD**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855047 | Water Loop | WHALEN | CASH*018AB**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
5295957 | Water Loop | TRANE | EXHF0368 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295958 | Water Loop | TRANE | EXHF0364 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
202923075 | Water Loop | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
205536344 | Water Loop | AAON, Inc. | WV-072-2-0-DCAC-C0-10-200-A |  | 81000 | 17 | 96200 | 5.4 | 6.75 | No
10268233 | Water Loop | GEOCOMFORT | GBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268234 | Water Loop | HYDRON MODULE | HBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268235 | Water Loop | TETCO | TBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268236 | Water Loop | GEOCOMFORT | GBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268237 | Water Loop | HYDRON MODULE | HBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268238 | Water Loop | TETCO | TBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
202443465 | Water Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202443468 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202443469 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
8105913 | Water Loop | TRANE | DXHF0248 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
207200571 | Water Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207200572 | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
202330279 | Water Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 14200 | 17 | 17900 | 6.3 | 1.1833 | No
202330280 | Water Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 14200 | 17 | 17900 | 6.3 | 1.1833 | No
207178527 | Water Loop | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207200556 | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207200557 | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
203363069 | Water Loop | WILLIAMS | EW010A1D*A |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
4217883 | Water Loop | DAIKIN | WCCH4015*E*04* |  | 16000 | 17.6 | 18100 | 5.6 | 1.3333 | No
4217885 | Water Loop | DAIKIN | WCCH4015*J*04* |  | 15600 | 17.6 | 17200 | 5.6 | 1.3 | No
8789591 | Water Loop | GEOSTAR | 101/102H030**1*(0,3)***** |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789592 | Water Loop | GeoSmart Energy | GS030**1*(0,3)********H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789593 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789596 | Water Loop | GEOSTAR | 101/102H030**1*(1,4)***** |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8789597 | Water Loop | GeoSmart Energy | GS030**1*(1,4)********H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8103479 | Water Loop | TRANE | DXHF0241 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105907 | Water Loop | TRANE | DXHF0242 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105909 | Water Loop | TRANE | DXHF0243 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105911 | Water Loop | TRANE | DXHF0244 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105912 | Water Loop | TRANE | DXHF0247 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
10581109 | Water Loop | 5 SERIES | NDP038H1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
10581114 | Water Loop | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
8560801 | Water Loop | 5 SERIES | NSV/NSH030H1*(1,4) |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
202350098 | Water Loop | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No

## Commercial Ground Water HP
AHRI Certified Reference Number | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage | Tax Credit (IRA) Eligibility
206438907 | Ground Water | CARRIER | 50PSV012**C0/BA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438908 | Ground Water | CARRIER | 50PSV012**C4/DA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438909 | Ground Water | CARRIER | 50PSH012**C0/BA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438910 | Ground Water | CARRIER | 50PSH012**C4/DA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438911 | Ground Water | CARRIER | 50PSV012**N0/BA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438912 | Ground Water | CARRIER | 50PSV012**N4/DA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438913 | Ground Water | CARRIER | 50PSH012**N0/BA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438914 | Ground Water | CARRIER | 50PSH012**N4/DA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206570649 | Ground Water | 7 SERIES | NVV/NVH036C1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
215415748 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)042A*VB |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415749 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)042A*VC |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415750 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)048A*B |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415751 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)048A*C |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415752 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)048A*VB |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415753 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)048A*VC |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415756 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)060A*VB |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415757 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)060A*VC |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415770 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)015A*B |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415771 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)015A*C |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415772 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)015A*VB |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415773 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)015A*VC |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415774 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)018A*B |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415775 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)018A*C |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415776 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)018A*VB |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415777 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)018A*VC |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415778 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)024A*B |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415779 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)024A*C |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415780 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)024A*VB |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415781 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)024A*VC |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415784 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)030A*VB |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415785 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)030A*VC |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415788 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)036A*VB |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415789 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)036A*VC |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415792 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)042A*VB |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415793 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)042A*VC |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415794 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)048A*B |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415795 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)048A*C |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415796 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)048A*VB |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415797 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)048A*VC |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415800 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)060A*VB |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415801 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)060A*VC |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
217351892 | Ground Water | KEEPRITE | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351893 | Ground Water | KEEPRITE | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351894 | Ground Water | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351895 | Ground Water | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351896 | Ground Water | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351897 | Ground Water | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351898 | Ground Water | KEEPRITE | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351900 | Ground Water | KEEPRITE | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351901 | Ground Water | KEEPRITE | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351903 | Ground Water | KEEPRITE | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
216625866 | Ground Water | GeoSmart Energy | S5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625867 | Ground Water | GeoSmart Energy | S5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625868 | Ground Water | GeoSmart Energy | S5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625869 | Ground Water | GeoSmart Energy | S5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625870 | Ground Water | GeoSmart Energy | S5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625871 | Ground Water | GeoSmart Energy | S5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625872 | Ground Water | GeoSmart Energy | S5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625873 | Ground Water | GeoSmart Energy | S5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625874 | Ground Water | GeoSmart Energy | S5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625875 | Ground Water | GeoSmart Energy | S5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625876 | Ground Water | GeoSmart Energy | S5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625877 | Ground Water | GeoSmart Energy | S5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625878 | Ground Water | GeoSmart Energy | S5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625879 | Ground Water | GeoSmart Energy | S5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625880 | Ground Water | GeoSmart Energy | S5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625881 | Ground Water | GeoSmart Energy | S5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216687113 | Ground Water | WaterFurnace | W5SS024BD1 | W5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687114 | Ground Water | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687115 | Ground Water | WaterFurnace | W5SS048BD1 | W5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687116 | Ground Water | WaterFurnace | W5SS060BD1 | W5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687117 | Ground Water | WaterFurnace | W5SS066BD1 | W5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216687118 | Ground Water | WaterFurnace | W5SZ024BD1 | W5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687119 | Ground Water | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687120 | Ground Water | WaterFurnace | W5SZ048BD1 | W5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687121 | Ground Water | WaterFurnace | W5SZ060BD1 | W5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687122 | Ground Water | WaterFurnace | W5SZ066BD1 | W5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216687731 | Ground Water | GEOSTAR | G5SS024BD1 | G5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | No
216687732 | Ground Water | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | No
216687733 | Ground Water | GEOSTAR | G5SS048BD1 | G5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | No
216687734 | Ground Water | GEOSTAR | G5SS060BD1 | G5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | No
216687735 | Ground Water | GEOSTAR | G5SS066BD1 | G5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | No
216687736 | Ground Water | GEOSTAR | G5SZ024BD1 | G5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | No
216687737 | Ground Water | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | No
216687738 | Ground Water | GEOSTAR | G5SZ048BD1 | G5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | No
216687739 | Ground Water | GEOSTAR | G5SZ060BD1 | G5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | No
216687740 | Ground Water | GEOSTAR | G5SZ066BD1 | G5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | No
216714606 | Ground Water | GEOSTAR | G3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
216714607 | Ground Water | GEOSTAR | G3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
216714612 | Ground Water | GEOSTAR | G3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714613 | Ground Water | GEOSTAR | G3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714614 | Ground Water | GEOSTAR | G3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714615 | Ground Water | GEOSTAR | G3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714620 | Ground Water | GEOSTAR | G3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714621 | Ground Water | GEOSTAR | G3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714622 | Ground Water | GEOSTAR | G3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
207337510 | Ground Water | GEOSTAR | 103H022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
207337511 | Ground Water | GEOSTAR | 103H030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207337512 | Ground Water | GEOSTAR | 103H030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207337513 | Ground Water | GEOSTAR | 103J036**1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | No
207337514 | Ground Water | GEOSTAR | 103J036**1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | No
214839280 | Ground Water | BOSCH | RL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839281 | Ground Water | BOSCH | RL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839282 | Ground Water | BOSCH | RL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839283 | Ground Water | BOSCH | RL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839284 | Ground Water | BOSCH | RL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839285 | Ground Water | BOSCH | RL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
217351779 | Ground Water | BRYANT | GW024WA********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351781 | Ground Water | BRYANT | GW048WA********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351784 | Ground Water | ARCOAIRE | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351785 | Ground Water | ARCOAIRE | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351786 | Ground Water | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351787 | Ground Water | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351788 | Ground Water | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351789 | Ground Water | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351790 | Ground Water | ARCOAIRE | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351792 | Ground Water | ARCOAIRE | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351793 | Ground Water | ARCOAIRE | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351795 | Ground Water | ARCOAIRE | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351796 | Ground Water | ARCOAIRE | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351797 | Ground Water | ARCOAIRE | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351798 | Ground Water | ARCOAIRE | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351799 | Ground Water | ARCOAIRE | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351800 | Ground Water | ARCOAIRE | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351801 | Ground Water | ARCOAIRE | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351803 | Ground Water | ARCOAIRE | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351804 | Ground Water | ARCOAIRE | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
202330346 | Ground Water | AAON, Inc. | WH-060-3-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202330411 | Ground Water | AAON, Inc. | WV-060-1-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330412 | Ground Water | AAON, Inc. | WV-060-A-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330415 | Ground Water | AAON, Inc. | WV-060-2-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330416 | Ground Water | AAON, Inc. | WV-060-3-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330436 | Ground Water | AAON, Inc. | RQ-003-1-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330438 | Ground Water | AAON, Inc. | RQ-003-2-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330439 | Ground Water | AAON, Inc. | RQ-003-3-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330440 | Ground Water | AAON, Inc. | RQ-003-4-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330444 | Ground Water | AAON, Inc. | RQ-004-1-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330445 | Ground Water | AAON, Inc. | RQ-004-1-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330446 | Ground Water | AAON, Inc. | RQ-004-2-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330447 | Ground Water | AAON, Inc. | RQ-004-3-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330448 | Ground Water | AAON, Inc. | RQ-004-4-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330449 | Ground Water | AAON, Inc. | RQ-004-2-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330450 | Ground Water | AAON, Inc. | RQ-004-3-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330451 | Ground Water | AAON, Inc. | RQ-004-4-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330452 | Ground Water | AAON, Inc. | RQ-005-1-0-BCAY-V0-10-000-A |  | 66900 | 22 | 56500 | 4.4 | 5.575 | No
202330453 | Ground Water | AAON, Inc. | RQ-005-1-0-DCAY-S0-10-000-A |  | 61500 | 22.3 | 53000 | 4.6 | 5.125 | No
202330454 | Ground Water | AAON, Inc. | RQ-005-2-0-BCAY-V0-10-000-A |  | 66900 | 22 | 56500 | 4.4 | 5.575 | No
205752888 | Ground Water | ClimateMaster | TCH/V006A*W/K |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
205754885 | Ground Water | Johnson Controls | JCH/V015A*W/K B |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205754886 | Ground Water | SKYMARK | JCH/V015A*W/K C |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205754887 | Ground Water | Johnson Controls | JCH/V018A B |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205754888 | Ground Water | SKYMARK | JCH/V018A C |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205754889 | Ground Water | Johnson Controls | JCH/V018A*W/K B |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205754890 | Ground Water | SKYMARK | JCH/V018A*W/K C |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205754895 | Ground Water | Johnson Controls | JCH/V030A*W/K B |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205754896 | Ground Water | SKYMARK | JCH/V030A*W/K C |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
214595658 | Ground Water | AAON, Inc. | RN-009-2-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595659 | Ground Water | AAON, Inc. | RN-009-3-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595660 | Ground Water | AAON, Inc. | RN-009-4-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595661 | Ground Water | AAON, Inc. | RN-009-2-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595662 | Ground Water | AAON, Inc. | RN-009-3-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595663 | Ground Water | AAON, Inc. | RN-009-4-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595670 | Ground Water | AAON, Inc. | RN-011-2-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595671 | Ground Water | AAON, Inc. | RN-011-3-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595672 | Ground Water | AAON, Inc. | RN-011-4-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595673 | Ground Water | AAON, Inc. | RN-011-2-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595674 | Ground Water | AAON, Inc. | RN-011-3-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595675 | Ground Water | AAON, Inc. | RN-011-4-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
215268781 | Ground Water | WaterFurnace | V5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268782 | Ground Water | WaterFurnace | V5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268783 | Ground Water | WaterFurnace | V5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268784 | Ground Water | WaterFurnace | V5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268785 | Ground Water | WaterFurnace | V5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268786 | Ground Water | WaterFurnace | V5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268787 | Ground Water | WaterFurnace | V5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268788 | Ground Water | WaterFurnace | V5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268789 | Ground Water | WaterFurnace | V5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268790 | Ground Water | WaterFurnace | V5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268791 | Ground Water | WaterFurnace | V5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268792 | Ground Water | WaterFurnace | V5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268793 | Ground Water | WaterFurnace | V5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268794 | Ground Water | WaterFurnace | V5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268795 | Ground Water | WaterFurnace | V5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268796 | Ground Water | WaterFurnace | V5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215270403 | Ground Water | GEO-THERMAL SPLIT | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
215270405 | Ground Water | GEO-THERMAL SPLIT | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
215270409 | Ground Water | CARRIER | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270411 | Ground Water | CARRIER | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215270415 | Ground Water | BRYANT | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
202330530 | Ground Water | AAON, Inc. | M2-004-1-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330531 | Ground Water | AAON, Inc. | M2-004-1-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330532 | Ground Water | AAON, Inc. | M2-004-1-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330533 | Ground Water | AAON, Inc. | M2-004-2-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330534 | Ground Water | AAON, Inc. | M2-004-2-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330535 | Ground Water | AAON, Inc. | M2-004-2-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330536 | Ground Water | AAON, Inc. | M2-004-2-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330537 | Ground Water | AAON, Inc. | M2-004-3-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330538 | Ground Water | AAON, Inc. | M2-004-3-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330539 | Ground Water | AAON, Inc. | M2-004-3-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330540 | Ground Water | AAON, Inc. | M2-004-3-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330541 | Ground Water | AAON, Inc. | M2-004-4-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330542 | Ground Water | AAON, Inc. | M2-004-4-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330543 | Ground Water | AAON, Inc. | M2-004-4-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330544 | Ground Water | AAON, Inc. | M2-004-4-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330547 | Ground Water | AAON, Inc. | M2-005-1-H-DCAC-S0-10-000-A |  | 62100 | 23.7 | 50000 | 4.1 | 5.175 | No
202330548 | Ground Water | AAON, Inc. | M2-005-1-H-DCBC-S0-10-000-A |  | 65000 | 23.5 | 50400 | 4.1 | 5.4167 | No
202330551 | Ground Water | AAON, Inc. | M2-005-2-H-DCAC-S0-10-000-A |  | 62100 | 23.7 | 50000 | 4.1 | 5.175 | No
202330552 | Ground Water | AAON, Inc. | M2-005-2-H-DCBC-S0-10-000-A |  | 65000 | 23.5 | 50400 | 4.1 | 5.4167 | No
202330555 | Ground Water | AAON, Inc. | M2-005-3-H-DCAC-S0-10-000-A |  | 62100 | 23.7 | 50000 | 4.1 | 5.175 | No
202330556 | Ground Water | AAON, Inc. | M2-005-3-H-DCBC-S0-10-000-A |  | 65000 | 23.5 | 50400 | 4.1 | 5.4167 | No
202330559 | Ground Water | AAON, Inc. | M2-005-4-H-DCAC-S0-10-000-A |  | 62100 | 23.7 | 50000 | 4.1 | 5.175 | No
202330560 | Ground Water | AAON, Inc. | M2-005-4-H-DCBC-S0-10-000-A |  | 65000 | 23.5 | 50400 | 4.1 | 5.4167 | No
202330562 | Ground Water | AAON, Inc. | M2-006-2-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
202330564 | Ground Water | AAON, Inc. | M2-006-2-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
202330566 | Ground Water | AAON, Inc. | M2-006-3-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
202330568 | Ground Water | AAON, Inc. | M2-006-3-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
202330570 | Ground Water | AAON, Inc. | M2-006-4-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
202330572 | Ground Water | AAON, Inc. | M2-006-4-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
215415734 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)024A*B |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415735 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)024A*C |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415736 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)024A*VB |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415737 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)024A*VC |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415740 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)030A*VB |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415741 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)030A*VC |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415744 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)036A*VB |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415745 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)036A*VC |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
214772068 | Ground Water | TRANE | GEVK042B |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772069 | Ground Water | TRANE | GEVK0424 |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772070 | Ground Water | TRANE | GEVK048B |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772071 | Ground Water | TRANE | GEVK0484 |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772072 | Ground Water | TRANE | GEVK060B |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772073 | Ground Water | TRANE | GEVK0604 |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772074 | Ground Water | TRANE | EXVK0097 |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214772075 | Ground Water | TRANE | EXVK0127 |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214772076 | Ground Water | TRANE | EXVK0157 |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214772077 | Ground Water | TRANE | EXVK0187 |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214772078 | Ground Water | TRANE | EXVK024B |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
216054500 | Ground Water | GEOCOMFORT | GZS006* |  | 6900 | 22.9 | 6300 | 4.3 | 0.575 | Yes
216057509 | Ground Water | GEOCOMFORT | GBT060* | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
216057511 | Ground Water | GEOCOMFORT | GVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216057512 | Ground Water | GEOCOMFORT | GYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216057513 | Ground Water | GEOCOMFORT | GZS015* |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
216057514 | Ground Water | GEOCOMFORT | GZS017* |  | 18000 | 21.9 | 15800 | 4.1 | 1.5 | Yes
216057515 | Ground Water | GEOCOMFORT | GZS018* |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
216057517 | Ground Water | GEOCOMFORT | GYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216065302 | Ground Water | GEOCOMFORT | GWS036* |  | 35600 | 22.9 | 38300 | 4.1 | 2.9667 | Yes
216065303 | Ground Water | GEOCOMFORT | GWS048* |  | 52500 | 22.9 | 58700 | 4.2 | 4.375 | Yes
216065306 | Ground Water | GEOCOMFORT | GWT048* |  | 52700 | 21.2 | 61100 | 4.2 | 4.3917 | Yes
216128491 | Ground Water | GEOSTAR | G5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216128493 | Ground Water | GEOSTAR | G5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216128495 | Ground Water | GEOSTAR | G5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216128497 | Ground Water | GEOSTAR | G5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216411469 | Ground Water | ClimateMaster | SJ/PN024A | SAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
216411470 | Ground Water | ClimateMaster | SJ/PN036A | SAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
216411471 | Ground Water | ClimateMaster | SJ/PN048A | SAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
216411472 | Ground Water | ClimateMaster | SJ/PN060A | SAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
216419856 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
216419857 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
216419860 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
216419863 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
216419865 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
216419867 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
216419868 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
216419871 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
216419879 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
216419880 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
216419882 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
216419883 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
216419898 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
216419899 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
216419902 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
216419904 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
216419907 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
216419908 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215743525 | Ground Water | TRANE | GECK0127 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
215746915 | Ground Water | TRANE | GSK036A3 |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746916 | Ground Water | TRANE | GSK048A3 |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746918 | Ground Water | TRANE | GSK060A3 |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746919 | Ground Water | TRANE | GSK072A3 |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746920 | Ground Water | TRANE | GSK090A3 |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
215746921 | Ground Water | TRANE | GSK102A3 |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
215746923 | Ground Water | TRANE | GSK036A4 |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746924 | Ground Water | TRANE | GSK036AW |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746925 | Ground Water | TRANE | GSK048A4 |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746926 | Ground Water | TRANE | GSK048AW |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746927 | Ground Water | TRANE | GSK060A4 |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746928 | Ground Water | TRANE | GSK060AW |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746929 | Ground Water | TRANE | GSK072A4 |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746930 | Ground Water | TRANE | GSK072AW |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746931 | Ground Water | TRANE | GSK090A4 |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
215746932 | Ground Water | TRANE | GSK090AW |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
215746933 | Ground Water | TRANE | GSK102A4 |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
215746934 | Ground Water | TRANE | GSK102AW |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
215748031 | Ground Water | NORDIC | R-55-HACW-X-1T-*-*DE** |  | 48000 | 22.2 | 47000 | 4.5 | 4 | No
217642919 | Ground Water | GeoSmart Energy | S3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642920 | Ground Water | GeoSmart Energy | S3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642921 | Ground Water | GeoSmart Energy | S3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642922 | Ground Water | GeoSmart Energy | S3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642928 | Ground Water | GeoSmart Energy | S3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642929 | Ground Water | GeoSmart Energy | S3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642930 | Ground Water | GeoSmart Energy | S3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642931 | Ground Water | GeoSmart Energy | S3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642932 | Ground Water | GeoSmart Energy | S3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642938 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642941 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642943 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642945 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642946 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217903459 | Ground Water | WaterFurnace | V5R048*D4**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
4219424 | Ground Water | NORDIC | R45HACW-P-1T-*-SDE** |  | 38500 | 21.3 | 35700 | 4.3 | 3.2083 | Yes
4219425 | Ground Water | NORDIC | R55HACW-P-1T-*-SDE** |  | 50200 | 22.5 | 47200 | 4.5 | 4.1833 | Yes
205754919 | Ground Water | Johnson Controls | JSH/V006A B |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205754920 | Ground Water | SKYMARK | JSH/V006A C |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205754921 | Ground Water | Johnson Controls | JSH/V009A B |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
205754922 | Ground Water | SKYMARK | JSH/V009A C |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
205767467 | Ground Water | ClimateMaster | QEV/H/D1860 |  | 48000 | 35.5 | 60000 | 4.3 | 4 | Yes
205767468 | Ground Water | ClimateMaster | TYV/H024B |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | No
205767470 | Ground Water | ClimateMaster | TYV/H036B |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | No
205767471 | Ground Water | ClimateMaster | TYV/H042 |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | No
205767473 | Ground Water | ClimateMaster | TEV/H/D026B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
205767474 | Ground Water | ClimateMaster | TEV/H/D038B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
205767475 | Ground Water | ClimateMaster | TEV/H/D049B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
205767476 | Ground Water | ClimateMaster | TEV/H/D064B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
205767477 | Ground Water | ClimateMaster | TEV/H/D072B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
206608720 | Ground Water | GEOSTAR | 103J048**1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608721 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060J1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608722 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060J1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608723 | Ground Water | GEOSTAR | 103J060**1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608724 | Ground Water | GEOSTAR | 103J060**1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206611110 | Ground Water | COMFORT-AIRE | HEH/V024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
206611111 | Ground Water | CENTURY | HEH/V024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
206611114 | Ground Water | COMFORT-AIRE | HEH/V036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206611115 | Ground Water | CENTURY | HEH/V036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206611116 | Ground Water | COMFORT-AIRE | HEH/V042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
206611117 | Ground Water | CENTURY | HEH/V042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
206611120 | Ground Water | COMFORT-AIRE | HEH/V060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
206611121 | Ground Water | CENTURY | HEH/V060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
206722530 | Ground Water | ClimateMaster | TRH/V006A*W/K |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
202729325 | Ground Water | DAY & NIGHT | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729332 | Ground Water | HEIL | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202729333 | Ground Water | ARCOAIRE | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729334 | Ground Water | KEEPRITE | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729335 | Ground Water | TEMPSTAR | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729336 | Ground Water | COMFORTMAKER | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729337 | Ground Water | DAY & NIGHT | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202732300 | Ground Water | BOSCH | BP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732301 | Ground Water | CARRIER | GB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
202732302 | Ground Water | BRYANT | GB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732303 | Ground Water | ARCOAIRE | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
202732304 | Ground Water | HEIL | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732305 | Ground Water | KEEPRITE | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732306 | Ground Water | TEMPSTAR | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732307 | Ground Water | COMFORTMAKER | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732308 | Ground Water | DAY & NIGHT | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732913 | Ground Water | BOSCH-GEO | SM036-1CSN-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202732914 | Ground Water | BOSCH-GEO | BP018-1HZ*******C |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732915 | Ground Water | BOSCH | SM036-1CSN-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202732916 | Ground Water | BOSCH | BP018-1HZ*******C |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732917 | Ground Water | CARRIER | GB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732918 | Ground Water | BRYANT | GB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732919 | Ground Water | HEIL | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732920 | Ground Water | ARCOAIRE | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732921 | Ground Water | KEEPRITE | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732922 | Ground Water | TEMPSTAR | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732923 | Ground Water | COMFORTMAKER | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732924 | Ground Water | DAY & NIGHT | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732934 | Ground Water | TRANE | GWSC036H3 |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
214063784 | Ground Water | GeoSmart Energy | GBV/GBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214063785 | Ground Water | GeoSmart Energy | GBV/GBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214063786 | Ground Water | GeoSmart Energy | GBV/GBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214063788 | Ground Water | GeoSmart Energy | GBV/GBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214063789 | Ground Water | GeoSmart Energy | GBV/GBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214063790 | Ground Water | GeoSmart Energy | GBV/GBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214063791 | Ground Water | GeoSmart Energy | GBV/GBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067547 | Ground Water | GeoSmart Energy | GBV/GBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214067548 | Ground Water | GeoSmart Energy | GBV/GBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067549 | Ground Water | GeoSmart Energy | GBV/GBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067550 | Ground Water | GeoSmart Energy | GBV/GBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214067551 | Ground Water | GeoSmart Energy | GBV/GBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067552 | Ground Water | GeoSmart Energy | GBV/GBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067553 | Ground Water | GeoSmart Energy | GBV/GBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067554 | Ground Water | GeoSmart Energy | GBV/GBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067555 | Ground Water | GeoSmart Energy | GBV/GBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067556 | Ground Water | GeoSmart Energy | GBV/GBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067557 | Ground Water | GeoSmart Energy | GBV/GBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214067558 | Ground Water | GeoSmart Energy | GBV/GBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067559 | Ground Water | GeoSmart Energy | GBV/GBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067560 | Ground Water | GeoSmart Energy | GBV/GBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214067561 | Ground Water | GeoSmart Energy | GBV/GBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067562 | Ground Water | GeoSmart Energy | GBV/GBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067563 | Ground Water | GeoSmart Energy | GBV/GBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214067564 | Ground Water | GeoSmart Energy | GBV/GBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067565 | Ground Water | GeoSmart Energy | GBV/GBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067566 | Ground Water | GeoSmart Energy | GBV/GBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214067567 | Ground Water | GeoSmart Energy | GBV/GBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067568 | Ground Water | GeoSmart Energy | GBV/GBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067569 | Ground Water | GeoSmart Energy | GBV/GBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067570 | Ground Water | GeoSmart Energy | GBV/GBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067571 | Ground Water | GeoSmart Energy | GBV/GBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067572 | Ground Water | GeoSmart Energy | GBV/GBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067573 | Ground Water | GeoSmart Energy | GBV/GBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067574 | Ground Water | GeoSmart Energy | GBV/GBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067575 | Ground Water | GeoSmart Energy | GBV/GBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067576 | Ground Water | GeoSmart Energy | GBV/GBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067577 | Ground Water | GeoSmart Energy | GBV/GBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067578 | Ground Water | GeoSmart Energy | GBV/GBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
205503115 | Ground Water | BOSCH-GEO | SM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | Yes
205503116 | Ground Water | BOSCH-GEO | SM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | Yes
205503117 | Ground Water | BOSCH-GEO | SM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205503119 | Ground Water | BOSCH-GEO | LM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | No
205503120 | Ground Water | BOSCH-GEO | LM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | No
205503121 | Ground Water | BOSCH-GEO | LM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205503123 | Ground Water | BOSCH | SM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | Yes
205503124 | Ground Water | BOSCH | SM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | Yes
205503125 | Ground Water | BOSCH | SM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205503127 | Ground Water | FHP | LM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | No
205503128 | Ground Water | FHP | LM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | No
205503129 | Ground Water | FHP | LM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205652453 | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | Yes
205652454 | Ground Water | BOSCH-GEO | SM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | Yes
205652455 | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | Yes
205652457 | Ground Water | BOSCH-GEO | LM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | No
205652458 | Ground Water | BOSCH-GEO | LM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | No
205652459 | Ground Water | BOSCH-GEO | LM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | No
205652461 | Ground Water | BOSCH | SM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | Yes
205652462 | Ground Water | BOSCH | SM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | Yes
205652463 | Ground Water | BOSCH | SM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | Yes
205652465 | Ground Water | FHP | LM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | No
205652466 | Ground Water | FHP | LM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | No
205652467 | Ground Water | FHP | LM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | No
215224613 | Ground Water | CARRIER | 50WD*015***4*(A-H)** |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224614 | Ground Water | CARRIER | 50WD*015***4*(J-R)** |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224615 | Ground Water | CARRIER | 50WD*018***3*(A-H)** |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224616 | Ground Water | CARRIER | 50WD*018***3*(J-R)** |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224617 | Ground Water | CARRIER | 50WD*018***4*(A-H)** |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224618 | Ground Water | CARRIER | 50WD*018***4*(J-R)** |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
202732935 | Ground Water | TRANE | GWSC036H4 |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
202732936 | Ground Water | TRANE | GWSC036HW |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
202732937 | Ground Water | TRANE | GWSC048H3 |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
202732938 | Ground Water | TRANE | GWSC048H4 |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
202732939 | Ground Water | TRANE | GWSC048HW |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
202732940 | Ground Water | TRANE | GWSC060H3 |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
202732941 | Ground Water | TRANE | GWSC060H4 |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
202732942 | Ground Water | TRANE | GWSC060HW |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
215429151 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429152 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429153 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429158 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429159 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429160 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429161 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429162 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429163 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429170 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429171 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429172 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429173 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429174 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429175 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215743134 | Ground Water | TRANE | GECK006 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743135 | Ground Water | TRANE | GECK009 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743136 | Ground Water | TRANE | GECK012 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
215743520 | Ground Water | TRANE | GECK0062 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743521 | Ground Water | TRANE | GECK0067 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743522 | Ground Water | TRANE | GECK0092 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743523 | Ground Water | TRANE | GECK0097 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743524 | Ground Water | TRANE | GECK0122 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
7519574 | Ground Water | HYDRON MODULE | HVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519575 | Ground Water | TETCO | TVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519576 | Ground Water | GEOCOMFORT | GVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519577 | Ground Water | HYDRON MODULE | HVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519578 | Ground Water | TETCO | TVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519579 | Ground Water | GEOCOMFORT | GVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
207200608 | Ground Water | GeoSmart Energy | GTS038*1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207200609 | Ground Water | GeoSmart Energy | GTS038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207200613 | Ground Water | GeoSmart Energy | QT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
207200614 | Ground Water | GeoSmart Energy | VI036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
207200616 | Ground Water | GeoSmart Energy | VI060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
207216511 | Ground Water | GEOSTAR | GDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
207216512 | Ground Water | GEOSTAR | GDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
207216513 | Ground Water | GEOSTAR | GDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
207216514 | Ground Water | GEOSTAR | GDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216515 | Ground Water | GEOSTAR | GDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216516 | Ground Water | GEOSTAR | GDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216517 | Ground Water | GEOSTAR | GDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
207216518 | Ground Water | GEOSTAR | GDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
207216519 | Ground Water | GEOSTAR | GDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
214776161 | Ground Water | TRANE | GETK009 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
214776167 | Ground Water | TRANE | GETK0091-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
214776168 | Ground Water | TRANE | GETK0121-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776169 | Ground Water | TRANE | GETK0151-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776170 | Ground Water | TRANE | GETK0181-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
214776171 | Ground Water | TRANE | GETK0241-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776172 | Ground Water | TRANE | GETK0361-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
214776173 | Ground Water | TRANE | GETK0092 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
214776174 | Ground Water | TRANE | GETK0097 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
214776185 | Ground Water | TRANE | GETK0092-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
214776186 | Ground Water | TRANE | GETK0097-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
214776187 | Ground Water | TRANE | GETK0122-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776188 | Ground Water | TRANE | GETK0127-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776189 | Ground Water | TRANE | GETK0152-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776190 | Ground Water | TRANE | GETK0157-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776191 | Ground Water | TRANE | GETK0182-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
214776192 | Ground Water | TRANE | GETK0187-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
214776193 | Ground Water | TRANE | GETK0242-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776194 | Ground Water | TRANE | GETK0247-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776195 | Ground Water | TRANE | GETK0362-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
214776196 | Ground Water | TRANE | GETK0367-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
214796343 | Ground Water | WaterFurnace | W5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214796344 | Ground Water | WaterFurnace | W5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214796345 | Ground Water | WaterFurnace | W5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214796346 | Ground Water | WaterFurnace | W5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214796347 | Ground Water | WaterFurnace | W5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214796667 | Ground Water | WaterFurnace | W5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214796668 | Ground Water | WaterFurnace | W5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214796669 | Ground Water | WaterFurnace | W5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214810491 | Ground Water | GEOSTAR | G5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214810492 | Ground Water | GEOSTAR | G5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214810493 | Ground Water | GEOSTAR | G5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214810494 | Ground Water | GEOSTAR | G5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214810495 | Ground Water | GEOSTAR | G5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214810496 | Ground Water | GEOSTAR | G5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214810497 | Ground Water | GEOSTAR | G5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214810498 | Ground Water | GEOSTAR | G5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214823444 | Ground Water | GeoSmart Energy | S5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214823445 | Ground Water | GeoSmart Energy | S5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
202921908 | Ground Water | BOSCH | EP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921909 | Ground Water | BOSCH | EP036-3VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921910 | Ground Water | BOSCH | EP036-4VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921911 | Ground Water | BOSCH-GEO | BP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921912 | Ground Water | BOSCH | EP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921913 | Ground Water | BOSCH | EP036-3HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921914 | Ground Water | BOSCH | EP036-4HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921915 | Ground Water | BOSCH-GEO | BP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921952 | Ground Water | FHP | EP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921953 | Ground Water | FHP | EP036-3HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921954 | Ground Water | FHP | EP036-4HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921956 | Ground Water | BOSCH | BP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202921957 | Ground Water | FHP | EP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921958 | Ground Water | FHP | EP036-3VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921959 | Ground Water | FHP | EP036-4VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921960 | Ground Water | BOSCH | BP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922686 | Ground Water | CARRIER | 50PSH036***3/CA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922689 | Ground Water | CARRIER | 50PSH036***5/EA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922692 | Ground Water | CARRIER | 50PSH036***6/FA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922695 | Ground Water | CARRIER | GB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922697 | Ground Water | BRYANT | GB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922700 | Ground Water | HEIL | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922703 | Ground Water | ARCOAIRE | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922706 | Ground Water | KEEPRITE | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922708 | Ground Water | TEMPSTAR | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922711 | Ground Water | COMFORTMAKER | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922714 | Ground Water | DAY & NIGHT | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922716 | Ground Water | CARRIER | 50PSV036***3/CA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922719 | Ground Water | CARRIER | 50PSV036***5/EA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922722 | Ground Water | CARRIER | 50PSV036***6/FA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922725 | Ground Water | CARRIER | GB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922728 | Ground Water | BRYANT | GB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922731 | Ground Water | HEIL | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922734 | Ground Water | ARCOAIRE | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922737 | Ground Water | KEEPRITE | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922740 | Ground Water | TEMPSTAR | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922742 | Ground Water | COMFORTMAKER | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922745 | Ground Water | DAY & NIGHT | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
203113888 | Ground Water | GEOSTAR | 103J036**1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
212587993 | Ground Water | HYDROTECH | HRCX09*-7 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
212587994 | Ground Water | AE Air | HRCX09*-7 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
201907619 | Ground Water | WaterFurnace | URS048*0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907620 | Ground Water | WaterFurnace | URS048*0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907621 | Ground Water | WaterFurnace | URS048*0*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907622 | Ground Water | WaterFurnace | URS048*3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907623 | Ground Water | WaterFurnace | URS048*3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907624 | Ground Water | WaterFurnace | URS048*3*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907625 | Ground Water | WaterFurnace | URS048*4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907626 | Ground Water | WaterFurnace | URS048*4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907627 | Ground Water | WaterFurnace | URS048*4*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907628 | Ground Water | WaterFurnace | URD038*4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907629 | Ground Water | WaterFurnace | URD038*4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907630 | Ground Water | WaterFurnace | URD038*4*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907631 | Ground Water | WaterFurnace | URD049*4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201907632 | Ground Water | WaterFurnace | URD049*4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201907633 | Ground Water | WaterFurnace | URD049*4*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201926691 | Ground Water | WaterFurnace | URS060*0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926694 | Ground Water | WaterFurnace | URS060*0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926696 | Ground Water | WaterFurnace | URS060*0*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926699 | Ground Water | WaterFurnace | URS060*3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926702 | Ground Water | WaterFurnace | URS060*3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926705 | Ground Water | WaterFurnace | URS060*3*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926708 | Ground Water | WaterFurnace | URS060*4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926711 | Ground Water | WaterFurnace | URS060*4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926714 | Ground Water | WaterFurnace | URS060*4*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926717 | Ground Water | WaterFurnace | URS070*0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926719 | Ground Water | WaterFurnace | URS070*0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926724 | Ground Water | WaterFurnace | URS070*0*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926727 | Ground Water | WaterFurnace | URS070*3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926730 | Ground Water | WaterFurnace | URS070*3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926733 | Ground Water | WaterFurnace | URS070*3*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926736 | Ground Water | WaterFurnace | URS070*4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926738 | Ground Water | WaterFurnace | URS070*4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926741 | Ground Water | WaterFurnace | URS070*4*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207349401 | Ground Water | WaterFurnace | NBV/NBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349402 | Ground Water | WaterFurnace | NBV/NBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349403 | Ground Water | WaterFurnace | NBV/NBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349404 | Ground Water | WaterFurnace | NBV/NBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349405 | Ground Water | WaterFurnace | NBV/NBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349406 | Ground Water | WaterFurnace | NBV/NBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349407 | Ground Water | WaterFurnace | NBV/NBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349408 | Ground Water | WaterFurnace | NBV/NBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349409 | Ground Water | WaterFurnace | NBV/NBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349410 | Ground Water | WaterFurnace | NBV/NBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349411 | Ground Water | WaterFurnace | NBV/NBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349412 | Ground Water | WaterFurnace | NBV/NBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207530615 | Ground Water | BOSCH | CA009-1*C-*****D |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
207542447 | Ground Water | FHP | CA009-1*C-*****D |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
207549518 | Ground Water | CARRIER | 50PEC09***E3/CF |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
216621360 | Ground Water | GEOSTAR | G5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216621361 | Ground Water | GEOSTAR | G5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216621362 | Ground Water | GEOSTAR | G5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625455 | Ground Water | GEOSTAR | G5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625456 | Ground Water | GEOSTAR | G5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625457 | Ground Water | GEOSTAR | G5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625458 | Ground Water | GEOSTAR | G5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625459 | Ground Water | GEOSTAR | G5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625460 | Ground Water | GEOSTAR | G5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625461 | Ground Water | GEOSTAR | G5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625462 | Ground Water | GEOSTAR | G5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625463 | Ground Water | GEOSTAR | G5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625464 | Ground Water | GEOSTAR | G5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625465 | Ground Water | GEOSTAR | G5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625466 | Ground Water | GEOSTAR | G5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625467 | Ground Water | GEOSTAR | G5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625468 | Ground Water | GEOSTAR | G5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625469 | Ground Water | GEOSTAR | G5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625470 | Ground Water | GEOSTAR | G5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625645 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625646 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625647 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625648 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625649 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625650 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625651 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625652 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625653 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625654 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625655 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625656 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625657 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625658 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625659 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625660 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625661 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625662 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625663 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625664 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625665 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625666 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625667 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625668 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625669 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625670 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625671 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625672 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625673 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625674 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625675 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625676 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625677 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625678 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625679 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625680 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625681 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625682 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625683 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625684 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625685 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625686 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625687 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625688 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625689 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625690 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625691 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625692 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625693 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625694 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625695 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
204100658 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204100659 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204100660 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204100661 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204101161 | Ground Water | 5 SERIES | NDV/NDH064J1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204117015 | Ground Water | GEOSTAR | 101/102J064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204117016 | Ground Water | GEOSTAR | 103J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204117017 | Ground Water | GEOSTAR | 103J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204140569 | Ground Water | GEO-THERMAL SPLIT | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140570 | Ground Water | CARRIER | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | No
204140571 | Ground Water | BRYANT | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140572 | Ground Water | HEIL | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | No
204140573 | Ground Water | ARCOAIRE | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140574 | Ground Water | KEEPRITE | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140575 | Ground Water | TEMPSTAR | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140576 | Ground Water | COMFORTMAKER | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140577 | Ground Water | DAY & NIGHT | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
207177429 | Ground Water | TRANE | GEVG006A |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
216979845 | Ground Water | KEEPRITE | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979846 | Ground Water | TEMPSTAR | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979847 | Ground Water | COMFORTMAKER | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979848 | Ground Water | DAY & NIGHT | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
5440541 | Ground Water | GEOCOMFORT | GXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440542 | Ground Water | HYDRON MODULE | HXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440543 | Ground Water | TETCO | TXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440554 | Ground Water | GEOCOMFORT | GXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
5440555 | Ground Water | HYDRON MODULE | HXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
5440557 | Ground Water | TETCO | TXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
207337515 | Ground Water | GEOSTAR | 103J042**1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207337516 | Ground Water | GEOSTAR | 103J042**1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207337517 | Ground Water | GEOSTAR | 103H048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
207337518 | Ground Water | GEOSTAR | 103H048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
207337521 | Ground Water | GEOSTAR | 103H070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207337522 | Ground Water | GEOSTAR | 103H070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207338127 | Ground Water | GEOSTAR | 141/142C036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
207338129 | Ground Water | GEOSTAR | 141/142C060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | No
207338249 | Ground Water | TRANE | GETE0241-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207338250 | Ground Water | TRANE | GETE0242-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207338251 | Ground Water | TRANE | GETE0247-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207348654 | Ground Water | WaterFurnace | URS036*0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348655 | Ground Water | WaterFurnace | URS036*0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348656 | Ground Water | WaterFurnace | URS036*0*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348657 | Ground Water | WaterFurnace | URS036*3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348658 | Ground Water | WaterFurnace | URS036*3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348659 | Ground Water | WaterFurnace | URS036*3*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348660 | Ground Water | WaterFurnace | URS036*4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348661 | Ground Water | WaterFurnace | URS036*4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348662 | Ground Water | WaterFurnace | URS036*4*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348663 | Ground Water | WaterFurnace | URS048*0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348664 | Ground Water | WaterFurnace | URS048*0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348665 | Ground Water | WaterFurnace | URS048*0*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348666 | Ground Water | WaterFurnace | URS048*3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348667 | Ground Water | WaterFurnace | URS048*3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348668 | Ground Water | WaterFurnace | URS048*3*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348669 | Ground Water | WaterFurnace | URS048*4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348670 | Ground Water | WaterFurnace | URS048*4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348671 | Ground Water | WaterFurnace | URS048*4*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348672 | Ground Water | WaterFurnace | URS070*0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348673 | Ground Water | WaterFurnace | URS070*0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348674 | Ground Water | WaterFurnace | URS070*0*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348675 | Ground Water | WaterFurnace | URS070*3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348676 | Ground Water | WaterFurnace | URS070*3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348677 | Ground Water | WaterFurnace | URS070*3*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348678 | Ground Water | WaterFurnace | URS070*4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
215832281 | Ground Water | HYDROTECH | WSH6009D* |  | 10000 | 23 | 8000 | 4.2 | 0.83333 | No
215832282 | Ground Water | HYDROTECH | WSH6012D* |  | 13000 | 23 | 11000 | 4.6 | 1.0833 | No
215832283 | Ground Water | HYDROTECH | WSH6018D* |  | 20400 | 25 | 16000 | 4.3 | 1.7 | No
215832284 | Ground Water | HYDROTECH | WSH6024D* |  | 28000 | 25 | 21400 | 4.3 | 2.3333 | No
215832285 | Ground Water | HYDROTECH | WSH6030D* |  | 32400 | 24 | 26000 | 4.2 | 2.7 | No
215832286 | Ground Water | HYDROTECH | WSH6036D* |  | 39000 | 23.2 | 35000 | 4.1 | 3.25 | No
215832287 | Ground Water | HYDROTECH | WSH6042D* |  | 45500 | 23.3 | 38000 | 4.3 | 3.7917 | No
215832288 | Ground Water | HYDROTECH | WSH6048D* |  | 52500 | 23.6 | 45500 | 4.2 | 4.375 | No
215832289 | Ground Water | HYDROTECH | WSH6060D* |  | 64000 | 23.5 | 51000 | 4.3 | 5.3333 | No
215832290 | Ground Water | HYDROTECH | WSH6072D* |  | 78000 | 21.8 | 68000 | 4.1 | 6.5 | No
215832291 | Ground Water | AE Air | WSH6009D* |  | 10000 | 23 | 8000 | 4.2 | 0.83333 | No
215832292 | Ground Water | AE Air | WSH6012D* |  | 13000 | 23 | 11000 | 4.6 | 1.0833 | No
215832293 | Ground Water | AE Air | WSH6018D* |  | 20400 | 25 | 16000 | 4.3 | 1.7 | No
215832294 | Ground Water | AE Air | WSH6024D* |  | 28000 | 25 | 21400 | 4.3 | 2.3333 | No
215832295 | Ground Water | AE Air | WSH6030D* |  | 32400 | 24 | 26000 | 4.2 | 2.7 | No
215832296 | Ground Water | AE Air | WSH6036D* |  | 39000 | 23.2 | 35000 | 4.1 | 3.25 | No
215832297 | Ground Water | AE Air | WSH6042D* |  | 45500 | 23.3 | 38000 | 4.3 | 3.7917 | No
215832298 | Ground Water | AE Air | WSH6048D* |  | 52500 | 23.6 | 45500 | 4.2 | 4.375 | No
215832299 | Ground Water | AE Air | WSH6060D* |  | 64000 | 23.5 | 51000 | 4.3 | 5.3333 | No
215832300 | Ground Water | AE Air | WSH6072D* |  | 78000 | 21.8 | 68000 | 4.1 | 6.5 | No
215270417 | Ground Water | BRYANT | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215270421 | Ground Water | CARRIER | GZ024*******1**1 | FE****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270423 | Ground Water | CARRIER | GZ036*******1**2 | FE****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215270427 | Ground Water | BRYANT | GZ024*******1**1 | FE****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270429 | Ground Water | BRYANT | GZ036*******1**2 | FE****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215278610 | Ground Water | WaterFurnace | W3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215285739 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215285740 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | Yes
215285741 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | Yes
215285742 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
215285743 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
216801918 | Ground Water | BOSCH-GEO | TW025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
216801920 | Ground Water | BOSCH-GEO | TW049-1***-*****C |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
216801922 | Ground Water | BOSCH | WT025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801923 | Ground Water | BOSCH | WT025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801932 | Ground Water | CARRIER | 50PSW025***3/CB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801933 | Ground Water | CARRIER | 50PSW025***4/DB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801934 | Ground Water | CARRIER | 50PSW025***5/EB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801935 | Ground Water | CARRIER | 50PSW025***6/FB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801983 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**3*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801984 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**3*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801985 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**3*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801986 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**3*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801987 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**4*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801988 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**4*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801989 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**4*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
10304639 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304640 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304641 | Ground Water | GeoSmart Energy | GTZ026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304642 | Ground Water | GEOSTAR | 103H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10304646 | Ground Water | GEOSTAR | 103H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304657 | Ground Water | GeoSmart Energy | GTZ026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10305457 | Ground Water | GEOSTAR | 104H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10305458 | Ground Water | GEOSTAR | 104H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316642 | Ground Water | YORK BY JOHNSON CONTROLS | YAST026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316643 | Ground Water | GeoSmart Energy | GTS026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316644 | Ground Water | YORK BY JOHNSON CONTROLS | YAST026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316645 | Ground Water | GeoSmart Energy | GTS026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316654 | Ground Water | YORK BY JOHNSON CONTROLS | YAST049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316655 | Ground Water | GEOSTAR | 104H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316656 | Ground Water | GeoSmart Energy | GTS049*1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316657 | Ground Water | YORK BY JOHNSON CONTROLS | YAST049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316658 | Ground Water | GeoSmart Energy | GTS049*1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316660 | Ground Water | GEOSTAR | 104H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316661 | Ground Water | YORK BY JOHNSON CONTROLS | YAST064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
214595581 | Ground Water | AAON, Inc. | SB-004-2-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
214595583 | Ground Water | AAON, Inc. | SB-004-3-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
214595585 | Ground Water | AAON, Inc. | SB-004-4-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
214595607 | Ground Water | AAON, Inc. | M2-003-2-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595611 | Ground Water | AAON, Inc. | M2-003-3-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595615 | Ground Water | AAON, Inc. | M2-003-4-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595618 | Ground Water | AAON, Inc. | M2-004-1-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595619 | Ground Water | AAON, Inc. | M2-004-1-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
214595620 | Ground Water | AAON, Inc. | M2-004-2-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595621 | Ground Water | AAON, Inc. | M2-004-2-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595622 | Ground Water | AAON, Inc. | M2-004-2-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595623 | Ground Water | AAON, Inc. | M2-004-2-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
5646388 | Ground Water | HYDRON MODULE | HCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646389 | Ground Water | TETCO | TCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646391 | Ground Water | GEOCOMFORT | GXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646392 | Ground Water | HYDRON MODULE | HXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646393 | Ground Water | TETCO | TXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646394 | Ground Water | GEOCOMFORT | GXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646395 | Ground Water | HYDRON MODULE | HXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646396 | Ground Water | TETCO | TXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646397 | Ground Water | GEOCOMFORT | GXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646398 | Ground Water | HYDRON MODULE | HXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646399 | Ground Water | TETCO | TXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646765 | Ground Water | GEOCOMFORT | GCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
5646766 | Ground Water | HYDRON MODULE | HCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
5646767 | Ground Water | TETCO | TCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
5646768 | Ground Water | GEOCOMFORT | GCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646769 | Ground Water | HYDRON MODULE | HCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646770 | Ground Water | TETCO | TCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646771 | Ground Water | GEOCOMFORT | GCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646772 | Ground Water | HYDRON MODULE | HCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646773 | Ground Water | TETCO | TCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5699505 | Ground Water | TRANE | VSVE0421 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699525 | Ground Water | TRANE | VSVE0422 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699526 | Ground Water | TRANE | VSVE0424 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699527 | Ground Water | TRANE | VSVE0601 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699534 | Ground Water | TRANE | VSVE0602 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699535 | Ground Water | TRANE | VSVE0604 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699628 | Ground Water | TRANE | VSHE0241 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699631 | Ground Water | TRANE | VSHE0242 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699633 | Ground Water | TRANE | VSHE0244 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699634 | Ground Water | TRANE | VSHE0331 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699635 | Ground Water | TRANE | VSHE0332 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699637 | Ground Water | TRANE | VSHE0334 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699639 | Ground Water | TRANE | VSHE0421 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699644 | Ground Water | TRANE | VSHE0422 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699650 | Ground Water | TRANE | VSHE0424 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699652 | Ground Water | TRANE | VSHE0501 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699653 | Ground Water | TRANE | VSHE0502 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699654 | Ground Water | TRANE | VSHE0504 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699655 | Ground Water | TRANE | VSHE0601 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
6501973 | Ground Water | GEOSTAR | GBV/GBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501974 | Ground Water | GEOSTAR | GBV/GBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501975 | Ground Water | GEOSTAR | GBV/GBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501976 | Ground Water | GEOSTAR | GBV/GBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501977 | Ground Water | GEOSTAR | GBV/GBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501978 | Ground Water | GEOSTAR | GBV/GBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501979 | Ground Water | GEOSTAR | GBV/GBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501980 | Ground Water | GEOSTAR | GBV/GBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501981 | Ground Water | GEOSTAR | GBV/GBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501982 | Ground Water | GEOSTAR | GBV/GBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501983 | Ground Water | GEOSTAR | GBV/GBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501984 | Ground Water | GEOSTAR | GBV/GBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501985 | Ground Water | GEOSTAR | GBV/GBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501986 | Ground Water | GEOSTAR | GBV/GBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501987 | Ground Water | GEOSTAR | GBV/GBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501988 | Ground Water | GEOSTAR | GBV/GBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501989 | Ground Water | GEOSTAR | GBV/GBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501990 | Ground Water | GEOSTAR | GBV/GBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501991 | Ground Water | GEOSTAR | GBV/GBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501993 | Ground Water | GEOSTAR | GBV/GBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501994 | Ground Water | GEOSTAR | GBV/GBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501996 | Ground Water | GEOSTAR | GBV/GBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501997 | Ground Water | GEOSTAR | GBV/GBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501999 | Ground Water | GEOSTAR | GBV/GBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6502000 | Ground Water | GEOSTAR | GBV/GBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6502002 | Ground Water | GEOSTAR | GBV/GBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502003 | Ground Water | GEOSTAR | GBV/GBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502004 | Ground Water | GEOSTAR | GBV/GBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502005 | Ground Water | GEOSTAR | GBV/GBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502006 | Ground Water | GEOSTAR | GBV/GBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502007 | Ground Water | GEOSTAR | GBV/GBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207335338 | Ground Water | GEOSTAR | 111K038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
207335397 | Ground Water | GeoSmart Energy | GT026**1*(1,4)*J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335398 | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335399 | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335400 | Ground Water | GeoSmart Energy | GT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335401 | Ground Water | GeoSmart Energy | GT072**1*(1,4)*J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335402 | Ground Water | GeoSmart Energy | GS012**1*0*J |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207335403 | Ground Water | GeoSmart Energy | GS018**1*(1,4)*J |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335404 | Ground Water | GeoSmart Energy | GS018**1*0*J |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | Yes
207335406 | Ground Water | GeoSmart Energy | GS022**1*(1,4)*J |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
207335407 | Ground Water | GeoSmart Energy | GS030**1*(0,3)*J |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | Yes
207335408 | Ground Water | GeoSmart Energy | GS030**1*(1,4)*J |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335409 | Ground Water | GeoSmart Energy | GS036**1*(0,3)*K |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207335410 | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*K |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207335411 | Ground Water | GeoSmart Energy | GS042**1*(0,3)*K |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | Yes
207335412 | Ground Water | GeoSmart Energy | GS048**1*(0,3)*K |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | Yes
207335413 | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*K |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335414 | Ground Water | GeoSmart Energy | GS060**1*(1,4)*K |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335415 | Ground Water | GeoSmart Energy | GS060**1*0*K |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | Yes
207335416 | Ground Water | GeoSmart Energy | GS070**1*(1,4)*J |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335514 | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335570 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS012**1*0****J |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207335571 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****J |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335572 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(1,4)****J |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
207335573 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335574 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*K |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207335575 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335576 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*K |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335577 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****K |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335578 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****J |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335579 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335580 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335581 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335582 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335583 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335584 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335585 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335586 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335587 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
209156961 | Ground Water | AE Air | WSV6024A |  | 25400 | 24 | 22000 | 4.1 | 2.1167 | No
209156963 | Ground Water | AE Air | WSV6036A |  | 41500 | 24 | 35500 | 4.1 | 3.4583 | No
209156964 | Ground Water | AE Air | WSV6042A |  | 46500 | 24 | 39000 | 4.2 | 3.875 | No
209156970 | Ground Water | AE Air | WSV6060A |  | 65000 | 23 | 53500 | 4.1 | 5.4167 | No
209156972 | Ground Water | AE Air | WSV6090A |  | 101000 | 22 | 73000 | 4.1 | 8.4167 | No
209156974 | Ground Water | AE Air | WSS6006*6* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
209156975 | Ground Water | AE Air | WSS6009*6* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
209156976 | Ground Water | AE Air | WSS6012*6* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
209156977 | Ground Water | AE Air | WSS6015*6* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
209156981 | Ground Water | AE Air | WSHXE06A6* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
209156987 | Ground Water | AE Air | WSHXE06A7* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
209156993 | Ground Water | AE Air | WSS6006*7* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
209156994 | Ground Water | AE Air | WSS6009*7* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
209156995 | Ground Water | AE Air | WSS6012*7* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
216979849 | Ground Water | HEIL | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979850 | Ground Water | ARCOAIRE | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979851 | Ground Water | KEEPRITE | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979852 | Ground Water | TEMPSTAR | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979853 | Ground Water | COMFORTMAKER | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979854 | Ground Water | DAY & NIGHT | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979855 | Ground Water | HEIL | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979856 | Ground Water | ARCOAIRE | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979857 | Ground Water | KEEPRITE | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979858 | Ground Water | TEMPSTAR | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979859 | Ground Water | COMFORTMAKER | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979860 | Ground Water | DAY & NIGHT | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979861 | Ground Water | HEIL | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979862 | Ground Water | ARCOAIRE | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979863 | Ground Water | KEEPRITE | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979864 | Ground Water | TEMPSTAR | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979865 | Ground Water | COMFORTMAKER | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979866 | Ground Water | DAY & NIGHT | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979867 | Ground Water | HEIL | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979868 | Ground Water | ARCOAIRE | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979869 | Ground Water | KEEPRITE | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979870 | Ground Water | TEMPSTAR | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979871 | Ground Water | COMFORTMAKER | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979872 | Ground Water | DAY & NIGHT | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979873 | Ground Water | HEIL | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979874 | Ground Water | ARCOAIRE | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979875 | Ground Water | KEEPRITE | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979876 | Ground Water | TEMPSTAR | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979877 | Ground Water | COMFORTMAKER | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979878 | Ground Water | DAY & NIGHT | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979879 | Ground Water | HEIL | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979880 | Ground Water | ARCOAIRE | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979881 | Ground Water | KEEPRITE | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979882 | Ground Water | TEMPSTAR | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979883 | Ground Water | COMFORTMAKER | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979884 | Ground Water | DAY & NIGHT | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979885 | Ground Water | HEIL | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216979886 | Ground Water | ARCOAIRE | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979887 | Ground Water | KEEPRITE | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979888 | Ground Water | TEMPSTAR | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979889 | Ground Water | COMFORTMAKER | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979890 | Ground Water | DAY & NIGHT | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979891 | Ground Water | HEIL | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979892 | Ground Water | ARCOAIRE | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979893 | Ground Water | KEEPRITE | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979894 | Ground Water | TEMPSTAR | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979895 | Ground Water | COMFORTMAKER | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979896 | Ground Water | DAY & NIGHT | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
217014524 | Ground Water | CARRIER | GCA72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014525 | Ground Water | BRYANT | GCA72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014526 | Ground Water | CARRIER | GCA72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014527 | Ground Water | BRYANT | GCA72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
7487661 | Ground Water | GEOCOMFORT | GYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487662 | Ground Water | HYDRON MODULE | HYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487663 | Ground Water | TETCO | TYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487664 | Ground Water | TETCO | TYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487665 | Ground Water | HYDRON MODULE | HYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487666 | Ground Water | GEOCOMFORT | GYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487667 | Ground Water | GEOCOMFORT | GYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487668 | Ground Water | HYDRON MODULE | HYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487669 | Ground Water | TETCO | TYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7499543 | Ground Water | FHP | LM024-1CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499546 | Ground Water | FHP | LM024-2CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499547 | Ground Water | FHP | LM024-3CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499548 | Ground Water | FHP | LM024-4CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499550 | Ground Water | FHP | LM036-1VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499552 | Ground Water | FHP | LM036-2VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499553 | Ground Water | FHP | LM036-3VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499554 | Ground Water | FHP | LM036-4VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499556 | Ground Water | FHP | LM048-1VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499559 | Ground Water | FHP | LM048-3VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499560 | Ground Water | FHP | LM048-4VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499562 | Ground Water | FHP | LM060-1VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
5440573 | Ground Water | GEOCOMFORT | GXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440574 | Ground Water | HYDRON MODULE | HXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440575 | Ground Water | TETCO | TXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440576 | Ground Water | GEOCOMFORT | GXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440577 | Ground Water | HYDRON MODULE | HXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440578 | Ground Water | TETCO | TXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440703 | Ground Water | GEOCOMFORT | GXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440704 | Ground Water | HYDRON MODULE | HXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440705 | Ground Water | TETCO | TXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440708 | Ground Water | GEOCOMFORT | GXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440709 | Ground Water | HYDRON MODULE | HXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440710 | Ground Water | TETCO | TXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5599272 | Ground Water | BOSCH-GEO | SM036-1CF/HZ/VT |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
5599275 | Ground Water | BOSCH-GEO | SM060-1CF/HZ/VT |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
5599276 | Ground Water | BOSCH-GEO | SM070-1CF/HZ/VT |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
217037819 | Ground Water | GeoSmart Energy | S5SZ060BD1 | S5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037820 | Ground Water | GeoSmart Energy | S5SZ066BD1 | S5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037821 | Ground Water | GeoSmart Energy | S5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037822 | Ground Water | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037823 | Ground Water | GeoSmart Energy | S5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037824 | Ground Water | GeoSmart Energy | S5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037825 | Ground Water | GeoSmart Energy | S5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037826 | Ground Water | GeoSmart Energy | S5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037827 | Ground Water | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037828 | Ground Water | GeoSmart Energy | S5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037829 | Ground Water | GeoSmart Energy | S5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037830 | Ground Water | GeoSmart Energy | S5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217351749 | Ground Water | CARRIER | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351750 | Ground Water | CARRIER | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351752 | Ground Water | CARRIER | GW024WA********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351754 | Ground Water | CARRIER | GW048WA********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351757 | Ground Water | BRYANT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351758 | Ground Water | BRYANT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351759 | Ground Water | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351760 | Ground Water | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351761 | Ground Water | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351762 | Ground Water | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351763 | Ground Water | BRYANT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351765 | Ground Water | BRYANT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351766 | Ground Water | BRYANT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351768 | Ground Water | BRYANT | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351769 | Ground Water | BRYANT | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351770 | Ground Water | BRYANT | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351771 | Ground Water | BRYANT | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351772 | Ground Water | BRYANT | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351773 | Ground Water | BRYANT | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351774 | Ground Water | BRYANT | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351776 | Ground Water | BRYANT | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351777 | Ground Water | BRYANT | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
203344888 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
203344891 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
203363126 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**0*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363127 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**0*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
7167540 | Ground Water | CARRIER | 50PTD/H/V024***4/DA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167541 | Ground Water | CARRIER | 50PTD/H/V024***6/FA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167542 | Ground Water | CARRIER | 50PTD/H/V036***3/CA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167543 | Ground Water | CARRIER | 50PTD/H/V036***5/EA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167544 | Ground Water | CARRIER | 50PTD/H/V036***4/DA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167545 | Ground Water | CARRIER | 50PTD/H/V036***6/FA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167546 | Ground Water | CARRIER | 50PTD/H/V048***3/CA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167547 | Ground Water | CARRIER | 50PTD/H/V048***5/EA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167548 | Ground Water | CARRIER | 50PTD/H/V048***6/FA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167549 | Ground Water | CARRIER | 50PTD/H/V060***3/CA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7167550 | Ground Water | CARRIER | 50PTD/H/V060***5/EA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7167551 | Ground Water | CARRIER | 50PTD/H/V060***6/FA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7167552 | Ground Water | CARRIER | 50PTD/H/V070***3/CA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167553 | Ground Water | CARRIER | 50PTD/H/V070***5/EA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167554 | Ground Water | CARRIER | 50PTD/H/V070***6/FA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7170602 | Ground Water | GEOCOMFORT | GVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
7170603 | Ground Water | HYDRON MODULE | HVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
7170604 | Ground Water | TETCO | TVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
206438717 | Ground Water | BOSCH | EP007-1HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438718 | Ground Water | BOSCH | EP007-2HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438719 | Ground Water | BOSCH | EP009-1HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
216569714 | Ground Water | GeoCool | GCHPV/H/D036BT**A*** |  | 41500 | 27.2 | 36600 | 4.9 | 3.4583 | No
216569715 | Ground Water | GeoCool | GCHPV/H/D048BT**A*** |  | 54800 | 26 | 48200 | 4.9 | 4.5667 | No
216569813 | Ground Water | GeoCool | GCHPV/H/D060BT**A*** |  | 69500 | 24 | 61600 | 4.9 | 5.7917 | No
216621309 | Ground Water | GEOSTAR | G5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216621310 | Ground Water | GEOSTAR | G5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216621311 | Ground Water | GEOSTAR | G5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216621312 | Ground Water | GEOSTAR | G5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216621313 | Ground Water | GEOSTAR | G5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216621314 | Ground Water | GEOSTAR | G5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216621315 | Ground Water | GEOSTAR | G5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216621316 | Ground Water | GEOSTAR | G5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216621317 | Ground Water | GEOSTAR | G5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216621318 | Ground Water | GEOSTAR | G5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216621319 | Ground Water | GEOSTAR | G5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216621323 | Ground Water | GEOSTAR | G5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216621324 | Ground Water | GEOSTAR | G5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216621325 | Ground Water | GEOSTAR | G5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621326 | Ground Water | GEOSTAR | G5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621327 | Ground Water | GEOSTAR | G5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621328 | Ground Water | GEOSTAR | G5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621329 | Ground Water | GEOSTAR | G5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621330 | Ground Water | GEOSTAR | G5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621331 | Ground Water | GEOSTAR | G5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621332 | Ground Water | GEOSTAR | G5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621333 | Ground Water | GEOSTAR | G5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621334 | Ground Water | GEOSTAR | G5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621335 | Ground Water | GEOSTAR | G5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621336 | Ground Water | GEOSTAR | G5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621337 | Ground Water | GEOSTAR | G5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621338 | Ground Water | GEOSTAR | G5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621339 | Ground Water | GEOSTAR | G5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621340 | Ground Water | GEOSTAR | G5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621341 | Ground Water | GEOSTAR | G5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621342 | Ground Water | GEOSTAR | G5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621343 | Ground Water | GEOSTAR | G5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621344 | Ground Water | GEOSTAR | G5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621345 | Ground Water | GEOSTAR | G5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621346 | Ground Water | GEOSTAR | G5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621347 | Ground Water | GEOSTAR | G5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621348 | Ground Water | GEOSTAR | G5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621349 | Ground Water | GEOSTAR | G5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621350 | Ground Water | GEOSTAR | G5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621351 | Ground Water | GEOSTAR | G5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621352 | Ground Water | GEOSTAR | G5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621353 | Ground Water | GEOSTAR | G5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621354 | Ground Water | GEOSTAR | G5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621355 | Ground Water | GEOSTAR | G5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621356 | Ground Water | GEOSTAR | G5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621357 | Ground Water | GEOSTAR | G5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621358 | Ground Water | GEOSTAR | G5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621359 | Ground Water | GEOSTAR | G5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
217967018 | Ground Water | TRANE | VSHK024A |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
217967019 | Ground Water | TRANE | VSVK024A |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967020 | Ground Water | TRANE | VSHK033A |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967021 | Ground Water | TRANE | VSVK033A |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967022 | Ground Water | TRANE | VSHK042A |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967023 | Ground Water | TRANE | VSVK042A |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
217967024 | Ground Water | TRANE | VSHK050A |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967025 | Ground Water | TRANE | VSVK050A |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967026 | Ground Water | TRANE | VSHK060A |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967027 | Ground Water | TRANE | VSVK060A |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
217967028 | Ground Water | TRANE | VSHK024B |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
217967029 | Ground Water | TRANE | VSVK024B |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967030 | Ground Water | TRANE | VSHK033B |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967031 | Ground Water | TRANE | VSVK033B |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967032 | Ground Water | TRANE | VSHK042B |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967033 | Ground Water | TRANE | VSVK042B |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
217967034 | Ground Water | TRANE | VSHK050B |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967035 | Ground Water | TRANE | VSVK050B |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967036 | Ground Water | TRANE | VSHK060B |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967037 | Ground Water | TRANE | VSVK060B |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
7519580 | Ground Water | HYDRON MODULE | HVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519581 | Ground Water | TETCO | TVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519582 | Ground Water | GEOCOMFORT | GVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519583 | Ground Water | HYDRON MODULE | HVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519584 | Ground Water | TETCO | TVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519727 | Ground Water | GEOCOMFORT | GVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
7519748 | Ground Water | HYDRON MODULE | HVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
7519756 | Ground Water | TETCO | TVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
7519769 | Ground Water | GEOCOMFORT | GVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519770 | Ground Water | HYDRON MODULE | HVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519771 | Ground Water | TETCO | TVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519772 | Ground Water | GEOCOMFORT | GVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519773 | Ground Water | HYDRON MODULE | HVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519774 | Ground Water | TETCO | TVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519775 | Ground Water | GEOCOMFORT | GVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519776 | Ground Water | HYDRON MODULE | HVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519777 | Ground Water | TETCO | TVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7520238 | Ground Water | GEOCOMFORT | GVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520239 | Ground Water | HYDRON MODULE | HVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520240 | Ground Water | TETCO | TVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520241 | Ground Water | GEOCOMFORT | GVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520242 | Ground Water | HYDRON MODULE | HVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520243 | Ground Water | TETCO | TVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520244 | Ground Water | TETCO | TVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520245 | Ground Water | HYDRON MODULE | HVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520246 | Ground Water | GEOCOMFORT | GVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520247 | Ground Water | HYDRON MODULE | HVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520248 | Ground Water | TETCO | TVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520249 | Ground Water | GEOCOMFORT | GVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520250 | Ground Water | GEOCOMFORT | GVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520251 | Ground Water | HYDRON MODULE | HVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520252 | Ground Water | TETCO | TVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520253 | Ground Water | GEOCOMFORT | GVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520254 | Ground Water | HYDRON MODULE | HVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520255 | Ground Water | TETCO | TVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520256 | Ground Water | GEOCOMFORT | GVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520257 | Ground Water | HYDRON MODULE | HVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520258 | Ground Water | TETCO | TVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520259 | Ground Water | GEOCOMFORT | GVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520260 | Ground Water | HYDRON MODULE | HVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520261 | Ground Water | TETCO | TVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7523956 | Ground Water | GEOCOMFORT | GVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
7523957 | Ground Water | HYDRON MODULE | HVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
7523958 | Ground Water | TETCO | TVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
7523959 | Ground Water | GEOCOMFORT | GVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
7523960 | Ground Water | HYDRON MODULE | HVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
7523961 | Ground Water | TETCO | TVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
217642876 | Ground Water | GeoSmart Energy | S3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642879 | Ground Water | GeoSmart Energy | S3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642881 | Ground Water | GeoSmart Energy | S3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642883 | Ground Water | GeoSmart Energy | S3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642884 | Ground Water | GeoSmart Energy | S3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642886 | Ground Water | GeoSmart Energy | S3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642888 | Ground Water | GeoSmart Energy | S3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642891 | Ground Water | GeoSmart Energy | S3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642892 | Ground Water | GeoSmart Energy | S3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642893 | Ground Water | GeoSmart Energy | S3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
7409789 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
7409859 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
7409937 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
7410008 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
7410095 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
7410164 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410223 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410291 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
7410355 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410435 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410522 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
7410657 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7410717 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
7410825 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7410908 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7411002 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7411100 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411231 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411301 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7411380 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411778 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411875 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7411949 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
217351835 | Ground Water | COMFORTMAKER | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351838 | Ground Water | DAY & NIGHT | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351839 | Ground Water | DAY & NIGHT | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351840 | Ground Water | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351841 | Ground Water | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351842 | Ground Water | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351843 | Ground Water | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351844 | Ground Water | DAY & NIGHT | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351846 | Ground Water | DAY & NIGHT | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351847 | Ground Water | DAY & NIGHT | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351849 | Ground Water | DAY & NIGHT | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351850 | Ground Water | DAY & NIGHT | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351851 | Ground Water | DAY & NIGHT | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351852 | Ground Water | DAY & NIGHT | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351853 | Ground Water | DAY & NIGHT | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351854 | Ground Water | DAY & NIGHT | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351855 | Ground Water | DAY & NIGHT | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351857 | Ground Water | DAY & NIGHT | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351858 | Ground Water | DAY & NIGHT | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351860 | Ground Water | DAY & NIGHT | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351862 | Ground Water | DAY & NIGHT | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351865 | Ground Water | HEIL | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351866 | Ground Water | HEIL | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351867 | Ground Water | HEIL | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351868 | Ground Water | HEIL | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351869 | Ground Water | HEIL | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351870 | Ground Water | HEIL | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351871 | Ground Water | HEIL | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351873 | Ground Water | HEIL | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351874 | Ground Water | HEIL | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351876 | Ground Water | HEIL | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351877 | Ground Water | HEIL | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351878 | Ground Water | HEIL | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351879 | Ground Water | HEIL | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
205312008 | Ground Water | GEOSTAR | ZBV/ZBH042**4*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312009 | Ground Water | GEOSTAR | ZBV/ZBH042**0*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312010 | Ground Water | GEOSTAR | ZBV/ZBH042**3*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312011 | Ground Water | GEOSTAR | ZBV/ZBH042**4*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312027 | Ground Water | GEOSTAR | ZBV/ZBH060**0*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312028 | Ground Water | GEOSTAR | ZBV/ZBH060**3*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312029 | Ground Water | GEOSTAR | ZBV/ZBH060**4*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312030 | Ground Water | GEOSTAR | ZBV/ZBH060**0*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312031 | Ground Water | GEOSTAR | ZBV/ZBH060**3*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312032 | Ground Water | GEOSTAR | ZBV/ZBH060**4*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312037 | Ground Water | GEOSTAR | ZBV/ZBH070**0*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449797 | Ground Water | WaterFurnace | UBV/UBH042**4*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449798 | Ground Water | WaterFurnace | UBV/UBH042**0*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449799 | Ground Water | WaterFurnace | UBV/UBH042**3*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449800 | Ground Water | WaterFurnace | UBV/UBH042**4*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449816 | Ground Water | WaterFurnace | UBV/UBH060**0*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449817 | Ground Water | WaterFurnace | UBV/UBH060**3*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449818 | Ground Water | WaterFurnace | UBV/UBH060**4*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449819 | Ground Water | WaterFurnace | UBV/UBH060**0*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449820 | Ground Water | WaterFurnace | UBV/UBH060**3*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449821 | Ground Water | WaterFurnace | UBV/UBH060**4*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449826 | Ground Water | WaterFurnace | UBV/UBH070**0*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449827 | Ground Water | WaterFurnace | UBV/UBH070**3*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449828 | Ground Water | WaterFurnace | UBV/UBH070**4*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449829 | Ground Water | WaterFurnace | UBV/UBH070**0*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449830 | Ground Water | WaterFurnace | UBV/UBH070**3*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449831 | Ground Water | WaterFurnace | UBV/UBH070**4*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
6674620 | Ground Water | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674621 | Ground Water | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674622 | Ground Water | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674623 | Ground Water | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6676515 | Ground Water | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676516 | Ground Water | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676518 | Ground Water | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676519 | Ground Water | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6677645 | Ground Water | BOSCH | LM048-1VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
6677682 | Ground Water | BOSCH | LM048-3VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
6677754 | Ground Water | BOSCH | LM048-4VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
6677875 | Ground Water | BOSCH | LM060-1VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677876 | Ground Water | BOSCH | LM060-3VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677878 | Ground Water | BOSCH | LM060-4VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677886 | Ground Water | BOSCH | LM070-1VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
6677887 | Ground Water | BOSCH | LM070-3VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
6677889 | Ground Water | BOSCH | LM070-4VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
203143790 | Ground Water | TETCO | TVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203238019 | Ground Water | BOSCH-GEO | BP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203238020 | Ground Water | GEO-THERMAL SPLIT | GZ036***C***1**2 | FE/V****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203238919 | Ground Water | BOSCH-GEO | SM024-1VT/CFN-*****A |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203238923 | Ground Water | BOSCH-GEO | SM024-1HZC-*****A |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | No
203238926 | Ground Water | BOSCH-GEO | SM024-1HZN-*****A |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | No
203253412 | Ground Water | BOSCH | BP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203253413 | Ground Water | BOSCH | SM024-1HZC-*****A |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203253414 | Ground Water | BOSCH | SM024-1HZC-*****C |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203253415 | Ground Water | BOSCH | SM024-1HZN-*****A |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203253416 | Ground Water | BOSCH | SM024-1HZN-*****C |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203254061 | Ground Water | BOSCH-GEO | SM070-1VT*-*****C |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
203254465 | Ground Water | BOSCH | SM070-1VT*******C |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
203254574 | Ground Water | CARRIER | GZ036***C***1**2 | FE/V****005 | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
203254575 | Ground Water | BRYANT | GZ036***C***1**2 | FE/V****005 | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254576 | Ground Water | HEIL | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
203254577 | Ground Water | ARCOAIRE | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254578 | Ground Water | KEEPRITE | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254579 | Ground Water | TEMPSTAR | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254580 | Ground Water | COMFORTMAKER | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254581 | Ground Water | DAY & NIGHT | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254606 | Ground Water | CARRIER | GB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203254607 | Ground Water | BRYANT | GB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254608 | Ground Water | ARCOAIRE | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
213154474 | Ground Water | GeoSmart Energy | GT038**1*1********L |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
213154475 | Ground Water | GeoSmart Energy | GT049**1*1********L |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
213154476 | Ground Water | GeoSmart Energy | GT064**1*1********L |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
213154477 | Ground Water | GeoSmart Energy | GT072**1*1********L |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
213307834 | Ground Water | GeoSmart Energy | QT038**1*(1,2)*****K |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
213307835 | Ground Water | GeoSmart Energy | QT049**1*(1,2)*****J |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
213348376 | Ground Water | ClimateMaster | TRT072D |  | 76000 | 21.3 | 72000 | 4.4 | 6.3333 | No
213351451 | Ground Water | YORK BY JOHNSON CONTROLS | YLFT048**1*4*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
203265288 | Ground Water | BOSCH-GEO | SM048-1VT/CFC-*****A |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265289 | Ground Water | BOSCH-GEO | SM048-1VT/CFN-*****A |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265290 | Ground Water | BOSCH-GEO | SM048-1HZC-*****A |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265291 | Ground Water | BOSCH-GEO | SM048-1HZN-*****A |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265529 | Ground Water | BOSCH | SM048-1HZC-*****A |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265533 | Ground Water | BOSCH | SM048-1HZC-*****C |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265538 | Ground Water | BOSCH | SM048-1HZN-*****A |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265540 | Ground Water | BOSCH | SM048-1HZN-*****C |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265973 | Ground Water | CARRIER | GC048V/C**C***1**1 |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265976 | Ground Water | BRYANT | GC048V/C**C***1*X1 |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265980 | Ground Water | CARRIER | GC048V/C**N***1**1 |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265983 | Ground Water | BRYANT | GC048V/C**N***1*X1 |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265987 | Ground Water | CARRIER | GC048H**C***1**1 |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265989 | Ground Water | BRYANT | GC048H**C***1*X1 |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265990 | Ground Water | CARRIER | GC048H**N***1**1 |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265991 | Ground Water | BRYANT | GC048H**N***1*X1 |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203268807 | Ground Water | BOSCH | SM060-1HZ*******C |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
203303750 | Ground Water | BOSCH-GEO | CE035-1VT/HZ/CF*-*****B |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
203303751 | Ground Water | BOSCH-GEO | BP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303773 | Ground Water | BOSCH | CE035-1VT/HZ/CF*-*****B |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303774 | Ground Water | BOSCH | BP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303777 | Ground Water | CARRIER | GB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303778 | Ground Water | BRYANT | GB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303779 | Ground Water | HEIL | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303780 | Ground Water | ARCOAIRE | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303781 | Ground Water | KEEPRITE | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303782 | Ground Water | TEMPSTAR | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303783 | Ground Water | COMFORTMAKER | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303784 | Ground Water | DAY & NIGHT | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303785 | Ground Water | CARRIER | GP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
214839501 | Ground Water | CARRIER | 50WC*042(L/M/S/T)**6*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
211594122 | Ground Water | TRANE | GEHG018A |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
211594123 | Ground Water | TRANE | GEHG024A |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594124 | Ground Water | TRANE | GEHG030A |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594125 | Ground Water | TRANE | GEHG036A |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594126 | Ground Water | TRANE | GEHG042A |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594127 | Ground Water | TRANE | GEHG048A |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594128 | Ground Water | TRANE | GEHG060A |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
211594129 | Ground Water | TRANE | EXHG009A |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
211594130 | Ground Water | TRANE | EXHG012A |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
211594131 | Ground Water | TRANE | EXHG015A |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
211594132 | Ground Water | TRANE | EXHG018A |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
211594133 | Ground Water | TRANE | EXHG024A |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594134 | Ground Water | TRANE | EXHG030A |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594135 | Ground Water | TRANE | EXHG036A |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594136 | Ground Water | TRANE | EXHG042A |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594137 | Ground Water | TRANE | EXHG048A |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594138 | Ground Water | TRANE | EXHG060A |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594139 | Ground Water | TRANE | EXHG070A |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
211594212 | Ground Water | TRANE | DXHG024A |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594213 | Ground Water | TRANE | DXHG036A |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594214 | Ground Water | TRANE | DXHG048A |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594215 | Ground Water | TRANE | DXHG060A |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
211594216 | Ground Water | TRANE | DXHG070A |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
211594222 | Ground Water | TRANE | GEHG0067 |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
211594223 | Ground Water | TRANE | GEHG0097 |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
211594224 | Ground Water | TRANE | GEHG0127 |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
211594225 | Ground Water | TRANE | GEHG0157 |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
211594226 | Ground Water | TRANE | GEHG0187 |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
211594227 | Ground Water | TRANE | GEHG024B |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594228 | Ground Water | TRANE | GEHG0244 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594229 | Ground Water | TRANE | GEHG0247 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594230 | Ground Water | TRANE | GEHG030B |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594231 | Ground Water | TRANE | GEHG0304 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594232 | Ground Water | TRANE | GEHG0307 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594233 | Ground Water | TRANE | GEHG036B |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594234 | Ground Water | TRANE | GEHG0364 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594235 | Ground Water | TRANE | GEHG0367 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594236 | Ground Water | TRANE | GEHG042B |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594237 | Ground Water | TRANE | GEHG0424 |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594238 | Ground Water | TRANE | GEHG048B |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594239 | Ground Water | TRANE | GEHG0484 |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594240 | Ground Water | TRANE | GEHG060B |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
215415870 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415871 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415872 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415873 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415874 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415875 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415876 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415877 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415878 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
215415879 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
215415880 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
215415881 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
215415884 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
215415885 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
215415886 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
215415887 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
215415888 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
215415889 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
215415909 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215415910 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215415911 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | Yes
215415912 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | Yes
215415913 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | Yes
215415914 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | Yes
215415915 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
963501 | Ground Water | WaterFurnace | NLH/NXH095**3 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963502 | Ground Water | WaterFurnace | NLH/NXH095**4 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963503 | Ground Water | WaterFurnace | NLH/NXH095**5 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963504 | Ground Water | WaterFurnace | NLH/NXH120**3 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963505 | Ground Water | WaterFurnace | NLH/NXH120**4 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963506 | Ground Water | WaterFurnace | NLH/NXH120**5 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963507 | Ground Water | WaterFurnace | NLV/NXV080T*3 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963508 | Ground Water | WaterFurnace | NLV/NXV080T*4 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963509 | Ground Water | WaterFurnace | NLV/NXV080T*5 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963510 | Ground Water | WaterFurnace | NLV/NXV095T*3 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963511 | Ground Water | WaterFurnace | NLV/NXV095T*4 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963512 | Ground Water | WaterFurnace | NLV/NXV095T*5 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963513 | Ground Water | WaterFurnace | NLV/NXV120T*3 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
963514 | Ground Water | WaterFurnace | NLV/NXV120T*4 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
963515 | Ground Water | WaterFurnace | NLV/NXV120T*5 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
1483426 | Ground Water | BOSCH | BP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
1483428 | Ground Water | BOSCH | BP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
1483429 | Ground Water | BOSCH | BP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3059231 | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3059237 | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3093286 | Ground Water | TRANE | GEHE072 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
3093289 | Ground Water | TRANE | GEVE072 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
3093290 | Ground Water | TRANE | GEVE090 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
3627926 | Ground Water | WaterFurnace | USV/USH015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
3627927 | Ground Water | WaterFurnace | USV/USH015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
202146929 | Ground Water | HYDRON MODULE | HZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
202146930 | Ground Water | TETCO | TZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
202146931 | Ground Water | TETCO | TZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146932 | Ground Water | TETCO | TZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
202146933 | Ground Water | TETCO | TZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
202146936 | Ground Water | GEOCOMFORT | GZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146939 | Ground Water | HYDRON MODULE | HZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146942 | Ground Water | TETCO | TZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146943 | Ground Water | GEOCOMFORT | GZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146944 | Ground Water | GEOCOMFORT | GZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146945 | Ground Water | GEOCOMFORT | GZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146946 | Ground Water | GEOCOMFORT | GZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146947 | Ground Water | GEOCOMFORT | GZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146948 | Ground Water | GEOCOMFORT | GZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146949 | Ground Water | GEOCOMFORT | GZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146950 | Ground Water | GEOCOMFORT | GZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146951 | Ground Water | GEOCOMFORT | GZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146952 | Ground Water | HYDRON MODULE | HZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146953 | Ground Water | HYDRON MODULE | HZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
10272221 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10272222 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10272228 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10298936 | Ground Water | WaterFurnace | UVV/UVH036**0*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
10298937 | Ground Water | WaterFurnace | UVV/UVH036**3*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
10298938 | Ground Water | WaterFurnace | UVV/UVH036**4*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
10298941 | Ground Water | WaterFurnace | UVV/UVH048**0*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298942 | Ground Water | WaterFurnace | UVV/UVH048**3*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298943 | Ground Water | WaterFurnace | UVV/UVH048**4*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298944 | Ground Water | WaterFurnace | UVV/UVH060**0*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
10298946 | Ground Water | WaterFurnace | UVV/UVH060**3*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
10298947 | Ground Water | WaterFurnace | UVV/UVH060**4*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
214839009 | Ground Water | FHP | EC072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839010 | Ground Water | FHP | EC072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839011 | Ground Water | FHP | EC072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839012 | Ground Water | FHP | EC096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214839013 | Ground Water | FHP | EC096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214839014 | Ground Water | FHP | EC096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
202146873 | Ground Water | GEOCOMFORT | GZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146874 | Ground Water | GEOCOMFORT | GZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146875 | Ground Water | GEOCOMFORT | GZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146876 | Ground Water | HYDRON MODULE | HZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
202146877 | Ground Water | HYDRON MODULE | HZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146878 | Ground Water | HYDRON MODULE | HZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146879 | Ground Water | HYDRON MODULE | HZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146880 | Ground Water | TETCO | TZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
202146881 | Ground Water | TETCO | TZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146882 | Ground Water | TETCO | TZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146883 | Ground Water | TETCO | TZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
207178493 | Ground Water | GEOSTAR | 164J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178495 | Ground Water | GEOSTAR | 163J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178496 | Ground Water | GEOSTAR | 163J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178497 | Ground Water | GEOSTAR | 163J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178498 | Ground Water | GEOSTAR | 163J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178499 | Ground Water | GEOSTAR | 164J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178500 | Ground Water | GEOSTAR | 163J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178519 | Ground Water | GEOSTAR | 164H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178520 | Ground Water | GEOSTAR | 164H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178521 | Ground Water | GEOSTAR | 164H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178522 | Ground Water | GEOSTAR | 164H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178523 | Ground Water | GEOSTAR | 164H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207178524 | Ground Water | GEOSTAR | 164H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207178525 | Ground Water | GEOSTAR | 161/162J064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207178536 | Ground Water | GEOSTAR | 163H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178537 | Ground Water | GEOSTAR | 163H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207349053 | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
207349059 | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
207349379 | Ground Water | WaterFurnace | NBV/NBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349380 | Ground Water | WaterFurnace | NBV/NBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349381 | Ground Water | WaterFurnace | NBV/NBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349382 | Ground Water | WaterFurnace | NBV/NBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349383 | Ground Water | WaterFurnace | NBV/NBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349384 | Ground Water | WaterFurnace | NBV/NBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349385 | Ground Water | WaterFurnace | NBV/NBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349386 | Ground Water | WaterFurnace | NBV/NBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349387 | Ground Water | WaterFurnace | NBV/NBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349388 | Ground Water | WaterFurnace | NBV/NBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349389 | Ground Water | WaterFurnace | NBV/NBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349390 | Ground Water | WaterFurnace | NBV/NBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349391 | Ground Water | WaterFurnace | NBV/NBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349392 | Ground Water | WaterFurnace | NBV/NBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349393 | Ground Water | WaterFurnace | NBV/NBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349394 | Ground Water | WaterFurnace | NBV/NBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349395 | Ground Water | WaterFurnace | NBV/NBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349396 | Ground Water | WaterFurnace | NBV/NBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349397 | Ground Water | WaterFurnace | NBV/NBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349398 | Ground Water | WaterFurnace | NBV/NBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349399 | Ground Water | WaterFurnace | NBV/NBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349400 | Ground Water | WaterFurnace | NBV/NBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214839496 | Ground Water | CARRIER | 50WC*042(G-K;N-R)**3*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839497 | Ground Water | CARRIER | 50WC*042(L/M/S/T)**3*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839498 | Ground Water | CARRIER | 50WC*042(G-K;N-R)**5*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839499 | Ground Water | CARRIER | 50WC*042(L/M/S/T)**5*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839500 | Ground Water | CARRIER | 50WC*042(G-K;N-R)**6*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
206347324 | Ground Water | COMFORT-AIRE | HEV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206347325 | Ground Water | CENTURY | HEV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206347960 | Ground Water | HYDROTECH | WSS6006*6* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
206347961 | Ground Water | HYDROTECH | WSS6009*6* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
206347962 | Ground Water | HYDROTECH | WSS6012*6* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
206347963 | Ground Water | HYDROTECH | WSS6015*6* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
206422417 | Ground Water | CENTURY | HBH/V015*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
206422418 | Ground Water | COMFORT-AIRE | HBH/V015*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
206422419 | Ground Water | CENTURY | HBH/V018*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
206422420 | Ground Water | COMFORT-AIRE | HBH/V018*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
206422421 | Ground Water | CENTURY | HBH/V024*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
206422422 | Ground Water | COMFORT-AIRE | HBH/V024*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
206422423 | Ground Water | CENTURY | HBH/V030*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
8738070 | Ground Water | GEOCOMFORT | GVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738071 | Ground Water | HYDRON MODULE | HVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738072 | Ground Water | TETCO | TVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738073 | Ground Water | GEOCOMFORT | GVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738074 | Ground Water | HYDRON MODULE | HVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738075 | Ground Water | TETCO | TVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738076 | Ground Water | GEOCOMFORT | GVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738077 | Ground Water | HYDRON MODULE | HVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738078 | Ground Water | TETCO | TVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
203383888 | Ground Water | CARRIER | 50PSV048***6/FA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383889 | Ground Water | CARRIER | 50PSH048***3/CA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383890 | Ground Water | CARRIER | 50PSH048***5/EA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383891 | Ground Water | CARRIER | 50PSH048***6/FA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383892 | Ground Water | FHP | EP018-1VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383893 | Ground Water | FHP | EP018-2VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383894 | Ground Water | FHP | EP018-1HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383895 | Ground Water | FHP | EP018-2HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383896 | Ground Water | FHP | EP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383897 | Ground Water | FHP | EP042-3VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383898 | Ground Water | FHP | EP042-4VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383899 | Ground Water | FHP | EP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383900 | Ground Water | FHP | EP042-3HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383901 | Ground Water | FHP | EP042-4HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383902 | Ground Water | FHP | EP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383903 | Ground Water | FHP | EP048-3VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383904 | Ground Water | FHP | EP048-4VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383905 | Ground Water | FHP | EP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383906 | Ground Water | FHP | EP048-3HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383907 | Ground Water | FHP | EP048-4HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203459712 | Ground Water | BOSCH-GEO | LM036-1CSC-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459713 | Ground Water | BOSCH-GEO | LM036-1CSN-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459714 | Ground Water | BOSCH-GEO | LM048-1CSC-*****A | LM048-1AV/AH*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
203459725 | Ground Water | FHP | LM036-1CSC-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459726 | Ground Water | FHP | LM036-1CSN-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459727 | Ground Water | FHP | LM048-1CSC-*****A | LM048-1AV/AH*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
203459750 | Ground Water | BOSCH | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | No
203459757 | Ground Water | FHP | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | No
203466717 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
203471325 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
203490411 | Ground Water | GeoSmart Energy | GTZ049*1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
203490420 | Ground Water | GeoSmart Energy | GTZ049*1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
202146884 | Ground Water | GEOCOMFORT | GZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146885 | Ground Water | GEOCOMFORT | GZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146886 | Ground Water | GEOCOMFORT | GZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146887 | Ground Water | HYDRON MODULE | HZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146888 | Ground Water | HYDRON MODULE | HZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146889 | Ground Water | HYDRON MODULE | HZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146890 | Ground Water | TETCO | TZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146891 | Ground Water | TETCO | TZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146892 | Ground Water | TETCO | TZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146893 | Ground Water | GEOCOMFORT | GZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146894 | Ground Water | GEOCOMFORT | GZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146895 | Ground Water | GEOCOMFORT | GZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146896 | Ground Water | GEOCOMFORT | GZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146897 | Ground Water | HYDRON MODULE | HZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146898 | Ground Water | HYDRON MODULE | HZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146899 | Ground Water | HYDRON MODULE | HZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146900 | Ground Water | HYDRON MODULE | HZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146901 | Ground Water | TETCO | TZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146902 | Ground Water | TETCO | TZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146903 | Ground Water | TETCO | TZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146904 | Ground Water | GEOCOMFORT | GZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146905 | Ground Water | GEOCOMFORT | GZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146906 | Ground Water | GEOCOMFORT | GZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146907 | Ground Water | HYDRON MODULE | HZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146908 | Ground Water | HYDRON MODULE | HZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146909 | Ground Water | HYDRON MODULE | HZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146910 | Ground Water | TETCO | TZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146911 | Ground Water | TETCO | TZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146912 | Ground Water | TETCO | TZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146913 | Ground Water | GEOCOMFORT | GZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
202146914 | Ground Water | GEOCOMFORT | GZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146915 | Ground Water | GEOCOMFORT | GZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146916 | Ground Water | HYDRON MODULE | HZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
202146917 | Ground Water | HYDRON MODULE | HZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146918 | Ground Water | HYDRON MODULE | HZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146919 | Ground Water | TETCO | TZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
202146920 | Ground Water | TETCO | TZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146921 | Ground Water | TETCO | TZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146922 | Ground Water | GEOCOMFORT | GZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
202146923 | Ground Water | GEOCOMFORT | GZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146924 | Ground Water | GEOCOMFORT | GZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
202146925 | Ground Water | GEOCOMFORT | GZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
202146926 | Ground Water | HYDRON MODULE | HZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
202146927 | Ground Water | HYDRON MODULE | HZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146928 | Ground Water | HYDRON MODULE | HZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
963498 | Ground Water | WaterFurnace | NLH/NXH080**3 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
963499 | Ground Water | WaterFurnace | NLH/NXH080**4 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
963500 | Ground Water | WaterFurnace | NLH/NXH080**5 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
214595715 | Ground Water | AAON, Inc. | M2-014-2-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214595716 | Ground Water | AAON, Inc. | M2-014-3-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214595717 | Ground Water | AAON, Inc. | M2-014-4-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214771921 | Ground Water | TRANE | GEVK009A |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214771922 | Ground Water | TRANE | GEVK012A |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214771923 | Ground Water | TRANE | GEVK015A |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214771924 | Ground Water | TRANE | GEVK018A |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214771925 | Ground Water | TRANE | GEVK024A |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214771926 | Ground Water | TRANE | GEVK030A |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214771927 | Ground Water | TRANE | GEVK036A |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214771928 | Ground Water | TRANE | GEVK042A |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214771929 | Ground Water | TRANE | GEVK048A |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214771930 | Ground Water | TRANE | GEVK060A |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214771931 | Ground Water | TRANE | EXVK009A |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214771932 | Ground Water | TRANE | EXVK012A |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
215893693 | Ground Water | DUAL AIR | CFF024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | No
215893695 | Ground Water | DUAL AIR | CFF031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | No
215893697 | Ground Water | DUAL AIR | CFF036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | No
215893699 | Ground Water | DUAL AIR | CFF041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | No
215893701 | Ground Water | DUAL AIR | CFF060 |  | 57937 | 21.1 | 46600 | 4.1 | 4.8281 | No
215893703 | Ground Water | MIAMI HEAT PUMP | HPF024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | No
215893704 | Ground Water | MIAMI HEAT PUMP | HPF031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | No
215893706 | Ground Water | MIAMI HEAT PUMP | HPF036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | No
215893707 | Ground Water | MIAMI HEAT PUMP | HPF041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | No
215893709 | Ground Water | MIAMI HEAT PUMP | HPF060 |  | 57937 | 21.1 | 46600 | 4.1 | 4.8281 | No
215893711 | Ground Water | DUAL AIR | CFF049 |  | 43569 | 21.1 | 37280 | 4.1 | 3.6307 | No
215893713 | Ground Water | MIAMI HEAT PUMP | HPF049 |  | 43569 | 21.1 | 37280 | 4.1 | 3.6307 | No
216014181 | Ground Water | RHEEM | RPVV/H/D036D |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
216054107 | Ground Water | WaterFurnace | W5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216054108 | Ground Water | WaterFurnace | W5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216054109 | Ground Water | WaterFurnace | W5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216054110 | Ground Water | WaterFurnace | W5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216054475 | Ground Water | GEOCOMFORT | GBS018* | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
216054476 | Ground Water | GEOCOMFORT | GBT024* | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
216054477 | Ground Water | GEOCOMFORT | GBT036* | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
216054478 | Ground Water | GEOCOMFORT | GBT048* | EAD048 | 51500 | 22.5 | 51300 | 4.5 | 4.2917 | Yes
216054479 | Ground Water | GEOCOMFORT | GVS009* |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
216054480 | Ground Water | GEOCOMFORT | GVS012* |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
216054481 | Ground Water | GEOCOMFORT | GVS018* |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
216054482 | Ground Water | GEOCOMFORT | GVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
216054483 | Ground Water | GEOCOMFORT | GVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216054484 | Ground Water | GEOCOMFORT | GVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216054485 | Ground Water | GEOCOMFORT | GVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216054486 | Ground Water | GEOCOMFORT | GVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216054487 | Ground Water | GEOCOMFORT | GYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216054488 | Ground Water | GEOCOMFORT | GYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216054489 | Ground Water | GEOCOMFORT | GYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216054492 | Ground Water | GEOCOMFORT | GZT024* |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
216054493 | Ground Water | GEOCOMFORT | GZT030* |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
216054494 | Ground Water | GEOCOMFORT | GZT036* |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
216054495 | Ground Water | GEOCOMFORT | GZT042* |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
205311951 | Ground Water | GEOSTAR | ZBV/ZBH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
216625808 | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625809 | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625810 | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625811 | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625812 | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625813 | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625814 | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625815 | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625816 | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625817 | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625818 | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625819 | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625820 | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625821 | Ground Water | GeoSmart Energy | S5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625822 | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625823 | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625824 | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625825 | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625826 | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625827 | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625828 | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625829 | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625830 | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625831 | Ground Water | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625832 | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625833 | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625834 | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625835 | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625836 | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625837 | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625838 | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625839 | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625840 | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625841 | Ground Water | GeoSmart Energy | S5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625842 | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625843 | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625844 | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625845 | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625846 | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625847 | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625848 | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625849 | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625850 | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625851 | Ground Water | GeoSmart Energy | S5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625852 | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625853 | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625854 | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625855 | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625856 | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625857 | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625858 | Ground Water | GeoSmart Energy | S5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625859 | Ground Water | GeoSmart Energy | S5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625860 | Ground Water | GeoSmart Energy | S5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625861 | Ground Water | GeoSmart Energy | S5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625862 | Ground Water | GeoSmart Energy | S5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625863 | Ground Water | GeoSmart Energy | S5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215224301 | Ground Water | BOSCH-GEO | RF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224302 | Ground Water | BOSCH-GEO | RF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
217642897 | Ground Water | GeoSmart Energy | S3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642898 | Ground Water | GeoSmart Energy | S3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642899 | Ground Water | GeoSmart Energy | S3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642900 | Ground Water | GeoSmart Energy | S3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642901 | Ground Water | GeoSmart Energy | S3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642902 | Ground Water | GeoSmart Energy | S3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642903 | Ground Water | GeoSmart Energy | S3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642911 | Ground Water | GeoSmart Energy | S3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642912 | Ground Water | GeoSmart Energy | S3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642913 | Ground Water | GeoSmart Energy | S3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642914 | Ground Water | GeoSmart Energy | S3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642915 | Ground Water | GeoSmart Energy | S3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642916 | Ground Water | GeoSmart Energy | S3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642917 | Ground Water | GeoSmart Energy | S3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642918 | Ground Water | GeoSmart Energy | S3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
8964161 | Ground Water | BRYANT | GC060C/H/V******1*X1 + UI |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
8964162 | Ground Water | CARRIER | GC060C/H/V******1**1 + UI |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
8964163 | Ground Water | BRYANT | GC072C/H/V******1*X1 + UI |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
8964164 | Ground Water | CARRIER | GC072C/H/V******1**1 + UI |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
8993504 | Ground Water | YORK BY JOHNSON CONTROLS | YCC/YCW/YCS/YCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
8993505 | Ground Water | YORK BY JOHNSON CONTROLS | YCC/YCW/YCS/YCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
9008839 | Ground Water | BOSCH | ES025-1CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9008840 | Ground Water | BOSCH | ES025-2CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9008841 | Ground Water | BOSCH | ES035-1CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9008842 | Ground Water | BOSCH | ES035-3CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9008843 | Ground Water | BOSCH | ES035-4CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9009353 | Ground Water | FHP | ES025-1CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9009366 | Ground Water | FHP | ES025-2CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9009369 | Ground Water | FHP | ES035-1CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9009382 | Ground Water | FHP | ES035-3CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9009391 | Ground Water | FHP | ES035-4CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
216743652 | Ground Water | BOSCH | CP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743653 | Ground Water | BOSCH | CP048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743654 | Ground Water | BOSCH | CP048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743655 | Ground Water | BOSCH-GEO | RP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216743656 | Ground Water | BOSCH | CP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743657 | Ground Water | BOSCH | CP060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743658 | Ground Water | BOSCH | CP060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743659 | Ground Water | BOSCH-GEO | RP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216743660 | Ground Water | BOSCH | CP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216743661 | Ground Water | BOSCH | CP060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216743662 | Ground Water | BOSCH | CP060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216743663 | Ground Water | BOSCH-GEO | RP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
216743664 | Ground Water | BOSCH | CP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743665 | Ground Water | BOSCH | CP070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743666 | Ground Water | BOSCH | CP070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743667 | Ground Water | BOSCH-GEO | RP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
216743668 | Ground Water | BOSCH | CP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743669 | Ground Water | BOSCH | CP070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743670 | Ground Water | BOSCH | CP070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743671 | Ground Water | BOSCH-GEO | RP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
216743672 | Ground Water | BOSCH | CP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743673 | Ground Water | BOSCH | CP070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743674 | Ground Water | BOSCH | CP070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743675 | Ground Water | BOSCH-GEO | RP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
216743676 | Ground Water | BOSCH | CP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743677 | Ground Water | BOSCH | CP070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743678 | Ground Water | BOSCH | CP070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216759673 | Ground Water | WaterFurnace | W7SZ030BV1**F | W7BM030BN1**2 | 35800 | 27.8 | 40700 | 4.5 | 2.9833 | Yes
216759674 | Ground Water | WaterFurnace | W7SZ042BV1**F | W7BM042BN1**2 | 44400 | 28.8 | 51300 | 4.4 | 3.7 | Yes
216759816 | Ground Water | WaterFurnace | W5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759817 | Ground Water | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759818 | Ground Water | WaterFurnace | W5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759819 | Ground Water | WaterFurnace | W5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759820 | Ground Water | WaterFurnace | W5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759821 | Ground Water | GEOSTAR | G5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759822 | Ground Water | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759823 | Ground Water | GEOSTAR | G5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
4219426 | Ground Water | NORDIC | R65HACW-P-1T-*-SDE** |  | 62600 | 21.5 | 58700 | 4.5 | 5.2167 | Yes
4219434 | Ground Water | NORDIC | TF55HACW-P-1T-*-SDE** |  | 51100 | 22.5 | 47100 | 4.4 | 4.2583 | Yes
4219443 | Ground Water | NORDIC | RS45HACW-P-1T-* | AH-45-P-1-***** | 38500 | 21.3 | 35700 | 4.3 | 3.2083 | Yes
4219444 | Ground Water | NORDIC | RS55HACW-P-1T-* | AH-55-P-1-***** | 50200 | 22.5 | 47200 | 4.5 | 4.1833 | Yes
4219445 | Ground Water | NORDIC | RS65HACW-P-1T-* | AH-65-P-1-***** | 62600 | 21.5 | 58700 | 4.5 | 5.2167 | Yes
203303786 | Ground Water | BRYANT | GP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303787 | Ground Water | HEIL | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
203303788 | Ground Water | ARCOAIRE | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303789 | Ground Water | KEEPRITE | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303790 | Ground Water | TEMPSTAR | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303791 | Ground Water | COMFORTMAKER | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303792 | Ground Water | DAY & NIGHT | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
214772079 | Ground Water | TRANE | EXVK0244 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772080 | Ground Water | TRANE | EXVK0247 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772081 | Ground Water | TRANE | EXVK030B |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772082 | Ground Water | TRANE | EXVK0304 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772083 | Ground Water | TRANE | EXVK0307 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772084 | Ground Water | TRANE | EXVK036B |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772085 | Ground Water | TRANE | EXVK0364 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772086 | Ground Water | TRANE | EXVK0367 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772087 | Ground Water | TRANE | EXVK042B |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772088 | Ground Water | TRANE | EXVK0424 |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772089 | Ground Water | TRANE | EXVK048B |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772090 | Ground Water | TRANE | EXVK0484 |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772091 | Ground Water | TRANE | EXVK060B |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772092 | Ground Water | TRANE | EXVK0604 |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772093 | Ground Water | TRANE | EXVK070B |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772094 | Ground Water | TRANE | EXVK0704 |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772095 | Ground Water | TRANE | DXVK024A |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772096 | Ground Water | TRANE | DXVK036A |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772097 | Ground Water | TRANE | DXVK048A |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772098 | Ground Water | TRANE | DXVK060A |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772099 | Ground Water | TRANE | DXVK070A |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772101 | Ground Water | TRANE | GEHK0097 |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214772102 | Ground Water | TRANE | GEHK0127 |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214772103 | Ground Water | TRANE | GEHK0157 |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214772104 | Ground Water | TRANE | GEHK0187 |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214772105 | Ground Water | TRANE | GEHK024B |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772106 | Ground Water | TRANE | GEHK0244 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772107 | Ground Water | TRANE | GEHK0247 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772108 | Ground Water | TRANE | GEHK030B |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772109 | Ground Water | TRANE | GEHK0304 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772110 | Ground Water | TRANE | GEHK0307 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772111 | Ground Water | TRANE | GEHK036B |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772112 | Ground Water | TRANE | GEHK0364 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772113 | Ground Water | TRANE | GEHK0367 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772114 | Ground Water | TRANE | GEHK042B |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772115 | Ground Water | TRANE | GEHK0424 |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772116 | Ground Water | TRANE | GEHK048B |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772117 | Ground Water | TRANE | GEHK0484 |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772118 | Ground Water | TRANE | GEHK060B |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772119 | Ground Water | TRANE | GEHK0604 |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772120 | Ground Water | TRANE | EXHK0097 |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214772121 | Ground Water | TRANE | EXHK0127 |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214772122 | Ground Water | TRANE | EXHK0157 |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214772123 | Ground Water | TRANE | EXHK0187 |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214772124 | Ground Water | TRANE | EXHK024B |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772125 | Ground Water | TRANE | EXHK0244 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772126 | Ground Water | TRANE | EXHK0247 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772127 | Ground Water | TRANE | EXHK030B |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772128 | Ground Water | TRANE | EXHK0304 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772129 | Ground Water | TRANE | EXHK0307 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772130 | Ground Water | TRANE | EXHK036B |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772131 | Ground Water | TRANE | EXHK0364 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772132 | Ground Water | TRANE | EXHK0367 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772133 | Ground Water | TRANE | EXHK042B |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772134 | Ground Water | TRANE | EXHK0424 |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
216419909 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
216419912 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
216419920 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
216419921 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
216419922 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
216419924 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
216419941 | Ground Water | Whalen | WZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
216419942 | Ground Water | Whalen | WZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
216419945 | Ground Water | Whalen | WZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
216419946 | Ground Water | Whalen | WZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
202146867 | Ground Water | HYDRON MODULE | HZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146868 | Ground Water | HYDRON MODULE | HZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146869 | Ground Water | TETCO | TZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
202146870 | Ground Water | TETCO | TZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146871 | Ground Water | TETCO | TZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146872 | Ground Water | GEOCOMFORT | GZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
207822807 | Ground Water | HYDROTECH | HRCX30*-6 |  | 30000 | 23.5 | 25000 | 4.1 | 2.5 | Yes
207822813 | Ground Water | HYDROTECH | HRCX36*-6 |  | 35500 | 21.6 | 31500 | 4.1 | 2.9583 | Yes
208106952 | Ground Water | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
208106953 | Ground Water | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
208106954 | Ground Water | 5 SERIES GEO-READY | NGV/NGH064*1*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
215224045 | Ground Water | BOSCH | CF018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224046 | Ground Water | BOSCH | CF018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
205973166 | Ground Water | Enertech | ERE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205973167 | Ground Water | Enertech | ERE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205973168 | Ground Water | Enertech | ERE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205973169 | Ground Water | Enertech | ERE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
205973771 | Ground Water | COMFORT-AIRE | HEV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205973772 | Ground Water | CENTURY | HEV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205973775 | Ground Water | COMFORT-AIRE | HEV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205973776 | Ground Water | CENTURY | HEV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205973779 | Ground Water | COMFORT-AIRE | HEV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205973780 | Ground Water | CENTURY | HEV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205973781 | Ground Water | COMFORT-AIRE | HZS048B | MWG48**-B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
4660771 | Ground Water | TRANE | GEVE0728 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4660776 | Ground Water | TRANE | GEVE0908 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
4947178 | Ground Water | TRANE | VSVE0241 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947179 | Ground Water | TRANE | VSVE0242 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947180 | Ground Water | TRANE | VSVE0244 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947183 | Ground Water | TRANE | VSVE0331 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947184 | Ground Water | TRANE | VSVE0332 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947185 | Ground Water | TRANE | VSVE0334 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947240 | Ground Water | TRANE | VSVE0501 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
4947241 | Ground Water | TRANE | VSVE0502 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
4947242 | Ground Water | TRANE | VSVE0504 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
206900466 | Ground Water | WaterFurnace | UDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900467 | Ground Water | WaterFurnace | UDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900469 | Ground Water | WaterFurnace | UDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900470 | Ground Water | WaterFurnace | UDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900471 | Ground Water | WaterFurnace | UDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900472 | Ground Water | WaterFurnace | UDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900473 | Ground Water | WaterFurnace | UDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900474 | Ground Water | WaterFurnace | UDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900475 | Ground Water | WaterFurnace | UDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900553 | Ground Water | GEOSTAR | GDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900554 | Ground Water | GEOSTAR | GDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900555 | Ground Water | GEOSTAR | GDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900556 | Ground Water | GEOSTAR | GDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900557 | Ground Water | GEOSTAR | GDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900558 | Ground Water | GEOSTAR | GDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900559 | Ground Water | GEOSTAR | GDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900560 | Ground Water | GEOSTAR | GDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900561 | Ground Water | GEOSTAR | GDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
211594241 | Ground Water | TRANE | GEHG0604 |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
211594242 | Ground Water | TRANE | EXHG0097 |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
211594243 | Ground Water | TRANE | EXHG0127 |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
211594244 | Ground Water | TRANE | EXHG0157 |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
211594245 | Ground Water | TRANE | EXHG0187 |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
211594246 | Ground Water | TRANE | EXHG024B |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594247 | Ground Water | TRANE | EXHG0244 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594248 | Ground Water | TRANE | EXHG0247 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594249 | Ground Water | TRANE | EXHG030B |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594250 | Ground Water | TRANE | EXHG0304 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594251 | Ground Water | TRANE | EXHG0307 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594252 | Ground Water | TRANE | EXHG036B |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594253 | Ground Water | TRANE | EXHG0364 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594254 | Ground Water | TRANE | EXHG0367 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594255 | Ground Water | TRANE | EXHG042B |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594256 | Ground Water | TRANE | EXHG0424 |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594257 | Ground Water | TRANE | EXHG048B |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594258 | Ground Water | TRANE | EXHG0484 |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594259 | Ground Water | TRANE | EXHG060B |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594260 | Ground Water | TRANE | EXHG0604 |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594261 | Ground Water | TRANE | EXHG070B |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
211594262 | Ground Water | TRANE | EXHG0704 |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
211594263 | Ground Water | TRANE | DXHG024B |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594264 | Ground Water | TRANE | DXHG0244 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594265 | Ground Water | TRANE | DXHG0247 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594266 | Ground Water | TRANE | DXHG036B |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594267 | Ground Water | TRANE | DXHG0364 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594268 | Ground Water | TRANE | DXHG0367 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594269 | Ground Water | TRANE | DXHG048B |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594270 | Ground Water | TRANE | DXHG0484 |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594271 | Ground Water | TRANE | DXHG060B |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
211594272 | Ground Water | TRANE | DXHG0604 |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
211594273 | Ground Water | TRANE | DXHG070B |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
211594274 | Ground Water | TRANE | DXHG0704 |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
212428693 | Ground Water | HYDROTECH | WSH6009A6* |  | 10000 | 23 | 8500 | 4.2 | 0.83333 | Yes
212428694 | Ground Water | HYDROTECH | WSH6012A6* |  | 12500 | 23.1 | 11000 | 4.6 | 1.0417 | Yes
212428695 | Ground Water | HYDROTECH | WSH6018A6* |  | 20500 | 26 | 16000 | 4.3 | 1.7083 | Yes
212428696 | Ground Water | HYDROTECH | WSH6024A6* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | Yes
212428697 | Ground Water | HYDROTECH | WSH6030A6* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | Yes
8964157 | Ground Water | BRYANT | GC036C/H/V******1*X1 + UI |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
8964158 | Ground Water | CARRIER | GC036C/H/V******1**1 + UI |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
203696349 | Ground Water | HYDROTECH | WSV6024A |  | 25400 | 24 | 22000 | 4.1 | 2.1167 | No
203696351 | Ground Water | HYDROTECH | WSV6036A |  | 41500 | 24 | 35500 | 4.1 | 3.4583 | No
203817319 | Ground Water | BOSCH-GEO | CE061-1HZC-*****B |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818209 | Ground Water | CARRIER | GP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818210 | Ground Water | BRYANT | GP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818211 | Ground Water | HEIL | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818212 | Ground Water | ARCOAIRE | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818214 | Ground Water | KEEPRITE | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818215 | Ground Water | TEMPSTAR | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818216 | Ground Water | COMFORTMAKER | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818217 | Ground Water | DAY & NIGHT | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818278 | Ground Water | BOSCH | CE061-1HZC-*****B |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203993050 | Ground Water | GEOSTAR | 111H049**1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
203995293 | Ground Water | HYDROTECH | WSV6042A |  | 46500 | 24 | 39000 | 4.2 | 3.875 | No
202211042 | Ground Water | WaterFurnace | URD038*0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211043 | Ground Water | WaterFurnace | URD038*0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211044 | Ground Water | WaterFurnace | URD038*0*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211045 | Ground Water | WaterFurnace | URD038*3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211046 | Ground Water | WaterFurnace | URD038*3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211047 | Ground Water | WaterFurnace | URD038*3*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211048 | Ground Water | WaterFurnace | URD049*0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211049 | Ground Water | WaterFurnace | URD049*0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211050 | Ground Water | WaterFurnace | URD049*0*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211051 | Ground Water | WaterFurnace | URD049*3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211052 | Ground Water | WaterFurnace | URD049*3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211053 | Ground Water | WaterFurnace | URD049*3*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211054 | Ground Water | WaterFurnace | URD064*0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211055 | Ground Water | WaterFurnace | URD064*0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211056 | Ground Water | WaterFurnace | URD064*0*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211057 | Ground Water | WaterFurnace | URD064*3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211058 | Ground Water | WaterFurnace | URD064*3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211059 | Ground Water | WaterFurnace | URD064*3*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211060 | Ground Water | WaterFurnace | URD072*0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211061 | Ground Water | WaterFurnace | URD072*0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211062 | Ground Water | WaterFurnace | URD072*0*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211063 | Ground Water | WaterFurnace | URD072*3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211064 | Ground Water | WaterFurnace | URD072*3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211065 | Ground Water | WaterFurnace | URD072*3*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211066 | Ground Water | WaterFurnace | URT096*3*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
202262237 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202262238 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ042J1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202272873 | Ground Water | BOSCH-GEO | BP018-1VT*******C |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202319683 | Ground Water | BOSCH-GEO | SM048-1CSC-*****A | SM048-1AV*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
7412057 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412158 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7412253 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412381 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412626 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412712 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412777 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412856 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412926 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7413034 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7413487 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7414142 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414232 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414335 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414470 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414553 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414651 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414828 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414896 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415098 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415209 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7415301 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415373 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415455 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7415878 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416559 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416688 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7416782 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416889 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416979 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7417060 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417146 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417250 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7417329 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417419 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417586 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417698 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417776 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417867 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417918 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417992 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418047 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418154 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418286 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418360 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418435 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418524 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418635 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418715 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418803 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418887 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418965 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7419110 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7419218 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419321 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419403 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
202541572 | Ground Water | BOSCH-GEO | BP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202541573 | Ground Water | BOSCH | BP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202541574 | Ground Water | CARRIER | GB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202541575 | Ground Water | BRYANT | GB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202543170 | Ground Water | CARRIER | GB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202543171 | Ground Water | BRYANT | GB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202547425 | Ground Water | BOSCH | EC096-1VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547426 | Ground Water | BOSCH | EC096-3VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547427 | Ground Water | BOSCH | EC096-4VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
4651870 | Ground Water | GeoSmart Energy | ZS023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651873 | Ground Water | GEOSTAR | ZS023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651874 | Ground Water | GeoSmart Energy | ZS023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651882 | Ground Water | GEOSTAR | ZS042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651883 | Ground Water | GeoSmart Energy | ZS042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651888 | Ground Water | GEOSTAR | ZS042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651889 | Ground Water | GeoSmart Energy | ZS042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651894 | Ground Water | GEOSTAR | ZS042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651895 | Ground Water | GeoSmart Energy | ZS042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651936 | Ground Water | GEOSTAR | ZS048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651937 | Ground Water | GeoSmart Energy | ZS048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651942 | Ground Water | GeoSmart Energy | ZS048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651943 | Ground Water | GEOSTAR | ZS048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651948 | Ground Water | GEOSTAR | ZS048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651949 | Ground Water | GeoSmart Energy | ZS048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651954 | Ground Water | GEOSTAR | ZS060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651955 | Ground Water | GeoSmart Energy | ZS060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651966 | Ground Water | GEOSTAR | ZS060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651967 | Ground Water | GeoSmart Energy | ZS060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651972 | Ground Water | GEOSTAR | ZS070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651973 | Ground Water | GeoSmart Energy | ZS070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651978 | Ground Water | GEOSTAR | ZS070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651979 | Ground Water | GeoSmart Energy | ZS070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651984 | Ground Water | GEOSTAR | ZS070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651985 | Ground Water | GeoSmart Energy | ZS070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4659826 | Ground Water | TRANE | GEVE0721 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659827 | Ground Water | TRANE | GEVE0722 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659829 | Ground Water | TRANE | GEVE0724 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659831 | Ground Water | TRANE | GEVE0904 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
4659834 | Ground Water | TRANE | GEHE0721 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659835 | Ground Water | TRANE | GEHE0722 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659836 | Ground Water | TRANE | GEHE0728 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659837 | Ground Water | TRANE | GEHE0724 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
3628355 | Ground Water | WaterFurnace | USV/USH070**0*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628356 | Ground Water | WaterFurnace | USV/USH070**3*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628357 | Ground Water | WaterFurnace | USV/USH070**4*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628359 | Ground Water | WaterFurnace | USV/USH060**0*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628360 | Ground Water | WaterFurnace | USV/USH060**3*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628361 | Ground Water | WaterFurnace | USV/USH060**4*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628363 | Ground Water | WaterFurnace | USV/USH048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628364 | Ground Water | WaterFurnace | USV/USH048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628365 | Ground Water | WaterFurnace | USV/USH048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628367 | Ground Water | WaterFurnace | USV/USH042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628368 | Ground Water | WaterFurnace | USV/USH042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628369 | Ground Water | WaterFurnace | USV/USH042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628403 | Ground Water | WaterFurnace | USV/USH030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628404 | Ground Water | WaterFurnace | USV/USH030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628405 | Ground Water | WaterFurnace | USV/USH030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628406 | Ground Water | WaterFurnace | USV/USH030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628407 | Ground Water | WaterFurnace | USH023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628408 | Ground Water | WaterFurnace | USV/USH036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628409 | Ground Water | WaterFurnace | USV/USH036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628410 | Ground Water | WaterFurnace | USV/USH036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628411 | Ground Water | WaterFurnace | USH023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628412 | Ground Water | WaterFurnace | USH023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628413 | Ground Water | WaterFurnace | USH023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
216625864 | Ground Water | GeoSmart Energy | S5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625865 | Ground Water | GeoSmart Energy | S5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
207337469 | Ground Water | GEOSTAR | 103H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337470 | Ground Water | GEOSTAR | 103H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337471 | Ground Water | GEOSTAR | 163H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337472 | Ground Water | GEOSTAR | 163H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337473 | Ground Water | GEOSTAR | 104H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337474 | Ground Water | GEOSTAR | 104H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337475 | Ground Water | GEOSTAR | 164H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337476 | Ground Water | GEOSTAR | 164H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337477 | Ground Water | GEOSTAR | 103J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337478 | Ground Water | GEOSTAR | 103J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337479 | Ground Water | GEOSTAR | 163J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337480 | Ground Water | GEOSTAR | 163J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337481 | Ground Water | GEOSTAR | 104J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337482 | Ground Water | GEOSTAR | 104J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337483 | Ground Water | GEOSTAR | 164J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337484 | Ground Water | GEOSTAR | 164J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337485 | Ground Water | GEOSTAR | 103J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337486 | Ground Water | GEOSTAR | 103J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337487 | Ground Water | GEOSTAR | 163J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337488 | Ground Water | GEOSTAR | 163J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337489 | Ground Water | GEOSTAR | 104H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337490 | Ground Water | GEOSTAR | 104H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337491 | Ground Water | GEOSTAR | 164H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337492 | Ground Water | GEOSTAR | 164H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337493 | Ground Water | GEOSTAR | 103J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337494 | Ground Water | GEOSTAR | 103J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337495 | Ground Water | GEOSTAR | 163J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337496 | Ground Water | GEOSTAR | 163J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337497 | Ground Water | GEOSTAR | 104H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337498 | Ground Water | GEOSTAR | 104H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337499 | Ground Water | GEOSTAR | 164H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337500 | Ground Water | GEOSTAR | 164H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337501 | Ground Water | GEOSTAR | 103H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337502 | Ground Water | GEOSTAR | 103H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337503 | Ground Water | GEOSTAR | 163H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337504 | Ground Water | GEOSTAR | 163H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337505 | Ground Water | GEOSTAR | 104H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337506 | Ground Water | GEOSTAR | 104H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337507 | Ground Water | GEOSTAR | 164H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337508 | Ground Water | GEOSTAR | 164H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337509 | Ground Water | GEOSTAR | 103H022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
6501898 | Ground Water | GEOSTAR | GBV/GBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501899 | Ground Water | GEOSTAR | GBV/GBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501900 | Ground Water | GEOSTAR | GBV/GBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501901 | Ground Water | GEOSTAR | GBV/GBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501902 | Ground Water | GEOSTAR | GBV/GBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501903 | Ground Water | GEOSTAR | GBV/GBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501904 | Ground Water | GEOSTAR | GBV/GBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501905 | Ground Water | GEOSTAR | GBV/GBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501906 | Ground Water | GEOSTAR | GBV/GBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501907 | Ground Water | GEOSTAR | GBV/GBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501908 | Ground Water | GEOSTAR | GBV/GBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501909 | Ground Water | GEOSTAR | GBV/GBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501910 | Ground Water | GEOSTAR | GBV/GBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501911 | Ground Water | GEOSTAR | GBV/GBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501912 | Ground Water | GEOSTAR | GBV/GBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501913 | Ground Water | GEOSTAR | GBV/GBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501914 | Ground Water | GEOSTAR | GBV/GBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501915 | Ground Water | GEOSTAR | GBV/GBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501916 | Ground Water | GEOSTAR | GBV/GBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501917 | Ground Water | GEOSTAR | GBV/GBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501918 | Ground Water | GEOSTAR | GBV/GBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501919 | Ground Water | GEOSTAR | GBV/GBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501920 | Ground Water | GEOSTAR | GBV/GBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501921 | Ground Water | GEOSTAR | GBV/GBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501922 | Ground Water | GEOSTAR | GBV/GBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501923 | Ground Water | GEOSTAR | GBV/GBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501924 | Ground Water | GEOSTAR | GBV/GBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501925 | Ground Water | GEOSTAR | GBV/GBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501926 | Ground Water | GEOSTAR | GBV/GBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501927 | Ground Water | GEOSTAR | GBV/GBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501928 | Ground Water | GEOSTAR | GBV/GBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501929 | Ground Water | GEOSTAR | GBV/GBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501930 | Ground Water | GEOSTAR | GBV/GBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501931 | Ground Water | GEOSTAR | GBV/GBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501932 | Ground Water | GEOSTAR | GBV/GBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501933 | Ground Water | GEOSTAR | GBV/GBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501934 | Ground Water | GEOSTAR | GBV/GBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501935 | Ground Water | GEOSTAR | GBV/GBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501936 | Ground Water | GEOSTAR | GBV/GBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501937 | Ground Water | GEOSTAR | GBV/GBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501938 | Ground Water | GEOSTAR | GBV/GBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501939 | Ground Water | GEOSTAR | GBV/GBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501940 | Ground Water | GEOSTAR | GBV/GBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501941 | Ground Water | GEOSTAR | GBV/GBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501942 | Ground Water | GEOSTAR | GBV/GBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501943 | Ground Water | GEOSTAR | GBV/GBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501944 | Ground Water | GEOSTAR | GBV/GBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501945 | Ground Water | GEOSTAR | GBV/GBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501946 | Ground Water | GEOSTAR | GBV/GBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501947 | Ground Water | GEOSTAR | GBV/GBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501948 | Ground Water | GEOSTAR | GBV/GBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501949 | Ground Water | GEOSTAR | GBV/GBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501950 | Ground Water | GEOSTAR | GBV/GBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501951 | Ground Water | GEOSTAR | GBV/GBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501952 | Ground Water | GEOSTAR | GBV/GBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501953 | Ground Water | GEOSTAR | GBV/GBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
9100359 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100361 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100362 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
207177460 | Ground Water | TRANE | EXVG009A |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
207177461 | Ground Water | TRANE | EXVG0097 |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
207177462 | Ground Water | TRANE | EXVG012A |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
207177463 | Ground Water | TRANE | EXVG0127 |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
207177464 | Ground Water | TRANE | EXVG015A |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
207177465 | Ground Water | TRANE | EXVG0157 |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
207177466 | Ground Water | TRANE | EXVG018A |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
207177467 | Ground Water | TRANE | EXVG0187 |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
207177468 | Ground Water | TRANE | EXVG024A |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177469 | Ground Water | TRANE | EXVG024B |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177470 | Ground Water | TRANE | EXVG0244 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177471 | Ground Water | TRANE | EXVG0247 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177472 | Ground Water | TRANE | EXVG030A |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177473 | Ground Water | TRANE | EXVG030B |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177474 | Ground Water | TRANE | EXVG0304 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177475 | Ground Water | TRANE | EXVG0307 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177476 | Ground Water | TRANE | EXVG036A |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177477 | Ground Water | TRANE | EXVG036B |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177478 | Ground Water | TRANE | EXVG0364 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177479 | Ground Water | TRANE | EXVG0367 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177480 | Ground Water | TRANE | EXVG042A |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177481 | Ground Water | TRANE | EXVG042B |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177482 | Ground Water | TRANE | EXVG0424 |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177483 | Ground Water | TRANE | EXVG048A |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177484 | Ground Water | TRANE | EXVG048B |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177485 | Ground Water | TRANE | EXVG0484 |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177486 | Ground Water | TRANE | EXVG060A |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177487 | Ground Water | TRANE | EXVG060B |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177488 | Ground Water | TRANE | EXVG0604 |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177489 | Ground Water | TRANE | EXVG070A |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177490 | Ground Water | TRANE | EXVG070B |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177491 | Ground Water | TRANE | EXVG0704 |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177492 | Ground Water | TRANE | DXVG024A |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177493 | Ground Water | TRANE | DXVG024B |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177494 | Ground Water | TRANE | DXVG0244 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177495 | Ground Water | TRANE | DXVG0247 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177496 | Ground Water | TRANE | DXVG036A |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177497 | Ground Water | TRANE | DXVG036B |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177498 | Ground Water | TRANE | DXVG0364 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177499 | Ground Water | TRANE | DXVG0367 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177500 | Ground Water | TRANE | DXVG048A |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
207177501 | Ground Water | TRANE | DXVG048B |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
207177502 | Ground Water | TRANE | DXVG0484 |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
207177503 | Ground Water | TRANE | DXVG060A |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177504 | Ground Water | TRANE | DXVG060B |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177505 | Ground Water | TRANE | DXVG0604 |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177506 | Ground Water | TRANE | DXVG070A |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207177507 | Ground Water | TRANE | DXVG070B |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207177508 | Ground Water | TRANE | DXVG0704 |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207178484 | Ground Water | GEOSTAR | 163H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178485 | Ground Water | GEOSTAR | 164H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178486 | Ground Water | GEOSTAR | 164H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178487 | Ground Water | GEOSTAR | 163H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
214595624 | Ground Water | AAON, Inc. | M2-004-3-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595625 | Ground Water | AAON, Inc. | M2-004-3-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595626 | Ground Water | AAON, Inc. | M2-004-3-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595627 | Ground Water | AAON, Inc. | M2-004-3-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
214595628 | Ground Water | AAON, Inc. | M2-004-4-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595629 | Ground Water | AAON, Inc. | M2-004-4-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595630 | Ground Water | AAON, Inc. | M2-004-4-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595631 | Ground Water | AAON, Inc. | M2-004-4-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
216625696 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625697 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625698 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625699 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625700 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625701 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625702 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625703 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625704 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625705 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625706 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625707 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625708 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625709 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625710 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625711 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625712 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625713 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625714 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625715 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625716 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625717 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625718 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625719 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625720 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625721 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625722 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625723 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625724 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625725 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625726 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625727 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625728 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625729 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625730 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625731 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625732 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625733 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625734 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625735 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625736 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625737 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625738 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625739 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625740 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625741 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625742 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625743 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625744 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625745 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625746 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625747 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625748 | Ground Water | GeoSmart Energy | S5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625749 | Ground Water | GeoSmart Energy | S5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625750 | Ground Water | GeoSmart Energy | S5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625751 | Ground Water | GeoSmart Energy | S5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
202330518 | Ground Water | AAON, Inc. | M2-003-2-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330522 | Ground Water | AAON, Inc. | M2-003-3-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330526 | Ground Water | AAON, Inc. | M2-003-4-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330529 | Ground Water | AAON, Inc. | M2-004-1-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
9105368 | Ground Water | GEOCOMFORT | GVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105369 | Ground Water | HYDRON MODULE | HVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105370 | Ground Water | TETCO | TVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105371 | Ground Water | GEOCOMFORT | GVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105372 | Ground Water | HYDRON MODULE | HVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105373 | Ground Water | TETCO | TVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9111997 | Ground Water | BOSCH | SM024-1VT/CF*-*****B |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | No
9111998 | Ground Water | BOSCH | SM036-1VT/CF*-*****B |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | No
9113111 | Ground Water | BOSCH | SM048-1VT/CF*-*****B* |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | No
9113180 | Ground Water | BOSCH | SM060-1VT/CF*-*****B |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | No
9113181 | Ground Water | BOSCH | SM070-1VT/CF*-*****B |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | No
9113182 | Ground Water | BOSCH | SM024-1VT/CF*-*****B |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | Yes
9113183 | Ground Water | BOSCH | SM036-1VT/CF*-*****B |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | Yes
9113184 | Ground Water | BOSCH | SM048-1VT/CF*-*****B* |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | Yes
9113185 | Ground Water | BOSCH | SM060-1VT/CF*-*****B |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | Yes
9113186 | Ground Water | BOSCH | SM070-1VT/CF*-*****B |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
215415814 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)015A*B |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415815 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)015A*C |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415816 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)015A*VB |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415817 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)015A*VC |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415818 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)018A*B |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415819 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)018A*C |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415820 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)018A*VB |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415821 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)018A*VC |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415822 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)024A*B |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
215415823 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)024A*C |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
215415824 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)030A*B |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
215415825 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)030A*C |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
215415828 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)042A*B |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
215415829 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)042A*C |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
215415830 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)048A*B |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
215415831 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)048A*C |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
215415832 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)060A*B |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
215415833 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)060A*C |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
215415834 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415835 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415836 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415837 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415840 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415841 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415844 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415845 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415848 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415849 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415850 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415851 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415852 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415853 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415856 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415857 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
216743615 | Ground Water | BOSCH | CA009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216743616 | Ground Water | BOSCH | CA009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216743617 | Ground Water | BOSCH-GEO | RP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216743618 | Ground Water | BOSCH | CP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743619 | Ground Water | BOSCH | CP024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743620 | Ground Water | BOSCH | CP024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743621 | Ground Water | BOSCH | CP024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743622 | Ground Water | BOSCH-GEO | RP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216743623 | Ground Water | BOSCH | CP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743624 | Ground Water | BOSCH | CP024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743625 | Ground Water | BOSCH | CP024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743626 | Ground Water | BOSCH | CP024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743627 | Ground Water | BOSCH-GEO | RP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216743628 | Ground Water | BOSCH | CP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743629 | Ground Water | BOSCH | CP024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743630 | Ground Water | BOSCH | CP024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743631 | Ground Water | BOSCH | CP024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743632 | Ground Water | BOSCH-GEO | RP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216743633 | Ground Water | BOSCH | CP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743634 | Ground Water | BOSCH | CP024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743635 | Ground Water | BOSCH | CP024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
7785665 | Ground Water | DAIKIN | WVHW3021*J (W/ECM MOTOR) |  | 24100 | 23.2 | 19900 | 4.2 | 2.0083 | No
7795914 | Ground Water | GEOCOMFORT | GVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795915 | Ground Water | HYDRON MODULE | HVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795916 | Ground Water | TETCO | TVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795918 | Ground Water | GEOCOMFORT | GVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795919 | Ground Water | HYDRON MODULE | HVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795920 | Ground Water | TETCO | TVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795921 | Ground Water | GEOCOMFORT | GVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795922 | Ground Water | HYDRON MODULE | HVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795923 | Ground Water | TETCO | TVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795924 | Ground Water | GEOCOMFORT | GVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795925 | Ground Water | HYDRON MODULE | HVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795926 | Ground Water | TETCO | TVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795943 | Ground Water | GEOCOMFORT | GVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
7795944 | Ground Water | HYDRON MODULE | HVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
7795945 | Ground Water | TETCO | TVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
7795946 | Ground Water | GEOCOMFORT | GVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795947 | Ground Water | HYDRON MODULE | HVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795948 | Ground Water | TETCO | TVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
212505504 | Ground Water | AE Air | WSH6030AM* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212505505 | Ground Water | AE Air | WSH6060A6* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | Yes
212505506 | Ground Water | AE Air | WSH6072A6* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | Yes
212505507 | Ground Water | HYDROTECH | WSH6024AM* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212505508 | Ground Water | HYDROTECH | WSH6030AM* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212505509 | Ground Water | HYDROTECH | WSH6036AM* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212505510 | Ground Water | HYDROTECH | WSH6042AM* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212505511 | Ground Water | HYDROTECH | WSH6048AM* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212505512 | Ground Water | AE Air | WSH6024AM* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212505513 | Ground Water | AE Air | WSH6036AM* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212505514 | Ground Water | AE Air | WSH6042AM* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212505515 | Ground Water | AE Air | WSH6048AM* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508378 | Ground Water | HYDROTECH | WSH6024AN* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212508380 | Ground Water | HYDROTECH | WSH6030AN* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212508382 | Ground Water | HYDROTECH | WSH6036AN* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212508384 | Ground Water | HYDROTECH | WSH6042AN* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212508386 | Ground Water | HYDROTECH | WSH6048AN* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508387 | Ground Water | HYDROTECH | WSH6060AM* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
212508388 | Ground Water | HYDROTECH | WSH6060AN* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
212508389 | Ground Water | HYDROTECH | WSH6072AM* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508390 | Ground Water | HYDROTECH | WSH6072AN* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508395 | Ground Water | AE Air | WSH6024AN* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212508397 | Ground Water | AE Air | WSH6030AN* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212508399 | Ground Water | AE Air | WSH6036AN* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212508401 | Ground Water | AE Air | WSH6042AN* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212508403 | Ground Water | AE Air | WSH6048AN* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508404 | Ground Water | AE Air | WSH6072AM* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508405 | Ground Water | AE Air | WSH6072AN* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212509300 | Ground Water | AE Air | WSH6060AM* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
212509301 | Ground Water | AE Air | WSH6060AN* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
217897469 | Ground Water | CENTURY | MJN060A | MAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
217897470 | Ground Water | COMFORT-AIRE | MJN060A | MAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
217897473 | Ground Water | CENTURY | MWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
217897474 | Ground Water | COMFORT-AIRE | MWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
217902632 | Ground Water | Johnson Controls | BWM060A*B |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | No
217902633 | Ground Water | SKYMARK | BWM060A*C |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | No
217903418 | Ground Water | WaterFurnace | V5R036*S0**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903419 | Ground Water | WaterFurnace | V5R036*S0**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903420 | Ground Water | WaterFurnace | V5R036*S0**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903421 | Ground Water | WaterFurnace | V5R048*S0**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903422 | Ground Water | WaterFurnace | V5R048*S0**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903423 | Ground Water | WaterFurnace | V5R048*S0**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903424 | Ground Water | WaterFurnace | V5R060*S0**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903425 | Ground Water | WaterFurnace | V5R060*S0**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903426 | Ground Water | WaterFurnace | V5R060*S0**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903427 | Ground Water | WaterFurnace | V5R072*S0**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903428 | Ground Water | WaterFurnace | V5R072*S0**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903429 | Ground Water | WaterFurnace | V5R072*S0**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903430 | Ground Water | WaterFurnace | V5R036*S3**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903431 | Ground Water | WaterFurnace | V5R036*S3**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903432 | Ground Water | WaterFurnace | V5R036*S3**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903433 | Ground Water | WaterFurnace | V5R036*S4**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903434 | Ground Water | WaterFurnace | V5R036*S4**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903435 | Ground Water | WaterFurnace | V5R036*S4**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903436 | Ground Water | WaterFurnace | V5R048*S3**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903437 | Ground Water | WaterFurnace | V5R048*S3**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903438 | Ground Water | WaterFurnace | V5R048*S3**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903439 | Ground Water | WaterFurnace | V5R048*S4**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903440 | Ground Water | WaterFurnace | V5R048*S4**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903441 | Ground Water | WaterFurnace | V5R048*S4**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903442 | Ground Water | WaterFurnace | V5R060*S3**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903443 | Ground Water | WaterFurnace | V5R060*S3**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903444 | Ground Water | WaterFurnace | V5R060*S3**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903445 | Ground Water | WaterFurnace | V5R060*S4**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903446 | Ground Water | WaterFurnace | V5R060*S4**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903447 | Ground Water | WaterFurnace | V5R060*S4**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903448 | Ground Water | WaterFurnace | V5R072*S3**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903449 | Ground Water | WaterFurnace | V5R072*S3**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903450 | Ground Water | WaterFurnace | V5R072*S3**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903451 | Ground Water | WaterFurnace | V5R072*S4**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903452 | Ground Water | WaterFurnace | V5R072*S4**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903453 | Ground Water | WaterFurnace | V5R072*S4**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903454 | Ground Water | WaterFurnace | V5R036*D4**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903455 | Ground Water | WaterFurnace | V5R036*D4**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903456 | Ground Water | WaterFurnace | V5R036*D4**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903457 | Ground Water | WaterFurnace | V5R048*D4**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903458 | Ground Water | WaterFurnace | V5R048*D4**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
202330455 | Ground Water | AAON, Inc. | RQ-005-3-0-BCAY-V0-10-000-A |  | 66900 | 22 | 56500 | 4.4 | 5.575 | No
202330456 | Ground Water | AAON, Inc. | RQ-005-4-0-BCAY-V0-10-000-A |  | 66900 | 22 | 56500 | 4.4 | 5.575 | No
202330457 | Ground Water | AAON, Inc. | RQ-005-2-0-DCAY-S0-10-000-A |  | 61500 | 22.3 | 53000 | 4.6 | 5.125 | No
202330458 | Ground Water | AAON, Inc. | RQ-005-3-0-DCAY-S0-10-000-A |  | 61500 | 22.3 | 53000 | 4.6 | 5.125 | No
202330459 | Ground Water | AAON, Inc. | RQ-005-4-0-DCAY-S0-10-000-A |  | 61500 | 22.3 | 53000 | 4.6 | 5.125 | No
202330469 | Ground Water | AAON, Inc. | RN-006-2-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
202330470 | Ground Water | AAON, Inc. | RN-006-3-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
202330471 | Ground Water | AAON, Inc. | RN-006-4-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
202330486 | Ground Water | AAON, Inc. | SB-004-1-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330488 | Ground Water | AAON, Inc. | SB-004-2-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330490 | Ground Water | AAON, Inc. | SB-004-3-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330492 | Ground Water | AAON, Inc. | SB-004-4-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330514 | Ground Water | AAON, Inc. | M2-003-1-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
9100364 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100365 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100367 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100368 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
207177430 | Ground Water | TRANE | GEVG0067 |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
207177431 | Ground Water | TRANE | GEVG009A |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
207177432 | Ground Water | TRANE | GEVG0097 |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
207177433 | Ground Water | TRANE | GEVG012A |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
207177434 | Ground Water | TRANE | GEVG0127 |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
207177435 | Ground Water | TRANE | GEVG015A |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
207177436 | Ground Water | TRANE | GEVG0157 |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
207177437 | Ground Water | TRANE | GEVG018A |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
207177438 | Ground Water | TRANE | GEVG0187 |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
207177439 | Ground Water | TRANE | GEVG024A |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177440 | Ground Water | TRANE | GEVG024B |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177441 | Ground Water | TRANE | GEVG0244 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177442 | Ground Water | TRANE | GEVG0247 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177443 | Ground Water | TRANE | GEVG030A |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177444 | Ground Water | TRANE | GEVG030B |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177445 | Ground Water | TRANE | GEVG0304 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177446 | Ground Water | TRANE | GEVG0307 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177447 | Ground Water | TRANE | GEVG036A |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177448 | Ground Water | TRANE | GEVG036B |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177449 | Ground Water | TRANE | GEVG0364 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177450 | Ground Water | TRANE | GEVG0367 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177451 | Ground Water | TRANE | GEVG042A |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177452 | Ground Water | TRANE | GEVG042B |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177453 | Ground Water | TRANE | GEVG0424 |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177454 | Ground Water | TRANE | GEVG048A |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177455 | Ground Water | TRANE | GEVG048B |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177456 | Ground Water | TRANE | GEVG0484 |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177457 | Ground Water | TRANE | GEVG060A |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
207177458 | Ground Water | TRANE | GEVG060B |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
207177459 | Ground Water | TRANE | GEVG0604 |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
9011292 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
9032337 | Ground Water | HYDROTECH | HRCC09*-2 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
9032648 | Ground Water | HYDROTECH | HRCX18*-6 |  | 20000 | 22.5 | 16000 | 4.1 | 1.6667 | Yes
9033424 | Ground Water | HYDROTECH | HRCX09*-6 |  | 11500 | 26.5 | 8800 | 4.5 | 0.95833 | Yes
9033758 | Ground Water | HYDROTECH | HRCX24*-6 |  | 26000 | 26.5 | 22000 | 4.4 | 2.1667 | Yes
9033759 | Ground Water | HYDROTECH | HRCX12*-6 |  | 13000 | 25 | 10500 | 4.1 | 1.0833 | Yes
4651271 | Ground Water | WaterFurnace | USH023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651272 | Ground Water | WaterFurnace | USH023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651273 | Ground Water | WaterFurnace | USH023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651274 | Ground Water | WaterFurnace | USH023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651339 | Ground Water | WaterFurnace | USV/USH024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651340 | Ground Water | WaterFurnace | USV/USH024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651341 | Ground Water | WaterFurnace | USV/USH024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651342 | Ground Water | WaterFurnace | USV/USH024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651403 | Ground Water | WaterFurnace | USV/USH030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651404 | Ground Water | WaterFurnace | USV/USH030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
215268325 | Ground Water | WaterFurnace | V3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
215268328 | Ground Water | WaterFurnace | V3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268329 | Ground Water | WaterFurnace | V3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268330 | Ground Water | WaterFurnace | V3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268334 | Ground Water | WaterFurnace | V3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268335 | Ground Water | WaterFurnace | V3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268336 | Ground Water | WaterFurnace | V3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268337 | Ground Water | WaterFurnace | V3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268338 | Ground Water | WaterFurnace | V3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268339 | Ground Water | WaterFurnace | V3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268340 | Ground Water | WaterFurnace | V3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268348 | Ground Water | WaterFurnace | V3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268349 | Ground Water | WaterFurnace | V3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268350 | Ground Water | WaterFurnace | V3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268351 | Ground Water | WaterFurnace | V3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268352 | Ground Water | WaterFurnace | V3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268353 | Ground Water | WaterFurnace | V3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268354 | Ground Water | WaterFurnace | V3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268355 | Ground Water | WaterFurnace | V3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268356 | Ground Water | WaterFurnace | V3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268357 | Ground Water | WaterFurnace | V3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268358 | Ground Water | WaterFurnace | V3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268359 | Ground Water | WaterFurnace | V3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268365 | Ground Water | WaterFurnace | V3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268366 | Ground Water | WaterFurnace | V3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268367 | Ground Water | WaterFurnace | V3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268368 | Ground Water | WaterFurnace | V3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268369 | Ground Water | WaterFurnace | V3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268663 | Ground Water | WaterFurnace | V5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
215268664 | Ground Water | WaterFurnace | V5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
215268665 | Ground Water | WaterFurnace | V5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268666 | Ground Water | WaterFurnace | V5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268667 | Ground Water | WaterFurnace | V5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268668 | Ground Water | WaterFurnace | V5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216743640 | Ground Water | BOSCH | CP036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743641 | Ground Water | BOSCH | CP036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743642 | Ground Water | BOSCH-GEO | RP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216743643 | Ground Water | BOSCH | CP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743644 | Ground Water | BOSCH | CP036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743645 | Ground Water | BOSCH | CP036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743646 | Ground Water | BOSCH | CP036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743647 | Ground Water | BOSCH-GEO | RP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216743648 | Ground Water | BOSCH | CP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743649 | Ground Water | BOSCH | CP048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743650 | Ground Water | BOSCH | CP048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743651 | Ground Water | BOSCH-GEO | RP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
5273062 | Ground Water | WaterFurnace | NBV/NBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
5273082 | Ground Water | WaterFurnace | NBV/NBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
5273138 | Ground Water | WaterFurnace | NBV/NBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
5274236 | Ground Water | WaterFurnace | NBV/NBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
5295936 | Ground Water | WaterFurnace | NBV/NBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
5295937 | Ground Water | WaterFurnace | NBV/NBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
5295944 | Ground Water | WaterFurnace | NBV/NBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295945 | Ground Water | WaterFurnace | NBV/NBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295947 | Ground Water | WaterFurnace | NBV/NBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295948 | Ground Water | WaterFurnace | NBV/NBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295960 | Ground Water | WaterFurnace | NBV/NBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
5295962 | Ground Water | WaterFurnace | NBV/NBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
5295964 | Ground Water | WaterFurnace | NBV/NBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295966 | Ground Water | WaterFurnace | NBV/NBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295968 | Ground Water | WaterFurnace | NBV/NBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295969 | Ground Water | WaterFurnace | NBV/NBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295980 | Ground Water | WaterFurnace | NBV/NBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295981 | Ground Water | WaterFurnace | NBV/NBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295982 | Ground Water | WaterFurnace | NBV/NBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295983 | Ground Water | WaterFurnace | NBV/NBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
216625542 | Ground Water | GEOSTAR | G5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625543 | Ground Water | GEOSTAR | G5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625614 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625615 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625616 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625617 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625618 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625619 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625620 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625621 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625622 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625623 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625624 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625625 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625626 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625627 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625628 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625629 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625630 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625631 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625632 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625633 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625634 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625635 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625636 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625637 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625638 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625639 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
201926779 | Ground Water | WaterFurnace | URD064*4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926783 | Ground Water | WaterFurnace | URD064*4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926787 | Ground Water | WaterFurnace | URD064*4*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926799 | Ground Water | WaterFurnace | URD072*4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926802 | Ground Water | WaterFurnace | URD072*4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926804 | Ground Water | WaterFurnace | URD072*4*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926809 | Ground Water | WaterFurnace | URT096*4*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
201930362 | Ground Water | GEOCOMFORT | GZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
202084059 | Ground Water | GEOCOMFORT | GZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
202084060 | Ground Water | HYDRON MODULE | HZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
202084061 | Ground Water | HYDRON MODULE | HZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
202084062 | Ground Water | TETCO | TZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
202084063 | Ground Water | TETCO | TZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
202132024 | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-038-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
202132025 | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-050-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
202132026 | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-060-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
202146863 | Ground Water | GEOCOMFORT | GZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
202146864 | Ground Water | GEOCOMFORT | GZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146865 | Ground Water | GEOCOMFORT | GZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146866 | Ground Water | HYDRON MODULE | HZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
215224294 | Ground Water | BOSCH-GEO | RF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224295 | Ground Water | BOSCH-GEO | RF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224296 | Ground Water | BOSCH-GEO | RF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224297 | Ground Water | BOSCH-GEO | RF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | Yes
215224298 | Ground Water | BOSCH-GEO | RF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | Yes
215224299 | Ground Water | BOSCH-GEO | RF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | Yes
215224300 | Ground Water | BOSCH-GEO | RF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | Yes
205901397 | Ground Water | DUAL AIR | CFX049 |  | 43569 | 21.1 | 37280 | 4.1 | 3.6307 | Yes
205901398 | Ground Water | MIAMI HEAT PUMP | HPX049 |  | 43569 | 21.1 | 37280 | 4.1 | 3.6307 | Yes
205901399 | Ground Water | Johnson Controls | JCH/V015A B |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205901400 | Ground Water | SKYMARK | JCH/V015A C |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205958295 | Ground Water | BOSCH-GEO | SM036-1CS*-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205958297 | Ground Water | BOSCH | SM036-1CS*-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205961527 | Ground Water | Johnson Controls | JRE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205961528 | Ground Water | Johnson Controls | JRE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205961529 | Ground Water | Johnson Controls | JRE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205961530 | Ground Water | Johnson Controls | JRE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
217014536 | Ground Water | COMFORTMAKER | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014537 | Ground Water | DAY & NIGHT | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014538 | Ground Water | HEIL | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014539 | Ground Water | ARCOAIRE | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014540 | Ground Water | KEEPRITE | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014541 | Ground Water | TEMPSTAR | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014542 | Ground Water | COMFORTMAKER | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014543 | Ground Water | DAY & NIGHT | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014544 | Ground Water | HEIL | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014545 | Ground Water | ARCOAIRE | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014546 | Ground Water | KEEPRITE | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014547 | Ground Water | TEMPSTAR | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014548 | Ground Water | COMFORTMAKER | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014549 | Ground Water | DAY & NIGHT | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014550 | Ground Water | HEIL | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014551 | Ground Water | ARCOAIRE | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014552 | Ground Water | KEEPRITE | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014553 | Ground Water | TEMPSTAR | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014554 | Ground Water | COMFORTMAKER | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014555 | Ground Water | DAY & NIGHT | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217037791 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS024BD1 | Y5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037792 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | Y5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037793 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS048BD1 | Y5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037794 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS060BD1 | Y5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037795 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS066BD1 | Y5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037796 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ024BD1 | Y5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037797 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | Y5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037798 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ048BD1 | Y5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037799 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ060BD1 | Y5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037800 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ066BD1 | Y5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037801 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037802 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037803 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037804 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037805 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037806 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037807 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037808 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037809 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037810 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037811 | Ground Water | GeoSmart Energy | S5SS024BD1 | S5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037812 | Ground Water | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037813 | Ground Water | GeoSmart Energy | S5SS048BD1 | S5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037814 | Ground Water | GeoSmart Energy | S5SS060BD1 | S5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037815 | Ground Water | GeoSmart Energy | S5SS066BD1 | S5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037816 | Ground Water | GeoSmart Energy | S5SZ024BD1 | S5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037817 | Ground Water | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037818 | Ground Water | GeoSmart Energy | S5SZ048BD1 | S5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
206726863 | Ground Water | HYDRON MODULE | HBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
206726864 | Ground Water | TETCO | TBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
206726865 | Ground Water | TETCO | TBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
206726878 | Ground Water | GEOCOMFORT | GBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726879 | Ground Water | HYDRON MODULE | HBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726880 | Ground Water | TETCO | TBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726881 | Ground Water | GEOCOMFORT | GBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
206726882 | Ground Water | HYDRON MODULE | HBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
206726883 | Ground Water | TETCO | TBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
4651405 | Ground Water | WaterFurnace | USV/USH030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651407 | Ground Water | WaterFurnace | USV/USH030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651417 | Ground Water | WaterFurnace | USV/USH036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651418 | Ground Water | WaterFurnace | USV/USH036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651419 | Ground Water | WaterFurnace | USV/USH036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651420 | Ground Water | WaterFurnace | USV/USH036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651530 | Ground Water | WaterFurnace | USV/USH042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651532 | Ground Water | WaterFurnace | USV/USH042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651533 | Ground Water | WaterFurnace | USV/USH042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651546 | Ground Water | WaterFurnace | USV/USH048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651547 | Ground Water | WaterFurnace | USV/USH048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651548 | Ground Water | WaterFurnace | USV/USH048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651574 | Ground Water | WaterFurnace | USV/USH060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651575 | Ground Water | WaterFurnace | USV/USH060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651576 | Ground Water | WaterFurnace | USV/USH060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651577 | Ground Water | WaterFurnace | USV/USH070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651578 | Ground Water | WaterFurnace | USV/USH070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651579 | Ground Water | WaterFurnace | USV/USH070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651610 | Ground Water | GEOSTAR | ZS023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651611 | Ground Water | GeoSmart Energy | ZS023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651614 | Ground Water | GEOSTAR | ZS024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651615 | Ground Water | GeoSmart Energy | ZS024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651618 | Ground Water | GEOSTAR | ZS024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651619 | Ground Water | GeoSmart Energy | ZS024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651622 | Ground Water | GEOSTAR | ZS024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651623 | Ground Water | GeoSmart Energy | ZS024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651626 | Ground Water | GEOSTAR | ZS024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651627 | Ground Water | GeoSmart Energy | ZS024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651630 | Ground Water | GEOSTAR | ZS030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651631 | Ground Water | GeoSmart Energy | ZS030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651634 | Ground Water | GEOSTAR | ZS030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651635 | Ground Water | GeoSmart Energy | ZS030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651639 | Ground Water | GEOSTAR | ZS030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651640 | Ground Water | GeoSmart Energy | ZS030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651644 | Ground Water | GEOSTAR | ZS030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651645 | Ground Water | GeoSmart Energy | ZS030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651657 | Ground Water | GEOSTAR | ZS036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651658 | Ground Water | GeoSmart Energy | ZS036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651665 | Ground Water | GEOSTAR | ZS036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651666 | Ground Water | GeoSmart Energy | ZS036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651726 | Ground Water | GEOSTAR | ZS036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651727 | Ground Water | GeoSmart Energy | ZS036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651732 | Ground Water | GEOSTAR | ZS036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651733 | Ground Water | GeoSmart Energy | ZS036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651865 | Ground Water | GEOSTAR | ZS023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651866 | Ground Water | GeoSmart Energy | ZS023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651869 | Ground Water | GEOSTAR | ZS023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
202350481 | Ground Water | AAON, Inc. | M2-011-2-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350484 | Ground Water | AAON, Inc. | M2-011-3-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350487 | Ground Water | AAON, Inc. | M2-011-4-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350489 | Ground Water | AAON, Inc. | M2-014-2-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350490 | Ground Water | AAON, Inc. | M2-014-2-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350491 | Ground Water | AAON, Inc. | M2-014-3-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350492 | Ground Water | AAON, Inc. | M2-014-3-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350493 | Ground Water | AAON, Inc. | M2-014-4-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350494 | Ground Water | AAON, Inc. | M2-014-4-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350495 | Ground Water | AAON, Inc. | M2-011-2-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
202350496 | Ground Water | AAON, Inc. | M2-011-3-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
202350497 | Ground Water | AAON, Inc. | M2-011-4-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
202350498 | Ground Water | AAON, Inc. | M2-014-2-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
202350499 | Ground Water | AAON, Inc. | M2-014-2-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
5296014 | Ground Water | WaterFurnace | NBV/NBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296015 | Ground Water | WaterFurnace | NBV/NBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296220 | Ground Water | WaterFurnace | NBV/NBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296221 | Ground Water | WaterFurnace | NBV/NBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296222 | Ground Water | WaterFurnace | NBV/NBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296223 | Ground Water | WaterFurnace | NBV/NBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296225 | Ground Water | WaterFurnace | NBV/NBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296226 | Ground Water | WaterFurnace | NBV/NBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296227 | Ground Water | WaterFurnace | NBV/NBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296228 | Ground Water | WaterFurnace | NBV/NBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296229 | Ground Water | WaterFurnace | NBV/NBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296230 | Ground Water | WaterFurnace | NBV/NBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5315753 | Ground Water | WaterFurnace | NBV/NBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315754 | Ground Water | WaterFurnace | NBV/NBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315755 | Ground Water | WaterFurnace | NBV/NBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315756 | Ground Water | WaterFurnace | NBV/NBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315758 | Ground Water | WaterFurnace | NBV/NBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315759 | Ground Water | WaterFurnace | NBV/NBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315760 | Ground Water | WaterFurnace | NBV/NBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315761 | Ground Water | WaterFurnace | NBV/NBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315762 | Ground Water | WaterFurnace | NBV/NBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315763 | Ground Water | WaterFurnace | NBV/NBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315774 | Ground Water | WaterFurnace | NBV/NBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315776 | Ground Water | WaterFurnace | NBV/NBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315777 | Ground Water | WaterFurnace | NBV/NBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315778 | Ground Water | WaterFurnace | NBV/NBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214595564 | Ground Water | AAON, Inc. | RN-006-4-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595565 | Ground Water | AAON, Inc. | RN-006-2-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595566 | Ground Water | AAON, Inc. | RN-006-3-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595567 | Ground Water | AAON, Inc. | RN-006-4-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
200083572 | Ground Water | COMFORT-AIRE | HBH/V015 |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
200083573 | Ground Water | CENTURY | HBH/V015 |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
200083574 | Ground Water | COMFORT-AIRE | HBH/V018 |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
200083575 | Ground Water | CENTURY | HBH/V018 |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
200083642 | Ground Water | COMFORT-AIRE | HZV/H/D036B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
200083643 | Ground Water | CENTURY | HZV/H/D036B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
200083644 | Ground Water | COMFORT-AIRE | HZV/H/D024B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
200083645 | Ground Water | CENTURY | HZV/H/D024B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
200083646 | Ground Water | COMFORT-AIRE | HZV/H/D048B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
200083647 | Ground Water | CENTURY | HZV/H/D048B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
200083648 | Ground Water | COMFORT-AIRE | HZV/H/D060B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
200083649 | Ground Water | CENTURY | HZV/H/D060B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
200083650 | Ground Water | COMFORT-AIRE | HZV/H/D070B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
200083651 | Ground Water | CENTURY | HZV/H/D070B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
200083684 | Ground Water | COMFORT-AIRE | HZS024B | WDG024**A-*B | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
200083685 | Ground Water | CENTURY | HZS024B | WDG024**A-*B | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
200083686 | Ground Water | COMFORT-AIRE | HZS024B | WDG024**B-*B | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
200083687 | Ground Water | CENTURY | HZS024B | WDG024**B-*B | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
200083688 | Ground Water | COMFORT-AIRE | HZS024B | MWG24*A-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083689 | Ground Water | CENTURY | HZS024B | MWG24*A-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083690 | Ground Water | COMFORT-AIRE | HZS024B | MWG24*C-B | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
200083691 | Ground Water | CENTURY | HZS024B | MWG24*C-B | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
200083692 | Ground Water | COMFORT-AIRE | HZS024B | MWG24*B-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083693 | Ground Water | CENTURY | HZS024B | MWG24*B-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083694 | Ground Water | COMFORT-AIRE | HZS036B | MWG36**-B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | No
200083695 | Ground Water | CENTURY | HZS036B | MWG36**-B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
200083696 | Ground Water | COMFORT-AIRE | HZS036B | WDG036***-*B | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
200083697 | Ground Water | CENTURY | HZS036B | WDG036***-*B | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
200083700 | Ground Water | COMFORT-AIRE | HZS048B | WDG048***-*B | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
200083701 | Ground Water | CENTURY | HZS048B | WDG048***-*B | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
216772566 | Ground Water | Enertech | EVS009* |  | 11900 | 24.2 | 10150 | 4.43 | 0.99167 | Yes
216772567 | Ground Water | Enertech | EVS012* |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
216772568 | Ground Water | Enertech | EVS018* |  | 24025 | 33.6 | 19600 | 5.32 | 2.0021 | Yes
216772569 | Ground Water | Enertech | EVT024* |  | 27825 | 27.3 | 23900 | 4.96 | 2.3188 | No
216772570 | Ground Water | Enertech | EVT030* |  | 35000 | 25.8 | 30300 | 4.72 | 2.9167 | Yes
216772571 | Ground Water | Enertech | EVT036* |  | 41050 | 24.3 | 36900 | 4.7 | 3.4208 | Yes
216772572 | Ground Water | Enertech | EVT042* |  | 49200 | 25.3 | 41900 | 4.89 | 4.1 | Yes
216772573 | Ground Water | Enertech | EVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216772574 | Ground Water | Enertech | EYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216772575 | Ground Water | Enertech | EYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216772576 | Ground Water | Enertech | EYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216772579 | Ground Water | Enertech | EZT024* |  | 28200 | 25 | 23175 | 4.68 | 2.35 | No
216772580 | Ground Water | Enertech | EZT030* |  | 34550 | 23.2 | 30075 | 4.5 | 2.8792 | Yes
216772581 | Ground Water | Enertech | EZT036* |  | 39400 | 25.2 | 34775 | 4.6 | 3.2833 | Yes
216772582 | Ground Water | Enertech | EZT042* |  | 47250 | 24.6 | 40300 | 4.4 | 3.9375 | Yes
216772583 | Ground Water | Enertech | EZT048* |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
216772584 | Ground Water | Enertech | EZT060* |  | 62000 | 21.8 | 58500 | 4.25 | 5.1667 | Yes
216772585 | Ground Water | Enertech | EVS006* |  | 7625 | 25.9 | 6500 | 4.49 | 0.63542 | Yes
216772586 | Ground Water | Enertech | EVS015* |  | 18150 | 35.1 | 14400 | 5.4 | 1.5125 | Yes
216772587 | Ground Water | Enertech | EZS006* |  | 6900 | 22.9 | 6300 | 4.3 | 0.575 | No
216772588 | Ground Water | Enertech | EBT060* | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
216772590 | Ground Water | Enertech | EVT060* |  | 64200 | 22 | 58550 | 4.49 | 5.35 | Yes
216772591 | Ground Water | Enertech | EYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216772592 | Ground Water | Enertech | EZS015* |  | 16000 | 26.3 | 14300 | 4.8 | 1.3333 | Yes
216772593 | Ground Water | Enertech | EZS017* |  | 18475 | 22.2 | 15950 | 4.38 | 1.5396 | Yes
216772594 | Ground Water | Enertech | EZS018* |  | 21500 | 30.1 | 17500 | 4.7 | 1.7917 | Yes
216772596 | Ground Water | Enertech | EYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216772598 | Ground Water | Enertech | EWS036* |  | 35600 | 22.9 | 38300 | 4.1 | 2.9667 | Yes
216772599 | Ground Water | Enertech | EWS048* |  | 52500 | 22.9 | 58700 | 4.2 | 4.375 | Yes
216772602 | Ground Water | Enertech | EWT048* |  | 52700 | 21.2 | 61100 | 4.2 | 4.3917 | Yes
216801023 | Ground Water | CARRIER | 50PEC09****3/CG |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801024 | Ground Water | CARRIER | 50PEC09****4/DG |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801031 | Ground Water | FHP | CA009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801032 | Ground Water | FHP | CA009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801911 | Ground Water | BOSCH | WT025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801912 | Ground Water | BOSCH | WT025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217642975 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642976 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642977 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642978 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642979 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642980 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642981 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642982 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642983 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642984 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642990 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642991 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642992 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642993 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642994 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
206422424 | Ground Water | COMFORT-AIRE | HBH/V030*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
217351730 | Ground Water | CARRIER | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351731 | Ground Water | CARRIER | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351732 | Ground Water | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351733 | Ground Water | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351734 | Ground Water | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351735 | Ground Water | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351736 | Ground Water | CARRIER | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351738 | Ground Water | CARRIER | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351739 | Ground Water | CARRIER | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351741 | Ground Water | CARRIER | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351742 | Ground Water | CARRIER | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351743 | Ground Water | CARRIER | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351744 | Ground Water | CARRIER | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351745 | Ground Water | CARRIER | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351746 | Ground Water | CARRIER | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351747 | Ground Water | CARRIER | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217897457 | Ground Water | CENTURY | MJN036A | MKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
217897458 | Ground Water | COMFORT-AIRE | MJN036A | MKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
217897463 | Ground Water | CENTURY | MJN024A | MAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
217897464 | Ground Water | COMFORT-AIRE | MJN024A | MAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
217897465 | Ground Water | CENTURY | MJN036A | MAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
217897466 | Ground Water | COMFORT-AIRE | MJN036A | MAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
217897467 | Ground Water | CENTURY | MJN048A | MAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
217897468 | Ground Water | COMFORT-AIRE | MJN048A | MAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
205311952 | Ground Water | GEOSTAR | ZBV/ZBH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
205311983 | Ground Water | GEOSTAR | ZBV/ZBH030**0*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311984 | Ground Water | GEOSTAR | ZBV/ZBH030**2*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311985 | Ground Water | GEOSTAR | ZBV/ZBH030**3*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311986 | Ground Water | GEOSTAR | ZBV/ZBH030**4*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311987 | Ground Water | GEOSTAR | ZBV/ZBH030**0*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311988 | Ground Water | GEOSTAR | ZBV/ZBH030**2*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311989 | Ground Water | GEOSTAR | ZBV/ZBH030**3*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311990 | Ground Water | GEOSTAR | ZBV/ZBH030**4*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311991 | Ground Water | GEOSTAR | ZBV/ZBH036**0*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311992 | Ground Water | GEOSTAR | ZBV/ZBH036**2*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311993 | Ground Water | GEOSTAR | ZBV/ZBH036**3*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311994 | Ground Water | GEOSTAR | ZBV/ZBH036**4*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311995 | Ground Water | GEOSTAR | ZBV/ZBH036**0*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311996 | Ground Water | GEOSTAR | ZBV/ZBH036**2*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311997 | Ground Water | GEOSTAR | ZBV/ZBH036**3*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311998 | Ground Water | GEOSTAR | ZBV/ZBH036**4*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311999 | Ground Water | GEOSTAR | ZBV/ZBH036**0*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312000 | Ground Water | GEOSTAR | ZBV/ZBH036**2*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312001 | Ground Water | GEOSTAR | ZBV/ZBH036**3*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312002 | Ground Water | GEOSTAR | ZBV/ZBH036**4*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312006 | Ground Water | GEOSTAR | ZBV/ZBH042**0*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312007 | Ground Water | GEOSTAR | ZBV/ZBH042**3*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202146985 | Ground Water | TETCO | TZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146986 | Ground Water | TETCO | TZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146987 | Ground Water | TETCO | TZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146988 | Ground Water | TETCO | TZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146989 | Ground Water | TETCO | TZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
202146990 | Ground Water | TETCO | TZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146991 | Ground Water | GEOCOMFORT | GZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
202146992 | Ground Water | GEOCOMFORT | GZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146993 | Ground Water | GEOCOMFORT | GZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146994 | Ground Water | GEOCOMFORT | GZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146995 | Ground Water | GEOCOMFORT | GZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
214771933 | Ground Water | TRANE | EXVK015A |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214771934 | Ground Water | TRANE | EXVK018A |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214771935 | Ground Water | TRANE | EXVK024A |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214771936 | Ground Water | TRANE | EXVK030A |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214771937 | Ground Water | TRANE | EXVK036A |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214771938 | Ground Water | TRANE | EXVK042A |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214771939 | Ground Water | TRANE | EXVK048A |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
207335588 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335589 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335590 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335591 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335592 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335593 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207337449 | Ground Water | GEOSTAR | 12(1,2)A048 |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
3706370 | Ground Water | GEOSTAR | ZS018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3706371 | Ground Water | GEOSTAR | ZS023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706373 | Ground Water | GEOSTAR | ZS023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706374 | Ground Water | GEOSTAR | ZS023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706375 | Ground Water | GEOSTAR | ZS023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706376 | Ground Water | GEOSTAR | ZS024**0*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706377 | Ground Water | GEOSTAR | ZS024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706378 | Ground Water | GEOSTAR | ZS024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706379 | Ground Water | GEOSTAR | ZS024**4*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706380 | Ground Water | GEOSTAR | ZS030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706381 | Ground Water | GEOSTAR | ZS030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706382 | Ground Water | GEOSTAR | ZS030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706383 | Ground Water | GEOSTAR | ZS030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706384 | Ground Water | GEOSTAR | ZS036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706385 | Ground Water | GEOSTAR | ZS036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706387 | Ground Water | GEOSTAR | ZS036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706391 | Ground Water | GEOSTAR | ZS042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706392 | Ground Water | GEOSTAR | ZS042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706393 | Ground Water | GEOSTAR | ZS042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706394 | Ground Water | GEOSTAR | ZS048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3706395 | Ground Water | GEOSTAR | ZS048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3706396 | Ground Water | GEOSTAR | ZS048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3811671 | Ground Water | WaterFurnace | USV/USH024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3811673 | Ground Water | WaterFurnace | USV/USH024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
202147712 | Ground Water | GEOCOMFORT | GZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147713 | Ground Water | HYDRON MODULE | HZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147714 | Ground Water | TETCO | TZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
205767623 | Ground Water | ClimateMaster | TCH/V015A*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205767624 | Ground Water | ClimateMaster | TRH/V015A*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205767626 | Ground Water | ClimateMaster | TES/P038B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
205767627 | Ground Water | ClimateMaster | TES/P049B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
205780261 | Ground Water | GEOSTAR | 111J038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205782086 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ042J1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
205782087 | Ground Water | GEOSTAR | 103J042**1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
205782239 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205782240 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
205782241 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782242 | Ground Water | YORK BY JOHNSON CONTROLS | YAST038**1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782243 | Ground Water | GeoSmart Energy | GSZ036*1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205782244 | Ground Water | GeoSmart Energy | GSZ042*1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
205782245 | Ground Water | GeoSmart Energy | GTZ038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782246 | Ground Water | GeoSmart Energy | GTS038*1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
205782247 | Ground Water | GeoSmart Energy | GTS038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782567 | Ground Water | YORK BY JOHNSON CONTROLS | YACT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205782571 | Ground Water | GeoSmart Energy | QT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205788273 | Ground Water | Johnson Controls | JSH/V/D018B B |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
205788274 | Ground Water | SKYMARK | JSH/V/D018B C |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
205788275 | Ground Water | Johnson Controls | JSH/V/D018B*K B |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205788276 | Ground Water | SKYMARK | JSH/V/D018B*K C |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205788277 | Ground Water | Johnson Controls | JSH/V/D024C B |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | No
205788278 | Ground Water | SKYMARK | JSH/V/D024C C |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | No
205788279 | Ground Water | Johnson Controls | JSH/V/D024C*K B |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | No
205788280 | Ground Water | SKYMARK | JSH/V/D024C*K C |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | No
205788281 | Ground Water | Johnson Controls | JSH/V/D030C B |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | No
205788282 | Ground Water | SKYMARK | JSH/V/D030C C |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | No
205788283 | Ground Water | Johnson Controls | JSH/V/D036C B |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | No
205788284 | Ground Water | SKYMARK | JSH/V/D036C C |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | No
205788285 | Ground Water | Johnson Controls | JSH/V/D036C*K B |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | No
205788286 | Ground Water | SKYMARK | JSH/V/D036C*K C |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | No
205788287 | Ground Water | Johnson Controls | JSH/V/D042C B |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | No
205788288 | Ground Water | SKYMARK | JSH/V/D042C C |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | No
205788289 | Ground Water | Johnson Controls | JSH/V/D042C*K B |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205788290 | Ground Water | SKYMARK | JSH/V/D042C*K C |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205788293 | Ground Water | Johnson Controls | JSH/V/D060C B |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | No
205788294 | Ground Water | SKYMARK | JSH/V/D060C C |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | No
202146996 | Ground Water | GEOCOMFORT | GZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
202146997 | Ground Water | GEOCOMFORT | GZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202146998 | Ground Water | GEOCOMFORT | GZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202146999 | Ground Water | GEOCOMFORT | GZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147000 | Ground Water | HYDRON MODULE | HZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
202147001 | Ground Water | HYDRON MODULE | HZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147002 | Ground Water | HYDRON MODULE | HZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147003 | Ground Water | HYDRON MODULE | HZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147004 | Ground Water | HYDRON MODULE | HZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147005 | Ground Water | HYDRON MODULE | HZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
202147006 | Ground Water | HYDRON MODULE | HZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147007 | Ground Water | HYDRON MODULE | HZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147008 | Ground Water | HYDRON MODULE | HZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147009 | Ground Water | TETCO | TZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
202147010 | Ground Water | TETCO | TZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147011 | Ground Water | TETCO | TZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147012 | Ground Water | TETCO | TZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147013 | Ground Water | TETCO | TZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147014 | Ground Water | TETCO | TZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
202147015 | Ground Water | TETCO | TZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147016 | Ground Water | TETCO | TZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147017 | Ground Water | TETCO | TZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147018 | Ground Water | GEOCOMFORT | GZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147019 | Ground Water | GEOCOMFORT | GZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147020 | Ground Water | GEOCOMFORT | GZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147021 | Ground Water | GEOCOMFORT | GZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147022 | Ground Water | GEOCOMFORT | GZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147023 | Ground Water | GEOCOMFORT | GZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147024 | Ground Water | HYDRON MODULE | HZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147025 | Ground Water | HYDRON MODULE | HZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147026 | Ground Water | HYDRON MODULE | HZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147027 | Ground Water | HYDRON MODULE | HZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147028 | Ground Water | HYDRON MODULE | HZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147029 | Ground Water | HYDRON MODULE | HZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147030 | Ground Water | TETCO | TZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147031 | Ground Water | TETCO | TZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147032 | Ground Water | TETCO | TZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147033 | Ground Water | TETCO | TZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147034 | Ground Water | TETCO | TZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147035 | Ground Water | TETCO | TZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147036 | Ground Water | GEOCOMFORT | GZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147037 | Ground Water | GEOCOMFORT | GZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147038 | Ground Water | GEOCOMFORT | GZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147039 | Ground Water | GEOCOMFORT | GZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147040 | Ground Water | GEOCOMFORT | GZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
217754991 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217754992 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217754993 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755000 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755001 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755002 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755007 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755008 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755009 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755010 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755011 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755012 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755019 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755020 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755021 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755022 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755023 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755024 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217893588 | Ground Water | Engineered Comfort | 44VHB/VCB-19 |  | 21000 | 21.1 | 18500 | 4.1 | 1.75 | Yes
217897411 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
217897412 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
200083804 | Ground Water | NORTHERN HEAT PUMP | RA-VE-061-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
200083805 | Ground Water | NORTHSTAR SERIES | RA-VE-061-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
201756620 | Ground Water | NORTHERN HEAT PUMP | RA-VE-041-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
201756621 | Ground Water | NORTHSTAR SERIES | RA-VE-041-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
201756622 | Ground Water | NORTHERN HEAT PUMP | RA-VE-053-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
201756623 | Ground Water | NORTHSTAR SERIES | RA-VE-053-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
205973782 | Ground Water | CENTURY | HZS048B | MWG48**-B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
205996637 | Ground Water | Johnson Controls | JCH/V024A*W/K B |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205996638 | Ground Water | SKYMARK | JCH/V024A*W/K C |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205996643 | Ground Water | Johnson Controls | JEV/H/D026B B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | No
205996644 | Ground Water | Johnson Controls | JEV/H/D038B B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | No
205996645 | Ground Water | Johnson Controls | JEV/H/D049B B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | No
205996646 | Ground Water | Johnson Controls | JEV/H/D064B B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | No
205996647 | Ground Water | Johnson Controls | JEV/H/D072B B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | No
217642948 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642950 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642953 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642954 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642955 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642959 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642960 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642961 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642962 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642963 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642964 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642965 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642973 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642974 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
9100310 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100311 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100313 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100314 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100316 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100317 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100319 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100320 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100325 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
9100326 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
9100327 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
9100328 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
9100330 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
9100332 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
9100335 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100337 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100338 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100340 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100341 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100343 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100345 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100346 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100348 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100349 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100351 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100352 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100354 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100355 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100357 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100358 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
207348679 | Ground Water | WaterFurnace | URS070*4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348680 | Ground Water | WaterFurnace | URS070*4*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348681 | Ground Water | WaterFurnace | URS060*0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348682 | Ground Water | WaterFurnace | URS060*0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348683 | Ground Water | WaterFurnace | URS060*0*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348684 | Ground Water | WaterFurnace | URS060*3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348685 | Ground Water | WaterFurnace | URS060*3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348686 | Ground Water | WaterFurnace | URS060*3*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348687 | Ground Water | WaterFurnace | URS060*4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348688 | Ground Water | WaterFurnace | URS060*4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348689 | Ground Water | WaterFurnace | URS060*4*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348707 | Ground Water | WaterFurnace | URD038*0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348708 | Ground Water | WaterFurnace | URD038*0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348709 | Ground Water | WaterFurnace | URD038*0*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348710 | Ground Water | WaterFurnace | URD038*3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348711 | Ground Water | WaterFurnace | URD038*3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348712 | Ground Water | WaterFurnace | URD038*3*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348713 | Ground Water | WaterFurnace | URD038*4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348714 | Ground Water | WaterFurnace | URD038*4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348715 | Ground Water | WaterFurnace | URD038*4*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348716 | Ground Water | WaterFurnace | URD049*0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348717 | Ground Water | WaterFurnace | URD049*0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348718 | Ground Water | WaterFurnace | URD049*0*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348719 | Ground Water | WaterFurnace | URD049*3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348720 | Ground Water | WaterFurnace | URD049*3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348721 | Ground Water | WaterFurnace | URD049*3*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348722 | Ground Water | WaterFurnace | URD049*4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348723 | Ground Water | WaterFurnace | URD049*4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348724 | Ground Water | WaterFurnace | URD049*4*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348725 | Ground Water | WaterFurnace | URD064*0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348726 | Ground Water | WaterFurnace | URD064*0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348727 | Ground Water | WaterFurnace | URD064*0*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348728 | Ground Water | WaterFurnace | URD064*3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348729 | Ground Water | WaterFurnace | URD064*3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348730 | Ground Water | WaterFurnace | URD064*3*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348731 | Ground Water | WaterFurnace | URD064*4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348732 | Ground Water | WaterFurnace | URD064*4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348733 | Ground Water | WaterFurnace | URD064*4*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348734 | Ground Water | WaterFurnace | URD072*0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348735 | Ground Water | WaterFurnace | URD072*0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348736 | Ground Water | WaterFurnace | URD072*0*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348737 | Ground Water | WaterFurnace | URD072*3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348738 | Ground Water | WaterFurnace | URD072*3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348739 | Ground Water | WaterFurnace | URD072*3*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348740 | Ground Water | WaterFurnace | URD072*4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348741 | Ground Water | WaterFurnace | URD072*4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348742 | Ground Water | WaterFurnace | URD072*4*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
205767488 | Ground Water | ClimateMaster | TSH/V006A |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205767489 | Ground Water | ClimateMaster | TSH/V/D018B |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
205767490 | Ground Water | ClimateMaster | TSH/V/D018B*K |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205767496 | Ground Water | ClimateMaster | TCH/V015A |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205767497 | Ground Water | ClimateMaster | TCH/V018A |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
215224810 | Ground Water | HEIL | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224811 | Ground Water | ARCOAIRE | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224812 | Ground Water | KEEPRITE | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224813 | Ground Water | TEMPSTAR | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224814 | Ground Water | COMFORTMAKER | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224815 | Ground Water | DAY & NIGHT | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224816 | Ground Water | HEIL | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224817 | Ground Water | ARCOAIRE | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224818 | Ground Water | KEEPRITE | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224819 | Ground Water | TEMPSTAR | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224820 | Ground Water | COMFORTMAKER | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224821 | Ground Water | DAY & NIGHT | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
206438824 | Ground Water | FHP | EP012-2HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438869 | Ground Water | CARRIER | 50PSH/V007***4/DA* |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438870 | Ground Water | CARRIER | 50PSH/V007***3/CA* |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438871 | Ground Water | CARRIER | 50PSH/V009***3/CA* |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438872 | Ground Water | CARRIER | 50PSH/V009***4/DA* |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438873 | Ground Water | CARRIER | 50PSH/V012***3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438874 | Ground Water | CARRIER | 50PSH/V015***3/CA* |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438875 | Ground Water | CARRIER | 50PSH/V015***4/DA* |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438876 | Ground Water | CARRIER | 50PSH/V030***4/DA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438877 | Ground Water | CARRIER | 50PSH/V030***6/FA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438878 | Ground Water | CARRIER | 50PSH/V030***5/EA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438879 | Ground Water | CARRIER | 50PSH/V030***3/CA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438880 | Ground Water | CARRIER | 50PSH/V060***6/FA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438881 | Ground Water | CARRIER | 50PSH/V060***5/EA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438882 | Ground Water | CARRIER | 50PSH/V060***3/CA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438883 | Ground Water | CARRIER | 50PSH/V070***3/CA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438884 | Ground Water | CARRIER | 50PSH/V070***5/EA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438885 | Ground Water | CARRIER | 50PSH/V070***6/FA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438903 | Ground Water | CARRIER | 50PSV012**C3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438904 | Ground Water | CARRIER | 50PSH012**C3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438905 | Ground Water | CARRIER | 50PSV012**N3/CA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438906 | Ground Water | CARRIER | 50PSH012**N3/CA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
214067579 | Ground Water | GeoSmart Energy | GBV/GBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067580 | Ground Water | GeoSmart Energy | GBV/GBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067581 | Ground Water | GeoSmart Energy | GBV/GBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067582 | Ground Water | GeoSmart Energy | GBV/GBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067583 | Ground Water | GeoSmart Energy | GBV/GBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067584 | Ground Water | GeoSmart Energy | GBV/GBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067585 | Ground Water | GeoSmart Energy | GBV/GBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067586 | Ground Water | GeoSmart Energy | GBV/GBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067587 | Ground Water | GeoSmart Energy | GBV/GBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067588 | Ground Water | GeoSmart Energy | GBV/GBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214067589 | Ground Water | GeoSmart Energy | GBV/GBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067590 | Ground Water | GeoSmart Energy | GBV/GBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067591 | Ground Water | GeoSmart Energy | GBV/GBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214067592 | Ground Water | GeoSmart Energy | GBV/GBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067593 | Ground Water | GeoSmart Energy | GBV/GBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067594 | Ground Water | GeoSmart Energy | GBV/GBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
216727177 | Ground Water | CARRIER | GZ024*******1**1 | FE*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
216727179 | Ground Water | CARRIER | GZ036*******1**2 | FE*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
216727183 | Ground Water | BRYANT | GZ024*******1**1 | FE*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
216727185 | Ground Water | BRYANT | GZ036*******1**2 | FE*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
214844588 | Ground Water | WaterFurnace | W7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
214844645 | Ground Water | WaterFurnace | W7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
214844646 | Ground Water | WaterFurnace | W7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
214844647 | Ground Water | WaterFurnace | W7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
215223342 | Ground Water | WaterFurnace | V5C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215223348 | Ground Water | WaterFurnace | V3C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215223349 | Ground Water | WaterFurnace | V3C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215223354 | Ground Water | WaterFurnace | V5C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215224027 | Ground Water | BOSCH | CF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224028 | Ground Water | BOSCH | CF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224029 | Ground Water | BOSCH | CF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224030 | Ground Water | BOSCH | CF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224031 | Ground Water | BOSCH | CF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224032 | Ground Water | BOSCH | CF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224033 | Ground Water | BOSCH | CF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224034 | Ground Water | BOSCH | CF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224035 | Ground Water | BOSCH | CF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224036 | Ground Water | BOSCH | CF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224037 | Ground Water | BOSCH | CF007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224038 | Ground Water | BOSCH | CF007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224039 | Ground Water | BOSCH | CF009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224040 | Ground Water | BOSCH | CF009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224041 | Ground Water | BOSCH | CF012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224042 | Ground Water | BOSCH | CF012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224043 | Ground Water | BOSCH | CF015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224044 | Ground Water | BOSCH | CF015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
201907610 | Ground Water | WaterFurnace | URS036*0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907611 | Ground Water | WaterFurnace | URS036*0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907612 | Ground Water | WaterFurnace | URS036*0*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907613 | Ground Water | WaterFurnace | URS036*3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907614 | Ground Water | WaterFurnace | URS036*3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907615 | Ground Water | WaterFurnace | URS036*3*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907616 | Ground Water | WaterFurnace | URS036*4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907617 | Ground Water | WaterFurnace | URS036*4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907618 | Ground Water | WaterFurnace | URS036*4*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214823446 | Ground Water | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
217903460 | Ground Water | WaterFurnace | V5R060*D4**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903461 | Ground Water | WaterFurnace | V5R060*D4**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903462 | Ground Water | WaterFurnace | V5R060*D4**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903463 | Ground Water | WaterFurnace | V5R072*D4**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903464 | Ground Water | WaterFurnace | V5R072*D4**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903465 | Ground Water | WaterFurnace | V5R072*D4**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903466 | Ground Water | WaterFurnace | V5R096*T4**5* |  | 96600 | 24.9 | 85800 | 4.5 | 8.05 | No
217903467 | Ground Water | WaterFurnace | V5R120*T4**5* |  | 128500 | 23.3 | 113700 | 4.5 | 10.7083 | No
217903468 | Ground Water | WaterFurnace | V5R036*D0**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903469 | Ground Water | WaterFurnace | V5R036*D0**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903470 | Ground Water | WaterFurnace | V5R036*D0**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903471 | Ground Water | WaterFurnace | V5R036*D3**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903472 | Ground Water | WaterFurnace | V5R036*D3**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903473 | Ground Water | WaterFurnace | V5R036*D3**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903474 | Ground Water | WaterFurnace | V5R048*D0**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903475 | Ground Water | WaterFurnace | V5R048*D0**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903476 | Ground Water | WaterFurnace | V5R048*D0**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903477 | Ground Water | WaterFurnace | V5R048*D3**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903478 | Ground Water | WaterFurnace | V5R048*D3**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903479 | Ground Water | WaterFurnace | V5R048*D3**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903480 | Ground Water | WaterFurnace | V5R060*D0**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903481 | Ground Water | WaterFurnace | V5R060*D0**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903482 | Ground Water | WaterFurnace | V5R060*D0**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903483 | Ground Water | WaterFurnace | V5R060*D3**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903484 | Ground Water | WaterFurnace | V5R060*D3**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903485 | Ground Water | WaterFurnace | V5R060*D3**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903486 | Ground Water | WaterFurnace | V5R072*D0**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903487 | Ground Water | WaterFurnace | V5R072*D0**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
209156996 | Ground Water | AE Air | WSS6015*7* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
209180330 | Ground Water | HYDROTECH | WSV6018B* |  | 20000 | 21.1 | 16500 | 4.1 | 1.6667 | Yes
209180331 | Ground Water | HYDROTECH | WSV6036B* |  | 37000 | 22 | 35000 | 4.1 | 3.0833 | Yes
209180332 | Ground Water | HYDROTECH | WSV6042B* |  | 44000 | 24 | 38500 | 4.4 | 3.6667 | Yes
209180334 | Ground Water | HYDROTECH | WSV6048B* |  | 55500 | 23 | 47000 | 4.3 | 4.625 | Yes
209180335 | Ground Water | AE Air | WSV6018B* |  | 20000 | 21.1 | 16500 | 4.1 | 1.6667 | Yes
209180336 | Ground Water | AE Air | WSV6036B* |  | 37000 | 22 | 35000 | 4.1 | 3.0833 | Yes
209180337 | Ground Water | AE Air | WSV6042B* |  | 44000 | 24 | 38500 | 4.4 | 3.6667 | Yes
209180338 | Ground Water | AE Air | WSV6048B* |  | 55500 | 23 | 47000 | 4.3 | 4.625 | Yes
209323637 | Ground Water | HYDROTECH | WSV6009B* |  | 11000 | 26 | 9000 | 4.3 | 0.91667 | Yes
209323638 | Ground Water | AE Air | WSV6009B* |  | 11000 | 26 | 9000 | 4.3 | 0.91667 | Yes
209945912 | Ground Water | WaterFurnace | NBV/NBH009**0*6 |  | 11000 | 23 | 10700 | 4.5 | 0.91667 | No
209945913 | Ground Water | WaterFurnace | NBV/NBH009**2*6 |  | 11000 | 23 | 10700 | 4.5 | 0.91667 | No
209945914 | Ground Water | WaterFurnace | NBV/NBH012**0*6 |  | 13400 | 23.5 | 12400 | 4.3 | 1.1167 | No
209945915 | Ground Water | WaterFurnace | NBV/NBH012**2*6 |  | 13400 | 23.5 | 12400 | 4.3 | 1.1167 | No
211127895 | Ground Water | WaterFurnace | NVV/NVH036D1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
211127897 | Ground Water | WaterFurnace | NVV/NVH060D1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
211127898 | Ground Water | GEOSTAR | 141/142D036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
211127900 | Ground Water | GEOSTAR | 141/142D060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
211306507 | Ground Water | WaterFurnace | NVZ033*1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | Yes
211306508 | Ground Water | WaterFurnace | NVZ042*1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | Yes
217351904 | Ground Water | KEEPRITE | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351905 | Ground Water | KEEPRITE | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351906 | Ground Water | KEEPRITE | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351907 | Ground Water | KEEPRITE | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351908 | Ground Water | KEEPRITE | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351909 | Ground Water | KEEPRITE | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351911 | Ground Water | KEEPRITE | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351912 | Ground Water | KEEPRITE | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351914 | Ground Water | KEEPRITE | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351916 | Ground Water | KEEPRITE | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351919 | Ground Water | TEMPSTAR | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351920 | Ground Water | TEMPSTAR | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351921 | Ground Water | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351922 | Ground Water | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351923 | Ground Water | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351924 | Ground Water | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351925 | Ground Water | TEMPSTAR | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351927 | Ground Water | TEMPSTAR | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351928 | Ground Water | TEMPSTAR | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351930 | Ground Water | TEMPSTAR | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351931 | Ground Water | TEMPSTAR | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351932 | Ground Water | TEMPSTAR | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351933 | Ground Water | TEMPSTAR | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351934 | Ground Water | TEMPSTAR | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351935 | Ground Water | TEMPSTAR | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351936 | Ground Water | TEMPSTAR | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351938 | Ground Water | TEMPSTAR | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351939 | Ground Water | TEMPSTAR | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351941 | Ground Water | TEMPSTAR | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351943 | Ground Water | TEMPSTAR | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
8737989 | Ground Water | HYDRON MODULE | HVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737990 | Ground Water | TETCO | TVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737991 | Ground Water | GEOCOMFORT | GVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737992 | Ground Water | HYDRON MODULE | HVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737993 | Ground Water | TETCO | TVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8738031 | Ground Water | GEOCOMFORT | GVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738032 | Ground Water | HYDRON MODULE | HVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738033 | Ground Water | TETCO | TVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738034 | Ground Water | GEOCOMFORT | GVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738035 | Ground Water | HYDRON MODULE | HVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738036 | Ground Water | TETCO | TVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738037 | Ground Water | GEOCOMFORT | GVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738038 | Ground Water | HYDRON MODULE | HVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738039 | Ground Water | TETCO | TVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738040 | Ground Water | GEOCOMFORT | GVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
8738041 | Ground Water | HYDRON MODULE | HVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
8738042 | Ground Water | TETCO | TVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
8738051 | Ground Water | GEOCOMFORT | GVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738052 | Ground Water | HYDRON MODULE | HVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738053 | Ground Water | TETCO | TVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738054 | Ground Water | GEOCOMFORT | GVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738055 | Ground Water | HYDRON MODULE | HVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738056 | Ground Water | TETCO | TVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738057 | Ground Water | GEOCOMFORT | GVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738058 | Ground Water | HYDRON MODULE | HVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738059 | Ground Water | TETCO | TVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738060 | Ground Water | GEOCOMFORT | GVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738061 | Ground Water | HYDRON MODULE | HVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738062 | Ground Water | TETCO | TVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738067 | Ground Water | GEOCOMFORT | GVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
8738068 | Ground Water | HYDRON MODULE | HVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
8738069 | Ground Water | TETCO | TVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
203337768 | Ground Water | BOSCH-GEO | CE025-1VT/HZ/CF*-*****B |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337769 | Ground Water | BOSCH | CE025-1VT/HZ/CF*-*****B |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337770 | Ground Water | CARRIER | GP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337771 | Ground Water | BRYANT | GP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337772 | Ground Water | HEIL | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337773 | Ground Water | ARCOAIRE | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337774 | Ground Water | KEEPRITE | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337775 | Ground Water | TEMPSTAR | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337776 | Ground Water | COMFORTMAKER | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337777 | Ground Water | DAY & NIGHT | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203343532 | Ground Water | BOSCH-GEO | SM024-1CS*******A | SM024-1AV/AH*-*****A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | Yes
203343535 | Ground Water | BOSCH | SM024-1CS*******A | SM024-1AV/AH*-*****A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | Yes
213087558 | Ground Water | WaterFurnace | NDS049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213087559 | Ground Water | WaterFurnace | NDS049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213087562 | Ground Water | WaterFurnace | NDS064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213087563 | Ground Water | WaterFurnace | NDS064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213154439 | Ground Water | GeoSmart Energy | GTS026*1******K | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
213154440 | Ground Water | GeoSmart Energy | GTS026*1******K | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
213154441 | Ground Water | GeoSmart Energy | GTS049*1******K | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213154442 | Ground Water | GeoSmart Energy | GTS049*1******K | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213154443 | Ground Water | GeoSmart Energy | GTS072*1******K | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
213154444 | Ground Water | GeoSmart Energy | GTS072*1******K | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
213154445 | Ground Water | GeoSmart Energy | GTS064*1******K | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213154446 | Ground Water | GeoSmart Energy | GTS064*1******K | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213154447 | Ground Water | GeoSmart Energy | GTS038*1******K | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
213154448 | Ground Water | GeoSmart Energy | GTS038*1******K | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154451 | Ground Water | GeoSmart Energy | YT048**1*4********C |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
213154454 | Ground Water | GeoSmart Energy | GTZ026*1******K | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
213154455 | Ground Water | GeoSmart Energy | GTZ026*1******K | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
213154456 | Ground Water | GeoSmart Energy | GTZ038*1******K | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154457 | Ground Water | GeoSmart Energy | GTZ038*1******K | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154458 | Ground Water | GeoSmart Energy | GTZ049*1******K | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
213154459 | Ground Water | GeoSmart Energy | GTZ049*1******K | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
213154460 | Ground Water | GeoSmart Energy | GTZ064*1******K | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
213154461 | Ground Water | GeoSmart Energy | GTZ064*1******K | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
213154462 | Ground Water | GeoSmart Energy | GTZ072*1******K | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
213154463 | Ground Water | GeoSmart Energy | GTZ072*1******K | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
213154464 | Ground Water | GeoSmart Energy | GS012**1*0********L |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
213154465 | Ground Water | GeoSmart Energy | GS018**1*1********L |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
213154466 | Ground Water | GeoSmart Energy | GS022**1*1********L |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
213154467 | Ground Water | GeoSmart Energy | GS030**1*1********L |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
213154468 | Ground Water | GeoSmart Energy | GS036**1*1********L |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
213154469 | Ground Water | GeoSmart Energy | GS042**1*1********L |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
213154470 | Ground Water | GeoSmart Energy | GS048**1*1********L |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
213154471 | Ground Water | GeoSmart Energy | GS060**1*1********L |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
213154472 | Ground Water | GeoSmart Energy | GS070**1*1********L |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
213154473 | Ground Water | GeoSmart Energy | GT026**1*1********L |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
202146954 | Ground Water | HYDRON MODULE | HZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146955 | Ground Water | HYDRON MODULE | HZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146956 | Ground Water | HYDRON MODULE | HZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146957 | Ground Water | HYDRON MODULE | HZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146958 | Ground Water | HYDRON MODULE | HZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146959 | Ground Water | HYDRON MODULE | HZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146960 | Ground Water | HYDRON MODULE | HZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146961 | Ground Water | TETCO | TZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146962 | Ground Water | TETCO | TZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146963 | Ground Water | TETCO | TZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146964 | Ground Water | TETCO | TZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146965 | Ground Water | TETCO | TZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146966 | Ground Water | TETCO | TZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146967 | Ground Water | TETCO | TZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146968 | Ground Water | TETCO | TZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146969 | Ground Water | TETCO | TZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146970 | Ground Water | GEOCOMFORT | GZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
202146971 | Ground Water | GEOCOMFORT | GZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146972 | Ground Water | GEOCOMFORT | GZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146973 | Ground Water | GEOCOMFORT | GZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146974 | Ground Water | GEOCOMFORT | GZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146975 | Ground Water | GEOCOMFORT | GZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
202146976 | Ground Water | GEOCOMFORT | GZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146977 | Ground Water | HYDRON MODULE | HZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
202146978 | Ground Water | HYDRON MODULE | HZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146979 | Ground Water | HYDRON MODULE | HZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146980 | Ground Water | HYDRON MODULE | HZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146981 | Ground Water | HYDRON MODULE | HZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146982 | Ground Water | HYDRON MODULE | HZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
202146983 | Ground Water | HYDRON MODULE | HZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146984 | Ground Water | TETCO | TZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
204835632 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
204835633 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205129920 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205129921 | Ground Water | GEOSTAR | 103J036**1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205145424 | Ground Water | GEOCOMFORT | GVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145425 | Ground Water | GEOCOMFORT | GVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145426 | Ground Water | GEOCOMFORT | GVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145427 | Ground Water | HYDRON MODULE | HVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145428 | Ground Water | HYDRON MODULE | HVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145429 | Ground Water | HYDRON MODULE | HVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145430 | Ground Water | TETCO | TVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145431 | Ground Water | TETCO | TVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145432 | Ground Water | TETCO | TVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145433 | Ground Water | GEOCOMFORT | GVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145434 | Ground Water | GEOCOMFORT | GVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145435 | Ground Water | GEOCOMFORT | GVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145436 | Ground Water | HYDRON MODULE | HVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145437 | Ground Water | HYDRON MODULE | HVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145438 | Ground Water | HYDRON MODULE | HVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145439 | Ground Water | TETCO | TVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145527 | Ground Water | GEOCOMFORT | GVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145528 | Ground Water | HYDRON MODULE | HVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145529 | Ground Water | TETCO | TVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145530 | Ground Water | TETCO | TVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145531 | Ground Water | TETCO | TVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205148067 | Ground Water | HYDROTECH | WSV6060A |  | 65000 | 23 | 53500 | 4.1 | 5.4167 | No
216625471 | Ground Water | GEOSTAR | G5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625472 | Ground Water | GEOSTAR | G5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625473 | Ground Water | GEOSTAR | G5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625474 | Ground Water | GEOSTAR | G5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625475 | Ground Water | GEOSTAR | G5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625476 | Ground Water | GEOSTAR | G5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625477 | Ground Water | GEOSTAR | G5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625478 | Ground Water | GEOSTAR | G5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625479 | Ground Water | GEOSTAR | G5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625480 | Ground Water | GEOSTAR | G5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625481 | Ground Water | GEOSTAR | G5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625482 | Ground Water | GEOSTAR | G5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625483 | Ground Water | GEOSTAR | G5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625484 | Ground Water | GEOSTAR | G5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625485 | Ground Water | GEOSTAR | G5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625486 | Ground Water | GEOSTAR | G5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625487 | Ground Water | GEOSTAR | G5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625488 | Ground Water | GEOSTAR | G5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625489 | Ground Water | GEOSTAR | G5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625490 | Ground Water | GEOSTAR | G5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625491 | Ground Water | GEOSTAR | G5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625492 | Ground Water | GEOSTAR | G5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625493 | Ground Water | GEOSTAR | G5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625494 | Ground Water | GEOSTAR | G5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625495 | Ground Water | GEOSTAR | G5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625496 | Ground Water | GEOSTAR | G5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625497 | Ground Water | GEOSTAR | G5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625498 | Ground Water | GEOSTAR | G5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625499 | Ground Water | GEOSTAR | G5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625500 | Ground Water | GEOSTAR | G5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625501 | Ground Water | GEOSTAR | G5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625502 | Ground Water | GEOSTAR | G5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625503 | Ground Water | GEOSTAR | G5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625504 | Ground Water | GEOSTAR | G5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625505 | Ground Water | GEOSTAR | G5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625506 | Ground Water | GEOSTAR | G5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625507 | Ground Water | GEOSTAR | G5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
203495469 | Ground Water | GEOSTAR | 101/102J049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203495470 | Ground Water | GEOSTAR | 103J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
203495474 | Ground Water | GEOSTAR | 103J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
203363140 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363141 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363142 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363143 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363144 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363145 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363146 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363147 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363148 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363150 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**0*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363151 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**0*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363153 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**3*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363154 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**3*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363156 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**4*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363157 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**4*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363170 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**0*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363171 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**0*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363173 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**3*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363174 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**3*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363176 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**4*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363177 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**4*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363180 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**0*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363181 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**0*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363183 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**3*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363184 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**3*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363186 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**4*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363187 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**4*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
215287172 | Ground Water | GEOSTAR | G3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215287179 | Ground Water | GeoSmart Energy | S3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215287184 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215310891 | Ground Water | GEOSTAR | G7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
215310892 | Ground Water | GEOSTAR | G7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
215310893 | Ground Water | GEOSTAR | G7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
215310895 | Ground Water | GEOSTAR | G7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
215310990 | Ground Water | GeoSmart Energy | S7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
215310991 | Ground Water | GeoSmart Energy | S7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
215310992 | Ground Water | GeoSmart Energy | S7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
215310994 | Ground Water | GeoSmart Energy | S7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
216802003 | Ground Water | CARRIER | 50WT*036***5*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802004 | Ground Water | CARRIER | 50WT*036***5*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802005 | Ground Water | CARRIER | 50WT*036***6*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802006 | Ground Water | CARRIER | 50WT*036***6*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802007 | Ground Water | CARRIER | 50WT*048***3*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802008 | Ground Water | CARRIER | 50WT*048***3*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216802009 | Ground Water | CARRIER | 50WT*048***5*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802010 | Ground Water | CARRIER | 50WT*048***5*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216802011 | Ground Water | CARRIER | 50WT*048***6*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802012 | Ground Water | CARRIER | 50WT*048***6*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216802013 | Ground Water | CARRIER | 50WT*060***3*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802014 | Ground Water | CARRIER | 50WT*060***3*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802015 | Ground Water | CARRIER | 50WT*060***5*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802016 | Ground Water | CARRIER | 50WT*060***5*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802017 | Ground Water | CARRIER | 50WT*060***6*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802018 | Ground Water | CARRIER | 50WT*060***6*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802019 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**3*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802020 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**3*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802021 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**3*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802022 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**3*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802023 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**5*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802024 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**5*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802025 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**5*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802026 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**5*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
10318061 | Ground Water | GEOSTAR | 103H070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10318062 | Ground Water | GeoSmart Energy | GSZ070*1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
5699656 | Ground Water | TRANE | VSHE0602 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
5699657 | Ground Water | TRANE | VSHE0604 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
6501883 | Ground Water | GEOSTAR | GBV/GBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
6501884 | Ground Water | GEOSTAR | GBV/GBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
6501885 | Ground Water | GEOSTAR | GBV/GBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
6501886 | Ground Water | GEOSTAR | GBV/GBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
6501887 | Ground Water | GEOSTAR | GBV/GBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
6501888 | Ground Water | GEOSTAR | GBV/GBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501889 | Ground Water | GEOSTAR | GBV/GBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501890 | Ground Water | GEOSTAR | GBV/GBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
6501891 | Ground Water | GEOSTAR | GBV/GBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501892 | Ground Water | GEOSTAR | GBV/GBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501893 | Ground Water | GEOSTAR | GBV/GBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
6501894 | Ground Water | GEOSTAR | GBV/GBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501895 | Ground Water | GEOSTAR | GBV/GBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501896 | Ground Water | GEOSTAR | GBV/GBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
6501897 | Ground Water | GEOSTAR | GBV/GBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
206194160 | Ground Water | Johnson Controls | JCH/V006A*W/K B |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
206194161 | Ground Water | SKYMARK | JCH/V006A*W/K C |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
206194171 | Ground Water | Johnson Controls | JSH/V/D030C*K B |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
206194172 | Ground Water | SKYMARK | JSH/V/D030C*K C |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
206194173 | Ground Water | Johnson Controls | JSH/V/D048C*K B |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | No
206194174 | Ground Water | SKYMARK | JSH/V/D048C*K C |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | No
206194175 | Ground Water | Johnson Controls | JSH/V/D060C*K B |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | No
206194176 | Ground Water | SKYMARK | JSH/V/D060C*K C |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | No
216801990 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**4*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801991 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**5*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801992 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**5*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801993 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**5*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801994 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**5*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801995 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**6*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801996 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**6*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801997 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**6*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801998 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**6*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801999 | Ground Water | CARRIER | 50WT*036***3*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802000 | Ground Water | CARRIER | 50WT*036***3*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802001 | Ground Water | CARRIER | 50WT*036***4*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802002 | Ground Water | CARRIER | 50WT*036***4*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
10316662 | Ground Water | GEOSTAR | 104H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316663 | Ground Water | GeoSmart Energy | GTS064*1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316664 | Ground Water | YORK BY JOHNSON CONTROLS | YAST064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316666 | Ground Water | GEOSTAR | 104H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316667 | Ground Water | GeoSmart Energy | GTS064*1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316672 | Ground Water | GeoSmart Energy | GTS072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316673 | Ground Water | GEOSTAR | 104H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316674 | Ground Water | YORK BY JOHNSON CONTROLS | YAST072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316700 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316701 | Ground Water | GEOSTAR | 103H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316702 | Ground Water | GeoSmart Energy | GTZ072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10318010 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318016 | Ground Water | GeoSmart Energy | GSZ022*1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318017 | Ground Water | GEOSTAR | 103H022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10318018 | Ground Water | GeoSmart Energy | GSZ022*1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10318019 | Ground Water | GEOSTAR | 103H022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318020 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318021 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318022 | Ground Water | GEOSTAR | 103H030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10318023 | Ground Water | GeoSmart Energy | GSZ030*1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318024 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318025 | Ground Water | GeoSmart Energy | GSZ030*1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10318026 | Ground Water | GEOSTAR | 103H030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318045 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318046 | Ground Water | GeoSmart Energy | GSZ048*1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318047 | Ground Water | GEOSTAR | 103H048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
10318048 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318049 | Ground Water | GeoSmart Energy | GSZ048*1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318050 | Ground Water | GEOSTAR | 103H048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
10318051 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318052 | Ground Water | GeoSmart Energy | GSZ060*1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318054 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318055 | Ground Water | GeoSmart Energy | GSZ060*1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10318056 | Ground Water | GEOSTAR | 103H060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10318060 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
216802027 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**6*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802028 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**6*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802029 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**6*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802030 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**6*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216979809 | Ground Water | CARRIER | GCA24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979810 | Ground Water | BRYANT | GCA24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979811 | Ground Water | CARRIER | GCA24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979812 | Ground Water | BRYANT | GCA24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979813 | Ground Water | CARRIER | GCA24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979814 | Ground Water | BRYANT | GCA24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979815 | Ground Water | CARRIER | GCA24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979816 | Ground Water | BRYANT | GCA24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979817 | Ground Water | CARRIER | GCA36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979818 | Ground Water | BRYANT | GCA36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979819 | Ground Water | CARRIER | GCA36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216979820 | Ground Water | BRYANT | GCA36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979821 | Ground Water | CARRIER | GCA48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979822 | Ground Water | BRYANT | GCA48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979823 | Ground Water | CARRIER | GCA48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979824 | Ground Water | BRYANT | GCA48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979825 | Ground Water | CARRIER | GCA60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979826 | Ground Water | BRYANT | GCA60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979827 | Ground Water | CARRIER | GCA60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979828 | Ground Water | BRYANT | GCA60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979837 | Ground Water | HEIL | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979838 | Ground Water | ARCOAIRE | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979839 | Ground Water | KEEPRITE | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979840 | Ground Water | TEMPSTAR | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979841 | Ground Water | COMFORTMAKER | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979842 | Ground Water | DAY & NIGHT | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979843 | Ground Water | HEIL | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979844 | Ground Water | ARCOAIRE | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
7419473 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419527 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419618 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419681 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419733 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419797 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7420917 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7421327 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421397 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421438 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421969 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421970 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421971 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421972 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421973 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421974 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421975 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421976 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421977 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421980 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421989 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421999 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7422020 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422043 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422058 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422072 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422083 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422093 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422134 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422147 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422187 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422202 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422225 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422234 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422268 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422280 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422290 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422299 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422309 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
203363129 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**2*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363130 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**2*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363132 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**3*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363133 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**3*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363135 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**4*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363136 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**4*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363137 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363138 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363139 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
206900571 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900572 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900573 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900574 | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900575 | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900576 | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900577 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900578 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900579 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206438720 | Ground Water | BOSCH | EP009-2HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438721 | Ground Water | BOSCH | EP012-0HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438722 | Ground Water | BOSCH | EP012-0HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438723 | Ground Water | BOSCH | EP012-0VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438724 | Ground Water | BOSCH | EP012-0VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438725 | Ground Water | BOSCH | EP012-1HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438726 | Ground Water | BOSCH | EP012-1HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438727 | Ground Water | BOSCH | EP012-1VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438728 | Ground Water | BOSCH | EP012-1VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438729 | Ground Water | BOSCH | EP012-2HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438730 | Ground Water | BOSCH | EP012-2HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438731 | Ground Water | BOSCH | EP012-2VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438732 | Ground Water | BOSCH | EP012-2VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438733 | Ground Water | BOSCH | EP015-2HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438734 | Ground Water | BOSCH | EP030-1HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438735 | Ground Water | BOSCH | EP030-2HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438736 | Ground Water | BOSCH | EP030-3HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438737 | Ground Water | BOSCH | EP030-4HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438738 | Ground Water | BOSCH | EP060-3HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438739 | Ground Water | BOSCH | EP060-4HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438740 | Ground Water | BOSCH | EP070-3HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438741 | Ground Water | BOSCH | EP070-4HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438761 | Ground Water | BOSCH | EP012-1HZ/VT*-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438762 | Ground Water | BOSCH | EP015-1HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438763 | Ground Water | BOSCH | EP060-1HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438764 | Ground Water | BOSCH | EP070-1HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
9100370 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100371 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100373 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100374 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100377 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100378 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100380 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100381 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100383 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100384 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100390 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100391 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100393 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100394 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100396 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100397 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100400 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100401 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100403 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
217967038 | Ground Water | TRANE | VSHK0244 |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
217967039 | Ground Water | TRANE | VSVK0244 |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967040 | Ground Water | TRANE | VSHK0334 |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967041 | Ground Water | TRANE | VSVK0334 |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967042 | Ground Water | TRANE | VSHK0424 |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967043 | Ground Water | TRANE | VSVK0424 |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
217967044 | Ground Water | TRANE | VSHK0504 |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967045 | Ground Water | TRANE | VSVK0504 |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967046 | Ground Water | TRANE | VSHK0604 |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967047 | Ground Water | TRANE | VSVK0604 |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
201864513 | Ground Water | GEOCOMFORT | GZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864514 | Ground Water | HYDRON MODULE | HZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864515 | Ground Water | TETCO | TZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864519 | Ground Water | GEOCOMFORT | GZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864521 | Ground Water | HYDRON MODULE | HZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864523 | Ground Water | TETCO | TZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
214841657 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
214841658 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
214841660 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
214841662 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
214841664 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
214841665 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
214841666 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
214841668 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
202350500 | Ground Water | AAON, Inc. | M2-014-3-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
202350501 | Ground Water | AAON, Inc. | M2-014-3-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
202350502 | Ground Water | AAON, Inc. | M2-014-4-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
202350503 | Ground Water | AAON, Inc. | M2-014-4-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
202350512 | Ground Water | AAON, Inc. | WH-060-1-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202350513 | Ground Water | AAON, Inc. | WH-060-2-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
205767582 | Ground Water | ClimateMaster | TES/P038B | TAH038C | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
205767583 | Ground Water | ClimateMaster | TES/P049B | TAH049C | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
205767586 | Ground Water | ClimateMaster | TES/P026B | TAH026C***A* | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
205767587 | Ground Water | ClimateMaster | TES/P026B | TAH026C***B* | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
205767588 | Ground Water | ClimateMaster | TES/P026B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
205767589 | Ground Water | ClimateMaster | TES/P026B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
205767590 | Ground Water | ClimateMaster | TRE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205767591 | Ground Water | ClimateMaster | TRE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205767592 | Ground Water | ClimateMaster | TRE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205767593 | Ground Water | ClimateMaster | TRE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
205767605 | Ground Water | ClimateMaster | VEV/H/D1860 |  | 48000 | 35.5 | 60000 | 4.3 | 4 | Yes
205767606 | Ground Water | ClimateMaster | VEV/H/D0930 |  | 24000 | 42 | 30000 | 4.8 | 2 | Yes
205767607 | Ground Water | ClimateMaster | TZV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
205767608 | Ground Water | ClimateMaster | TZV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205767610 | Ground Water | ClimateMaster | TZV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
217351880 | Ground Water | HEIL | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351881 | Ground Water | HEIL | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351882 | Ground Water | HEIL | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351884 | Ground Water | HEIL | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351885 | Ground Water | HEIL | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351887 | Ground Water | HEIL | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351889 | Ground Water | HEIL | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
8714940 | Ground Water | CARRIER | GZ024******1**1 | FE/V***F003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8714941 | Ground Water | BRYANT | GZ024******1*X1 | FE/V***F003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8735477 | Ground Water | GEOCOMFORT | GVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735495 | Ground Water | HYDRON MODULE | HVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735512 | Ground Water | TETCO | TVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735538 | Ground Water | GEOCOMFORT | GVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735552 | Ground Water | HYDRON MODULE | HVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735567 | Ground Water | TETCO | TVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735607 | Ground Water | GEOCOMFORT | GVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735711 | Ground Water | HYDRON MODULE | HVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735721 | Ground Water | TETCO | TVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735754 | Ground Water | GEOCOMFORT | GVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735767 | Ground Water | HYDRON MODULE | HVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735778 | Ground Water | TETCO | TVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735903 | Ground Water | GEOCOMFORT | GVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735904 | Ground Water | HYDRON MODULE | HVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735905 | Ground Water | TETCO | TVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735906 | Ground Water | GEOCOMFORT | GVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735907 | Ground Water | HYDRON MODULE | HVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735908 | Ground Water | TETCO | TVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735909 | Ground Water | GEOCOMFORT | GVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735910 | Ground Water | HYDRON MODULE | HVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735911 | Ground Water | TETCO | TVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8737970 | Ground Water | GEOCOMFORT | GVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737971 | Ground Water | HYDRON MODULE | HVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737972 | Ground Water | TETCO | TVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737973 | Ground Water | GEOCOMFORT | GVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737974 | Ground Water | HYDRON MODULE | HVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737975 | Ground Water | TETCO | TVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737976 | Ground Water | GEOCOMFORT | GVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737977 | Ground Water | HYDRON MODULE | HVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737978 | Ground Water | TETCO | TVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737982 | Ground Water | GEOCOMFORT | GVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737983 | Ground Water | HYDRON MODULE | HVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737984 | Ground Water | TETCO | TVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737985 | Ground Water | GEOCOMFORT | GVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737986 | Ground Water | HYDRON MODULE | HVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737987 | Ground Water | TETCO | TVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737988 | Ground Water | GEOCOMFORT | GVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
205312038 | Ground Water | GEOSTAR | ZBV/ZBH070**3*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312039 | Ground Water | GEOSTAR | ZBV/ZBH070**4*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312040 | Ground Water | GEOSTAR | ZBV/ZBH070**0*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312041 | Ground Water | GEOSTAR | ZBV/ZBH070**3*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312042 | Ground Water | GEOSTAR | ZBV/ZBH070**4*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202147041 | Ground Water | GEOCOMFORT | GZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147042 | Ground Water | GEOCOMFORT | GZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147043 | Ground Water | HYDRON MODULE | HZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147044 | Ground Water | HYDRON MODULE | HZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147045 | Ground Water | HYDRON MODULE | HZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147046 | Ground Water | HYDRON MODULE | HZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147047 | Ground Water | HYDRON MODULE | HZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
202147048 | Ground Water | HYDRON MODULE | HZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147049 | Ground Water | HYDRON MODULE | HZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147050 | Ground Water | TETCO | TZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147051 | Ground Water | TETCO | TZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147052 | Ground Water | TETCO | TZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147053 | Ground Water | TETCO | TZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147054 | Ground Water | TETCO | TZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
202147055 | Ground Water | TETCO | TZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147056 | Ground Water | TETCO | TZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147061 | Ground Water | GEOCOMFORT | GZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147062 | Ground Water | GEOCOMFORT | GZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147067 | Ground Water | HYDRON MODULE | HZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147068 | Ground Water | HYDRON MODULE | HZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147073 | Ground Water | TETCO | TZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147074 | Ground Water | TETCO | TZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147690 | Ground Water | GEOCOMFORT | GZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147691 | Ground Water | HYDRON MODULE | HZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147692 | Ground Water | TETCO | TZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147693 | Ground Water | TETCO | TZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202147694 | Ground Water | GEOCOMFORT | GZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147695 | Ground Water | HYDRON MODULE | HZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147696 | Ground Water | TETCO | TZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147697 | Ground Water | GEOCOMFORT | GZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147698 | Ground Water | HYDRON MODULE | HZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147699 | Ground Water | TETCO | TZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147700 | Ground Water | GEOCOMFORT | GZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147701 | Ground Water | HYDRON MODULE | HZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147702 | Ground Water | TETCO | TZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147703 | Ground Water | GEOCOMFORT | GZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147704 | Ground Water | GEOCOMFORT | GZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147705 | Ground Water | HYDRON MODULE | HZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147706 | Ground Water | HYDRON MODULE | HZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147707 | Ground Water | TETCO | TZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147708 | Ground Water | TETCO | TZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202833355 | Ground Water | BOSCH | EC096-1VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833356 | Ground Water | BOSCH | EC096-3VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833357 | Ground Water | BOSCH | EC096-4VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833829 | Ground Water | CARRIER | 50H/VQP096**N3B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833831 | Ground Water | CARRIER | 50H/VQP096**C3B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833833 | Ground Water | FHP | EC096-1VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833835 | Ground Water | CARRIER | 50H/VQP096**N5B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833836 | Ground Water | CARRIER | 50H/VQP096**N6B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833839 | Ground Water | CARRIER | 50H/VQP096**C5B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833840 | Ground Water | CARRIER | 50H/VQP096**C6B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833843 | Ground Water | FHP | EC096-3VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833844 | Ground Water | FHP | EC096-4VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202835053 | Ground Water | BOSCH | SM036-1HZ*-*****C |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
202835056 | Ground Water | BOSCH | SM024-1VT*-*****C |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | Yes
202835057 | Ground Water | BOSCH | SM060-1VT*-*****C |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | Yes
202836307 | Ground Water | BOSCH | SM036-1VT*-*****C |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | Yes
202836309 | Ground Water | BOSCH | SM048-1VT*-*****C |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | Yes
206342108 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**3 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206342109 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**4 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206342110 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**5 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206342111 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**3 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342112 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**4 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342113 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**5 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342114 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**3 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342115 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**4 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342116 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**5 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342117 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*3 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342118 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*4 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342119 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*5 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342120 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342121 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342122 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342123 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*3 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206342124 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*5 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206342125 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*4 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206345837 | Ground Water | HYDROTECH | WSS6006*7* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
206345838 | Ground Water | HYDROTECH | WSS6009*7* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
206345839 | Ground Water | HYDROTECH | WSS6012*7* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
206345840 | Ground Water | HYDROTECH | WSS6015*7* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
215811946 | Ground Water | HYDROTECH | WSV6009D* |  | 11000 | 26 | 8800 | 4.3 | 0.91667 | No
215811947 | Ground Water | AE Air | WSV6009D* |  | 11000 | 26 | 8800 | 4.3 | 0.91667 | No
215811948 | Ground Water | HYDROTECH | WSV6012D* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | No
215811950 | Ground Water | AE Air | WSV6012D* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | No
215811951 | Ground Water | HYDROTECH | WSV6018D* |  | 20000 | 21.1 | 16000 | 4.1 | 1.6667 | No
215811952 | Ground Water | AE Air | WSV6018D* |  | 20000 | 21.1 | 16000 | 4.1 | 1.6667 | No
215811953 | Ground Water | HYDROTECH | WSV6024D* |  | 24000 | 23 | 22000 | 4.1 | 2 | No
215811954 | Ground Water | AE Air | WSV6024D* |  | 24000 | 23 | 22000 | 4.1 | 2 | No
215811955 | Ground Water | HYDROTECH | WSV6030D* |  | 30000 | 22.5 | 24000 | 4.1 | 2.5 | No
215811957 | Ground Water | AE Air | WSV6030D* |  | 30000 | 22.5 | 24000 | 4.1 | 2.5 | No
215811958 | Ground Water | HYDROTECH | WSV6036D* |  | 39000 | 22 | 35000 | 4.1 | 3.25 | No
215811959 | Ground Water | AE Air | WSV6036D* |  | 39000 | 22 | 35000 | 4.1 | 3.25 | No
215811960 | Ground Water | HYDROTECH | WSV6042D* |  | 44000 | 24 | 37000 | 4.3 | 3.6667 | No
215811961 | Ground Water | AE Air | WSV6042D* |  | 44000 | 24 | 37000 | 4.3 | 3.6667 | No
215811962 | Ground Water | HYDROTECH | WSV6048D* |  | 55000 | 23 | 38000 | 4.1 | 4.5833 | No
215811964 | Ground Water | AE Air | WSV6048D* |  | 55000 | 23 | 38000 | 4.1 | 4.5833 | No
215815841 | Ground Water | HYDROTECH | WSV6060D* |  | 67000 | 23.8 | 53500 | 4.3 | 5.5833 | No
215815842 | Ground Water | AE Air | WSV6060D* |  | 67000 | 23.8 | 53500 | 4.3 | 5.5833 | No
215815843 | Ground Water | HYDROTECH | WSV6072D* |  | 77000 | 22.1 | 63500 | 4.1 | 6.4167 | No
215815844 | Ground Water | AE Air | WSV6072D* |  | 77000 | 22.1 | 63500 | 4.1 | 6.4167 | No
205767508 | Ground Water | ClimateMaster | TRH/V015A |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205767509 | Ground Water | ClimateMaster | TRH/V018A |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205767513 | Ground Water | ClimateMaster | TSH/V/D024C |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | Yes
205767514 | Ground Water | ClimateMaster | TSH/V/D024C*K |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | Yes
205767515 | Ground Water | ClimateMaster | TSH/V/D030C |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | Yes
205767516 | Ground Water | ClimateMaster | TSH/V/D030C*K |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
205767517 | Ground Water | ClimateMaster | TSH/V/D036C |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | Yes
205767518 | Ground Water | ClimateMaster | TSH/V/D036C*K |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | Yes
205767519 | Ground Water | ClimateMaster | TSH/V/D042C |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | Yes
205767520 | Ground Water | ClimateMaster | TSH/V/D042C*K |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205767521 | Ground Water | ClimateMaster | TSH/V/D048C*K |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | Yes
205767522 | Ground Water | ClimateMaster | TSH/V/D060C |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | Yes
205767523 | Ground Water | ClimateMaster | TSH/V/D060C*K |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | Yes
205767525 | Ground Water | ClimateMaster | TSH/V/D070C*K |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | Yes
205767526 | Ground Water | ClimateMaster | TSH/V009A |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
205767541 | Ground Water | ClimateMaster | TCH/V018A*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205767542 | Ground Water | ClimateMaster | TCH/V024A*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205767543 | Ground Water | ClimateMaster | TCH/V030A*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205767548 | Ground Water | ClimateMaster | TRH/V018A*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205767549 | Ground Water | ClimateMaster | TRH/V024A*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205767550 | Ground Water | ClimateMaster | TRH/V030A*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205767554 | Ground Water | ClimateMaster | TZV/H024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205767556 | Ground Water | ClimateMaster | TZV/H036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
205767557 | Ground Water | ClimateMaster | TZV/H042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205767559 | Ground Water | ClimateMaster | TZV/H060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
202350417 | Ground Water | AAON, Inc. | RN-009-2-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350418 | Ground Water | AAON, Inc. | RN-009-3-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350419 | Ground Water | AAON, Inc. | RN-009-4-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350429 | Ground Water | AAON, Inc. | RN-011-2-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
202350430 | Ground Water | AAON, Inc. | RN-011-3-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
202350431 | Ground Water | AAON, Inc. | RN-011-4-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
215415916 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
215415917 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
215415918 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
215415919 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | No
215415920 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | No
215415921 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | No
215415922 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | No
215415923 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | No
215415924 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | No
215415925 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | No
215415926 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | No
215415927 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | No
215415928 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | No
215426638 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215426639 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215426640 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217531660 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)006A |  | 7000 | 30 | 5800 | 4.5 | 0.58333 | Yes
217531661 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)009A |  | 10500 | 28 | 9000 | 4.6 | 0.875 | Yes
217531662 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)012A |  | 13700 | 28.3 | 12200 | 4.3 | 1.1417 | Yes
217531663 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)018A |  | 22000 | 28.1 | 18900 | 4.9 | 1.8333 | Yes
8740368 | Ground Water | GEOCOMFORT | GVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
8740369 | Ground Water | HYDRON MODULE | HVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
8740370 | Ground Water | TETCO | TVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
8740371 | Ground Water | GEOCOMFORT | GVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740372 | Ground Water | HYDRON MODULE | HVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740373 | Ground Water | TETCO | TVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740374 | Ground Water | GEOCOMFORT | GVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740375 | Ground Water | HYDRON MODULE | HVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740376 | Ground Water | TETCO | TVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8791878 | Ground Water | GEOSTAR | 101/102H060**1*(1,4)***** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791879 | Ground Water | GeoSmart Energy | GS060**1*(1,4)********H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791880 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791883 | Ground Water | GEOSTAR | 101/102H060**1*0***** |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8791884 | Ground Water | GeoSmart Energy | GS060**1*0********H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8791885 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*0****H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8963989 | Ground Water | HEIL | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | No
8963990 | Ground Water | ARCOAIRE | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963991 | Ground Water | COMFORTMAKER | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963992 | Ground Water | DAY & NIGHT | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963993 | Ground Water | TEMPSTAR | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963994 | Ground Water | KEEPRITE | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
10435612 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435613 | Ground Water | GeoSmart Energy | GTZ072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
10435614 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10435615 | Ground Water | GEOSTAR | 103H070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10435616 | Ground Water | GeoSmart Energy | GSZ070*1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10435617 | Ground Water | GEOSTAR | 104H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435618 | Ground Water | YORK BY JOHNSON CONTROLS | YAST072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435619 | Ground Water | GeoSmart Energy | GTS072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10447649 | Ground Water | RHEEM | RPVS/EC025 | RCFL-HM2417 | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
10447650 | Ground Water | RHEEM | RPVS/EC025 | RCFL-HM2621 | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
10447662 | Ground Water | RHEEM | RPVS/EC036 | RCFL-HM38** | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
10447665 | Ground Water | RHEEM | RPVS/EC048 | RCFL-HM48** | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
217212068 | Ground Water | FHP | CP036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212070 | Ground Water | FHP | CP036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212071 | Ground Water | FHP | CP036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212072 | Ground Water | FHP | CP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
217212073 | Ground Water | FHP | CP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212074 | Ground Water | FHP | CP048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
217212076 | Ground Water | FHP | CP048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212077 | Ground Water | FHP | CP048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
217212078 | Ground Water | FHP | CP048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212079 | Ground Water | FHP | CP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212080 | Ground Water | FHP | CP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212082 | Ground Water | FHP | CP060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212083 | Ground Water | FHP | CP060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212084 | Ground Water | FHP | CP060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212085 | Ground Water | FHP | CP060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212086 | Ground Water | FHP | CP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212088 | Ground Water | FHP | CP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212089 | Ground Water | FHP | CP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212090 | Ground Water | FHP | CP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212091 | Ground Water | FHP | CP070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212093 | Ground Water | FHP | CP070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212094 | Ground Water | FHP | CP070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212095 | Ground Water | FHP | CP070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212097 | Ground Water | FHP | CP070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212098 | Ground Water | FHP | CP070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212099 | Ground Water | FHP | CP070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212101 | Ground Water | FHP | CP070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212102 | Ground Water | BOSCH | RP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
217212103 | Ground Water | BOSCH | RP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
217212105 | Ground Water | BOSCH | RP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
217212106 | Ground Water | BOSCH | RP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
217212107 | Ground Water | BOSCH | RP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
217212108 | Ground Water | BOSCH | RP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
217212109 | Ground Water | BOSCH | RP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
217212111 | Ground Water | BOSCH | RP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
217212112 | Ground Water | BOSCH | RP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
217212113 | Ground Water | BOSCH | RP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
217212114 | Ground Water | BOSCH | RP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217212115 | Ground Water | BOSCH | RP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217212116 | Ground Water | BOSCH | RP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217212117 | Ground Water | BOSCH | RP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217351071 | Ground Water | BOSCH | CP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
217351072 | Ground Water | BOSCH | CP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
217351073 | Ground Water | BOSCH | CP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
217351074 | Ground Water | BOSCH | CP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
217351075 | Ground Water | BOSCH | CP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
217351076 | Ground Water | BOSCH | CP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
217351077 | Ground Water | BOSCH | CP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
217351078 | Ground Water | BOSCH | CP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
217351079 | Ground Water | BOSCH | CP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | No
217351080 | Ground Water | BOSCH | CP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | No
217351081 | Ground Water | BOSCH | CP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | No
217351082 | Ground Water | BOSCH | CP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | No
217351083 | Ground Water | BOSCH | CP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | No
217351084 | Ground Water | BOSCH | CP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | No
217351086 | Ground Water | BOSCH | CP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | No
217351087 | Ground Water | BOSCH-GEO | RP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
217351088 | Ground Water | BOSCH-GEO | RP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
217351089 | Ground Water | BOSCH-GEO | RP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
217351090 | Ground Water | BOSCH-GEO | RP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
217351091 | Ground Water | BOSCH-GEO | RP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
217351092 | Ground Water | BOSCH-GEO | RP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
217351093 | Ground Water | BOSCH-GEO | RP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
217351094 | Ground Water | BOSCH-GEO | RP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
217351095 | Ground Water | BOSCH-GEO | RP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | Yes
217351096 | Ground Water | BOSCH-GEO | RP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | Yes
217351097 | Ground Water | BOSCH-GEO | RP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | Yes
217351098 | Ground Water | BOSCH-GEO | RP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | Yes
217351099 | Ground Water | BOSCH-GEO | RP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | Yes
217351100 | Ground Water | BOSCH-GEO | RP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | Yes
217351102 | Ground Water | BOSCH-GEO | RP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | Yes
217351103 | Ground Water | GEO-THERMAL SPLIT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351104 | Ground Water | GEO-THERMAL SPLIT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351105 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351106 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351107 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351108 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351109 | Ground Water | GEO-THERMAL SPLIT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351111 | Ground Water | GEO-THERMAL SPLIT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351112 | Ground Water | GEO-THERMAL SPLIT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351114 | Ground Water | GEO-THERMAL SPLIT | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
7499565 | Ground Water | FHP | LM060-3VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7499566 | Ground Water | FHP | LM060-4VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7499569 | Ground Water | FHP | LM070-1VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499571 | Ground Water | FHP | LM070-3VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499572 | Ground Water | FHP | LM070-4VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499702 | Ground Water | BOSCH | SM036-1CF/HZ/VT |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
7499719 | Ground Water | BOSCH | SM070-1CF/HZ/VT |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7519546 | Ground Water | GEOCOMFORT | GVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519547 | Ground Water | HYDRON MODULE | HVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519548 | Ground Water | TETCO | TVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519549 | Ground Water | GEOCOMFORT | GVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519550 | Ground Water | HYDRON MODULE | HVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519551 | Ground Water | TETCO | TVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519552 | Ground Water | GEOCOMFORT | GVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519553 | Ground Water | HYDRON MODULE | HVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519554 | Ground Water | TETCO | TVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519555 | Ground Water | GEOCOMFORT | GVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519556 | Ground Water | HYDRON MODULE | HVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519557 | Ground Water | TETCO | TVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519558 | Ground Water | GEOCOMFORT | GVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519559 | Ground Water | HYDRON MODULE | HVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519560 | Ground Water | TETCO | TVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519561 | Ground Water | GEOCOMFORT | GVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519562 | Ground Water | HYDRON MODULE | HVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519563 | Ground Water | TETCO | TVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519564 | Ground Water | GEOCOMFORT | GVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519565 | Ground Water | HYDRON MODULE | HVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519566 | Ground Water | TETCO | TVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519567 | Ground Water | GEOCOMFORT | GVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519568 | Ground Water | HYDRON MODULE | HVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519569 | Ground Water | TETCO | TVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519570 | Ground Water | GEOCOMFORT | GVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519571 | Ground Water | HYDRON MODULE | HVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519572 | Ground Water | TETCO | TVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519573 | Ground Water | GEOCOMFORT | GVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
5315780 | Ground Water | WaterFurnace | NBV/NBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315781 | Ground Water | WaterFurnace | NBV/NBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315782 | Ground Water | WaterFurnace | NBV/NBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315783 | Ground Water | WaterFurnace | NBV/NBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315784 | Ground Water | WaterFurnace | NBV/NBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315785 | Ground Water | WaterFurnace | NBV/NBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5316500 | Ground Water | WaterFurnace | NBV/NBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316501 | Ground Water | WaterFurnace | NBV/NBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316502 | Ground Water | WaterFurnace | NBV/NBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316503 | Ground Water | WaterFurnace | NBV/NBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316504 | Ground Water | WaterFurnace | NBV/NBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316505 | Ground Water | WaterFurnace | NBV/NBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316510 | Ground Water | WaterFurnace | NBV/NBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316511 | Ground Water | WaterFurnace | NBV/NBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316512 | Ground Water | WaterFurnace | NBV/NBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316513 | Ground Water | WaterFurnace | NBV/NBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316514 | Ground Water | WaterFurnace | NBV/NBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316515 | Ground Water | WaterFurnace | NBV/NBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316516 | Ground Water | WaterFurnace | NBV/NBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5317193 | Ground Water | WaterFurnace | NBV/NBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317194 | Ground Water | WaterFurnace | NBV/NBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317195 | Ground Water | WaterFurnace | NBV/NBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317196 | Ground Water | WaterFurnace | NBV/NBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317197 | Ground Water | WaterFurnace | NBV/NBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317198 | Ground Water | WaterFurnace | NBV/NBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317199 | Ground Water | WaterFurnace | NBV/NBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317200 | Ground Water | WaterFurnace | NBV/NBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317201 | Ground Water | WaterFurnace | NBV/NBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317202 | Ground Water | WaterFurnace | NBV/NBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317203 | Ground Water | WaterFurnace | NBV/NBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317205 | Ground Water | WaterFurnace | NBV/NBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317206 | Ground Water | WaterFurnace | NBV/NBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317207 | Ground Water | WaterFurnace | NBV/NBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317209 | Ground Water | WaterFurnace | NBV/NBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317210 | Ground Water | WaterFurnace | NBV/NBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317211 | Ground Water | WaterFurnace | NBV/NBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317270 | Ground Water | WaterFurnace | NBV/NBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317328 | Ground Water | WaterFurnace | NBV/NBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317329 | Ground Water | WaterFurnace | NBV/NBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317330 | Ground Water | WaterFurnace | NBV/NBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317331 | Ground Water | WaterFurnace | NBV/NBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317332 | Ground Water | WaterFurnace | NBV/NBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317333 | Ground Water | WaterFurnace | NBV/NBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317334 | Ground Water | WaterFurnace | NBV/NBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317335 | Ground Water | WaterFurnace | NBV/NBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5339321 | Ground Water | TTHERM GEO | TVA-036-1* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
5339322 | Ground Water | TTHERM GEO | TVA-048-1* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
5339323 | Ground Water | TTHERM GEO | TVA-060-1* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
217014528 | Ground Water | CARRIER | GCA72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014529 | Ground Water | BRYANT | GCA72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014530 | Ground Water | CARRIER | GCA72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014531 | Ground Water | BRYANT | GCA72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014532 | Ground Water | HEIL | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014533 | Ground Water | ARCOAIRE | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014534 | Ground Water | KEEPRITE | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014535 | Ground Water | TEMPSTAR | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
216625752 | Ground Water | GeoSmart Energy | S5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625753 | Ground Water | GeoSmart Energy | S5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625754 | Ground Water | GeoSmart Energy | S5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625755 | Ground Water | GeoSmart Energy | S5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625756 | Ground Water | GeoSmart Energy | S5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625757 | Ground Water | GeoSmart Energy | S5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625758 | Ground Water | GeoSmart Energy | S5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625759 | Ground Water | GeoSmart Energy | S5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625760 | Ground Water | GeoSmart Energy | S5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625761 | Ground Water | GeoSmart Energy | S5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625762 | Ground Water | GeoSmart Energy | S5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625763 | Ground Water | GeoSmart Energy | S5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625764 | Ground Water | GeoSmart Energy | S5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625765 | Ground Water | GeoSmart Energy | S5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625766 | Ground Water | GeoSmart Energy | S5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625767 | Ground Water | GeoSmart Energy | S5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625768 | Ground Water | GeoSmart Energy | S5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625769 | Ground Water | GeoSmart Energy | S5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625770 | Ground Water | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625771 | Ground Water | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625772 | Ground Water | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625773 | Ground Water | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625774 | Ground Water | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625775 | Ground Water | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625776 | Ground Water | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625777 | Ground Water | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625778 | Ground Water | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625779 | Ground Water | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625780 | Ground Water | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625781 | Ground Water | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625782 | Ground Water | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625783 | Ground Water | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625784 | Ground Water | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625785 | Ground Water | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625786 | Ground Water | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625787 | Ground Water | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625788 | Ground Water | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625789 | Ground Water | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625790 | Ground Water | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625791 | Ground Water | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625792 | Ground Water | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625793 | Ground Water | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625794 | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625795 | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625796 | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625797 | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625798 | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625799 | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625800 | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625801 | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625802 | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625803 | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625804 | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625805 | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625806 | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625807 | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268725 | Ground Water | WaterFurnace | V5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268726 | Ground Water | WaterFurnace | V5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268727 | Ground Water | WaterFurnace | V5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268728 | Ground Water | WaterFurnace | V5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268729 | Ground Water | WaterFurnace | V5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268730 | Ground Water | WaterFurnace | V5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268731 | Ground Water | WaterFurnace | V5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268732 | Ground Water | WaterFurnace | V5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268733 | Ground Water | WaterFurnace | V5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268734 | Ground Water | WaterFurnace | V5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
214063737 | Ground Water | GeoSmart Energy | GBV/GBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
214063738 | Ground Water | GeoSmart Energy | GBV/GBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
214063739 | Ground Water | GeoSmart Energy | GBV/GBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
214063740 | Ground Water | GeoSmart Energy | GBV/GBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
214063741 | Ground Water | GeoSmart Energy | GBV/GBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063742 | Ground Water | GeoSmart Energy | GBV/GBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063743 | Ground Water | GeoSmart Energy | GBV/GBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
214063744 | Ground Water | GeoSmart Energy | GBV/GBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063745 | Ground Water | GeoSmart Energy | GBV/GBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063746 | Ground Water | GeoSmart Energy | GBV/GBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
214063747 | Ground Water | GeoSmart Energy | GBV/GBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063748 | Ground Water | GeoSmart Energy | GBV/GBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063749 | Ground Water | GeoSmart Energy | GBV/GBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
214063750 | Ground Water | GeoSmart Energy | GBV/GBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063751 | Ground Water | GeoSmart Energy | GBV/GBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063752 | Ground Water | GeoSmart Energy | GBV/GBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214063753 | Ground Water | GeoSmart Energy | GBV/GBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063754 | Ground Water | GeoSmart Energy | GBV/GBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063755 | Ground Water | GeoSmart Energy | GBV/GBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214063756 | Ground Water | GeoSmart Energy | GBV/GBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063757 | Ground Water | GeoSmart Energy | GBV/GBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063758 | Ground Water | GeoSmart Energy | GBV/GBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063759 | Ground Water | GeoSmart Energy | GBV/GBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063760 | Ground Water | GeoSmart Energy | GBV/GBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063761 | Ground Water | GeoSmart Energy | GBV/GBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063762 | Ground Water | GeoSmart Energy | GBV/GBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214063763 | Ground Water | GeoSmart Energy | GBV/GBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063764 | Ground Water | GeoSmart Energy | GBV/GBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063765 | Ground Water | GeoSmart Energy | GBV/GBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214063766 | Ground Water | GeoSmart Energy | GBV/GBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063767 | Ground Water | GeoSmart Energy | GBV/GBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063768 | Ground Water | GeoSmart Energy | GBV/GBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214063769 | Ground Water | GeoSmart Energy | GBV/GBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063770 | Ground Water | GeoSmart Energy | GBV/GBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063771 | Ground Water | GeoSmart Energy | GBV/GBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214063772 | Ground Water | GeoSmart Energy | GBV/GBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063773 | Ground Water | GeoSmart Energy | GBV/GBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063774 | Ground Water | GeoSmart Energy | GBV/GBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063775 | Ground Water | GeoSmart Energy | GBV/GBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063776 | Ground Water | GeoSmart Energy | GBV/GBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063777 | Ground Water | GeoSmart Energy | GBV/GBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063778 | Ground Water | GeoSmart Energy | GBV/GBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214063779 | Ground Water | GeoSmart Energy | GBV/GBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214063780 | Ground Water | GeoSmart Energy | GBV/GBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214063781 | Ground Water | GeoSmart Energy | GBV/GBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214063782 | Ground Water | GeoSmart Energy | GBV/GBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214063783 | Ground Water | GeoSmart Energy | GBV/GBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
216419947 | Ground Water | Whalen | WZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
216439574 | Ground Water | GeoSmart Energy | S5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216439575 | Ground Water | GeoSmart Energy | S5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216439576 | Ground Water | GeoSmart Energy | S5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216439577 | Ground Water | GeoSmart Energy | S5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216508982 | Ground Water | ClimateMaster | SJ/PN024A | SKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
216508983 | Ground Water | ClimateMaster | SJ/PN036A | SKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
217897413 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
217897414 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
217897417 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
217897418 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
217897421 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
217897422 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
217897425 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
217897426 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
217897427 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
217897428 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
217897429 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
217897430 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
217897433 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
217897434 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
217897447 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
217897448 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
217897449 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
217897450 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
217897451 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
217897452 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
217897453 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
217897454 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
217897455 | Ground Water | CENTURY | MJN024A | MKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
217897456 | Ground Water | COMFORT-AIRE | MJN024A | MKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
214771940 | Ground Water | TRANE | EXVK060A |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214771941 | Ground Water | TRANE | EXVK070A |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214771943 | Ground Water | TRANE | GEHK009A |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214771944 | Ground Water | TRANE | GEHK012A |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214771945 | Ground Water | TRANE | GEHK015A |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214771946 | Ground Water | TRANE | GEHK018A |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214771947 | Ground Water | TRANE | GEHK024A |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214771948 | Ground Water | TRANE | GEHK030A |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214771949 | Ground Water | TRANE | GEHK036A |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214771950 | Ground Water | TRANE | GEHK042A |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214771951 | Ground Water | TRANE | GEHK048A |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214771952 | Ground Water | TRANE | GEHK060A |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214771953 | Ground Water | TRANE | EXHK009A |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214771954 | Ground Water | TRANE | EXHK012A |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214771955 | Ground Water | TRANE | EXHK015A |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214771956 | Ground Water | TRANE | EXHK018A |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214771957 | Ground Water | TRANE | EXHK024A |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214771958 | Ground Water | TRANE | EXHK030A |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214771959 | Ground Water | TRANE | EXHK036A |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214771960 | Ground Water | TRANE | EXHK042A |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214771961 | Ground Water | TRANE | EXHK048A |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214771962 | Ground Water | TRANE | EXHK060A |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214771963 | Ground Water | TRANE | EXHK070A |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772055 | Ground Water | TRANE | GEVK0097 |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214772056 | Ground Water | TRANE | GEVK0127 |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214772057 | Ground Water | TRANE | GEVK0157 |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214772058 | Ground Water | TRANE | GEVK0187 |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214772059 | Ground Water | TRANE | GEVK024B |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772060 | Ground Water | TRANE | GEVK0244 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772061 | Ground Water | TRANE | GEVK0247 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772062 | Ground Water | TRANE | GEVK030B |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772063 | Ground Water | TRANE | GEVK0304 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772064 | Ground Water | TRANE | GEVK0307 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772065 | Ground Water | TRANE | GEVK036B |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772066 | Ground Water | TRANE | GEVK0364 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772067 | Ground Water | TRANE | GEVK0367 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
212428698 | Ground Water | HYDROTECH | WSH6036A6* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | Yes
212428699 | Ground Water | HYDROTECH | WSH6042A6* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | Yes
212428700 | Ground Water | HYDROTECH | WSH6048A6* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | Yes
212428701 | Ground Water | AE Air | WSH6009A6* |  | 10000 | 23 | 8500 | 4.2 | 0.83333 | Yes
212428702 | Ground Water | AE Air | WSH6012A6* |  | 12500 | 23.1 | 11000 | 4.6 | 1.0417 | Yes
212428703 | Ground Water | AE Air | WSH6018A6* |  | 20500 | 26 | 16000 | 4.3 | 1.7083 | Yes
212428704 | Ground Water | AE Air | WSH6024A6* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | Yes
212428705 | Ground Water | AE Air | WSH6030A6* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | Yes
212428706 | Ground Water | AE Air | WSH6036A6* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | Yes
212428707 | Ground Water | AE Air | WSH6042A6* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | Yes
212428708 | Ground Water | AE Air | WSH6048A6* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | Yes
212505502 | Ground Water | HYDROTECH | WSH6060A6* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | Yes
212505503 | Ground Water | HYDROTECH | WSH6072A6* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | Yes
202679205 | Ground Water | BOSCH-GEO | SM036-1CSC-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202679208 | Ground Water | BOSCH | SM036-1CSC-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202729320 | Ground Water | HEIL | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202729321 | Ground Water | ARCOAIRE | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729322 | Ground Water | KEEPRITE | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729323 | Ground Water | TEMPSTAR | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729324 | Ground Water | COMFORTMAKER | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202350445 | Ground Water | AAON, Inc. | M2-007-2-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350447 | Ground Water | AAON, Inc. | M2-007-2-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
202350449 | Ground Water | AAON, Inc. | M2-007-3-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350451 | Ground Water | AAON, Inc. | M2-007-3-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
202350453 | Ground Water | AAON, Inc. | M2-007-4-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350455 | Ground Water | AAON, Inc. | M2-007-4-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
4504310 | Ground Water | BOSCH-GEO | BP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
4509712 | Ground Water | BOSCH-GEO | BP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
4510474 | Ground Water | BOSCH-GEO | BP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
4547265 | Ground Water | DUAL AIR | CFX024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | Yes
4547266 | Ground Water | DUAL AIR | CFX031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | Yes
4547267 | Ground Water | DUAL AIR | CFX036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | Yes
4547268 | Ground Water | DUAL AIR | CFX041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | Yes
4547869 | Ground Water | MIAMI HEAT PUMP | HPX024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | Yes
4547870 | Ground Water | MIAMI HEAT PUMP | HPX031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | Yes
4547871 | Ground Water | MIAMI HEAT PUMP | HPX036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | Yes
4547872 | Ground Water | MIAMI HEAT PUMP | HPX041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | Yes
214838955 | Ground Water | BOSCH | CL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838956 | Ground Water | BOSCH | CL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838957 | Ground Water | BOSCH | CL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838958 | Ground Water | BOSCH | CL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838959 | Ground Water | BOSCH | CL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838960 | Ground Water | BOSCH | CL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
216625508 | Ground Water | GEOSTAR | G5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625509 | Ground Water | GEOSTAR | G5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625510 | Ground Water | GEOSTAR | G5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625511 | Ground Water | GEOSTAR | G5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625512 | Ground Water | GEOSTAR | G5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625513 | Ground Water | GEOSTAR | G5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625514 | Ground Water | GEOSTAR | G5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625515 | Ground Water | GEOSTAR | G5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625516 | Ground Water | GEOSTAR | G5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625517 | Ground Water | GEOSTAR | G5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625518 | Ground Water | GEOSTAR | G5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625519 | Ground Water | GEOSTAR | G5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625520 | Ground Water | GEOSTAR | G5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625521 | Ground Water | GEOSTAR | G5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625522 | Ground Water | GEOSTAR | G5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625523 | Ground Water | GEOSTAR | G5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625524 | Ground Water | GEOSTAR | G5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625525 | Ground Water | GEOSTAR | G5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625526 | Ground Water | GEOSTAR | G5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625527 | Ground Water | GEOSTAR | G5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625528 | Ground Water | GEOSTAR | G5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625529 | Ground Water | GEOSTAR | G5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625530 | Ground Water | GEOSTAR | G5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625531 | Ground Water | GEOSTAR | G5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625532 | Ground Water | GEOSTAR | G5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625533 | Ground Water | GEOSTAR | G5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625534 | Ground Water | GEOSTAR | G5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625535 | Ground Water | GEOSTAR | G5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
208450079 | Ground Water | AE Air | HRCX18*-6 |  | 20000 | 22.5 | 16000 | 4.1 | 1.6667 | Yes
208450080 | Ground Water | AE Air | HRCX09*-6 |  | 11500 | 26.5 | 8800 | 4.5 | 0.95833 | Yes
208450081 | Ground Water | AE Air | HRCX24*-6 |  | 26000 | 26.5 | 22000 | 4.4 | 2.1667 | Yes
208450082 | Ground Water | AE Air | HRCX12*-6 |  | 13000 | 25 | 10500 | 4.1 | 1.0833 | Yes
208450083 | Ground Water | AE Air | HRCX30*-6 |  | 30000 | 23.5 | 25000 | 4.1 | 2.5 | Yes
208450084 | Ground Water | AE Air | HRCX36*-6 |  | 35500 | 21.6 | 31500 | 4.1 | 2.9583 | Yes
215224293 | Ground Water | BOSCH-GEO | RF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
216054496 | Ground Water | GEOCOMFORT | GZT048* |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
216054497 | Ground Water | GEOCOMFORT | GZT060* |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
216054498 | Ground Water | GEOCOMFORT | GVS006* |  | 7600 | 25.9 | 6500 | 4.4 | 0.63333 | Yes
216054499 | Ground Water | GEOCOMFORT | GVS015* |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
3628414 | Ground Water | WaterFurnace | USV/USH018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3628415 | Ground Water | WaterFurnace | USV/USH018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3628416 | Ground Water | WaterFurnace | USV/USH015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3628417 | Ground Water | WaterFurnace | USV/USH015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3655222 | Ground Water | GEOSTAR | GCC/GCW/GCS/GCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3655223 | Ground Water | GEOSTAR | GCC/GCW/GCS/GCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3696260 | Ground Water | GEOSTAR | ZS015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
3696261 | Ground Water | GEOSTAR | ZS015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
7422322 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7423168 | Ground Water | WaterFurnace | NBV/NBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7423169 | Ground Water | GEOSTAR | GBV/GBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7423171 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7487652 | Ground Water | GEOCOMFORT | GYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
7487653 | Ground Water | HYDRON MODULE | HYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
7487654 | Ground Water | TETCO | TYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
7487655 | Ground Water | TETCO | TYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487656 | Ground Water | GEOCOMFORT | GYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487657 | Ground Water | HYDRON MODULE | HYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487658 | Ground Water | HYDRON MODULE | HYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487659 | Ground Water | GEOCOMFORT | GYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487660 | Ground Water | TETCO | TYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
202547467 | Ground Water | FHP | EC096-1VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547468 | Ground Water | FHP | EC096-3VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547469 | Ground Water | FHP | EC096-4VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
206570651 | Ground Water | 7 SERIES | NVV/NVH060C1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206570652 | Ground Water | GEOSTAR | 141/142C036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206570654 | Ground Water | GEOSTAR | 141/142C060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206598629 | Ground Water | GeoSmart Energy | VI036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206598631 | Ground Water | GeoSmart Energy | VI060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206598632 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206598634 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206608717 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048J1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608718 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048J1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608719 | Ground Water | GEOSTAR | 103J048**1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
215224477 | Ground Water | FHP | CF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224478 | Ground Water | FHP | CF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224479 | Ground Water | FHP | CF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224480 | Ground Water | FHP | CF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224481 | Ground Water | FHP | CF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224482 | Ground Water | FHP | CF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224483 | Ground Water | FHP | CF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224484 | Ground Water | FHP | CF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224485 | Ground Water | FHP | CF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224486 | Ground Water | FHP | CF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224487 | Ground Water | FHP | CF007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224488 | Ground Water | FHP | CF007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224489 | Ground Water | FHP | CF009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224490 | Ground Water | FHP | CF009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224491 | Ground Water | FHP | CF012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224492 | Ground Water | FHP | CF012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224493 | Ground Water | FHP | CF015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224494 | Ground Water | FHP | CF015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224495 | Ground Water | FHP | CF018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224496 | Ground Water | FHP | CF018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
5295984 | Ground Water | WaterFurnace | NBV/NBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295985 | Ground Water | WaterFurnace | NBV/NBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295986 | Ground Water | WaterFurnace | NBV/NBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295987 | Ground Water | WaterFurnace | NBV/NBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295988 | Ground Water | WaterFurnace | NBV/NBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295989 | Ground Water | WaterFurnace | NBV/NBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295990 | Ground Water | WaterFurnace | NBV/NBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295991 | Ground Water | WaterFurnace | NBV/NBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295992 | Ground Water | WaterFurnace | NBV/NBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295993 | Ground Water | WaterFurnace | NBV/NBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295994 | Ground Water | WaterFurnace | NBV/NBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295995 | Ground Water | WaterFurnace | NBV/NBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295996 | Ground Water | WaterFurnace | NBV/NBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5295997 | Ground Water | WaterFurnace | NBV/NBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5295998 | Ground Water | WaterFurnace | NBV/NBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5295999 | Ground Water | WaterFurnace | NBV/NBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296000 | Ground Water | WaterFurnace | NBV/NBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296001 | Ground Water | WaterFurnace | NBV/NBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296002 | Ground Water | WaterFurnace | NBV/NBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296003 | Ground Water | WaterFurnace | NBV/NBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296004 | Ground Water | WaterFurnace | NBV/NBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296005 | Ground Water | WaterFurnace | NBV/NBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296006 | Ground Water | WaterFurnace | NBV/NBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296007 | Ground Water | WaterFurnace | NBV/NBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296008 | Ground Water | WaterFurnace | NBV/NBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296009 | Ground Water | WaterFurnace | NBV/NBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296010 | Ground Water | WaterFurnace | NBV/NBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296011 | Ground Water | WaterFurnace | NBV/NBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296012 | Ground Water | WaterFurnace | NBV/NBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296013 | Ground Water | WaterFurnace | NBV/NBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067595 | Ground Water | GeoSmart Energy | GBV/GBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067596 | Ground Water | GeoSmart Energy | GBV/GBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067597 | Ground Water | GeoSmart Energy | GBV/GBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067598 | Ground Water | GeoSmart Energy | GBV/GBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067600 | Ground Water | GeoSmart Energy | GBV/GBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067601 | Ground Water | GeoSmart Energy | GBV/GBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067603 | Ground Water | GeoSmart Energy | GBV/GBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067604 | Ground Water | GeoSmart Energy | GBV/GBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067606 | Ground Water | GeoSmart Energy | GBV/GBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067607 | Ground Water | GeoSmart Energy | GBV/GBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067608 | Ground Water | GeoSmart Energy | GBV/GBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067609 | Ground Water | GeoSmart Energy | GBV/GBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067865 | Ground Water | GeoSmart Energy | GBV/GBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067866 | Ground Water | GeoSmart Energy | GBV/GBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067867 | Ground Water | GeoSmart Energy | GBV/GBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067868 | Ground Water | GeoSmart Energy | GBV/GBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
214067869 | Ground Water | GeoSmart Energy | GBV/GBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067870 | Ground Water | GeoSmart Energy | GBV/GBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067871 | Ground Water | GeoSmart Energy | GBV/GBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067872 | Ground Water | GeoSmart Energy | GBV/GBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214595542 | Ground Water | AAON, Inc. | RQ-003-2-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595543 | Ground Water | AAON, Inc. | RQ-003-3-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595544 | Ground Water | AAON, Inc. | RQ-003-4-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595548 | Ground Water | AAON, Inc. | RQ-004-1-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595549 | Ground Water | AAON, Inc. | RQ-004-2-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595550 | Ground Water | AAON, Inc. | RQ-004-3-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595551 | Ground Water | AAON, Inc. | RQ-004-4-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595552 | Ground Water | AAON, Inc. | RQ-004-2-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595553 | Ground Water | AAON, Inc. | RQ-004-3-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595554 | Ground Water | AAON, Inc. | RQ-004-4-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595555 | Ground Water | AAON, Inc. | RQ-005-1-0-FCAY-S0-10-000-A |  | 61500 | 21.9 | 50900 | 4.5 | 5.125 | No
214595556 | Ground Water | AAON, Inc. | RQ-005-2-0-GCAY-V0-10-000-A |  | 66900 | 21.6 | 54200 | 4.3 | 5.575 | No
214595557 | Ground Water | AAON, Inc. | RQ-005-3-0-GCAY-V0-10-000-A |  | 66900 | 21.6 | 54200 | 4.3 | 5.575 | No
214595558 | Ground Water | AAON, Inc. | RQ-005-4-0-GCAY-V0-10-000-A |  | 66900 | 21.6 | 54200 | 4.3 | 5.575 | No
214595559 | Ground Water | AAON, Inc. | RQ-005-2-0-FCAY-S0-10-000-A |  | 61500 | 21.9 | 50900 | 4.5 | 5.125 | No
214595560 | Ground Water | AAON, Inc. | RQ-005-3-0-FCAY-S0-10-000-A |  | 61500 | 21.9 | 50900 | 4.5 | 5.125 | No
214595561 | Ground Water | AAON, Inc. | RQ-005-4-0-FCAY-S0-10-000-A |  | 61500 | 21.9 | 50900 | 4.5 | 5.125 | No
214595562 | Ground Water | AAON, Inc. | RN-006-2-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595563 | Ground Water | AAON, Inc. | RN-006-3-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
207200558 | Ground Water | GeoSmart Energy | GT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207200565 | Ground Water | GeoSmart Energy | GS060**1*(1,4)*H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207200566 | Ground Water | GeoSmart Energy | GS060**1*0*H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5646343 | Ground Water | GEOCOMFORT | GXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646344 | Ground Water | HYDRON MODULE | HXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646345 | Ground Water | TETCO | TXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646346 | Ground Water | GEOCOMFORT | GXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646347 | Ground Water | HYDRON MODULE | HXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646348 | Ground Water | TETCO | TXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646349 | Ground Water | GEOCOMFORT | GXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646350 | Ground Water | HYDRON MODULE | HXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646351 | Ground Water | TETCO | TXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646371 | Ground Water | GEOCOMFORT | GXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646372 | Ground Water | HYDRON MODULE | HXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646373 | Ground Water | TETCO | TXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646374 | Ground Water | GEOCOMFORT | GXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646375 | Ground Water | HYDRON MODULE | HXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646376 | Ground Water | TETCO | TXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646377 | Ground Water | GEOCOMFORT | GXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646378 | Ground Water | HYDRON MODULE | HXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646379 | Ground Water | TETCO | TXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646381 | Ground Water | GEOCOMFORT | GCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
5646382 | Ground Water | HYDRON MODULE | HCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
5646383 | Ground Water | TETCO | TCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
5646384 | Ground Water | GEOCOMFORT | GCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646385 | Ground Water | HYDRON MODULE | HCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646386 | Ground Water | TETCO | TCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646387 | Ground Water | GEOCOMFORT | GCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
4230749 | Ground Water | DAIKIN | WCCW4024*E*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
4230751 | Ground Water | DAIKIN | WCCW4024*F*01* |  | 0 | 22.8 | 23500 | 4.2 | 0 | No
4230753 | Ground Water | DAIKIN | WCCW4024*J*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
4230922 | Ground Water | DAIKIN | WCCW4024*K*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
215268313 | Ground Water | WaterFurnace | V3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
215268316 | Ground Water | WaterFurnace | V3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268318 | Ground Water | WaterFurnace | V3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268320 | Ground Water | WaterFurnace | V3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268321 | Ground Water | WaterFurnace | V3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268323 | Ground Water | WaterFurnace | V3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
204031803 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
204031812 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
217351122 | Ground Water | GEO-THERMAL SPLIT | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351123 | Ground Water | GEO-THERMAL SPLIT | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351671 | Ground Water | BOSCH | RP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
217351672 | Ground Water | BOSCH | RP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
217351673 | Ground Water | BOSCH | RP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
217351674 | Ground Water | BOSCH | RP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
217351675 | Ground Water | BOSCH | RP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
217351676 | Ground Water | BOSCH | RP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
217351677 | Ground Water | BOSCH | RP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
217351678 | Ground Water | BOSCH | RP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
217351679 | Ground Water | BOSCH | RP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | Yes
217351680 | Ground Water | BOSCH | RP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | Yes
217351681 | Ground Water | BOSCH | RP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | Yes
217351682 | Ground Water | BOSCH | RP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | Yes
217351683 | Ground Water | BOSCH | RP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | Yes
217351684 | Ground Water | BOSCH | RP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | Yes
217351686 | Ground Water | BOSCH | RP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | Yes
217351687 | Ground Water | BOSCH | TW025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351689 | Ground Water | BOSCH | TW049-1***-*****C |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351692 | Ground Water | FHP | CP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
217351693 | Ground Water | FHP | CP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
217351694 | Ground Water | FHP | CP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
217351695 | Ground Water | FHP | CP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
217351696 | Ground Water | FHP | CP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
217351697 | Ground Water | FHP | CP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
217351698 | Ground Water | FHP | CP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
217351699 | Ground Water | FHP | CP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
217351700 | Ground Water | FHP | CP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | No
217351701 | Ground Water | FHP | CP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | No
217351702 | Ground Water | FHP | CP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | No
217351703 | Ground Water | FHP | CP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | No
217351704 | Ground Water | FHP | CP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | No
217351705 | Ground Water | FHP | CP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | No
217351707 | Ground Water | FHP | CP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | No
217351708 | Ground Water | FHP | WT025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351709 | Ground Water | FHP | WT025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351720 | Ground Water | FHP | WT025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351721 | Ground Water | FHP | WT025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216625640 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625641 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625642 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625643 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625644 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
214772135 | Ground Water | TRANE | EXHK048B |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772136 | Ground Water | TRANE | EXHK0484 |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772137 | Ground Water | TRANE | EXHK060B |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772138 | Ground Water | TRANE | EXHK0604 |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772139 | Ground Water | TRANE | EXHK070B |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772140 | Ground Water | TRANE | EXHK0704 |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772141 | Ground Water | TRANE | DXHK024A |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772142 | Ground Water | TRANE | DXHK036A |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772143 | Ground Water | TRANE | DXHK048A |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772144 | Ground Water | TRANE | DXHK060A |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772145 | Ground Water | TRANE | DXHK070A |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772146 | Ground Water | TRANE | DXVK024B |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772147 | Ground Water | TRANE | DXVK0244 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772148 | Ground Water | TRANE | DXVK036B |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772149 | Ground Water | TRANE | DXVK0364 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772150 | Ground Water | TRANE | DXVK048B |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772151 | Ground Water | TRANE | DXVK0484 |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772152 | Ground Water | TRANE | DXVK060B |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772153 | Ground Water | TRANE | DXVK0604 |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772154 | Ground Water | TRANE | DXVK070B |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772155 | Ground Water | TRANE | DXVK0704 |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772156 | Ground Water | TRANE | DXHK024B |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772157 | Ground Water | TRANE | DXHK0244 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772158 | Ground Water | TRANE | DXHK036B |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772159 | Ground Water | TRANE | DXHK0364 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772160 | Ground Water | TRANE | DXHK048B |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772161 | Ground Water | TRANE | DXHK0484 |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772162 | Ground Water | TRANE | DXHK060B |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772163 | Ground Water | TRANE | DXHK0604 |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772164 | Ground Water | TRANE | DXHK070B |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772165 | Ground Water | TRANE | DXHK0704 |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772166 | Ground Water | TRANE | DXVK0247 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772167 | Ground Water | TRANE | DXVK0367 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772168 | Ground Water | TRANE | DXHK0247 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772169 | Ground Water | TRANE | DXHK0367 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214773311 | Ground Water | TRANE | GEVK072 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214773312 | Ground Water | TRANE | GEVK090 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776122 | Ground Water | TRANE | GEVK0721 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776123 | Ground Water | TRANE | GEVK0724 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776124 | Ground Water | TRANE | GEVK0728 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776125 | Ground Water | TRANE | GEVK0904 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776126 | Ground Water | TRANE | GEVK0908 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776134 | Ground Water | TRANE | GEVK0722 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
10346272 | Ground Water | GEOCOMFORT | GZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346273 | Ground Water | HYDRON MODULE | HZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346274 | Ground Water | TETCO | TZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346276 | Ground Water | GEOCOMFORT | GZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346277 | Ground Water | HYDRON MODULE | HZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346278 | Ground Water | TETCO | TZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346377 | Ground Water | GEOCOMFORT | GZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346378 | Ground Water | HYDRON MODULE | HZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346379 | Ground Water | TETCO | TZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346380 | Ground Water | GEOCOMFORT | GZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346381 | Ground Water | HYDRON MODULE | HZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346382 | Ground Water | TETCO | TZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10384616 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ070H1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10384620 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
10384621 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435611 | Ground Water | GEOSTAR | 103H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
214839122 | Ground Water | FHP | CL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839123 | Ground Water | FHP | CL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839124 | Ground Water | FHP | CL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839125 | Ground Water | FHP | CL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839126 | Ground Water | FHP | CL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839127 | Ground Water | FHP | CL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
206194177 | Ground Water | Johnson Controls | JSH/V/D070C*K B |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | No
206194178 | Ground Water | SKYMARK | JSH/V/D070C*K C |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | No
206199262 | Ground Water | RHEEM | RPVV/H/D026D |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
206199264 | Ground Water | RHEEM | RPVV/H/D049D |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
206199265 | Ground Water | RHEEM | RPVV/H/D064D |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
206199266 | Ground Water | RHEEM | RPVV/H/D072D |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
206223143 | Ground Water | ClimateMaster | TRT036D |  | 40000 | 22.1 | 35000 | 4.6 | 3.3333 | No
206223145 | Ground Water | ClimateMaster | TRT060D |  | 70000 | 23.7 | 59200 | 4.5 | 5.8333 | No
206223146 | Ground Water | CENTURY | HZS024B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
206223147 | Ground Water | COMFORT-AIRE | HZS024B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
206223148 | Ground Water | CENTURY | HZS024B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
206223149 | Ground Water | COMFORT-AIRE | HZS024B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
206223150 | Ground Water | CENTURY | HZS036B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
206223151 | Ground Water | COMFORT-AIRE | HZS036B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
206223152 | Ground Water | CENTURY | HZS048B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
206223153 | Ground Water | COMFORT-AIRE | HZS048B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
206229666 | Ground Water | BOSCH | EP024-1HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229667 | Ground Water | BOSCH | EP024-2HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229668 | Ground Water | BOSCH | EP024-3HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229669 | Ground Water | BOSCH | EP024-4HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229670 | Ground Water | BOSCH | EP024-1HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229671 | Ground Water | BOSCH | EP024-2HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229672 | Ground Water | BOSCH | EP024-3HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229673 | Ground Water | BOSCH | EP024-4HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229674 | Ground Water | FHP | EP024-1HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229675 | Ground Water | FHP | EP024-2HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229676 | Ground Water | FHP | EP024-3HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229677 | Ground Water | FHP | EP024-4HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229678 | Ground Water | FHP | EP024-1HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229679 | Ground Water | FHP | EP024-2HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229680 | Ground Water | FHP | EP024-3HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229681 | Ground Water | FHP | EP024-4HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229682 | Ground Water | CARRIER | 50PSH/V024**C3/CA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229683 | Ground Water | CARRIER | 50PSH/V024**C4/DA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229684 | Ground Water | CARRIER | 50PSH/V024**C5/EA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229685 | Ground Water | CARRIER | 50PSH/V024**C6/FA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229686 | Ground Water | CARRIER | 50PSH/V024**N3/CA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229687 | Ground Water | CARRIER | 50PSH/V024**N4/DA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229688 | Ground Water | CARRIER | 50PSH/V024**N5/EA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229689 | Ground Water | CARRIER | 50PSH/V024**N6/FA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206262126 | Ground Water | HYDROTECH | WSV6090A |  | 101000 | 22 | 73000 | 4.1 | 8.4167 | No
208771547 | Ground Water | HYDROTECH | WSV6012B* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | Yes
208771548 | Ground Water | HYDROTECH | WSV6024B* |  | 24000 | 23 | 22000 | 4.1 | 2 | Yes
208771549 | Ground Water | HYDROTECH | WSV6030B* |  | 35500 | 22.5 | 30000 | 4.1 | 2.9583 | Yes
208816675 | Ground Water | HYDROTECH | WSHXE06A6* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
208816703 | Ground Water | HYDROTECH | WSHXE06A7* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
208856966 | Ground Water | HYDROTECH | WSV6060B* |  | 68000 | 23.8 | 53500 | 4.3 | 5.6667 | Yes
208856967 | Ground Water | HYDROTECH | WSV6072B* |  | 77500 | 22.6 | 66000 | 4.1 | 6.4583 | Yes
208856972 | Ground Water | AE Air | WSV6012B* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | Yes
208856973 | Ground Water | AE Air | WSV6024B* |  | 24000 | 23 | 22000 | 4.1 | 2 | Yes
208856974 | Ground Water | AE Air | WSV6030B* |  | 35500 | 22.5 | 30000 | 4.1 | 2.9583 | Yes
208856975 | Ground Water | AE Air | WSV6060B* |  | 68000 | 23.8 | 53500 | 4.3 | 5.6667 | Yes
208856976 | Ground Water | AE Air | WSV6072B* |  | 77500 | 22.6 | 66000 | 4.1 | 6.4583 | Yes
209156925 | Ground Water | AE Air | HRCC09*-2 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
217903488 | Ground Water | WaterFurnace | V5R072*D0**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903489 | Ground Water | WaterFurnace | V5R072*D3**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903490 | Ground Water | WaterFurnace | V5R072*D3**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903491 | Ground Water | WaterFurnace | V5R072*D3**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903492 | Ground Water | WaterFurnace | V5R096*T3**5* |  | 96600 | 24.9 | 85800 | 4.5 | 8.05 | No
217903493 | Ground Water | WaterFurnace | V5R120*T3**5* |  | 128500 | 23.3 | 113700 | 4.5 | 10.7083 | No
207312016 | Ground Water | WaterFurnace | SDV049J1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
207312019 | Ground Water | WaterFurnace | SDV038K1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
207312171 | Ground Water | WaterFurnace | NDV/NDH026J1*(1,4) |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207312172 | Ground Water | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207312173 | Ground Water | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207312174 | Ground Water | WaterFurnace | NDV/NDH072J1*(1,4) |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207312176 | Ground Water | WaterFurnace | NDV/NDH064K1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207312224 | Ground Water | WaterFurnace | NSV/NSH018J1*(1,4) |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207312225 | Ground Water | WaterFurnace | NSV/NSH030J1*(1,4) |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207312226 | Ground Water | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207312227 | Ground Water | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207312228 | Ground Water | WaterFurnace | NSV/NSH048K1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207312229 | Ground Water | WaterFurnace | NSV/NSH060K1*(1,4)* |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207312230 | Ground Water | WaterFurnace | NSV/NSH070J1*(1,4) |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207312262 | Ground Water | WaterFurnace | NSV/NSH012J1*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207312263 | Ground Water | WaterFurnace | NSV/NSH018J1*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | Yes
207312265 | Ground Water | WaterFurnace | NSV/NSH030J1*(0,3) |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | Yes
207312266 | Ground Water | WaterFurnace | NSV/NSH036K1*(0,3) |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207312267 | Ground Water | WaterFurnace | NSV/NSH042K1*(0,3) |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | Yes
207312268 | Ground Water | WaterFurnace | NSV/NSH048K1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | Yes
207312269 | Ground Water | WaterFurnace | NSV/NSH060K1*0* |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | Yes
207312271 | Ground Water | WaterFurnace | NSV/NSH022J1*(1,4) |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
215268735 | Ground Water | WaterFurnace | V5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
215268736 | Ground Water | WaterFurnace | V5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
215268737 | Ground Water | WaterFurnace | V5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268738 | Ground Water | WaterFurnace | V5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268739 | Ground Water | WaterFurnace | V5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268740 | Ground Water | WaterFurnace | V5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268741 | Ground Water | WaterFurnace | V5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268742 | Ground Water | WaterFurnace | V5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268743 | Ground Water | WaterFurnace | V5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268744 | Ground Water | WaterFurnace | V5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268745 | Ground Water | WaterFurnace | V5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268746 | Ground Water | WaterFurnace | V5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268747 | Ground Water | WaterFurnace | V5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268748 | Ground Water | WaterFurnace | V5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268749 | Ground Water | WaterFurnace | V5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268750 | Ground Water | WaterFurnace | V5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268751 | Ground Water | WaterFurnace | V5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268752 | Ground Water | WaterFurnace | V5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268753 | Ground Water | WaterFurnace | V5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268754 | Ground Water | WaterFurnace | V5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268755 | Ground Water | WaterFurnace | V5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268756 | Ground Water | WaterFurnace | V5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268757 | Ground Water | WaterFurnace | V5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268758 | Ground Water | WaterFurnace | V5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268759 | Ground Water | WaterFurnace | V5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268760 | Ground Water | WaterFurnace | V5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268761 | Ground Water | WaterFurnace | V5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268762 | Ground Water | WaterFurnace | V5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268763 | Ground Water | WaterFurnace | V5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268764 | Ground Water | WaterFurnace | V5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268765 | Ground Water | WaterFurnace | V5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268766 | Ground Water | WaterFurnace | V5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268767 | Ground Water | WaterFurnace | V5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268768 | Ground Water | WaterFurnace | V5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268769 | Ground Water | WaterFurnace | V5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268770 | Ground Water | WaterFurnace | V5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268771 | Ground Water | WaterFurnace | V5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268772 | Ground Water | WaterFurnace | V5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268773 | Ground Water | WaterFurnace | V5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268774 | Ground Water | WaterFurnace | V5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268775 | Ground Water | WaterFurnace | V5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268776 | Ground Water | WaterFurnace | V5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268777 | Ground Water | WaterFurnace | V5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268778 | Ground Water | WaterFurnace | V5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268779 | Ground Water | WaterFurnace | V5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268780 | Ground Water | WaterFurnace | V5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215224679 | Ground Water | BOSCH | RF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224680 | Ground Water | BOSCH | RF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224681 | Ground Water | BOSCH | RF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224682 | Ground Water | BOSCH | RF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224683 | Ground Water | BOSCH | RF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | Yes
215224684 | Ground Water | BOSCH | RF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | Yes
215224685 | Ground Water | BOSCH | RF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | Yes
215224686 | Ground Water | BOSCH | RF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | Yes
215224687 | Ground Water | BOSCH | RF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224688 | Ground Water | BOSCH | RF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224782 | Ground Water | CARRIER | GBA18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224783 | Ground Water | BRYANT | GBA18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224784 | Ground Water | CARRIER | GBA18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224785 | Ground Water | BRYANT | GBA18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
216743636 | Ground Water | BOSCH | CP024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743637 | Ground Water | BOSCH-GEO | RP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216743638 | Ground Water | BOSCH | CP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743639 | Ground Water | BOSCH | CP036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
202443461 | Ground Water | GeoSmart Energy | GSZ036*1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202443462 | Ground Water | GeoSmart Energy | GSZ042*1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202443463 | Ground Water | GeoSmart Energy | GTZ038*1*J | SAH038* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202443470 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202443471 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202443472 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202443473 | Ground Water | YORK BY JOHNSON CONTROLS | YAST038**1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
202449772 | Ground Water | WaterFurnace | UBV/UBH030**0*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449773 | Ground Water | WaterFurnace | UBV/UBH030**2*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449774 | Ground Water | WaterFurnace | UBV/UBH030**3*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449775 | Ground Water | WaterFurnace | UBV/UBH030**4*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449776 | Ground Water | WaterFurnace | UBV/UBH030**0*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449777 | Ground Water | WaterFurnace | UBV/UBH030**2*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449778 | Ground Water | WaterFurnace | UBV/UBH030**3*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449779 | Ground Water | WaterFurnace | UBV/UBH030**4*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449780 | Ground Water | WaterFurnace | UBV/UBH036**0*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449781 | Ground Water | WaterFurnace | UBV/UBH036**2*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449782 | Ground Water | WaterFurnace | UBV/UBH036**3*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449783 | Ground Water | WaterFurnace | UBV/UBH036**4*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449784 | Ground Water | WaterFurnace | UBV/UBH036**0*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449785 | Ground Water | WaterFurnace | UBV/UBH036**2*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449786 | Ground Water | WaterFurnace | UBV/UBH036**3*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449787 | Ground Water | WaterFurnace | UBV/UBH036**4*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449788 | Ground Water | WaterFurnace | UBV/UBH036**0*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449789 | Ground Water | WaterFurnace | UBV/UBH036**2*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449790 | Ground Water | WaterFurnace | UBV/UBH036**3*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449791 | Ground Water | WaterFurnace | UBV/UBH036**4*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449795 | Ground Water | WaterFurnace | UBV/UBH042**0*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449796 | Ground Water | WaterFurnace | UBV/UBH042**3*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
6501954 | Ground Water | GEOSTAR | GBV/GBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501955 | Ground Water | GEOSTAR | GBV/GBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501956 | Ground Water | GEOSTAR | GBV/GBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501957 | Ground Water | GEOSTAR | GBV/GBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501958 | Ground Water | GEOSTAR | GBV/GBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501959 | Ground Water | GEOSTAR | GBV/GBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501960 | Ground Water | GEOSTAR | GBV/GBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501961 | Ground Water | GEOSTAR | GBV/GBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501962 | Ground Water | GEOSTAR | GBV/GBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501963 | Ground Water | GEOSTAR | GBV/GBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501964 | Ground Water | GEOSTAR | GBV/GBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501965 | Ground Water | GEOSTAR | GBV/GBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501966 | Ground Water | GEOSTAR | GBV/GBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501967 | Ground Water | GEOSTAR | GBV/GBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501968 | Ground Water | GEOSTAR | GBV/GBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501969 | Ground Water | GEOSTAR | GBV/GBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501970 | Ground Water | GEOSTAR | GBV/GBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501971 | Ground Water | GEOSTAR | GBV/GBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501972 | Ground Water | GEOSTAR | GBV/GBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207200576 | Ground Water | GeoSmart Energy | GTZ026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207200577 | Ground Water | GeoSmart Energy | GTZ026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207200578 | Ground Water | GeoSmart Energy | GTS026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207200579 | Ground Water | GeoSmart Energy | GTS026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207200580 | Ground Water | GeoSmart Energy | GTS049*1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207200581 | Ground Water | GeoSmart Energy | GTS049*1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207200582 | Ground Water | GeoSmart Energy | GTS064*1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207200583 | Ground Water | GeoSmart Energy | GTS064*1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207200584 | Ground Water | GeoSmart Energy | GTS072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200585 | Ground Water | GeoSmart Energy | GTZ072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200586 | Ground Water | GeoSmart Energy | GSZ022*1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
207200587 | Ground Water | GeoSmart Energy | GSZ022*1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207200588 | Ground Water | GeoSmart Energy | GSZ030*1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207200589 | Ground Water | GeoSmart Energy | GSZ030*1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207200590 | Ground Water | GeoSmart Energy | GSZ048*1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
207200591 | Ground Water | GeoSmart Energy | GSZ048*1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207200592 | Ground Water | GeoSmart Energy | GSZ060*1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
207200593 | Ground Water | GeoSmart Energy | GSZ060*1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207200594 | Ground Water | GeoSmart Energy | GSZ070*1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207200595 | Ground Water | GeoSmart Energy | GTZ072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207200596 | Ground Water | GeoSmart Energy | GSZ070*1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
207200597 | Ground Water | GeoSmart Energy | GTS072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200598 | Ground Water | GeoSmart Energy | GSZ036*1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207200599 | Ground Water | GeoSmart Energy | GSZ042*1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207200600 | Ground Water | GeoSmart Energy | GTZ038*1*J | SAH038* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207200601 | Ground Water | GeoSmart Energy | GTZ049*1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207200602 | Ground Water | GeoSmart Energy | GTZ049*1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207200603 | Ground Water | GeoSmart Energy | GTS064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207200604 | Ground Water | GeoSmart Energy | GTS064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207200605 | Ground Water | GeoSmart Energy | GSZ036*1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207200606 | Ground Water | GeoSmart Energy | GSZ042*1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207200607 | Ground Water | GeoSmart Energy | GTZ038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
217122387 | Ground Water | ClimateMaster | SWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
217193306 | Ground Water | WaterFurnace | V7A(V/H)024*V0**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193307 | Ground Water | WaterFurnace | V7A(V/H)036*V0**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193308 | Ground Water | WaterFurnace | V7A(V/H)048*V0**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193309 | Ground Water | WaterFurnace | V7A(V/H)060*V0**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217193552 | Ground Water | WaterFurnace | V7A(V/H)024*V3**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193553 | Ground Water | WaterFurnace | V7A(V/H)024*V4**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193554 | Ground Water | WaterFurnace | V7A(V/H)036*V3**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193555 | Ground Water | WaterFurnace | V7A(V/H)036*V4**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193556 | Ground Water | WaterFurnace | V7A(V/H)048*V3**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193557 | Ground Water | WaterFurnace | V7A(V/H)048*V4**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193558 | Ground Water | WaterFurnace | V7A(V/H)060*V3**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217193559 | Ground Water | WaterFurnace | V7A(V/H)060*V4**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217212043 | Ground Water | FHP | CP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212044 | Ground Water | FHP | CP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212045 | Ground Water | FHP | CP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212046 | Ground Water | FHP | CP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212048 | Ground Water | FHP | CP024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212049 | Ground Water | FHP | CP024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212050 | Ground Water | FHP | CP024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212051 | Ground Water | FHP | CP024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212052 | Ground Water | FHP | CP024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212054 | Ground Water | FHP | CP024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212055 | Ground Water | FHP | CP024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212056 | Ground Water | FHP | CP024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212057 | Ground Water | FHP | CP024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212059 | Ground Water | FHP | CP024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212060 | Ground Water | FHP | CP024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212061 | Ground Water | FHP | CP024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212062 | Ground Water | FHP | CP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212064 | Ground Water | FHP | CP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212065 | Ground Water | FHP | CP036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212066 | Ground Water | FHP | CP036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212067 | Ground Water | FHP | CP036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
7795949 | Ground Water | GEOCOMFORT | GVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795950 | Ground Water | HYDRON MODULE | HVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795951 | Ground Water | TETCO | TVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795952 | Ground Water | GEOCOMFORT | GVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795953 | Ground Water | HYDRON MODULE | HVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795954 | Ground Water | TETCO | TVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
8000290 | Ground Water | GEOCOOL | GCHP01024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | No
8000291 | Ground Water | GEOCOOL | GCHP01031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | No
8000292 | Ground Water | GEOCOOL | GCHP01036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | No
8000293 | Ground Water | GEOCOOL | GCHP01041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | No
8077723 | Ground Water | GEOCOMFORT | GYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077724 | Ground Water | HYDRON MODULE | HYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077725 | Ground Water | TETCO | TYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077726 | Ground Water | GEOCOMFORT | GYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077727 | Ground Water | HYDRON MODULE | HYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077728 | Ground Water | TETCO | TYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077729 | Ground Water | GEOCOMFORT | GYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077730 | Ground Water | HYDRON MODULE | HYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077731 | Ground Water | TETCO | TYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077735 | Ground Water | GEOCOMFORT | GYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077736 | Ground Water | HYDRON MODULE | HYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077737 | Ground Water | TETCO | TYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077738 | Ground Water | GEOCOMFORT | GYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077739 | Ground Water | HYDRON MODULE | HYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077740 | Ground Water | TETCO | TYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077741 | Ground Water | GEOCOMFORT | GYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077742 | Ground Water | HYDRON MODULE | HYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077743 | Ground Water | TETCO | TYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
205767612 | Ground Water | ClimateMaster | TZV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205767615 | Ground Water | ClimateMaster | QEV/H/D0930 |  | 24000 | 42 | 30000 | 4.8 | 2 | Yes
205767616 | Ground Water | ClimateMaster | TYV/H060B |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | No
215268669 | Ground Water | WaterFurnace | V5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268670 | Ground Water | WaterFurnace | V5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268671 | Ground Water | WaterFurnace | V5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268672 | Ground Water | WaterFurnace | V5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268673 | Ground Water | WaterFurnace | V5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268674 | Ground Water | WaterFurnace | V5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
215268675 | Ground Water | WaterFurnace | V5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
215268676 | Ground Water | WaterFurnace | V5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268677 | Ground Water | WaterFurnace | V5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268678 | Ground Water | WaterFurnace | V5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268679 | Ground Water | WaterFurnace | V5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268680 | Ground Water | WaterFurnace | V5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268681 | Ground Water | WaterFurnace | V5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268682 | Ground Water | WaterFurnace | V5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268683 | Ground Water | WaterFurnace | V5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268684 | Ground Water | WaterFurnace | V5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268685 | Ground Water | WaterFurnace | V5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268686 | Ground Water | WaterFurnace | V5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268687 | Ground Water | WaterFurnace | V5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268688 | Ground Water | WaterFurnace | V5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268689 | Ground Water | WaterFurnace | V5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268690 | Ground Water | WaterFurnace | V5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268691 | Ground Water | WaterFurnace | V5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268692 | Ground Water | WaterFurnace | V5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268693 | Ground Water | WaterFurnace | V5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268694 | Ground Water | WaterFurnace | V5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268695 | Ground Water | WaterFurnace | V5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268696 | Ground Water | WaterFurnace | V5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268697 | Ground Water | WaterFurnace | V5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268698 | Ground Water | WaterFurnace | V5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268699 | Ground Water | WaterFurnace | V5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268700 | Ground Water | WaterFurnace | V5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268701 | Ground Water | WaterFurnace | V5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268702 | Ground Water | WaterFurnace | V5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268703 | Ground Water | WaterFurnace | V5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268704 | Ground Water | WaterFurnace | V5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268705 | Ground Water | WaterFurnace | V5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268706 | Ground Water | WaterFurnace | V5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268707 | Ground Water | WaterFurnace | V5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268708 | Ground Water | WaterFurnace | V5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268709 | Ground Water | WaterFurnace | V5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268710 | Ground Water | WaterFurnace | V5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268711 | Ground Water | WaterFurnace | V5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268712 | Ground Water | WaterFurnace | V5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268713 | Ground Water | WaterFurnace | V5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268714 | Ground Water | WaterFurnace | V5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268715 | Ground Water | WaterFurnace | V5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268716 | Ground Water | WaterFurnace | V5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268717 | Ground Water | WaterFurnace | V5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268718 | Ground Water | WaterFurnace | V5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268719 | Ground Water | WaterFurnace | V5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268720 | Ground Water | WaterFurnace | V5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268721 | Ground Water | WaterFurnace | V5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268722 | Ground Water | WaterFurnace | V5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268723 | Ground Water | WaterFurnace | V5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268724 | Ground Water | WaterFurnace | V5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216759824 | Ground Water | GEOSTAR | G5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759825 | Ground Water | GEOSTAR | G5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759826 | Ground Water | WaterFurnace | W5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759827 | Ground Water | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759828 | Ground Water | WaterFurnace | W5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759829 | Ground Water | WaterFurnace | W5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759830 | Ground Water | WaterFurnace | W5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759831 | Ground Water | GEOSTAR | G5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | No
216759832 | Ground Water | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | No
216759833 | Ground Water | GEOSTAR | G5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | No
216759834 | Ground Water | GEOSTAR | G5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | No
216759835 | Ground Water | GEOSTAR | G5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | No
216767321 | Ground Water | TETCO | TVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
203372397 | Ground Water | HEIL | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
203372398 | Ground Water | ARCOAIRE | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372399 | Ground Water | KEEPRITE | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372400 | Ground Water | TEMPSTAR | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372401 | Ground Water | COMFORTMAKER | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372402 | Ground Water | DAY & NIGHT | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372403 | Ground Water | HEIL | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
203372404 | Ground Water | ARCOAIRE | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372405 | Ground Water | KEEPRITE | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372406 | Ground Water | TEMPSTAR | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372407 | Ground Water | COMFORTMAKER | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372408 | Ground Water | DAY & NIGHT | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372993 | Ground Water | BOSCH | SM060-1HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
203372994 | Ground Water | BOSCH | SM070-1HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
203372995 | Ground Water | BOSCH | SM070-1HZ*-*****C |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
203380957 | Ground Water | BOSCH | EP018-1VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203380958 | Ground Water | BOSCH | EP018-2VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203380959 | Ground Water | BOSCH | EP018-1HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203380960 | Ground Water | BOSCH | EP018-2HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203380963 | Ground Water | BOSCH | EP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380964 | Ground Water | BOSCH | EP042-3VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380965 | Ground Water | BOSCH | EP042-4VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380966 | Ground Water | BOSCH | EP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380967 | Ground Water | BOSCH | EP042-3HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380968 | Ground Water | BOSCH | EP042-4HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380969 | Ground Water | BOSCH | EP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203380970 | Ground Water | BOSCH | EP048-3VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203380971 | Ground Water | BOSCH | EP048-4VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203380972 | Ground Water | BOSCH | EP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203380973 | Ground Water | BOSCH | EP048-3HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203380974 | Ground Water | BOSCH | EP048-4HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383876 | Ground Water | CARRIER | 50PSV018***3/CA |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383877 | Ground Water | CARRIER | 50PSV018***4/DA |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383878 | Ground Water | CARRIER | 50PSH018***3/CA |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383879 | Ground Water | CARRIER | 50PSH018***4/DA |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383880 | Ground Water | CARRIER | 50PSV042***3/CA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383881 | Ground Water | CARRIER | 50PSV042***5/EA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383882 | Ground Water | CARRIER | 50PSV042***6/FA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383883 | Ground Water | CARRIER | 50PSH042***3/CA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383884 | Ground Water | CARRIER | 50PSH042***5/EA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383885 | Ground Water | CARRIER | 50PSH042***6/FA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383886 | Ground Water | CARRIER | 50PSV048***3/CA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383887 | Ground Water | CARRIER | 50PSV048***5/EA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202147709 | Ground Water | GEOCOMFORT | GZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147710 | Ground Water | HYDRON MODULE | HZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147711 | Ground Water | TETCO | TZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
215224599 | Ground Water | CARRIER | 50WD*007***3*(A-H)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224600 | Ground Water | CARRIER | 50WD*007***3*(J-R)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224601 | Ground Water | CARRIER | 50WD*007***4*(A-H)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224602 | Ground Water | CARRIER | 50WD*007***4*(J-R)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224603 | Ground Water | CARRIER | 50WD*009***3*(A-H)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224604 | Ground Water | CARRIER | 50WD*009***3*(J-R)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224605 | Ground Water | CARRIER | 50WD*009***4*(A-H)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224606 | Ground Water | CARRIER | 50WD*009***4*(J-R)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224607 | Ground Water | CARRIER | 50WD*012***3*(A-H)** |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224608 | Ground Water | CARRIER | 50WD*012***3*(J-R)** |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224609 | Ground Water | CARRIER | 50WD*012***4*(A-H)** |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224610 | Ground Water | CARRIER | 50WD*012***4*(J-R)** |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224611 | Ground Water | CARRIER | 50WD*015***3*(A-H)** |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224612 | Ground Water | CARRIER | 50WD*015***3*(J-R)** |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
217351806 | Ground Water | ARCOAIRE | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351808 | Ground Water | ARCOAIRE | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351811 | Ground Water | COMFORTMAKER | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351812 | Ground Water | COMFORTMAKER | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351813 | Ground Water | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351814 | Ground Water | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351815 | Ground Water | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351816 | Ground Water | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351817 | Ground Water | COMFORTMAKER | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351819 | Ground Water | COMFORTMAKER | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351820 | Ground Water | COMFORTMAKER | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351822 | Ground Water | COMFORTMAKER | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351823 | Ground Water | COMFORTMAKER | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351824 | Ground Water | COMFORTMAKER | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351825 | Ground Water | COMFORTMAKER | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351826 | Ground Water | COMFORTMAKER | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351827 | Ground Water | COMFORTMAKER | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351828 | Ground Water | COMFORTMAKER | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351830 | Ground Water | COMFORTMAKER | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351831 | Ground Water | COMFORTMAKER | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351833 | Ground Water | COMFORTMAKER | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
216767322 | Ground Water | TETCO | TVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216767323 | Ground Water | TETCO | TVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216767324 | Ground Water | TETCO | TVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216767325 | Ground Water | TETCO | TVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216767326 | Ground Water | TETCO | TYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216767327 | Ground Water | TETCO | TYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216767328 | Ground Water | TETCO | TYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216767329 | Ground Water | TETCO | TVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216767330 | Ground Water | TETCO | TYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216767332 | Ground Water | TETCO | TYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216767333 | Ground Water | HYDRON MODULE | HVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
216767334 | Ground Water | HYDRON MODULE | HVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216767335 | Ground Water | HYDRON MODULE | HVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216767336 | Ground Water | HYDRON MODULE | HVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216767337 | Ground Water | HYDRON MODULE | HVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216767338 | Ground Water | HYDRON MODULE | HYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216767339 | Ground Water | HYDRON MODULE | HYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216767340 | Ground Water | HYDRON MODULE | HYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216767341 | Ground Water | HYDRON MODULE | HVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216767342 | Ground Water | HYDRON MODULE | HYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216767344 | Ground Water | HYDRON MODULE | HYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216772562 | Ground Water | Enertech | EBS018* | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
216772563 | Ground Water | Enertech | EBT024* | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
216772564 | Ground Water | Enertech | EBT036* | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
216772565 | Ground Water | Enertech | EBT048* | EAD048 | 51500 | 22.5 | 51300 | 4.5 | 4.2917 | Yes
7022707 | Ground Water | GeoSmart Energy | ZS060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
7022708 | Ground Water | GEOSTAR | ZS060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
7137597 | Ground Water | GEO-THERMAL SPLIT | GS024**1**1 | FE/V****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
7167375 | Ground Water | BRYANT | GB024H/V******1*X1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
7167376 | Ground Water | CARRIER | GB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
7167377 | Ground Water | BRYANT | GB030H/V******1*X1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
7167378 | Ground Water | CARRIER | GB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
7167412 | Ground Water | BRYANT | GT072C/H/V******1*X1 |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167413 | Ground Water | CARRIER | GT072C/H/V******1**1 |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167538 | Ground Water | CARRIER | 50PTD/H/V024***3/CA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167539 | Ground Water | CARRIER | 50PTD/H/V024***5/EA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
207318098 | Ground Water | WaterFurnace | LD(V,H)048A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
207323881 | Ground Water | WaterFurnace | NDZ026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207323882 | Ground Water | WaterFurnace | NDZ026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207323883 | Ground Water | WaterFurnace | NDS026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207323884 | Ground Water | WaterFurnace | NDS026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207323885 | Ground Water | WaterFurnace | NDZ038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323886 | Ground Water | WaterFurnace | NDZ038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323887 | Ground Water | WaterFurnace | NDS038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323888 | Ground Water | WaterFurnace | NDZ049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207323889 | Ground Water | WaterFurnace | NDZ049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207323890 | Ground Water | WaterFurnace | NDS049H1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207323891 | Ground Water | WaterFurnace | NDS049H1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
214823447 | Ground Water | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214823448 | Ground Water | GeoSmart Energy | S5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214823449 | Ground Water | GeoSmart Energy | S5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214823450 | Ground Water | GeoSmart Energy | S5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214823451 | Ground Water | GeoSmart Energy | S5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214823480 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214823481 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214823482 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214823484 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214823485 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214823486 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214823487 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214823488 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214837733 | Ground Water | BOSCH | EC072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837734 | Ground Water | BOSCH | EC072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837735 | Ground Water | BOSCH | EC072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837736 | Ground Water | BOSCH | EC096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837737 | Ground Water | BOSCH | EC096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837738 | Ground Water | BOSCH | EC096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837742 | Ground Water | CARRIER | 50H/VQP072***3C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837743 | Ground Water | CARRIER | 50H/VQP072***5C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837744 | Ground Water | CARRIER | 50H/VQP072***6C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837745 | Ground Water | CARRIER | 50H/VQP096***3C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837746 | Ground Water | CARRIER | 50H/VQP096***5C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837747 | Ground Water | CARRIER | 50H/VQP096***6C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
216569713 | Ground Water | GeoCool | GCHPV/H/D024BT**A*** |  | 28500 | 27.4 | 24500 | 4.8 | 2.375 | No
206438779 | Ground Water | FHP | EP007-2HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438780 | Ground Water | FHP | EP007-1HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438781 | Ground Water | FHP | EP009-1HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438782 | Ground Water | FHP | EP009-2HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438783 | Ground Water | FHP | EP012-1HZ/VT*-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438784 | Ground Water | FHP | EP015-1HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438785 | Ground Water | FHP | EP015-2HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438786 | Ground Water | FHP | EP030-2HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438787 | Ground Water | FHP | EP030-4HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438788 | Ground Water | FHP | EP030-3HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438789 | Ground Water | FHP | EP030-1HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438790 | Ground Water | FHP | EP060-4HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438791 | Ground Water | FHP | EP060-3HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438792 | Ground Water | FHP | EP060-1HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438793 | Ground Water | FHP | EP070-1HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438794 | Ground Water | FHP | EP070-3HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438795 | Ground Water | FHP | EP070-4HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438813 | Ground Water | FHP | EP012-1VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438814 | Ground Water | FHP | EP012-1HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438815 | Ground Water | FHP | EP012-1VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438816 | Ground Water | FHP | EP012-1HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438817 | Ground Water | FHP | EP012-0VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438818 | Ground Water | FHP | EP012-2VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438819 | Ground Water | FHP | EP012-0HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438820 | Ground Water | FHP | EP012-2HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438821 | Ground Water | FHP | EP012-0VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438822 | Ground Water | FHP | EP012-2VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438823 | Ground Water | FHP | EP012-0HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
7170606 | Ground Water | GEOCOMFORT | GVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170607 | Ground Water | HYDRON MODULE | HVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170608 | Ground Water | TETCO | TVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170609 | Ground Water | GEOCOMFORT | GVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170610 | Ground Water | HYDRON MODULE | HVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170611 | Ground Water | TETCO | TVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170612 | Ground Water | GEOCOMFORT | GVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
7170613 | Ground Water | HYDRON MODULE | HVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
7170614 | Ground Water | TETCO | TVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
10581121 | Ground Water | GEOSTAR | 107H064**1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
207323892 | Ground Water | WaterFurnace | NDZ064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207323893 | Ground Water | WaterFurnace | NDZ064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207323894 | Ground Water | WaterFurnace | NDS064H1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207323895 | Ground Water | WaterFurnace | NDS064H1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207323896 | Ground Water | WaterFurnace | NDZ072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207323897 | Ground Water | WaterFurnace | NDZ072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207323898 | Ground Water | WaterFurnace | NDS072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207323899 | Ground Water | WaterFurnace | NDS072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207323900 | Ground Water | WaterFurnace | NDS038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207323901 | Ground Water | WaterFurnace | NSZ022H1* | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207323902 | Ground Water | WaterFurnace | NSZ030H1* | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207323903 | Ground Water | WaterFurnace | NSZ036J1* | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207323904 | Ground Water | WaterFurnace | NSZ042J1* | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207323905 | Ground Water | WaterFurnace | NSZ048J1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207323906 | Ground Water | WaterFurnace | NSZ048J1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207323907 | Ground Water | WaterFurnace | NSZ060J1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207323908 | Ground Water | WaterFurnace | NSZ060J1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207323909 | Ground Water | WaterFurnace | NSZ070H1* | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207323910 | Ground Water | WaterFurnace | NSZ022H1* | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207323911 | Ground Water | WaterFurnace | NSZ030H1* | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207323912 | Ground Water | WaterFurnace | NSZ036J1* | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207323913 | Ground Water | WaterFurnace | NSZ042J1* | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207323914 | Ground Water | WaterFurnace | NSZ070H1* | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207324064 | Ground Water | WaterFurnace | NVV/NVH036C1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
207324066 | Ground Water | WaterFurnace | NVV/NVH060C1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | No
207335134 | Ground Water | GEOSTAR | 101/102J012**1*0***** |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
207335135 | Ground Water | GEOSTAR | 101/102J018**1*(1,4)***** |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335136 | Ground Water | GEOSTAR | 101/102J030**1*(1,4)***** |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335137 | Ground Water | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207335138 | Ground Water | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335139 | Ground Water | GEOSTAR | 101/102K048**1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335140 | Ground Water | GEOSTAR | 101/102K060**1*(1,4)****** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335141 | Ground Water | GEOSTAR | 101/102J070**1*(1,4)***** |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335142 | Ground Water | GEOSTAR | 101/102J026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335143 | Ground Water | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335144 | Ground Water | GEOSTAR | 101/102K049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335145 | Ground Water | GEOSTAR | 101/102K064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335146 | Ground Water | GEOSTAR | 101/102J072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335147 | Ground Water | GEOSTAR | 161/162K064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335247 | Ground Water | GEOSTAR | 101/102J022**1*(1,4)***** |  | 21900 | 27.5 | 21900 | 5 | 1.825 | Yes
207335249 | Ground Water | GEOSTAR | 161/162J026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335251 | Ground Water | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335253 | Ground Water | GEOSTAR | 161/162K049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335255 | Ground Water | GEOSTAR | 161/162J072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335335 | Ground Water | GEOSTAR | 111J049**1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
8332268 | Ground Water | GEOCOMFORT | GYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332358 | Ground Water | HYDRON MODULE | HYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332380 | Ground Water | TETCO | TYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332431 | Ground Water | GEOCOMFORT | GYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332452 | Ground Water | HYDRON MODULE | HYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332472 | Ground Water | TETCO | TYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332525 | Ground Water | GEOCOMFORT | GYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332545 | Ground Water | HYDRON MODULE | HYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332563 | Ground Water | TETCO | TYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8560797 | Ground Water | 5 SERIES | NSV/NSH060H1*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8560805 | Ground Water | 5 SERIES | NSV/NSH060H1*(1,4) |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8560913 | Ground Water | GEOCOMFORT | GVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
8560914 | Ground Water | HYDRON MODULE | HVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
8560915 | Ground Water | TETCO | TVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
8560916 | Ground Water | GEOCOMFORT | GVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560917 | Ground Water | HYDRON MODULE | HVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560918 | Ground Water | TETCO | TVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560919 | Ground Water | GEOCOMFORT | GVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560920 | Ground Water | HYDRON MODULE | HVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560921 | Ground Water | TETCO | TVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560930 | Ground Water | GEOCOMFORT | GVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560931 | Ground Water | HYDRON MODULE | HVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560932 | Ground Water | TETCO | TVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560938 | Ground Water | GEOCOMFORT | GVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560939 | Ground Water | HYDRON MODULE | HVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560940 | Ground Water | TETCO | TVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560941 | Ground Water | GEOCOMFORT | GVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560942 | Ground Water | HYDRON MODULE | HVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560943 | Ground Water | TETCO | TVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560946 | Ground Water | GEOCOMFORT | GVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
8560947 | Ground Water | HYDRON MODULE | HVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
8560948 | Ground Water | TETCO | TVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
8560949 | Ground Water | GEOCOMFORT | GVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
8560950 | Ground Water | HYDRON MODULE | HVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
8560951 | Ground Water | TETCO | TVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
203113890 | Ground Water | GEOSTAR | 103J042**1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
203113892 | Ground Water | GEOSTAR | 103J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
203113894 | Ground Water | GEOSTAR | 104J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
203143108 | Ground Water | GEOCOMFORT | GVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143111 | Ground Water | GEOCOMFORT | GVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143114 | Ground Water | GEOCOMFORT | GVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143119 | Ground Water | GEOCOMFORT | GVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143124 | Ground Water | HYDRON MODULE | HVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143129 | Ground Water | HYDRON MODULE | HVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143133 | Ground Water | HYDRON MODULE | HVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143138 | Ground Water | HYDRON MODULE | HVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143143 | Ground Water | TETCO | TVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143148 | Ground Water | TETCO | TVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143153 | Ground Water | TETCO | TVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143157 | Ground Water | TETCO | TVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143746 | Ground Water | GEOCOMFORT | GVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
203143749 | Ground Water | GEOCOMFORT | GVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143752 | Ground Water | GEOCOMFORT | GVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143764 | Ground Water | HYDRON MODULE | HVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
203143767 | Ground Water | HYDRON MODULE | HVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143770 | Ground Water | HYDRON MODULE | HVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143781 | Ground Water | TETCO | TVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
203143785 | Ground Water | TETCO | TVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
217351115 | Ground Water | GEO-THERMAL SPLIT | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351116 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351117 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351118 | Ground Water | GEO-THERMAL SPLIT | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351119 | Ground Water | GEO-THERMAL SPLIT | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351120 | Ground Water | GEO-THERMAL SPLIT | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
203254609 | Ground Water | HEIL | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254610 | Ground Water | KEEPRITE | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254611 | Ground Water | TEMPSTAR | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254612 | Ground Water | COMFORTMAKER | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254614 | Ground Water | DAY & NIGHT | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254620 | Ground Water | BRYANT | GC024V/C**N***1*X1 |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203254624 | Ground Water | BRYANT | GC024H**C***1*X1 |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203254626 | Ground Water | BRYANT | GC024H**N***1*X1 |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203254744 | Ground Water | CARRIER | GC024V/C**N***1**1 |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203254748 | Ground Water | CARRIER | GC024H**C***1**1 |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203254752 | Ground Water | CARRIER | GC024H**N***1**1 |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203260718 | Ground Water | BOSCH-GEO | SM024-1VT/CFC******A |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
203260866 | Ground Water | CARRIER | GC024V/C**C***1**1 + UI |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
203260867 | Ground Water | BRYANT | GC024V/C**C***1*X1 + UI |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
202667081 | Ground Water | BOSCH-GEO | BP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
206726680 | Ground Water | WaterFurnace | UVV/UVH024**0*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
206726691 | Ground Water | WaterFurnace | UVV/UVH024**3*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
206726692 | Ground Water | WaterFurnace | UVV/UVH024**4*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
206726812 | Ground Water | GEOCOMFORT | GBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726813 | Ground Water | GEOCOMFORT | GBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726814 | Ground Water | HYDRON MODULE | HBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726815 | Ground Water | HYDRON MODULE | HBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726816 | Ground Water | TETCO | TBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726817 | Ground Water | TETCO | TBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726818 | Ground Water | GEOCOMFORT | GBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726819 | Ground Water | GEOCOMFORT | GBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726820 | Ground Water | HYDRON MODULE | HBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726821 | Ground Water | HYDRON MODULE | HBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726822 | Ground Water | TETCO | TBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726823 | Ground Water | TETCO | TBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726824 | Ground Water | GEOCOMFORT | GBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
206726825 | Ground Water | GEOCOMFORT | GBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726826 | Ground Water | HYDRON MODULE | HBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
206726827 | Ground Water | HYDRON MODULE | HBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726828 | Ground Water | TETCO | TBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
206726829 | Ground Water | TETCO | TBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726830 | Ground Water | GEOCOMFORT | GBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726831 | Ground Water | GEOCOMFORT | GBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726832 | Ground Water | HYDRON MODULE | HBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726833 | Ground Water | HYDRON MODULE | HBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726834 | Ground Water | TETCO | TBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726835 | Ground Water | TETCO | TBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726836 | Ground Water | GEOCOMFORT | GBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726837 | Ground Water | GEOCOMFORT | GBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726838 | Ground Water | HYDRON MODULE | HBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726839 | Ground Water | HYDRON MODULE | HBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726840 | Ground Water | TETCO | TBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726841 | Ground Water | TETCO | TBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726842 | Ground Water | GEOCOMFORT | GBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726843 | Ground Water | GEOCOMFORT | GBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726844 | Ground Water | HYDRON MODULE | HBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726845 | Ground Water | HYDRON MODULE | HBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726846 | Ground Water | TETCO | TBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726847 | Ground Water | TETCO | TBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726848 | Ground Water | GEOCOMFORT | GBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
206726849 | Ground Water | HYDRON MODULE | HBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
206726850 | Ground Water | TETCO | TBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
206726851 | Ground Water | GEOCOMFORT | GBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726852 | Ground Water | HYDRON MODULE | HBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726853 | Ground Water | TETCO | TBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726854 | Ground Water | GEOCOMFORT | GBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726855 | Ground Water | GEOCOMFORT | GBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726856 | Ground Water | HYDRON MODULE | HBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726857 | Ground Water | HYDRON MODULE | HBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726858 | Ground Water | TETCO | TBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726859 | Ground Water | TETCO | TBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726860 | Ground Water | GEOCOMFORT | GBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
206726861 | Ground Water | GEOCOMFORT | GBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
206726862 | Ground Water | HYDRON MODULE | HBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
211594118 | Ground Water | TRANE | GEHG006A |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
211594119 | Ground Water | TRANE | GEHG009A |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
211594120 | Ground Water | TRANE | GEHG012A |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
211594121 | Ground Water | TRANE | GEHG015A |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
3706350 | Ground Water | GEOSTAR | ZS015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3706351 | Ground Water | GEOSTAR | ZS015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3706369 | Ground Water | GEOSTAR | ZS018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
216714623 | Ground Water | GEOSTAR | G3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714624 | Ground Water | GEOSTAR | G3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714625 | Ground Water | GEOSTAR | G3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714626 | Ground Water | GEOSTAR | G3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714627 | Ground Water | GEOSTAR | G3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714636 | Ground Water | GEOSTAR | G3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714637 | Ground Water | GEOSTAR | G3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714638 | Ground Water | GEOSTAR | G3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714639 | Ground Water | GEOSTAR | G3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714640 | Ground Water | GEOSTAR | G3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714641 | Ground Water | GEOSTAR | G3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714642 | Ground Water | GEOSTAR | G3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714643 | Ground Water | GEOSTAR | G3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714644 | Ground Water | GEOSTAR | G3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714645 | Ground Water | GEOSTAR | G3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714646 | Ground Water | GEOSTAR | G3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714647 | Ground Water | GEOSTAR | G3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714648 | Ground Water | GEOSTAR | G3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714649 | Ground Water | GEOSTAR | G3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714656 | Ground Water | GEOSTAR | G3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714657 | Ground Water | GEOSTAR | G3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714658 | Ground Water | GEOSTAR | G3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714659 | Ground Water | GEOSTAR | G3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714660 | Ground Water | GEOSTAR | G3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714661 | Ground Water | GEOSTAR | G3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
202324846 | Ground Water | WaterFurnace | UBV/UBH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
202324847 | Ground Water | WaterFurnace | UBV/UBH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
202326797 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202326829 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202328433 | Ground Water | BOSCH | SM048-1CSC-*****A | SM048-1AV*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | Yes
202328436 | Ground Water | BOSCH | BP018-1VT*******C |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202330331 | Ground Water | AAON, Inc. | WH-060-1-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330332 | Ground Water | AAON, Inc. | WH-060-A-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330335 | Ground Water | AAON, Inc. | WH-060-2-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330336 | Ground Water | AAON, Inc. | WH-060-3-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330345 | Ground Water | AAON, Inc. | WH-060-A-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
10271778 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10271926 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10271930 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10271959 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ022H1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10271961 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ022H1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10271981 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ030H1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10271985 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ030H1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10272006 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048H1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10272008 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048H1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
10272012 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060H1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10272014 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060H1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10272021 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ070H1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10272215 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10272216 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10272219 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10272220 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
9100404 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100417 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100431 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9105364 | Ground Water | GEOCOMFORT | GVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
9105366 | Ground Water | HYDRON MODULE | HVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
9105367 | Ground Water | TETCO | TVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
204272856 | Ground Water | GeoSmart Energy | GT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204272857 | Ground Water | GeoSmart Energy | GTS064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204272858 | Ground Water | GeoSmart Energy | GTS064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204272859 | Ground Water | GeoSmart Energy | GTZ064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272860 | Ground Water | GeoSmart Energy | GTZ064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272890 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204272892 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272893 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204276830 | Ground Water | GEOSTAR | 104J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
204276831 | Ground Water | GEOSTAR | 103J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
204278291 | Ground Water | WaterFurnace | SDV038J1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
204283848 | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | SM048-1AH*******A | 52800 | 21.15 | 46600 | 4.4 | 4.4 | Yes
204283849 | Ground Water | BOSCH | SM048-1CS*-*****A | SM048-1AH*******A | 52800 | 21.15 | 46600 | 4.4 | 4.4 | Yes
204346746 | Ground Water | GeoCool | GCHPV/H/D024T**A*** |  | 29000 | 27.4 | 25700 | 5.4 | 2.4167 | No
204346873 | Ground Water | GeoCool | GCHPV/H/D036T**A*** |  | 43000 | 27.2 | 38000 | 5.3 | 3.5833 | No
204346874 | Ground Water | GeoCool | GCHPV/H/D048T**A*** |  | 56000 | 26 | 50000 | 4.9 | 4.6667 | No
204370721 | Ground Water | GeoCool | GCHPV/H/D060T**A*** |  | 72500 | 24 | 64500 | 4.9 | 6.0417 | No
207178492 | Ground Water | GEOSTAR | 163J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
214841675 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
214841676 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
214841677 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
214841678 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
214841679 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
214841680 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
214841682 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
214841684 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
214841686 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
214841687 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
214841688 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
214841690 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
214841697 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
214841698 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
214841699 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
214841700 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
214841701 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
214841702 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
214841704 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
214841705 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
214841706 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
214841707 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
214841708 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
214841710 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
214841711 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
214841712 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
207200617 | Ground Water | GeoSmart Energy | VI036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
207200622 | Ground Water | GeoSmart Energy | QT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
207200624 | Ground Water | GeoSmart Energy | VI048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
207200625 | Ground Water | GeoSmart Energy | VI060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
202330283 | Ground Water | AAON, Inc. | WH-018-1-H-ACAC-C0-10-200-A |  | 19500 | 26.5 | 16100 | 4.8 | 1.625 | No
202330284 | Ground Water | AAON, Inc. | WH-018-A-H-ACAC-C0-10-200-A |  | 19500 | 26.5 | 16100 | 4.8 | 1.625 | No
6580833 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
6580857 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
5696567 | Ground Water | 5 SERIES | NSV/NSH022G1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708463 | Ground Water | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708493 | Ground Water | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708550 | Ground Water | GEOSTAR | 101/102A022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708623 | Ground Water | GeoSmart Energy | GS022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5731224 | Ground Water | BARD | GTC36S2-A | GTA3600UD1AA+GTB1-A | 41000 | 21.6 | 37500 | 4.8 | 3.4167 | No
6581203 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
202330297 | Ground Water | AAON, Inc. | WH-030-1-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
202330298 | Ground Water | AAON, Inc. | WH-030-A-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
5505441 | Ground Water | BARD | GTC36S2-A | HE37942D175B2505AW/HE37942D210B2505AW | 40500 | 24 | 34000 | 4.85 | 3.375 | No
5612204 | Ground Water | GeoSmart Energy | VI048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
5612208 | Ground Water | GeoSmart Energy | VI060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
5613676 | Ground Water | GEOSTAR | 141/142A048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
5613677 | Ground Water | GEOSTAR | 141/142A060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
205993127 | Ground Water | HYDRON MODULE | HBT036 | HED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993128 | Ground Water | HYDRON MODULE | HBT036 | HAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993129 | Ground Water | TETCO | TBT036 | TED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993130 | Ground Water | TETCO | TBT036 | TAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993131 | Ground Water | GEOCOMFORT | GBT036*2 | GED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993132 | Ground Water | GEOCOMFORT | GBT036*2 | GAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993133 | Ground Water | HYDRON MODULE | HBT036*2 | HED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
10268245 | Ground Water | HYDRON MODULE | HBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268246 | Ground Water | TETCO | TBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268247 | Ground Water | GEOCOMFORT | GBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268248 | Ground Water | HYDRON MODULE | HBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268249 | Ground Water | TETCO | TBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268250 | Ground Water | GEOCOMFORT | GBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268251 | Ground Water | HYDRON MODULE | HBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
202607205 | Ground Water | WHALEN | CASH*054AM**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607206 | Ground Water | WHALEN | CASV*054AM**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
8849312 | Ground Water | 5 SERIES | NDV/NDH026H1*(1,4) |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7493326 | Ground Water | YORK BY JOHNSON CONTROLS | YLFT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
214855076 | Ground Water | WHALEN | CASH*042AD**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855077 | Ground Water | WHALEN | CASH*042AJ**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855078 | Ground Water | WHALEN | CASH*042AM**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855079 | Ground Water | WHALEN | CASV*042AB**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855080 | Ground Water | WHALEN | CASV*042AD**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855081 | Ground Water | WHALEN | CASV*042AJ**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855082 | Ground Water | WHALEN | CASV*042AM**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330368 | Ground Water | AAON, Inc. | WV-019-A-H-ACAC-C0-10-200-A |  | 21400 | 27 | 17000 | 4.1 | 1.7833 | No
202330371 | Ground Water | AAON, Inc. | WV-024-1-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330372 | Ground Water | AAON, Inc. | WV-024-A-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
10268252 | Ground Water | TETCO | TBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268253 | Ground Water | GEOCOMFORT | GBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268254 | Ground Water | HYDRON MODULE | HBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268255 | Ground Water | TETCO | TBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268260 | Ground Water | GEOCOMFORT | GBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268261 | Ground Water | HYDRON MODULE | HBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268262 | Ground Water | TETCO | TBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
202391450 | Ground Water | CARRIER | 50PSV012**C4/DA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391451 | Ground Water | CARRIER | 50PSH012**C0/BA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391452 | Ground Water | CARRIER | 50PSH012**C4/DA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391453 | Ground Water | CARRIER | 50PSV012**N0/BA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391454 | Ground Water | CARRIER | 50PSV012**N4/DA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391455 | Ground Water | CARRIER | 50PSH012**N0/BA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391456 | Ground Water | CARRIER | 50PSH012**N4/DA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
8106144 | Ground Water | TRANE | DXVF0704 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8106145 | Ground Water | TRANE | DXVF0708 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
202330425 | Ground Water | AAON, Inc. | WV-042-A-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202330426 | Ground Water | AAON, Inc. | WV-042-3-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202330427 | Ground Water | AAON, Inc. | WV-048-A-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202330428 | Ground Water | AAON, Inc. | WV-048-A-H-DCAC-C0-10-D00-A |  | 54500 | 22 | 54200 | 4.8 | 4.5417 | No
202330429 | Ground Water | AAON, Inc. | WV-048-3-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202330431 | Ground Water | AAON, Inc. | WV-060-A-H-DCAC-C0-10-D00-A |  | 64000 | 21.7 | 65000 | 4.9 | 5.3333 | No
202330466 | Ground Water | AAON, Inc. | RN-006-2-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
202330396 | Ground Water | AAON, Inc. | WV-042-A-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330399 | Ground Water | AAON, Inc. | WV-042-2-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330400 | Ground Water | AAON, Inc. | WV-042-3-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
205993162 | Ground Water | GEOCOMFORT | GBT024*2 | GAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993163 | Ground Water | HYDRON MODULE | HBT024*2 | HED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993164 | Ground Water | HYDRON MODULE | HBT024*2 | HAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993165 | Ground Water | TETCO | TBT024*2 | TED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993166 | Ground Water | TETCO | TBT024*2 | TAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993168 | Ground Water | GEOCOMFORT | GBT072 | GAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
10581116 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT064**1*1******H |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
10581117 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT072**1*1******H |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
10581118 | Ground Water | GEOSTAR | 107H026**1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
10581119 | Ground Water | GEOSTAR | 107H038**1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581120 | Ground Water | GEOSTAR | 107H049**1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
10581122 | Ground Water | GEOSTAR | 107H072**1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
203466716 | Ground Water | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203470605 | Ground Water | 5 SERIES | NSV/NSH048J1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
203470607 | Ground Water | 5 SERIES | NSV/NSH048J1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
203490410 | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203490414 | Ground Water | GeoSmart Energy | GS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
8560542 | Ground Water | 5 SERIES | NSV/NSH012H1*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8560785 | Ground Water | 5 SERIES | NSV/NSH018H1*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8560786 | Ground Water | 5 SERIES | NSV/NSH022H1*(0,3) |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8560787 | Ground Water | 5 SERIES | NSV/NSH030H1*(0,3) |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8560799 | Ground Water | 5 SERIES | NSV/NSH018H1*(1,4) |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8560800 | Ground Water | 5 SERIES | NSV/NSH022H1*(1,4) |  | 21900 | 27.5 | 19500 | 5 | 1.825 | No
214855090 | Ground Water | WHALEN | CASV*048AM**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855091 | Ground Water | WHALEN | CASH*054AB**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855092 | Ground Water | WHALEN | CASH*054AD**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855093 | Ground Water | WHALEN | CASH*054AJ**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855094 | Ground Water | WHALEN | CASH*054AM**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855095 | Ground Water | WHALEN | CASH*060AB**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855096 | Ground Water | WHALEN | CASH*060AD**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202350416 | Ground Water | AAON, Inc. | RN-009-4-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
202350426 | Ground Water | AAON, Inc. | RN-011-2-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
202350427 | Ground Water | AAON, Inc. | RN-011-3-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
202350428 | Ground Water | AAON, Inc. | RN-011-4-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
7167555 | Ground Water | CARRIER | 50PSH/V024***5/EA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7167556 | Ground Water | CARRIER | 50PSH/V024***6/FA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
205993134 | Ground Water | HYDRON MODULE | HBT036*2 | HAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993135 | Ground Water | TETCO | TBT036*2 | TED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993136 | Ground Water | TETCO | TBT036*2 | TAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993137 | Ground Water | GEOCOMFORT | GBT048 | GED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993138 | Ground Water | GEOCOMFORT | GBT048 | GAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993139 | Ground Water | HYDRON MODULE | HBT048 | HED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993140 | Ground Water | HYDRON MODULE | HBT048 | HAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
202607199 | Ground Water | WHALEN | CASH*054AB**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607200 | Ground Water | WHALEN | CASV*054AB**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607201 | Ground Water | WHALEN | CASH*054AD**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607202 | Ground Water | WHALEN | CASV*054AD**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607203 | Ground Water | WHALEN | CASH*054AJ**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607204 | Ground Water | WHALEN | CASV*054AJ**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
8789598 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8791888 | Ground Water | GEOSTAR | 101/102H070**1*(1,4)***** |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8791889 | Ground Water | GeoSmart Energy | GS070**1*(1,4)********H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8791890 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7499460 | Ground Water | FHP | EP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499461 | Ground Water | FHP | EP024-2HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499463 | Ground Water | FHP | EP024-3HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499464 | Ground Water | FHP | EP024-4HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499465 | Ground Water | FHP | EP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499466 | Ground Water | FHP | EP030-2HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499467 | Ground Water | FHP | EP030-3HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
214855048 | Ground Water | WHALEN | CASH*018AD**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855049 | Ground Water | WHALEN | CASV*018AB**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855050 | Ground Water | WHALEN | CASV*018AD**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855051 | Ground Water | WHALEN | CASH*024AB**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855052 | Ground Water | WHALEN | CASH*024AD**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855053 | Ground Water | WHALEN | CASH*024AJ**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855054 | Ground Water | WHALEN | CASH*024AM**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
7492839 | Ground Water | 3 SERIES | LD(V,H)048A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
207312264 | Ground Water | WaterFurnace | NSV/NSH022J1*(0,3) |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
207324061 | Ground Water | WaterFurnace | NVZ033A1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | No
207324062 | Ground Water | WaterFurnace | NVZ042A1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | No
207200559 | Ground Water | GeoSmart Energy | GS012**1*0*H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
207200560 | Ground Water | GeoSmart Energy | GS018**1*(1,4)*H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
207200561 | Ground Water | GeoSmart Energy | GS018**1*0*H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
207200562 | Ground Water | GeoSmart Energy | GS022**1*(0,3)*H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
207200563 | Ground Water | GeoSmart Energy | GS030**1*(0,3)*H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
207200564 | Ground Water | GeoSmart Energy | GS030**1*(1,4)*H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
207200567 | Ground Water | GeoSmart Energy | GS070**1*(1,4)*H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
206315256 | Ground Water | WHALEN | CASV*018AD**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206599757 | Ground Water | 5 SERIES | NSV/NSH060J1*0* |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
206599760 | Ground Water | 5 SERIES | NSV/NSH060J1*(1,4)* |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
206599762 | Ground Water | GEOSTAR | 101/102J060**1*0****** |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
206599765 | Ground Water | GEOSTAR | 101/102J060**1*(1,4)****** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207334458 | Ground Water | WaterFurnace | NDP026H1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
207334459 | Ground Water | WaterFurnace | NDP038H1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
207334460 | Ground Water | WaterFurnace | NDP049H1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
207334461 | Ground Water | WaterFurnace | NDP072H1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
207334462 | Ground Water | WaterFurnace | NDP064H1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
202330323 | Ground Water | AAON, Inc. | WH-048-1-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
5296257 | Ground Water | TRANE | EXVF0367 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296258 | Ground Water | TRANE | EXVF0368 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296259 | Ground Water | TRANE | EXVF0421 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296260 | Ground Water | TRANE | EXVF0422 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296261 | Ground Water | TRANE | EXVF0423 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296262 | Ground Water | TRANE | EXVF0424 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296263 | Ground Water | TRANE | EXVF0488 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
205536348 | Ground Water | AAON, Inc. | WV-072-3-0-DCAC-C0-10-200-A |  | 90800 | 25 | 79800 | 4.9 | 7.5667 | No
205536354 | Ground Water | AAON, Inc. | WV-096-2-0-DCAC-C0-10-200-A |  | 108200 | 23.2 | 99200 | 4.5 | 9.0167 | No
205536369 | Ground Water | AAON, Inc. | WV-096-3-0-DCAC-C0-10-200-A |  | 108200 | 23.2 | 99200 | 4.5 | 9.0167 | No
205782568 | Ground Water | YORK BY JOHNSON CONTROLS | YACT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
205782572 | Ground Water | GeoSmart Energy | QT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
10268203 | Ground Water | TETCO | TBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268204 | Ground Water | GEOCOMFORT | GBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268205 | Ground Water | HYDRON MODULE | HBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268206 | Ground Water | TETCO | TBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268207 | Ground Water | GEOCOMFORT | GBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268208 | Ground Water | HYDRON MODULE | HBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268209 | Ground Water | TETCO | TBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
202443455 | Ground Water | GeoSmart Energy | GS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202443457 | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202443458 | Ground Water | GeoSmart Energy | GS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202443459 | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202443460 | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
8786558 | Ground Water | GeoSmart Energy | GS018**1*(1,4)********H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8786559 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8786562 | Ground Water | GEOSTAR | 101/102H018**1*0***** |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8786563 | Ground Water | GeoSmart Energy | GS018**1*0********H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8786564 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*0****H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8789580 | Ground Water | GEOSTAR | 101/102H022**1*(0,3)***** |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8789581 | Ground Water | GeoSmart Energy | GS022**1*(0,3)********H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
7493299 | Ground Water | GeoSmart Energy | YT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
7493316 | Ground Water | GEOSTAR | 12(1,2)A048 |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
214855069 | Ground Water | WHALEN | CASH*036AJ**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855070 | Ground Water | WHALEN | CASH*036AM**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855071 | Ground Water | WHALEN | CASV*036AB**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855072 | Ground Water | WHALEN | CASV*036AD**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855073 | Ground Water | WHALEN | CASV*036AJ**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855074 | Ground Water | WHALEN | CASV*036AM**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855075 | Ground Water | WHALEN | CASH*042AB**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330367 | Ground Water | AAON, Inc. | WV-019-1-H-ACAC-C0-10-200-A |  | 21400 | 27 | 17000 | 4.1 | 1.7833 | No
6966789 | Ground Water | TRANE | EXVF0127 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
6966837 | Ground Water | TRANE | EXVF0151 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
6966860 | Ground Water | TRANE | EXVF0152 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
205993155 | Ground Water | GEOCOMFORT | GBT024 | GED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993156 | Ground Water | GEOCOMFORT | GBT024 | GAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993157 | Ground Water | HYDRON MODULE | HBT024 | HED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993158 | Ground Water | HYDRON MODULE | HBT024 | HAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993159 | Ground Water | TETCO | TBT024 | TED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993160 | Ground Water | TETCO | TBT024 | TAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993161 | Ground Water | GEOCOMFORT | GBT024*2 | GED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
10443595 | Ground Water | TETCO | TBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443596 | Ground Water | GEOCOMFORT | GBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443597 | Ground Water | HYDRON MODULE | HBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443598 | Ground Water | TETCO | TBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10445242 | Ground Water | WaterFurnace | SDV049H1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
10581108 | Ground Water | 5 SERIES | NDP026H1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
204344184 | Ground Water | 7 SERIES | NVV/NVH036B1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
204452547 | Ground Water | GeoSmart Energy | VI036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
204457696 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
204474784 | Ground Water | GEOSTAR | 141/142B036**1*(1,2) |  | 38000 | 31.5 | 41000 | 4.6 | 3.1667 | No
10268198 | Ground Water | GEOCOMFORT | GBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268199 | Ground Water | HYDRON MODULE | HBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268200 | Ground Water | TETCO | TBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268201 | Ground Water | GEOCOMFORT | GBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268202 | Ground Water | HYDRON MODULE | HBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
8786547 | Ground Water | GEOSTAR | 101/102H072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8786548 | Ground Water | GeoSmart Energy | GT072**1*(1,4)********H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8786549 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8786552 | Ground Water | GEOSTAR | 101/102H012**1*0***** |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786553 | Ground Water | GeoSmart Energy | GS012**1*0********H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786554 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS012**1*0****H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786557 | Ground Water | GEOSTAR | 101/102H018**1*(1,4)***** |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7499468 | Ground Water | FHP | EP030-4HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499480 | Ground Water | FHP | EP060-1HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499482 | Ground Water | FHP | EP060-3HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499483 | Ground Water | FHP | EP060-4HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499484 | Ground Water | FHP | EP070-1HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7499485 | Ground Water | FHP | EP070-3HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7499487 | Ground Water | FHP | EP070-4HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
214855062 | Ground Water | WHALEN | CASH*030AM**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855063 | Ground Water | WHALEN | CASV*030AB**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855064 | Ground Water | WHALEN | CASV*030AD**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855065 | Ground Water | WHALEN | CASV*030AJ**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855066 | Ground Water | WHALEN | CASV*030AM**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855067 | Ground Water | WHALEN | CASH*036AB**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855068 | Ground Water | WHALEN | CASH*036AD**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330355 | Ground Water | AAON, Inc. | WV-015-1-H-ACAC-C0-10-200-A |  | 16600 | 25.7 | 14700 | 4.2 | 1.3833 | No
202330356 | Ground Water | AAON, Inc. | WV-015-A-H-ACAC-C0-10-200-A |  | 16600 | 25.7 | 14700 | 4.2 | 1.3833 | No
202330359 | Ground Water | AAON, Inc. | WV-016-1-H-ACAC-C0-10-200-A |  | 17200 | 27.1 | 14800 | 4.2 | 1.4333 | No
202330360 | Ground Water | AAON, Inc. | WV-016-A-H-ACAC-C0-10-200-A |  | 17200 | 27.1 | 14800 | 4.2 | 1.4333 | No
6966727 | Ground Water | TRANE | EXVF0121 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
6966753 | Ground Water | TRANE | EXVF0122 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
207178494 | Ground Water | GEOSTAR | 161/162J049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5296247 | Ground Water | TRANE | EXVF0241 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
5296248 | Ground Water | TRANE | EXVF0242 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
5296249 | Ground Water | TRANE | EXVF0247 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
4230750 | Ground Water | DAIKIN | WCCW4024*E*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
4230752 | Ground Water | DAIKIN | WCCW4024*F*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
4230754 | Ground Water | DAIKIN | WCCW4024*J*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
4231098 | Ground Water | DAIKIN | WCCW4024*K*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
202350521 | Ground Water | AAON, Inc. | WV-036-2-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202350522 | Ground Water | AAON, Inc. | WV-042-1-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202350523 | Ground Water | AAON, Inc. | WV-042-2-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202350524 | Ground Water | AAON, Inc. | WV-048-1-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202350526 | Ground Water | AAON, Inc. | WV-048-2-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202330763 | Ground Water | WHALEN | CASH*024AJ**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330764 | Ground Water | WHALEN | CASV*024AJ**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330765 | Ground Water | WHALEN | CASH*024AM**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330766 | Ground Water | WHALEN | CASV*024AM**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330767 | Ground Water | WHALEN | CASH*030AJ**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330768 | Ground Water | WHALEN | CASV*030AJ**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330769 | Ground Water | WHALEN | CASH*030AM**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330467 | Ground Water | AAON, Inc. | RN-006-3-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
202330468 | Ground Water | AAON, Inc. | RN-006-4-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
202330472 | Ground Water | AAON, Inc. | RN-007-2-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330473 | Ground Water | AAON, Inc. | RN-007-3-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330474 | Ground Water | AAON, Inc. | RN-007-4-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330573 | Ground Water | AAON, Inc. | WH-006-B-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330574 | Ground Water | AAON, Inc. | WH-006-1-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330375 | Ground Water | AAON, Inc. | WV-024-2-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330376 | Ground Water | AAON, Inc. | WV-024-3-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330379 | Ground Water | AAON, Inc. | WV-030-1-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330380 | Ground Water | AAON, Inc. | WV-030-A-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330282 | Ground Water | AAON, Inc. | WH-018-A-H-ACAC-C0-10-100-A |  | 19600 | 23.5 | 17600 | 4.6 | 1.6333 | No
5295950 | Ground Water | TRANE | EXHF0301 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295951 | Ground Water | TRANE | EXHF0302 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295952 | Ground Water | TRANE | EXHF0307 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295953 | Ground Water | TRANE | EXHF0361 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295954 | Ground Water | TRANE | EXHF0362 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295955 | Ground Water | TRANE | EXHF0367 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295956 | Ground Water | TRANE | EXHF0363 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
10268263 | Ground Water | GEOCOMFORT | GBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268264 | Ground Water | HYDRON MODULE | HBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268265 | Ground Water | TETCO | TBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268268 | Ground Water | GEOCOMFORT | GBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268269 | Ground Water | HYDRON MODULE | HBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268270 | Ground Water | TETCO | TBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268271 | Ground Water | GEOCOMFORT | GBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
202391377 | Ground Water | AQUARIUS | EP012-0VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391378 | Ground Water | AQUARIUS | EP012-2VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391379 | Ground Water | AQUARIUS | EP012-0HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391380 | Ground Water | AQUARIUS | EP012-2HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391433 | Ground Water | FHP | EP012-2HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391434 | Ground Water | FHP | EP012-0HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391435 | Ground Water | FHP | EP012-2VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
8105933 | Ground Water | TRANE | DXHF0703 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105934 | Ground Water | TRANE | DXHF0704 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105935 | Ground Water | TRANE | DXHF0708 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105950 | Ground Water | TRANE | DXVF0241 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105955 | Ground Water | TRANE | DXVF0242 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105956 | Ground Water | TRANE | DXVF0243 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105960 | Ground Water | TRANE | DXVF0244 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
7167343 | Ground Water | CARRIER | 50PSH/V024***4/DA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7167344 | Ground Water | CARRIER | 50PSH/V030***4/DA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167345 | Ground Water | CARRIER | 50PSH/V030***6/FA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167346 | Ground Water | CARRIER | 50PSH/V030***5/EA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167347 | Ground Water | CARRIER | 50PSH/V030***3/CA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167357 | Ground Water | CARRIER | 50PSH/V060***6/FA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7167358 | Ground Water | CARRIER | 50PSH/V060***5/EA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
5296264 | Ground Water | TRANE | EXVF0428 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296265 | Ground Water | TRANE | EXVF0481 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296266 | Ground Water | TRANE | EXVF0482 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296267 | Ground Water | TRANE | EXVF0483 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296268 | Ground Water | TRANE | EXVF0484 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
205993113 | Ground Water | GEOCOMFORT | GBS018 | GED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993114 | Ground Water | GEOCOMFORT | GBS018 | GAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993115 | Ground Water | HYDRON MODULE | HBS018 | HED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993116 | Ground Water | HYDRON MODULE | HBS018 | HAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993117 | Ground Water | TETCO | TBS018 | TED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993118 | Ground Water | TETCO | TBS018 | TAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993119 | Ground Water | GEOCOMFORT | GBS018*2 | GED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
3919846 | Ground Water | AQUARIUS | EP007-2HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
3919847 | Ground Water | AQUARIUS | EP007-1HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
214855083 | Ground Water | WHALEN | CASH*048AB**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855084 | Ground Water | WHALEN | CASH*048AD**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855085 | Ground Water | WHALEN | CASH*048AJ**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855086 | Ground Water | WHALEN | CASH*048AM**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855087 | Ground Water | WHALEN | CASV*048AB**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855088 | Ground Water | WHALEN | CASV*048AD**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855089 | Ground Water | WHALEN | CASV*048AJ**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330777 | Ground Water | WHALEN | CASH*042AM**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330778 | Ground Water | WHALEN | CASV*042AM**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330779 | Ground Water | WHALEN | CASH*048AJ**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330780 | Ground Water | WHALEN | CASV*048AJ**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330781 | Ground Water | WHALEN | CASH*048AM**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330782 | Ground Water | WHALEN | CASV*048AM**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330783 | Ground Water | WHALEN | CASH*060AJ**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330748 | Ground Water | WHALEN | CASH*036AD**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330749 | Ground Water | WHALEN | CASV*036AD**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330750 | Ground Water | WHALEN | CASH*042AB**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330751 | Ground Water | WHALEN | CASV*042AB**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330752 | Ground Water | WHALEN | CASH*042AD**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330753 | Ground Water | WHALEN | CASV*042AD**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330754 | Ground Water | WHALEN | CASH*048AB**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
205993176 | Ground Water | HYDRON MODULE | HBT072*2 | HAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
205993178 | Ground Water | TETCO | TBT072*2 | TAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
205993179 | Ground Water | GEOCOMFORT | GBT060 | GAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
205993180 | Ground Water | HYDRON MODULE | HBT060 | HAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
205993181 | Ground Water | TETCO | TBT060 | TAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
205993182 | Ground Water | GEOCOMFORT | GBT060*2 | GAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
10443577 | Ground Water | GEOCOMFORT | GBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443578 | Ground Water | HYDRON MODULE | HBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443579 | Ground Water | TETCO | TBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443580 | Ground Water | GEOCOMFORT | GBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443581 | Ground Water | HYDRON MODULE | HBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443582 | Ground Water | TETCO | TBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443583 | Ground Water | GEOCOMFORT | GBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
203490416 | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
203494005 | Ground Water | GEOSTAR | 101/102J048**1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
203495471 | Ground Water | GEOSTAR | 101/102J048**1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
4219428 | Ground Water | NORDIC | RH25HACW-P-1T-*-SDE** |  | 26200 | 22 | 22500 | 4.2 | 2.1833 | No
4219442 | Ground Water | NORDIC | RS25HACW-P-1T-* | AH-25-P-1-***** | 26800 | 23.1 | 23100 | 4.4 | 2.2333 | No
203113882 | Ground Water | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
203113884 | Ground Water | GEOSTAR | 101/102J042**1*(0,3)***** |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
203113887 | Ground Water | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
202391369 | Ground Water | AQUARIUS | EP012-1VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
8105926 | Ground Water | TRANE | DXHF0481 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105927 | Ground Water | TRANE | DXHF0482 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105928 | Ground Water | TRANE | DXHF0483 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105929 | Ground Water | TRANE | DXHF0484 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105930 | Ground Water | TRANE | DXHF0488 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105931 | Ground Water | TRANE | DXHF0701 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105932 | Ground Water | TRANE | DXHF0702 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
7499447 | Ground Water | FHP | EP007-1HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7499448 | Ground Water | FHP | EP007-2HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7499450 | Ground Water | FHP | EP009-1HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7499451 | Ground Water | FHP | EP009-2HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7499453 | Ground Water | FHP | EP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
7499455 | Ground Water | FHP | EP015-1HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7499456 | Ground Water | FHP | EP015-2HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
214855055 | Ground Water | WHALEN | CASV*024AB**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855056 | Ground Water | WHALEN | CASV*024AD**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855057 | Ground Water | WHALEN | CASV*024AJ**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855058 | Ground Water | WHALEN | CASV*024AM**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855059 | Ground Water | WHALEN | CASH*030AB**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855060 | Ground Water | WHALEN | CASH*030AD**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855061 | Ground Water | WHALEN | CASH*030AJ**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330347 | Ground Water | AAON, Inc. | WV-009-B-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
202330348 | Ground Water | AAON, Inc. | WV-009-1-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
202330349 | Ground Water | AAON, Inc. | WV-009-A-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
202330350 | Ground Water | AAON, Inc. | WV-012-B-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
202330351 | Ground Water | AAON, Inc. | WV-012-1-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
202330352 | Ground Water | AAON, Inc. | WV-012-A-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
6965857 | Ground Water | TRANE | EXHF0121 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
6965858 | Ground Water | TRANE | EXHF0122 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
6965859 | Ground Water | TRANE | EXHF0127 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
5295943 | Ground Water | TRANE | EXHF0241 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
5295946 | Ground Water | TRANE | EXHF0242 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
5295949 | Ground Water | TRANE | EXHF0247 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
3919848 | Ground Water | AQUARIUS | EP009-1HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
3919850 | Ground Water | AQUARIUS | EP009-2HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
3919853 | Ground Water | AQUARIUS | EP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
3919854 | Ground Water | AQUARIUS | EP015-1HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
3919855 | Ground Water | AQUARIUS | EP015-2HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
3919884 | Ground Water | AQUARIUS | EP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
3919931 | Ground Water | AQUARIUS | EP024-2HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
202391436 | Ground Water | FHP | EP012-0VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391437 | Ground Water | FHP | EP012-2HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391438 | Ground Water | FHP | EP012-0HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391439 | Ground Water | FHP | EP012-2VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391440 | Ground Water | FHP | EP012-0VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391441 | Ground Water | FHP | EP012-1HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391442 | Ground Water | FHP | EP012-1VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
8105972 | Ground Water | TRANE | DXVF0368 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105973 | Ground Water | TRANE | DXVF0481 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105974 | Ground Water | TRANE | DXVF0482 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105975 | Ground Water | TRANE | DXVF0483 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105976 | Ground Water | TRANE | DXVF0484 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105977 | Ground Water | TRANE | DXVF0488 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105978 | Ground Water | TRANE | DXVF0601 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
202330391 | Ground Water | AAON, Inc. | WV-036-2-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330392 | Ground Water | AAON, Inc. | WV-036-3-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330395 | Ground Water | AAON, Inc. | WV-042-1-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330319 | Ground Water | AAON, Inc. | WH-042-2-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330320 | Ground Water | AAON, Inc. | WH-042-3-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330321 | Ground Water | AAON, Inc. | WH-048-1-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330322 | Ground Water | AAON, Inc. | WH-048-A-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
10443497 | Ground Water | HYDRON MODULE | HBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443498 | Ground Water | TETCO | TBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443499 | Ground Water | GEOCOMFORT | GBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443500 | Ground Water | HYDRON MODULE | HBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443501 | Ground Water | TETCO | TBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443502 | Ground Water | GEOCOMFORT | GBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443503 | Ground Water | HYDRON MODULE | HBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
3920503 | Ground Water | AQUARIUS | EP070-1HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
3920504 | Ground Water | AQUARIUS | EP070-3HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
3920505 | Ground Water | AQUARIUS | EP070-4HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
202330784 | Ground Water | WHALEN | CASV*060AJ**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330785 | Ground Water | WHALEN | CASH*060AM**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330786 | Ground Water | WHALEN | CASV*060AM**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202350093 | Ground Water | 5 SERIES | NSV/NSH036J1*(0,3) |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202350094 | Ground Water | 5 SERIES | NSV/NSH042J1*(0,3) |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202350095 | Ground Water | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202350096 | Ground Water | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
202330755 | Ground Water | WHALEN | CASV*048AB**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330756 | Ground Water | WHALEN | CASH*048AD**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330757 | Ground Water | WHALEN | CASV*048AD**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330758 | Ground Water | WHALEN | CASH*060AB**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330759 | Ground Water | WHALEN | CASV*060AB**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330760 | Ground Water | WHALEN | CASH*060AD**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330761 | Ground Water | WHALEN | CASV*060AD**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
7167359 | Ground Water | CARRIER | 50PSH/V060***3/CA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7167360 | Ground Water | CARRIER | 50PSH/V070***3/CA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7167361 | Ground Water | CARRIER | 50PSH/V070***5/EA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7167362 | Ground Water | CARRIER | 50PSH/V070***6/FA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
202330339 | Ground Water | AAON, Inc. | WH-036-A-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202330340 | Ground Water | AAON, Inc. | WH-036-3-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202330343 | Ground Water | AAON, Inc. | WH-048-A-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202330344 | Ground Water | AAON, Inc. | WH-048-3-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
206315249 | Ground Water | WHALEN | CASH*015AB**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315250 | Ground Water | WHALEN | CASV*015AB**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315251 | Ground Water | WHALEN | CASH*015AD**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315252 | Ground Water | WHALEN | CASV*015AD**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315253 | Ground Water | WHALEN | CASH*018AB**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206315254 | Ground Water | WHALEN | CASV*018AB**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206315255 | Ground Water | WHALEN | CASH*018AD**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
205993148 | Ground Water | TETCO | TBT048*2 | TAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993149 | Ground Water | GEOCOMFORT | GBT060 | GED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993150 | Ground Water | HYDRON MODULE | HBT060 | HED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993151 | Ground Water | TETCO | TBT060 | TED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993152 | Ground Water | GEOCOMFORT | GBT060*2 | GED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993153 | Ground Water | HYDRON MODULE | HBT060*2 | HED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993154 | Ground Water | TETCO | TBT060*2 | TED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205448524 | Ground Water | 7 SERIES INDOOR SPLITS | NVZ033A1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | No
204031802 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
204031806 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
202330770 | Ground Water | WHALEN | CASV*030AM**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330771 | Ground Water | WHALEN | CASH*036AJ**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330772 | Ground Water | WHALEN | CASV*036AJ**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330773 | Ground Water | WHALEN | CASH*036AM**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330774 | Ground Water | WHALEN | CASV*036AM**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330775 | Ground Water | WHALEN | CASH*042AJ**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330776 | Ground Water | WHALEN | CASV*042AJ**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330741 | Ground Water | WHALEN | CASV*024AD**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330742 | Ground Water | WHALEN | CASH*030AB**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330743 | Ground Water | WHALEN | CASV*030AB**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330744 | Ground Water | WHALEN | CASH*030AD**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330745 | Ground Water | WHALEN | CASV*030AD**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330746 | Ground Water | WHALEN | CASH*036AB**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330747 | Ground Water | WHALEN | CASV*036AB**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
7167332 | Ground Water | CARRIER | 50PSH/V007***4/DA |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
6936993 | Ground Water | BARD | GTC60S2-A | HE49948D210B2705AW | 67500 | 21.56 | 61500 | 4.3 | 5.625 | No
205993183 | Ground Water | HYDRON MODULE | HBT060*2 | HAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
205993184 | Ground Water | TETCO | TBT060*2 | TAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
10443584 | Ground Water | HYDRON MODULE | HBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443585 | Ground Water | TETCO | TBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443586 | Ground Water | GEOCOMFORT | GBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443587 | Ground Water | HYDRON MODULE | HBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443588 | Ground Water | TETCO | TBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443593 | Ground Water | GEOCOMFORT | GBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443594 | Ground Water | HYDRON MODULE | HBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
204031808 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
202391370 | Ground Water | AQUARIUS | EP012-1HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391371 | Ground Water | AQUARIUS | EP012-1VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391372 | Ground Water | AQUARIUS | EP012-1HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391373 | Ground Water | AQUARIUS | EP012-0VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391374 | Ground Water | AQUARIUS | EP012-2VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391375 | Ground Water | AQUARIUS | EP012-0HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391376 | Ground Water | AQUARIUS | EP012-2HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
8105965 | Ground Water | TRANE | DXVF0247 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105966 | Ground Water | TRANE | DXVF0248 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105967 | Ground Water | TRANE | DXVF0361 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105968 | Ground Water | TRANE | DXVF0362 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105969 | Ground Water | TRANE | DXVF0363 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105970 | Ground Water | TRANE | DXVF0364 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105971 | Ground Water | TRANE | DXVF0367 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
202330575 | Ground Water | AAON, Inc. | WH-006-A-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330576 | Ground Water | AAON, Inc. | WV-006-B-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330577 | Ground Water | AAON, Inc. | WV-006-1-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330578 | Ground Water | AAON, Inc. | WV-006-A-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330738 | Ground Water | WHALEN | CASH*024AB**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330739 | Ground Water | WHALEN | CASV*024AB**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330740 | Ground Water | WHALEN | CASH*024AD**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
207348743 | Ground Water | WaterFurnace | URT096*3*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
207348744 | Ground Water | WaterFurnace | URT096*4*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
207213249 | Ground Water | GeoSmart Energy | YT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
201846902 | Ground Water | GEOSTAR | 111H038**1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
5360714 | Ground Water | BARD | GTC36S2-A | GTADP-3642-* | 42000 | 23.9 | 38000 | 5 | 3.5 | No
5360715 | Ground Water | BARD | GTC48S2-A | GTADP-4860-C | 54500 | 23.5 | 48000 | 4.55 | 4.5417 | No
5360791 | Ground Water | BARD | GTC60S2-A | GTADP-4860-C | 67500 | 21.56 | 61500 | 4.3 | 5.625 | No
5440741 | Ground Water | 7 SERIES | NVV/NVH048A1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
5440778 | Ground Water | 7 SERIES | NVV/NVH060A1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
205993120 | Ground Water | GEOCOMFORT | GBS018*2 | GAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993121 | Ground Water | HYDRON MODULE | HBS018*2 | HED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993122 | Ground Water | HYDRON MODULE | HBS018*2 | HAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993123 | Ground Water | TETCO | TBS018*2 | TED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993124 | Ground Water | TETCO | TBS018*2 | TAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993125 | Ground Water | GEOCOMFORT | GBT036 | GED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993126 | Ground Water | GEOCOMFORT | GBT036 | GAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
8786527 | Ground Water | GEOSTAR | 101/102H026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
8786528 | Ground Water | GeoSmart Energy | GT026**1*(1,4)********H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
8786529 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214855104 | Ground Water | WHALEN | CASV*060AD**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855105 | Ground Water | WHALEN | CASV*060AJ**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855106 | Ground Water | WHALEN | CASV*060AM**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202350506 | Ground Water | AAON, Inc. | WH-036-1-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202350507 | Ground Water | AAON, Inc. | WH-036-2-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202350510 | Ground Water | AAON, Inc. | WH-048-1-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
214855043 | Ground Water | WHALEN | CASH*015AB**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855044 | Ground Water | WHALEN | CASH*015AD**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855045 | Ground Water | WHALEN | CASV*015AB**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855046 | Ground Water | WHALEN | CASV*015AD**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855047 | Ground Water | WHALEN | CASH*018AB**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
6945298 | Ground Water | BARD | GTC48S2-A | HE49948D210B2705AW | 54500 | 23.5 | 48000 | 4.55 | 4.5417 | No
10443504 | Ground Water | TETCO | TBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443509 | Ground Water | GEOCOMFORT | GBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443510 | Ground Water | HYDRON MODULE | HBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443511 | Ground Water | TETCO | TBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443512 | Ground Water | GEOCOMFORT | GBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443513 | Ground Water | HYDRON MODULE | HBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443514 | Ground Water | TETCO | TBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
5295957 | Ground Water | TRANE | EXHF0368 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295958 | Ground Water | TRANE | EXHF0364 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295959 | Ground Water | TRANE | EXHF0421 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295961 | Ground Water | TRANE | EXHF0422 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295963 | Ground Water | TRANE | EXHF0423 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295965 | Ground Water | TRANE | EXHF0424 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295967 | Ground Water | TRANE | EXHF0428 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
10268272 | Ground Water | HYDRON MODULE | HBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268273 | Ground Water | TETCO | TBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268274 | Ground Water | GEOCOMFORT | GBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268275 | Ground Water | HYDRON MODULE | HBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268276 | Ground Water | TETCO | TBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268277 | Ground Water | GEOCOMFORT | GBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268278 | Ground Water | HYDRON MODULE | HBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
9951968 | Ground Water | BARD | GV27S3AA |  | 26600 | 22.8 | 26200 | 5 | 2.2167 | No
9951969 | Ground Water | BARD | GV38S3AA |  | 41400 | 22 | 38600 | 4.7 | 3.45 | No
9951970 | Ground Water | BARD | GV51S3AA |  | 53500 | 21.7 | 49500 | 4.45 | 4.4583 | No
202350511 | Ground Water | AAON, Inc. | WH-048-2-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202350514 | Ground Water | AAON, Inc. | WV-024-1-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202350515 | Ground Water | AAON, Inc. | WV-024-1-H-DCAC-C0-10-D00-A |  | 29000 | 22.7 | 21800 | 4.4 | 2.4167 | No
202350516 | Ground Water | AAON, Inc. | WV-024-2-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202350517 | Ground Water | AAON, Inc. | WV-030-1-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202350518 | Ground Water | AAON, Inc. | WV-030-2-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202350519 | Ground Water | AAON, Inc. | WV-036-1-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202330303 | Ground Water | AAON, Inc. | WH-030-2-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
202330304 | Ground Water | AAON, Inc. | WH-030-3-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
202330305 | Ground Water | AAON, Inc. | WH-036-1-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330306 | Ground Water | AAON, Inc. | WH-036-A-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330307 | Ground Water | AAON, Inc. | WH-036-1-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330308 | Ground Water | AAON, Inc. | WH-036-A-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330309 | Ground Water | AAON, Inc. | WH-036-2-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330271 | Ground Water | AAON, Inc. | WH-009-B-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
202330272 | Ground Water | AAON, Inc. | WH-009-1-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
202330273 | Ground Water | AAON, Inc. | WH-009-A-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
205993141 | Ground Water | TETCO | TBT048 | TED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993142 | Ground Water | TETCO | TBT048 | TAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993143 | Ground Water | GEOCOMFORT | GBT048*2 | GED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993144 | Ground Water | GEOCOMFORT | GBT048*2 | GAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993145 | Ground Water | HYDRON MODULE | HBT048*2 | HED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993146 | Ground Water | HYDRON MODULE | HBT048*2 | HAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993147 | Ground Water | TETCO | TBT048*2 | TED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
5295970 | Ground Water | TRANE | EXHF0481 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295971 | Ground Water | TRANE | EXHF0482 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295972 | Ground Water | TRANE | EXHF0483 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295973 | Ground Water | TRANE | EXHF0484 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295974 | Ground Water | TRANE | EXHF0488 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
10268279 | Ground Water | TETCO | TBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10318053 | Ground Water | GEOSTAR | 103H060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10443493 | Ground Water | GEOCOMFORT | GBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443494 | Ground Water | HYDRON MODULE | HBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443495 | Ground Water | TETCO | TBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443496 | Ground Water | GEOCOMFORT | GBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
3920297 | Ground Water | AQUARIUS | EP030-2HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920298 | Ground Water | AQUARIUS | EP030-4HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920299 | Ground Water | AQUARIUS | EP030-3HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920300 | Ground Water | AQUARIUS | EP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920500 | Ground Water | AQUARIUS | EP060-4HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
3920501 | Ground Water | AQUARIUS | EP060-3HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
3920502 | Ground Water | AQUARIUS | EP060-1HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
202923075 | Ground Water | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
203113881 | Ground Water | GEOSTAR | 101/102J036**1*(0,3)***** |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202391443 | Ground Water | FHP | EP012-1HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391444 | Ground Water | FHP | EP012-1VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391445 | Ground Water | CARRIER | 50PSV012**C3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391446 | Ground Water | CARRIER | 50PSH012**C3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391447 | Ground Water | CARRIER | 50PSV012**N3/CA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391448 | Ground Water | CARRIER | 50PSH012**N3/CA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391449 | Ground Water | CARRIER | 50PSV012**C0/BA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
8105979 | Ground Water | TRANE | DXVF0602 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105980 | Ground Water | TRANE | DXVF0603 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105981 | Ground Water | TRANE | DXVF0604 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105982 | Ground Water | TRANE | DXVF0608 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105983 | Ground Water | TRANE | DXVF0701 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8105984 | Ground Water | TRANE | DXVF0702 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8105985 | Ground Water | TRANE | DXVF0703 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
202330403 | Ground Water | AAON, Inc. | WV-048-1-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330404 | Ground Water | AAON, Inc. | WV-048-A-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330407 | Ground Water | AAON, Inc. | WV-048-2-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330408 | Ground Water | AAON, Inc. | WV-048-3-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330417 | Ground Water | AAON, Inc. | WV-024-A-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202330383 | Ground Water | AAON, Inc. | WV-030-2-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330384 | Ground Water | AAON, Inc. | WV-030-3-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330387 | Ground Water | AAON, Inc. | WV-036-1-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330388 | Ground Water | AAON, Inc. | WV-036-A-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330310 | Ground Water | AAON, Inc. | WH-036-3-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330311 | Ground Water | AAON, Inc. | WH-036-2-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330312 | Ground Water | AAON, Inc. | WH-036-3-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330328 | Ground Water | AAON, Inc. | WH-048-3-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
5296250 | Ground Water | TRANE | EXVF0301 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296251 | Ground Water | TRANE | EXVF0302 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296252 | Ground Water | TRANE | EXVF0307 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296253 | Ground Water | TRANE | EXVF0361 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296254 | Ground Water | TRANE | EXVF0362 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296255 | Ground Water | TRANE | EXVF0363 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296256 | Ground Water | TRANE | EXVF0364 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
205448525 | Ground Water | 7 SERIES INDOOR SPLITS | NVZ042A1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | No
205536324 | Ground Water | AAON, Inc. | WH-072-2-H-DCAC-C0-10-200-A |  | 91000 | 24 | 75800 | 4.3 | 7.5833 | No
205536327 | Ground Water | AAON, Inc. | WH-072-3-H-DCAC-C0-10-200-A |  | 91000 | 24 | 75800 | 4.3 | 7.5833 | No
205536344 | Ground Water | AAON, Inc. | WV-072-2-0-DCAC-C0-10-200-A |  | 90800 | 25 | 79800 | 4.9 | 7.5667 | No
10268233 | Ground Water | GEOCOMFORT | GBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268234 | Ground Water | HYDRON MODULE | HBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268235 | Ground Water | TETCO | TBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268236 | Ground Water | GEOCOMFORT | GBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268237 | Ground Water | HYDRON MODULE | HBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268238 | Ground Water | TETCO | TBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268244 | Ground Water | GEOCOMFORT | GBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
202443465 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202443466 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202443467 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202443468 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202443469 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
8105913 | Ground Water | TRANE | DXHF0248 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105914 | Ground Water | TRANE | DXHF0361 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105916 | Ground Water | TRANE | DXHF0362 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105922 | Ground Water | TRANE | DXHF0363 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105923 | Ground Water | TRANE | DXHF0364 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105924 | Ground Water | TRANE | DXHF0367 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105925 | Ground Water | TRANE | DXHF0368 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
202330418 | Ground Water | AAON, Inc. | WV-024-A-H-DCAC-C0-10-D00-A |  | 29000 | 22.7 | 21800 | 4.4 | 2.4167 | No
202330419 | Ground Water | AAON, Inc. | WV-024-3-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202330420 | Ground Water | AAON, Inc. | WV-030-A-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202330421 | Ground Water | AAON, Inc. | WV-030-3-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202330422 | Ground Water | AAON, Inc. | WV-036-A-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202330424 | Ground Water | AAON, Inc. | WV-036-3-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
7167333 | Ground Water | CARRIER | 50PSH/V007***3/CA |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7167334 | Ground Water | CARRIER | 50PSH/V009***3/CA |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7167335 | Ground Water | CARRIER | 50PSH/V009***4/DA |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7167337 | Ground Water | CARRIER | 50PSH/V012***3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
7167338 | Ground Water | CARRIER | 50PSH/V015***3/CA |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7167339 | Ground Water | CARRIER | 50PSH/V015***4/DA |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7167342 | Ground Water | CARRIER | 50PSH/V024***3/CA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
6966875 | Ground Water | TRANE | EXVF0157 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
7076986 | Ground Water | AQUARIUS | EP024-3HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7076987 | Ground Water | AQUARIUS | EP024-4HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
207200569 | Ground Water | GeoSmart Energy | GS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
207200570 | Ground Water | GeoSmart Energy | GS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
207200571 | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207200572 | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
207200573 | Ground Water | GeoSmart Energy | GS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
207200574 | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
202330277 | Ground Water | AAON, Inc. | WH-015-1-H-ACAC-C0-10-100-A |  | 16500 | 26.1 | 14600 | 4.9 | 1.375 | No
202330278 | Ground Water | AAON, Inc. | WH-015-A-H-ACAC-C0-10-100-A |  | 16500 | 26.1 | 14600 | 4.9 | 1.375 | No
202330279 | Ground Water | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 17100 | 29.9 | 14400 | 5.2 | 1.425 | No
202330280 | Ground Water | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 17100 | 29.9 | 14400 | 5.2 | 1.425 | No
202330281 | Ground Water | AAON, Inc. | WH-018-1-H-ACAC-C0-10-100-A |  | 19600 | 23.5 | 17600 | 4.6 | 1.6333 | No
207178526 | Ground Water | GEOSTAR | 161/162H026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207178527 | Ground Water | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207178547 | Ground Water | GEOSTAR | 161/162H072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207200554 | Ground Water | GeoSmart Energy | GT026**1*(1,4)*H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207200555 | Ground Water | GeoSmart Energy | GT072**1*(1,4)*H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207200556 | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207200557 | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207335405 | Ground Water | GeoSmart Energy | GS022**1*(0,3)*J |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
207337519 | Ground Water | GEOSTAR | 103H060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
207337520 | Ground Water | GEOSTAR | 103H060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
8789582 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3)****H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8789586 | Ground Water | GEOSTAR | 101/102H022**1*(1,4)***** |  | 21900 | 27.5 | 19500 | 5 | 1.825 | No
8789591 | Ground Water | GEOSTAR | 101/102H030**1*(0,3)***** |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789592 | Ground Water | GeoSmart Energy | GS030**1*(0,3)********H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789593 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789596 | Ground Water | GEOSTAR | 101/102H030**1*(1,4)***** |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8789597 | Ground Water | GeoSmart Energy | GS030**1*(1,4)********H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8103479 | Ground Water | TRANE | DXHF0241 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105907 | Ground Water | TRANE | DXHF0242 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105909 | Ground Water | TRANE | DXHF0243 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105911 | Ground Water | TRANE | DXHF0244 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105912 | Ground Water | TRANE | DXHF0247 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
202330324 | Ground Water | AAON, Inc. | WH-048-A-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
202330325 | Ground Water | AAON, Inc. | WH-048-2-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330326 | Ground Water | AAON, Inc. | WH-048-3-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330327 | Ground Water | AAON, Inc. | WH-048-2-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
205993170 | Ground Water | HYDRON MODULE | HBT072 | HAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
205993172 | Ground Water | TETCO | TBT072 | TAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
205993174 | Ground Water | GEOCOMFORT | GBT072*2 | GAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
10581109 | Ground Water | 5 SERIES | NDP038H1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581110 | Ground Water | 5 SERIES | NDP049H1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
10581111 | Ground Water | 5 SERIES | NDP064H1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
10581112 | Ground Water | 5 SERIES | NDP072H1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
10581113 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT026**1*1******H |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
10581114 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581115 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT049**1*1******H |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
10206404 | Ground Water | BARD | GTC36S2-A | HE37942D210B2505AW | 42000 | 23.9 | 38000 | 5 | 3.5 | No
10206405 | Ground Water | BARD | GTC36S2-A | HE37942D175B2505AW | 42000 | 23.9 | 38000 | 5 | 3.5 | No
8560801 | Ground Water | 5 SERIES | NSV/NSH030H1*(1,4) |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8560806 | Ground Water | 5 SERIES | NSV/NSH070H1*(1,4) |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8570181 | Ground Water | 5 SERIES | NDV/NDH072H1*(1,4) |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214855097 | Ground Water | WHALEN | CASH*060AJ**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855098 | Ground Water | WHALEN | CASH*060AM**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855099 | Ground Water | WHALEN | CASV*054AB**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855100 | Ground Water | WHALEN | CASV*054AD**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855101 | Ground Water | WHALEN | CASV*054AJ**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855102 | Ground Water | WHALEN | CASV*054AM**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855103 | Ground Water | WHALEN | CASV*060AB**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202350098 | Ground Water | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202350414 | Ground Water | AAON, Inc. | RN-009-2-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
202350415 | Ground Water | AAON, Inc. | RN-009-3-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
202330315 | Ground Water | AAON, Inc. | WH-042-1-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330316 | Ground Water | AAON, Inc. | WH-042-A-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No

## Commercial Ground Loop HP
AHRI Certified Reference Number | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage | Tax Credit (IRA) Eligibility
206438907 | Ground Loop | CARRIER | 50PSV012**C0/BA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438908 | Ground Loop | CARRIER | 50PSV012**C4/DA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438909 | Ground Loop | CARRIER | 50PSH012**C0/BA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438910 | Ground Loop | CARRIER | 50PSH012**C4/DA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
215415772 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)015A*VB |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415773 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)015A*VC |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415776 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)018A*VB |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415777 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)018A*VC |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415778 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)024A*B |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415779 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)024A*C |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415780 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)024A*VB |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415781 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)024A*VC |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415784 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)030A*VB |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415785 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)030A*VC |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415788 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)036A*VB |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
215415789 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)036A*VC |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
217351892 | Ground Loop | KEEPRITE | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351893 | Ground Loop | KEEPRITE | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351896 | Ground Loop | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351897 | Ground Loop | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351898 | Ground Loop | KEEPRITE | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351900 | Ground Loop | KEEPRITE | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351901 | Ground Loop | KEEPRITE | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351903 | Ground Loop | KEEPRITE | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
216625866 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625867 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625868 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625869 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625870 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625871 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625872 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625873 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625874 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625875 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625876 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625877 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625878 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625879 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625880 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625881 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216687113 | Ground Loop | WaterFurnace | W5SS024BD1 | W5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216687114 | Ground Loop | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216687115 | Ground Loop | WaterFurnace | W5SS048BD1 | W5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216687116 | Ground Loop | WaterFurnace | W5SS060BD1 | W5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216687118 | Ground Loop | WaterFurnace | W5SZ024BD1 | W5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216687119 | Ground Loop | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216687120 | Ground Loop | WaterFurnace | W5SZ048BD1 | W5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216687121 | Ground Loop | WaterFurnace | W5SZ060BD1 | W5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216687731 | Ground Loop | GEOSTAR | G5SS024BD1 | G5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | No
216687732 | Ground Loop | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | No
216687733 | Ground Loop | GEOSTAR | G5SS048BD1 | G5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | No
216687734 | Ground Loop | GEOSTAR | G5SS060BD1 | G5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | No
216687736 | Ground Loop | GEOSTAR | G5SZ024BD1 | G5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | No
216687737 | Ground Loop | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | No
216687738 | Ground Loop | GEOSTAR | G5SZ048BD1 | G5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | No
216687739 | Ground Loop | GEOSTAR | G5SZ060BD1 | G5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | No
216714620 | Ground Loop | GEOSTAR | G3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714621 | Ground Loop | GEOSTAR | G3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714622 | Ground Loop | GEOSTAR | G3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
207337510 | Ground Loop | GEOSTAR | 103H022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
207337511 | Ground Loop | GEOSTAR | 103H030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
207337512 | Ground Loop | GEOSTAR | 103H030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
207337513 | Ground Loop | GEOSTAR | 103J036**1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | No
207337514 | Ground Loop | GEOSTAR | 103J036**1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | No
215400202 | Ground Loop | DAIKIN | WSSV036J1*H*C |  | 40500 | 20.65 | 27600 | 3.84 | 3.375 | No
215400203 | Ground Loop | DAIKIN | WSSV036K3*H*C |  | 40500 | 21.09 | 27600 | 3.83 | 3.375 | No
215400206 | Ground Loop | DAIKIN | WSSV042E1*H*T |  | 44800 | 21.3 | 29000 | 3.92 | 3.7333 | No
215400207 | Ground Loop | DAIKIN | WSSV042F3*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
215400210 | Ground Loop | DAIKIN | WSSV042E1*H*C |  | 44800 | 21.3 | 29000 | 3.92 | 3.7333 | No
215400211 | Ground Loop | DAIKIN | WSSV042F3*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
215400214 | Ground Loop | DAIKIN | WSSV048E1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215400215 | Ground Loop | DAIKIN | WSSV048F3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215400218 | Ground Loop | DAIKIN | WSSV048E1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215400219 | Ground Loop | DAIKIN | WSSV048F3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215402552 | Ground Loop | DAIKIN | WSSV024E1*H*T |  | 25400 | 21.11 | 15700 | 3.7 | 2.1167 | No
215402553 | Ground Loop | DAIKIN | WSSV024F3*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215402556 | Ground Loop | DAIKIN | WSSV024E1*H*C |  | 25400 | 21.11 | 15700 | 3.7 | 2.1167 | No
215402557 | Ground Loop | DAIKIN | WSSV024F3*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215402560 | Ground Loop | DAIKIN | WSSV030E1*H*T |  | 30200 | 21.8 | 20700 | 3.83 | 2.5167 | No
215402561 | Ground Loop | DAIKIN | WSSV030F3*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
215402564 | Ground Loop | DAIKIN | WSSV030E1*H*C |  | 30200 | 21.8 | 20700 | 3.83 | 2.5167 | No
215402565 | Ground Loop | DAIKIN | WSSV030F3*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
215402568 | Ground Loop | DAIKIN | WSSV036E1*H*T |  | 40500 | 21.9 | 27600 | 3.84 | 3.375 | No
215402569 | Ground Loop | DAIKIN | WSSV036F3*H*T |  | 40500 | 21.18 | 27600 | 3.83 | 3.375 | No
215402572 | Ground Loop | DAIKIN | WSSV036E1*H*C |  | 40500 | 21.9 | 27600 | 3.84 | 3.375 | No
215402573 | Ground Loop | DAIKIN | WSSV036F3*H*C |  | 40500 | 21.18 | 27600 | 3.83 | 3.375 | No
217351784 | Ground Loop | ARCOAIRE | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351785 | Ground Loop | ARCOAIRE | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351788 | Ground Loop | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351789 | Ground Loop | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351790 | Ground Loop | ARCOAIRE | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351792 | Ground Loop | ARCOAIRE | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351793 | Ground Loop | ARCOAIRE | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351795 | Ground Loop | ARCOAIRE | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351796 | Ground Loop | ARCOAIRE | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351797 | Ground Loop | ARCOAIRE | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351798 | Ground Loop | ARCOAIRE | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351799 | Ground Loop | ARCOAIRE | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351801 | Ground Loop | ARCOAIRE | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351802 | Ground Loop | ARCOAIRE | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351803 | Ground Loop | ARCOAIRE | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
205737516 | Ground Loop | ICE AIR LLC | 8VSHPGE15** |  | 15000 | 17.5 | 10500 | 3.7 | 1.25 | No
205746250 | Ground Loop | ICE AIR LLC | 8VSHPGE09** |  | 11000 | 21.3 | 6500 | 3.64 | 0.91667 | No
205746251 | Ground Loop | ICE AIR LLC | 8VSHPGE12** |  | 13800 | 20.1 | 9000 | 3.7 | 1.15 | No
205746252 | Ground Loop | ICE AIR LLC | 8VSHPGE18** |  | 19500 | 18.7 | 13400 | 3.63 | 1.625 | No
205746253 | Ground Loop | ICE AIR LLC | 8VSHPGE24** |  | 24800 | 18.4 | 17000 | 3.66 | 2.0667 | No
205754414 | Ground Loop | ICE AIR LLC | 8VSHPGE30** |  | 30000 | 17.3 | 21900 | 3.6 | 2.5 | No
205754885 | Ground Loop | Johnson Controls | JCH/V015A*W/K B |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
205754886 | Ground Loop | SKYMARK | JCH/V015A*W/K C |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
205754889 | Ground Loop | Johnson Controls | JCH/V018A*W/K B |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
205754890 | Ground Loop | SKYMARK | JCH/V018A*W/K C |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
214595658 | Ground Loop | AAON, Inc. | RN-009-2-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595659 | Ground Loop | AAON, Inc. | RN-009-3-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595660 | Ground Loop | AAON, Inc. | RN-009-4-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595661 | Ground Loop | AAON, Inc. | RN-009-2-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595662 | Ground Loop | AAON, Inc. | RN-009-3-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595663 | Ground Loop | AAON, Inc. | RN-009-4-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
5220672 | Ground Loop | DAIKIN | WGSV/WGSH024B*J |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917 | No
5220673 | Ground Loop | DAIKIN | WGSV/WGSH024B*K |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917 | No
5220675 | Ground Loop | DAIKIN | WGSV/WGSH030B*E |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083 | No
5220676 | Ground Loop | DAIKIN | WGSV/WGSH030B*F |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083 | No
5220677 | Ground Loop | DAIKIN | WGSV/WGSH030B*J |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083 | No
5220678 | Ground Loop | DAIKIN | WGSV/WGSH030B*K |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083 | No
5220681 | Ground Loop | DAIKIN | WGSV/WGSH036B*E |  | 38500 | 22 | 26200 | 4.3 | 3.2083 | No
215268781 | Ground Loop | WaterFurnace | V5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268782 | Ground Loop | WaterFurnace | V5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268783 | Ground Loop | WaterFurnace | V5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268784 | Ground Loop | WaterFurnace | V5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268785 | Ground Loop | WaterFurnace | V5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268786 | Ground Loop | WaterFurnace | V5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268787 | Ground Loop | WaterFurnace | V5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268788 | Ground Loop | WaterFurnace | V5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268789 | Ground Loop | WaterFurnace | V5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268790 | Ground Loop | WaterFurnace | V5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268791 | Ground Loop | WaterFurnace | V5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268792 | Ground Loop | WaterFurnace | V5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268793 | Ground Loop | WaterFurnace | V5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268794 | Ground Loop | WaterFurnace | V5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268795 | Ground Loop | WaterFurnace | V5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268796 | Ground Loop | WaterFurnace | V5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
202330530 | Ground Loop | AAON, Inc. | M2-004-1-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325 | No
202330531 | Ground Loop | AAON, Inc. | M2-004-1-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1 | No
202330532 | Ground Loop | AAON, Inc. | M2-004-1-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417 | No
202330533 | Ground Loop | AAON, Inc. | M2-004-2-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667 | No
202330534 | Ground Loop | AAON, Inc. | M2-004-2-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325 | No
202330535 | Ground Loop | AAON, Inc. | M2-004-2-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1 | No
202330536 | Ground Loop | AAON, Inc. | M2-004-2-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417 | No
202330537 | Ground Loop | AAON, Inc. | M2-004-3-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667 | No
202330538 | Ground Loop | AAON, Inc. | M2-004-3-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325 | No
202330539 | Ground Loop | AAON, Inc. | M2-004-3-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1 | No
202330540 | Ground Loop | AAON, Inc. | M2-004-3-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417 | No
202330541 | Ground Loop | AAON, Inc. | M2-004-4-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667 | No
202330542 | Ground Loop | AAON, Inc. | M2-004-4-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325 | No
202330543 | Ground Loop | AAON, Inc. | M2-004-4-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1 | No
202330544 | Ground Loop | AAON, Inc. | M2-004-4-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417 | No
202330562 | Ground Loop | AAON, Inc. | M2-006-2-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7 | No
202330564 | Ground Loop | AAON, Inc. | M2-006-2-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725 | No
202330566 | Ground Loop | AAON, Inc. | M2-006-3-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7 | No
202330568 | Ground Loop | AAON, Inc. | M2-006-3-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725 | No
202330570 | Ground Loop | AAON, Inc. | M2-006-4-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7 | No
202330572 | Ground Loop | AAON, Inc. | M2-006-4-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725 | No
215851780 | Ground Loop | DAIKIN | WSTH048K3*G/J*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083 | No
215851781 | Ground Loop | DAIKIN | WSTH048L3*G/J*C |  | 49300 | 19 | 36300 | 3.76 | 4.1083 | No
215851786 | Ground Loop | DAIKIN | WSTH060K3*G/J*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333 | No
215851798 | Ground Loop | DAIKIN | WSTV024J1*G/J*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667 | No
215851800 | Ground Loop | DAIKIN | WSTV024K3*G/J*C |  | 22400 | 17.45 | 17200 | 3.86 | 1.8667 | No
215851805 | Ground Loop | DAIKIN | WSTV030J1*G/J*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833 | No
215851806 | Ground Loop | DAIKIN | WSTV030K3*G/J*C |  | 32200 | 18.9 | 20800 | 3.66 | 2.6833 | No
215851812 | Ground Loop | DAIKIN | WSTV036J1*G/J*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583 | No
215851817 | Ground Loop | DAIKIN | WSTV042K3*G/J*C |  | 44800 | 18.96 | 27600 | 3.62 | 3.7333 | No
215851821 | Ground Loop | DAIKIN | WSTV048K3*G/J*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667 | No
215851823 | Ground Loop | DAIKIN | WSTV048L3*G/J*C |  | 52400 | 19.56 | 35200 | 3.78 | 4.3667 | No
215851828 | Ground Loop | DAIKIN | WSTV060K3*G/J*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583 | No
215851830 | Ground Loop | DAIKIN | WSTV060L3*G/J*C |  | 63100 | 19.01 | 46800 | 3.98 | 5.2583 | No
215852848 | Ground Loop | DAIKIN | WSTH024E1*G/J*C |  | 25100 | 19.92 | 17200 | 3.92 | 2.0917 | No
215852849 | Ground Loop | DAIKIN | WSTH024F3*G/J*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917 | No
215852852 | Ground Loop | DAIKIN | WSTH030E1*G/J*C |  | 32700 | 19.69 | 20600 | 3.75 | 2.725 | No
215852853 | Ground Loop | DAIKIN | WSTH030F3*G/J*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725 | No
9114315 | Ground Loop | GEOCOMFORT | GZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114316 | Ground Loop | HYDRON MODULE | HZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114317 | Ground Loop | TETCO | TZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114322 | Ground Loop | GEOCOMFORT | GZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | Yes
9114323 | Ground Loop | HYDRON MODULE | HZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | Yes
9114324 | Ground Loop | TETCO | TZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | Yes
9114325 | Ground Loop | GEOCOMFORT | GZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114326 | Ground Loop | HYDRON MODULE | HZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114327 | Ground Loop | TETCO | TZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114328 | Ground Loop | GEOCOMFORT | GZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114329 | Ground Loop | HYDRON MODULE | HZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114330 | Ground Loop | TETCO | TZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9850201 | Ground Loop | DAIKIN | WVFW1030*K***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583 | No
9910449 | Ground Loop | GEOCOMFORT | GZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | Yes
9910450 | Ground Loop | HYDRON MODULE | HZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | Yes
9910451 | Ground Loop | TETCO | TZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | Yes
9910452 | Ground Loop | GEOCOMFORT | GZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | No
9910453 | Ground Loop | HYDRON MODULE | HZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | No
9910454 | Ground Loop | TETCO | TZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | No
9910540 | Ground Loop | GEOCOMFORT | GZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | Yes
9910541 | Ground Loop | HYDRON MODULE | HZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | Yes
207198440 | Ground Loop | BOSCH | QV036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198441 | Ground Loop | BOSCH | QV036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198443 | Ground Loop | BOSCH | QV036-2HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198446 | Ground Loop | BOSCH | QV036-2VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198447 | Ground Loop | BOSCH | QV036-2VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198449 | Ground Loop | BOSCH | QV036-3HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198452 | Ground Loop | BOSCH | QV036-3VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198454 | Ground Loop | BOSCH | QV036-3VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198455 | Ground Loop | BOSCH | QV036-4HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198458 | Ground Loop | BOSCH | QV036-4VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198460 | Ground Loop | BOSCH | QV036-4VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198729 | Ground Loop | FHP | QV024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198730 | Ground Loop | FHP | QV024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198733 | Ground Loop | FHP | QV024-2HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
215405070 | Ground Loop | DAIKIN | WSSV060K3*H*C |  | 66300 | 19.8 | 48800 | 3.92 | 5.525 | No
215405071 | Ground Loop | DAIKIN | WSSV060L3*H*C |  | 66300 | 19.4 | 48800 | 3.88 | 5.525 | No
215405076 | Ground Loop | DAIKIN | WSSV070E1*H*T |  | 75400 | 19.4 | 54700 | 3.8 | 6.2833 | No
215405077 | Ground Loop | DAIKIN | WSSV070F3*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
215405078 | Ground Loop | DAIKIN | WSSV070K3*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
215405079 | Ground Loop | DAIKIN | WSSV070L3*H*T |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833 | No
215405084 | Ground Loop | DAIKIN | WSSV070E1*H*C |  | 75400 | 19.4 | 54700 | 3.8 | 6.2833 | No
215405085 | Ground Loop | DAIKIN | WSSV070F3*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
215405086 | Ground Loop | DAIKIN | WSSV070K3*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
215405087 | Ground Loop | DAIKIN | WSSV070L3*H*C |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833 | No
215415734 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)024A*B |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415735 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)024A*C |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415736 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)024A*VB |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415737 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)024A*VC |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415740 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)030A*VB |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415741 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)030A*VC |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415744 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)036A*VB |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
215415745 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)036A*VC |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
214772070 | Ground Loop | TRANE | GEVK048B |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214772071 | Ground Loop | TRANE | GEVK0484 |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214772072 | Ground Loop | TRANE | GEVK060B |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214772073 | Ground Loop | TRANE | GEVK0604 |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214772074 | Ground Loop | TRANE | EXVK0097 |  | 9000 | 21.2 | 6100 | 3.91 | 0.75 | No
214772075 | Ground Loop | TRANE | EXVK0127 |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167 | No
214772076 | Ground Loop | TRANE | EXVK0157 |  | 16200 | 18.7 | 11800 | 3.73 | 1.35 | No
214772077 | Ground Loop | TRANE | EXVK0187 |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417 | No
214772078 | Ground Loop | TRANE | EXVK024B |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
216057509 | Ground Loop | GEOCOMFORT | GBT060* | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
216057511 | Ground Loop | GEOCOMFORT | GVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
216057512 | Ground Loop | GEOCOMFORT | GYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583 | Yes
216057513 | Ground Loop | GEOCOMFORT | GZS015* |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | Yes
216057515 | Ground Loop | GEOCOMFORT | GZS018* |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | Yes
216057517 | Ground Loop | GEOCOMFORT | GYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583 | Yes
216128491 | Ground Loop | GEOSTAR | G5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667 | Yes
216128493 | Ground Loop | GEOSTAR | G5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917 | Yes
216128495 | Ground Loop | GEOSTAR | G5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083 | Yes
216128497 | Ground Loop | GEOSTAR | G5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583 | Yes
216411469 | Ground Loop | ClimateMaster | SJ/PN024A | SAN024A | 23900 | 19 | 17900 | 4 | 1.9917 | Yes
216411470 | Ground Loop | ClimateMaster | SJ/PN036A | SAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917 | Yes
216411471 | Ground Loop | ClimateMaster | SJ/PN048A | SAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833 | Yes
216411472 | Ground Loop | ClimateMaster | SJ/PN060A | SAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167 | Yes
216419856 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
216419857 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
216419860 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
216419863 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
216419880 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
216419883 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
216419898 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
216419899 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
216419902 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
216419904 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
215746915 | Ground Loop | TRANE | GSK036A3 |  | 41280 | 22.1 | 29804 | 4.28 | 3.44 | No
215746916 | Ground Loop | TRANE | GSK048A3 |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966 | No
215746918 | Ground Loop | TRANE | GSK060A3 |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603 | No
215746919 | Ground Loop | TRANE | GSK072A3 |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341 | No
215746920 | Ground Loop | TRANE | GSK090A3 |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743 | No
215746921 | Ground Loop | TRANE | GSK102A3 |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454 | No
215746922 | Ground Loop | TRANE | GSK120A3 |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112 | No
215746923 | Ground Loop | TRANE | GSK036A4 |  | 41280 | 22.1 | 29804 | 4.28 | 3.44 | No
215746924 | Ground Loop | TRANE | GSK036AW |  | 41280 | 22.1 | 29804 | 4.28 | 3.44 | No
215746925 | Ground Loop | TRANE | GSK048A4 |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966 | No
215746926 | Ground Loop | TRANE | GSK048AW |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966 | No
215746927 | Ground Loop | TRANE | GSK060A4 |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603 | No
215746928 | Ground Loop | TRANE | GSK060AW |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603 | No
215746929 | Ground Loop | TRANE | GSK072A4 |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341 | No
215746930 | Ground Loop | TRANE | GSK072AW |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341 | No
215746931 | Ground Loop | TRANE | GSK090A4 |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743 | No
215746932 | Ground Loop | TRANE | GSK090AW |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743 | No
215746933 | Ground Loop | TRANE | GSK102A4 |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454 | No
215746934 | Ground Loop | TRANE | GSK102AW |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454 | No
215746935 | Ground Loop | TRANE | GSK120A4 |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112 | No
215746936 | Ground Loop | TRANE | GSK120AW |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112 | No
215748220 | Ground Loop | ClimateMaster | SMS(S,M)15A*Q |  | 14800 | 17.5 | 11100 | 3.6 | 1.2333 | No
215748221 | Ground Loop | ClimateMaster | SMT(S,M)15A*Q |  | 15400 | 18.8 | 11000 | 3.7 | 1.2833 | No
215748224 | Ground Loop | ClimateMaster | SMT(S,M)18A*Q |  | 19000 | 17.8 | 13600 | 3.6 | 1.5833 | No
215748226 | Ground Loop | ClimateMaster | SMS(S,M)24A*Q |  | 24800 | 18.6 | 18400 | 3.6 | 2.0667 | No
215748227 | Ground Loop | ClimateMaster | SMT(S,M)24A*Q |  | 25900 | 20.4 | 18000 | 3.7 | 2.1583 | No
215748230 | Ground Loop | ClimateMaster | SMT(S,M)30A*Q |  | 30000 | 19 | 22300 | 3.7 | 2.5 | No
217642919 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642920 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642921 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642922 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642928 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642929 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642930 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642931 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642932 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642943 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642945 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642946 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217903459 | Ground Loop | WaterFurnace | V5R048*D4**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
4219425 | Ground Loop | NORDIC | R55HACW-P-1T-*-SDE** |  | 45400 | 17 | 35600 | 3.8 | 3.7833 | Yes
205767473 | Ground Loop | ClimateMaster | TEV/H/D026B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | Yes
205767474 | Ground Loop | ClimateMaster | TEV/H/D038B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | Yes
205767475 | Ground Loop | ClimateMaster | TEV/H/D049B |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | Yes
205767476 | Ground Loop | ClimateMaster | TEV/H/D064B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | Yes
206608720 | Ground Loop | GEOSTAR | 103J048**1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
206608721 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060J1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
206608722 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060J1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
206608723 | Ground Loop | GEOSTAR | 103J060**1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
206608724 | Ground Loop | GEOSTAR | 103J060**1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
206611120 | Ground Loop | COMFORT-AIRE | HEH/V060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
206611121 | Ground Loop | CENTURY | HEH/V060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
202729325 | Ground Loop | DAY & NIGHT | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729332 | Ground Loop | HEIL | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
202729333 | Ground Loop | ARCOAIRE | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202729334 | Ground Loop | KEEPRITE | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202729335 | Ground Loop | TEMPSTAR | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202729336 | Ground Loop | COMFORTMAKER | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202729337 | Ground Loop | DAY & NIGHT | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202732300 | Ground Loop | BOSCH | BP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732301 | Ground Loop | CARRIER | GB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
202732302 | Ground Loop | BRYANT | GB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732303 | Ground Loop | ARCOAIRE | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
202732304 | Ground Loop | HEIL | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732305 | Ground Loop | KEEPRITE | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732306 | Ground Loop | TEMPSTAR | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732307 | Ground Loop | COMFORTMAKER | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732308 | Ground Loop | DAY & NIGHT | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732914 | Ground Loop | BOSCH-GEO | BP018-1HZ*******C |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
202732916 | Ground Loop | BOSCH | BP018-1HZ*******C |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732917 | Ground Loop | CARRIER | GB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
202732918 | Ground Loop | BRYANT | GB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732919 | Ground Loop | HEIL | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
202732920 | Ground Loop | ARCOAIRE | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732921 | Ground Loop | KEEPRITE | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732922 | Ground Loop | TEMPSTAR | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732923 | Ground Loop | COMFORTMAKER | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732924 | Ground Loop | DAY & NIGHT | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
207083989 | Ground Loop | CARRIER | 50PCV036J/K*C/A6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
214063784 | Ground Loop | GeoSmart Energy | GBV/GBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214063785 | Ground Loop | GeoSmart Energy | GBV/GBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214063786 | Ground Loop | GeoSmart Energy | GBV/GBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214063788 | Ground Loop | GeoSmart Energy | GBV/GBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214063789 | Ground Loop | GeoSmart Energy | GBV/GBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214063790 | Ground Loop | GeoSmart Energy | GBV/GBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214063791 | Ground Loop | GeoSmart Energy | GBV/GBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067547 | Ground Loop | GeoSmart Energy | GBV/GBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
214067548 | Ground Loop | GeoSmart Energy | GBV/GBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214067549 | Ground Loop | GeoSmart Energy | GBV/GBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214067550 | Ground Loop | GeoSmart Energy | GBV/GBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
214067551 | Ground Loop | GeoSmart Energy | GBV/GBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214067552 | Ground Loop | GeoSmart Energy | GBV/GBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214067553 | Ground Loop | GeoSmart Energy | GBV/GBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214067554 | Ground Loop | GeoSmart Energy | GBV/GBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214067555 | Ground Loop | GeoSmart Energy | GBV/GBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214067556 | Ground Loop | GeoSmart Energy | GBV/GBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214067557 | Ground Loop | GeoSmart Energy | GBV/GBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
214067558 | Ground Loop | GeoSmart Energy | GBV/GBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214067559 | Ground Loop | GeoSmart Energy | GBV/GBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214067560 | Ground Loop | GeoSmart Energy | GBV/GBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
214067561 | Ground Loop | GeoSmart Energy | GBV/GBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214067562 | Ground Loop | GeoSmart Energy | GBV/GBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214067563 | Ground Loop | GeoSmart Energy | GBV/GBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
214067564 | Ground Loop | GeoSmart Energy | GBV/GBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067565 | Ground Loop | GeoSmart Energy | GBV/GBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067566 | Ground Loop | GeoSmart Energy | GBV/GBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
214067567 | Ground Loop | GeoSmart Energy | GBV/GBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067568 | Ground Loop | GeoSmart Energy | GBV/GBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067569 | Ground Loop | GeoSmart Energy | GBV/GBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214067570 | Ground Loop | GeoSmart Energy | GBV/GBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214067571 | Ground Loop | GeoSmart Energy | GBV/GBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214067572 | Ground Loop | GeoSmart Energy | GBV/GBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214067574 | Ground Loop | GeoSmart Energy | GBV/GBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214067575 | Ground Loop | GeoSmart Energy | GBV/GBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214067577 | Ground Loop | GeoSmart Energy | GBV/GBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214067578 | Ground Loop | GeoSmart Energy | GBV/GBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
205503116 | Ground Loop | BOSCH-GEO | SM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125 | Yes
205503120 | Ground Loop | BOSCH-GEO | LM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125 | No
205503124 | Ground Loop | BOSCH | SM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125 | Yes
205503128 | Ground Loop | FHP | LM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125 | No
205652453 | Ground Loop | BOSCH-GEO | SM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083 | Yes
205652454 | Ground Loop | BOSCH-GEO | SM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417 | Yes
205652455 | Ground Loop | BOSCH-GEO | SM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917 | Yes
205652457 | Ground Loop | BOSCH-GEO | LM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083 | No
205652458 | Ground Loop | BOSCH-GEO | LM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417 | No
205652459 | Ground Loop | BOSCH-GEO | LM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917 | No
205652461 | Ground Loop | BOSCH | SM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083 | Yes
205652462 | Ground Loop | BOSCH | SM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417 | Yes
205652463 | Ground Loop | BOSCH | SM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917 | Yes
205652465 | Ground Loop | FHP | LM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083 | No
205652466 | Ground Loop | FHP | LM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417 | No
205652467 | Ground Loop | FHP | LM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917 | No
215224613 | Ground Loop | CARRIER | 50WD*015***4*(A-H)** |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224614 | Ground Loop | CARRIER | 50WD*015***4*(J-R)** |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224615 | Ground Loop | CARRIER | 50WD*018***3*(A-H)** |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224616 | Ground Loop | CARRIER | 50WD*018***3*(J-R)** |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224617 | Ground Loop | CARRIER | 50WD*018***4*(A-H)** |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224618 | Ground Loop | CARRIER | 50WD*018***4*(J-R)** |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224619 | Ground Loop | CARRIER | 50WD*024***3*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224620 | Ground Loop | CARRIER | 50WD*024***3*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224621 | Ground Loop | CARRIER | 50WD*024***4*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224622 | Ground Loop | CARRIER | 50WD*024***4*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224623 | Ground Loop | CARRIER | 50WD*024***5*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224624 | Ground Loop | CARRIER | 50WD*024***5*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224625 | Ground Loop | CARRIER | 50WD*024***6*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224626 | Ground Loop | CARRIER | 50WD*024***6*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
202732937 | Ground Loop | TRANE | GWSC048H3 |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917 | No
202732938 | Ground Loop | TRANE | GWSC048H4 |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917 | No
202732939 | Ground Loop | TRANE | GWSC048HW |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917 | No
215685119 | Ground Loop | Dandelion Geo | DPG2048 |  | 50440 | 17.1 | 42300 | 4.7 | 4.2033 | Yes
215685120 | Ground Loop | Dandelion Geo | DPG2060 |  | 63000 | 17.6 | 54570 | 4.6 | 5.25 | Yes
7519574 | Ground Loop | HYDRON MODULE | HVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519575 | Ground Loop | TETCO | TVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519576 | Ground Loop | GEOCOMFORT | GVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519577 | Ground Loop | HYDRON MODULE | HVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519578 | Ground Loop | TETCO | TVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519579 | Ground Loop | GEOCOMFORT | GVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
207200608 | Ground Loop | GeoSmart Energy | GTS038*1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207200609 | Ground Loop | GeoSmart Energy | GTS038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207200613 | Ground Loop | GeoSmart Energy | QT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
207216511 | Ground Loop | GEOSTAR | GDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
207216512 | Ground Loop | GEOSTAR | GDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
207216513 | Ground Loop | GEOSTAR | GDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
207216514 | Ground Loop | GEOSTAR | GDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
207216515 | Ground Loop | GEOSTAR | GDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
207216516 | Ground Loop | GEOSTAR | GDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
207216517 | Ground Loop | GEOSTAR | GDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
207216518 | Ground Loop | GEOSTAR | GDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
207216519 | Ground Loop | GEOSTAR | GDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
214776169 | Ground Loop | TRANE | GETK0151-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167 | No
214776171 | Ground Loop | TRANE | GETK0241-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1 | No
214776189 | Ground Loop | TRANE | GETK0152-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167 | No
214776190 | Ground Loop | TRANE | GETK0157-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167 | No
214776193 | Ground Loop | TRANE | GETK0242-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1 | No
214776194 | Ground Loop | TRANE | GETK0247-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1 | No
214796343 | Ground Loop | WaterFurnace | W5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | Yes
214796344 | Ground Loop | WaterFurnace | W5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | Yes
214796345 | Ground Loop | WaterFurnace | W5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | Yes
214796346 | Ground Loop | WaterFurnace | W5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | Yes
214796347 | Ground Loop | WaterFurnace | W5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | Yes
214796667 | Ground Loop | WaterFurnace | W5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | Yes
214796668 | Ground Loop | WaterFurnace | W5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | Yes
214796669 | Ground Loop | WaterFurnace | W5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | Yes
214810491 | Ground Loop | GEOSTAR | G5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | Yes
214810492 | Ground Loop | GEOSTAR | G5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | Yes
214810493 | Ground Loop | GEOSTAR | G5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | Yes
214810494 | Ground Loop | GEOSTAR | G5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | Yes
214810495 | Ground Loop | GEOSTAR | G5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | Yes
214810496 | Ground Loop | GEOSTAR | G5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | Yes
214810497 | Ground Loop | GEOSTAR | G5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | Yes
214810498 | Ground Loop | GEOSTAR | G5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | Yes
214823444 | Ground Loop | GeoSmart Energy | S5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | Yes
214823445 | Ground Loop | GeoSmart Energy | S5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | Yes
8233354 | Ground Loop | DAIKIN | W.CCW.2.072*F |  | 80100 | 17.1 | 58700 | 3.75 | 6.675 | No
8233365 | Ground Loop | DAIKIN | W.CCW.2.072*K |  | 80100 | 17.1 | 58700 | 3.75 | 6.675 | No
202921908 | Ground Loop | BOSCH | EP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921909 | Ground Loop | BOSCH | EP036-3VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921910 | Ground Loop | BOSCH | EP036-4VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921911 | Ground Loop | BOSCH-GEO | BP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921912 | Ground Loop | BOSCH | EP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921913 | Ground Loop | BOSCH | EP036-3HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921914 | Ground Loop | BOSCH | EP036-4HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921915 | Ground Loop | BOSCH-GEO | BP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921952 | Ground Loop | FHP | EP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921953 | Ground Loop | FHP | EP036-3HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921954 | Ground Loop | FHP | EP036-4HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921956 | Ground Loop | BOSCH | BP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202921957 | Ground Loop | FHP | EP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921958 | Ground Loop | FHP | EP036-3VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921959 | Ground Loop | FHP | EP036-4VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921960 | Ground Loop | BOSCH | BP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922686 | Ground Loop | CARRIER | 50PSH036***3/CA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922689 | Ground Loop | CARRIER | 50PSH036***5/EA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922692 | Ground Loop | CARRIER | 50PSH036***6/FA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922695 | Ground Loop | CARRIER | GB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922697 | Ground Loop | BRYANT | GB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922700 | Ground Loop | HEIL | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922703 | Ground Loop | ARCOAIRE | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922706 | Ground Loop | KEEPRITE | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922708 | Ground Loop | TEMPSTAR | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922711 | Ground Loop | COMFORTMAKER | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922714 | Ground Loop | DAY & NIGHT | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922716 | Ground Loop | CARRIER | 50PSV036***3/CA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922719 | Ground Loop | CARRIER | 50PSV036***5/EA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922722 | Ground Loop | CARRIER | 50PSV036***6/FA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922725 | Ground Loop | CARRIER | GB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922728 | Ground Loop | BRYANT | GB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922731 | Ground Loop | HEIL | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922734 | Ground Loop | ARCOAIRE | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922737 | Ground Loop | KEEPRITE | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922740 | Ground Loop | TEMPSTAR | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922742 | Ground Loop | COMFORTMAKER | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922745 | Ground Loop | DAY & NIGHT | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
203113888 | Ground Loop | GEOSTAR | 103J036**1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
201907619 | Ground Loop | WaterFurnace | URS048*0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907620 | Ground Loop | WaterFurnace | URS048*0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907621 | Ground Loop | WaterFurnace | URS048*0*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907622 | Ground Loop | WaterFurnace | URS048*3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907623 | Ground Loop | WaterFurnace | URS048*3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907624 | Ground Loop | WaterFurnace | URS048*3*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907625 | Ground Loop | WaterFurnace | URS048*4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907626 | Ground Loop | WaterFurnace | URS048*4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907627 | Ground Loop | WaterFurnace | URS048*4*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907628 | Ground Loop | WaterFurnace | URD038*4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
201907629 | Ground Loop | WaterFurnace | URD038*4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
201907630 | Ground Loop | WaterFurnace | URD038*4*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
201907631 | Ground Loop | WaterFurnace | URD049*4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
201907632 | Ground Loop | WaterFurnace | URD049*4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
201907633 | Ground Loop | WaterFurnace | URD049*4*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
201926691 | Ground Loop | WaterFurnace | URS060*0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926694 | Ground Loop | WaterFurnace | URS060*0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926696 | Ground Loop | WaterFurnace | URS060*0*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926699 | Ground Loop | WaterFurnace | URS060*3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926702 | Ground Loop | WaterFurnace | URS060*3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926705 | Ground Loop | WaterFurnace | URS060*3*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926708 | Ground Loop | WaterFurnace | URS060*4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926711 | Ground Loop | WaterFurnace | URS060*4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926714 | Ground Loop | WaterFurnace | URS060*4*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926717 | Ground Loop | WaterFurnace | URS070*0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926719 | Ground Loop | WaterFurnace | URS070*0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926724 | Ground Loop | WaterFurnace | URS070*0*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926727 | Ground Loop | WaterFurnace | URS070*3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926730 | Ground Loop | WaterFurnace | URS070*3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926733 | Ground Loop | WaterFurnace | URS070*3*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926736 | Ground Loop | WaterFurnace | URS070*4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926738 | Ground Loop | WaterFurnace | URS070*4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926741 | Ground Loop | WaterFurnace | URS070*4*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207349401 | Ground Loop | WaterFurnace | NBV/NBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349402 | Ground Loop | WaterFurnace | NBV/NBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349403 | Ground Loop | WaterFurnace | NBV/NBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349404 | Ground Loop | WaterFurnace | NBV/NBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349405 | Ground Loop | WaterFurnace | NBV/NBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349406 | Ground Loop | WaterFurnace | NBV/NBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349407 | Ground Loop | WaterFurnace | NBV/NBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349408 | Ground Loop | WaterFurnace | NBV/NBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349409 | Ground Loop | WaterFurnace | NBV/NBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349410 | Ground Loop | WaterFurnace | NBV/NBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349411 | Ground Loop | WaterFurnace | NBV/NBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349412 | Ground Loop | WaterFurnace | NBV/NBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207657647 | Ground Loop | ClimateMaster | TSM15 D |  | 15500 | 18.8 | 11000 | 3.6 | 1.2917 | No
207657653 | Ground Loop | ClimateMaster | TSM30 D |  | 29000 | 17.6 | 22200 | 3.6 | 2.4167 | No
215837669 | Ground Loop | DAIKIN | WSMH024F3*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
215837671 | Ground Loop | DAIKIN | WSMH024J1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
215837672 | Ground Loop | DAIKIN | WSMH024K3*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
215837677 | Ground Loop | DAIKIN | WSMH024F3*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837679 | Ground Loop | DAIKIN | WSMH024J1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837680 | Ground Loop | DAIKIN | WSMH024K3*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837686 | Ground Loop | DAIKIN | WSMH024F3*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837687 | Ground Loop | DAIKIN | WSMH024J1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837689 | Ground Loop | DAIKIN | WSMH024K3*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837694 | Ground Loop | DAIKIN | WSMH030F3*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333 | No
215837697 | Ground Loop | DAIKIN | WSMH030K3*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333 | No
217754442 | Ground Loop | DAIKIN | WSSV036K1*H*C |  | 40500 | 21.09 | 27600 | 3.83 | 3.375 | No
217754444 | Ground Loop | DAIKIN | WSSV042F1*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217754445 | Ground Loop | DAIKIN | WSSV042K1*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217754447 | Ground Loop | DAIKIN | WSSV042F1*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217754448 | Ground Loop | DAIKIN | WSSV042K1*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217754450 | Ground Loop | DAIKIN | WSSV048F1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754451 | Ground Loop | DAIKIN | WSSV048K1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754452 | Ground Loop | DAIKIN | WSSV048L1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754454 | Ground Loop | DAIKIN | WSSV048F1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754455 | Ground Loop | DAIKIN | WSSV048K1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754456 | Ground Loop | DAIKIN | WSSV048L1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754458 | Ground Loop | DAIKIN | WSSV060F1*H*T |  | 66300 | 19.8 | 48800 | 3.96 | 5.525 | No
217754459 | Ground Loop | DAIKIN | WSSV060K1*H*T |  | 66300 | 19.8 | 48800 | 3.92 | 5.525 | No
217754460 | Ground Loop | DAIKIN | WSSV060L1*H*T |  | 66300 | 19.4 | 48800 | 3.88 | 5.525 | No
217754462 | Ground Loop | DAIKIN | WSSV060F1*H*C |  | 66300 | 19.8 | 48800 | 3.96 | 5.525 | No
217754463 | Ground Loop | DAIKIN | WSSV060K1*H*C |  | 66300 | 19.8 | 48800 | 3.92 | 5.525 | No
217754464 | Ground Loop | DAIKIN | WSSV060L1*H*C |  | 66300 | 19.4 | 48800 | 3.88 | 5.525 | No
217754466 | Ground Loop | DAIKIN | WSSV070F1*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
217754467 | Ground Loop | DAIKIN | WSSV070K1*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
217754468 | Ground Loop | DAIKIN | WSSV070L1*H*T |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833 | No
217754470 | Ground Loop | DAIKIN | WSSV070F1*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
217754471 | Ground Loop | DAIKIN | WSSV070K1*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
217754472 | Ground Loop | DAIKIN | WSSV070L1*H*C |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833 | No
217754551 | Ground Loop | DAIKIN | WSMH030F1*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
217754552 | Ground Loop | DAIKIN | WSMH030K1*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
217754555 | Ground Loop | DAIKIN | WSMH030F1*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
217754556 | Ground Loop | DAIKIN | WSMH030K1*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
216621360 | Ground Loop | GEOSTAR | G5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216621361 | Ground Loop | GEOSTAR | G5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216621362 | Ground Loop | GEOSTAR | G5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625456 | Ground Loop | GEOSTAR | G5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216625457 | Ground Loop | GEOSTAR | G5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625458 | Ground Loop | GEOSTAR | G5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625459 | Ground Loop | GEOSTAR | G5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625460 | Ground Loop | GEOSTAR | G5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625461 | Ground Loop | GEOSTAR | G5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625462 | Ground Loop | GEOSTAR | G5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625463 | Ground Loop | GEOSTAR | G5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625464 | Ground Loop | GEOSTAR | G5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625465 | Ground Loop | GEOSTAR | G5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625466 | Ground Loop | GEOSTAR | G5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625467 | Ground Loop | GEOSTAR | G5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625468 | Ground Loop | GEOSTAR | G5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625469 | Ground Loop | GEOSTAR | G5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625470 | Ground Loop | GEOSTAR | G5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625645 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625646 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625647 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625648 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625649 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625650 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625651 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625652 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625653 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625654 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625655 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625656 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625657 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625658 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625659 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625660 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625661 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625662 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625663 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625664 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625665 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625666 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625667 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625668 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625669 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625670 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625671 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625672 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625673 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625674 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625675 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625676 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625677 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625678 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625679 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625680 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625681 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625682 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625683 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625684 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625685 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625686 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625687 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625688 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625689 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625690 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625691 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625692 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625693 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625694 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625695 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
204100658 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204100659 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204100660 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204100661 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204101161 | Ground Loop | 5 SERIES | NDV/NDH064J1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
204117015 | Ground Loop | GEOSTAR | 101/102J064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
204117016 | Ground Loop | GEOSTAR | 103J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204117017 | Ground Loop | GEOSTAR | 103J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
216979845 | Ground Loop | KEEPRITE | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979846 | Ground Loop | TEMPSTAR | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979847 | Ground Loop | COMFORTMAKER | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979848 | Ground Loop | DAY & NIGHT | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
215399788 | Ground Loop | DAIKIN | WSMV024J1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
215399789 | Ground Loop | DAIKIN | WSMV024K3*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
215399792 | Ground Loop | DAIKIN | WSMV024J1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215399793 | Ground Loop | DAIKIN | WSMV024K3*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215399796 | Ground Loop | DAIKIN | WSMV024J1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215399797 | Ground Loop | DAIKIN | WSMV024K3*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215399812 | Ground Loop | DAIKIN | WSMV036J1*G/J*P |  | 37600 | 18.26 | 28000 | 3.6 | 3.1333 | No
215399816 | Ground Loop | DAIKIN | WSMV036J1*G/J*T |  | 37500 | 18.76 | 28000 | 3.72 | 3.125 | No
215399817 | Ground Loop | DAIKIN | WSMV036K3*G/J*T |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917 | No
215399820 | Ground Loop | DAIKIN | WSMV036J1*G/J*C |  | 37500 | 18.76 | 28000 | 3.72 | 3.125 | No
215399821 | Ground Loop | DAIKIN | WSMV036K3*G/J*C |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917 | No
215399825 | Ground Loop | DAIKIN | WSMV042K3*G/J*T |  | 42600 | 19.67 | 29700 | 3.63 | 3.55 | No
215399827 | Ground Loop | DAIKIN | WSMV042K3*G/J*C |  | 42600 | 19.67 | 29700 | 3.63 | 3.55 | No
215399830 | Ground Loop | DAIKIN | WSMV048K3*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
215399831 | Ground Loop | DAIKIN | WSMV048L3*G/J*P |  | 49700 | 18.61 | 36700 | 3.64 | 4.1417 | No
215399834 | Ground Loop | DAIKIN | WSMV048K3*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215399835 | Ground Loop | DAIKIN | WSMV048L3*G/J*T |  | 49300 | 19.09 | 36000 | 3.75 | 4.1083 | No
215399838 | Ground Loop | DAIKIN | WSMV048K3*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
5440541 | Ground Loop | GEOCOMFORT | GXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | Yes
5440542 | Ground Loop | HYDRON MODULE | HXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | Yes
5440543 | Ground Loop | TETCO | TXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | Yes
5440554 | Ground Loop | GEOCOMFORT | GXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | Yes
5440555 | Ground Loop | HYDRON MODULE | HXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | Yes
5440557 | Ground Loop | TETCO | TXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | Yes
207337515 | Ground Loop | GEOSTAR | 103J042**1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
207337516 | Ground Loop | GEOSTAR | 103J042**1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
207337517 | Ground Loop | GEOSTAR | 103H048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
207337518 | Ground Loop | GEOSTAR | 103H048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
207337521 | Ground Loop | GEOSTAR | 103H070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207337522 | Ground Loop | GEOSTAR | 103H070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207348654 | Ground Loop | WaterFurnace | URS036*0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348655 | Ground Loop | WaterFurnace | URS036*0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348656 | Ground Loop | WaterFurnace | URS036*0*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348657 | Ground Loop | WaterFurnace | URS036*3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348658 | Ground Loop | WaterFurnace | URS036*3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348659 | Ground Loop | WaterFurnace | URS036*3*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348660 | Ground Loop | WaterFurnace | URS036*4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348661 | Ground Loop | WaterFurnace | URS036*4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348662 | Ground Loop | WaterFurnace | URS036*4*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348663 | Ground Loop | WaterFurnace | URS048*0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348664 | Ground Loop | WaterFurnace | URS048*0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348665 | Ground Loop | WaterFurnace | URS048*0*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348666 | Ground Loop | WaterFurnace | URS048*3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348667 | Ground Loop | WaterFurnace | URS048*3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348668 | Ground Loop | WaterFurnace | URS048*3*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348669 | Ground Loop | WaterFurnace | URS048*4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348670 | Ground Loop | WaterFurnace | URS048*4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348671 | Ground Loop | WaterFurnace | URS048*4*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348672 | Ground Loop | WaterFurnace | URS070*0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348673 | Ground Loop | WaterFurnace | URS070*0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348674 | Ground Loop | WaterFurnace | URS070*0*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348675 | Ground Loop | WaterFurnace | URS070*3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348676 | Ground Loop | WaterFurnace | URS070*3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348677 | Ground Loop | WaterFurnace | URS070*3*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348678 | Ground Loop | WaterFurnace | URS070*4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
215827106 | Ground Loop | DAIKIN | WSLV120K1*G/J |  | 124600 | 17 | 95600 | 3.6 | 10.3833 | No
215832281 | Ground Loop | HYDROTECH | WSH6009D* |  | 9500 | 18.9 | 6500 | 3.6 | 0.79167 | No
215832282 | Ground Loop | HYDROTECH | WSH6012D* |  | 12000 | 17.9 | 8500 | 3.8 | 1 | No
215832283 | Ground Loop | HYDROTECH | WSH6018D* |  | 19000 | 18 | 12000 | 3.6 | 1.5833 | No
215832284 | Ground Loop | HYDROTECH | WSH6024D* |  | 26000 | 18.4 | 17500 | 3.6 | 2.1667 | No
215832285 | Ground Loop | HYDROTECH | WSH6030D* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
215832286 | Ground Loop | HYDROTECH | WSH6036D* |  | 36400 | 18 | 28000 | 3.6 | 3.0333 | No
215832287 | Ground Loop | HYDROTECH | WSH6042D* |  | 43500 | 18.5 | 31000 | 3.8 | 3.625 | No
215832288 | Ground Loop | HYDROTECH | WSH6048D* |  | 49500 | 18 | 36000 | 3.6 | 4.125 | No
215832289 | Ground Loop | HYDROTECH | WSH6060D* |  | 60000 | 18.1 | 41000 | 3.6 | 5 | No
215832290 | Ground Loop | HYDROTECH | WSH6072D* |  | 73000 | 17.1 | 55000 | 3.6 | 6.0833 | No
215832291 | Ground Loop | AE Air | WSH6009D* |  | 9500 | 18.9 | 6500 | 3.6 | 0.79167 | No
215832292 | Ground Loop | AE Air | WSH6012D* |  | 12000 | 17.9 | 8500 | 3.8 | 1 | No
215832293 | Ground Loop | AE Air | WSH6018D* |  | 19000 | 18 | 12000 | 3.6 | 1.5833 | No
215832294 | Ground Loop | AE Air | WSH6024D* |  | 26000 | 18.4 | 17500 | 3.6 | 2.1667 | No
215832295 | Ground Loop | AE Air | WSH6030D* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
215832296 | Ground Loop | AE Air | WSH6036D* |  | 36400 | 18 | 28000 | 3.6 | 3.0333 | No
215832297 | Ground Loop | AE Air | WSH6042D* |  | 43500 | 18.5 | 31000 | 3.8 | 3.625 | No
215832298 | Ground Loop | AE Air | WSH6048D* |  | 49500 | 18 | 36000 | 3.6 | 4.125 | No
215832299 | Ground Loop | AE Air | WSH6060D* |  | 60000 | 18.1 | 41000 | 3.6 | 5 | No
215832300 | Ground Loop | AE Air | WSH6072D* |  | 73000 | 17.1 | 55000 | 3.6 | 6.0833 | No
217752725 | Ground Loop | DAIKIN | WSTH024K1*H*C |  | 25100 | 19.32 | 17200 | 3.8 | 2.0917 | No
217752727 | Ground Loop | DAIKIN | WSTH030K1*H*C |  | 32700 | 19.1 | 20600 | 3.64 | 2.725 | No
217752729 | Ground Loop | DAIKIN | WSTH036K1*H*C |  | 38700 | 20.02 | 25900 | 3.64 | 3.225 | No
217752734 | Ground Loop | DAIKIN | WSTH048K1*H*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083 | No
217752735 | Ground Loop | DAIKIN | WSTH048L1*H*C |  | 49300 | 19 | 36300 | 3.76 | 4.1083 | No
217752738 | Ground Loop | DAIKIN | WSTH060K1*H*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333 | No
215285739 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | Yes
215285740 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667 | Yes
215285741 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083 | Yes
215285742 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | Yes
215285743 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | Yes
216801983 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**3*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801984 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**3*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801985 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**3*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801986 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**3*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801987 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**4*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801988 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**4*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801989 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**4*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
215852856 | Ground Loop | DAIKIN | WSTH036E1*G/J*C |  | 38700 | 20.64 | 25900 | 3.75 | 3.225 | No
215852857 | Ground Loop | DAIKIN | WSTH036F3*G/J*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225 | No
215852860 | Ground Loop | DAIKIN | WSTH042E1*G/J*C |  | 45900 | 20.06 | 28400 | 3.7 | 3.825 | No
215852861 | Ground Loop | DAIKIN | WSTH042F3*G/J*C |  | 45900 | 19.66 | 28400 | 3.63 | 3.825 | No
217754670 | Ground Loop | DAIKIN | WSMV042K1*G/J*T |  | 42600 | 19.67 | 29700 | 3.63 | 3.55 | No
217754674 | Ground Loop | DAIKIN | WSMV042K1*G/J*C |  | 42600 | 19.67 | 29700 | 3.63 | 3.55 | No
217754678 | Ground Loop | DAIKIN | WSMV048F1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
217754679 | Ground Loop | DAIKIN | WSMV048K1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
217754680 | Ground Loop | DAIKIN | WSMV048L1*G/J*P |  | 49700 | 18.61 | 36700 | 3.64 | 4.1417 | No
217754683 | Ground Loop | DAIKIN | WSMV048F1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
217754684 | Ground Loop | DAIKIN | WSMV048K1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
217754687 | Ground Loop | DAIKIN | WSMV048F1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
217754688 | Ground Loop | DAIKIN | WSMV048K1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
217754697 | Ground Loop | DAIKIN | WSMV060F1*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
217754698 | Ground Loop | DAIKIN | WSMV060K1*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
217754701 | Ground Loop | DAIKIN | WSMV060F1*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
217754702 | Ground Loop | DAIKIN | WSMV060K1*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
10304639 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10304640 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10304641 | Ground Loop | GeoSmart Energy | GTZ026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10304642 | Ground Loop | GEOSTAR | 103H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
10304646 | Ground Loop | GEOSTAR | 103H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10304657 | Ground Loop | GeoSmart Energy | GTZ026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
10305457 | Ground Loop | GEOSTAR | 104H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10305458 | Ground Loop | GEOSTAR | 104H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316642 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316643 | Ground Loop | GeoSmart Energy | GTS026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316644 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316645 | Ground Loop | GeoSmart Energy | GTS026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316654 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316655 | Ground Loop | GEOSTAR | 104H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316656 | Ground Loop | GeoSmart Energy | GTS049*1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316657 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316658 | Ground Loop | GeoSmart Energy | GTS049*1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316660 | Ground Loop | GEOSTAR | 104H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316661 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
9038320 | Ground Loop | HYDRON MODULE | HZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038321 | Ground Loop | TETCO | TZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
214595621 | Ground Loop | AAON, Inc. | M2-004-2-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325 | No
215852864 | Ground Loop | DAIKIN | WSTH060E1*G/J*C |  | 61600 | 19 | 44200 | 3.7 | 5.1333 | No
215852865 | Ground Loop | DAIKIN | WSTH060F3*G/J*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333 | No
215852872 | Ground Loop | DAIKIN | WSTV030E1*G/J*C |  | 32200 | 19.48 | 20800 | 3.78 | 2.6833 | No
215852873 | Ground Loop | DAIKIN | WSTV030F3*G/J*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833 | No
215852876 | Ground Loop | DAIKIN | WSTV036E1*G/J*C |  | 39100 | 21.12 | 25600 | 3.68 | 3.2583 | No
215852877 | Ground Loop | DAIKIN | WSTV036F3*G/J*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583 | No
215852880 | Ground Loop | DAIKIN | WSTV042E1*G/J*C |  | 44800 | 19.54 | 27600 | 3.74 | 3.7333 | No
215852881 | Ground Loop | DAIKIN | WSTV042F3*G/J*C |  | 44800 | 19.15 | 27600 | 3.66 | 3.7333 | No
215852886 | Ground Loop | DAIKIN | WSTV060E1*G/J*C |  | 63100 | 19.6 | 46800 | 4.1 | 5.2583 | No
215852887 | Ground Loop | DAIKIN | WSTV060F3*G/J*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583 | No
216739885 | Ground Loop | DAIKIN | WSDV036E1*G/J*C |  | 37100 | 19 | 27300 | 3.8 | 3.0917 | No
216739886 | Ground Loop | DAIKIN | WSDV036F3*G/J*C |  | 37100 | 18.6 | 27300 | 3.7 | 3.0917 | No
216739887 | Ground Loop | DAIKIN | WSDV036J1*G/J*C |  | 37100 | 18.6 | 27300 | 3.7 | 3.0917 | No
216739888 | Ground Loop | DAIKIN | WSDV036K3*G/J*C |  | 37100 | 18.4 | 27300 | 3.7 | 3.0917 | No
216739901 | Ground Loop | DAIKIN | WSDV060E1*G/J*C |  | 62000 | 17.3 | 46100 | 3.7 | 5.1667 | No
216739902 | Ground Loop | DAIKIN | WSDV060F3*G/J*C |  | 62000 | 17 | 46100 | 3.6 | 5.1667 | No
216739903 | Ground Loop | DAIKIN | WSDV060K3*G/J*C |  | 62000 | 17 | 46100 | 3.6 | 5.1667 | No
5646388 | Ground Loop | HYDRON MODULE | HCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646389 | Ground Loop | TETCO | TCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646391 | Ground Loop | GEOCOMFORT | GXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | Yes
5646392 | Ground Loop | HYDRON MODULE | HXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | Yes
5646393 | Ground Loop | TETCO | TXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | Yes
5646394 | Ground Loop | GEOCOMFORT | GXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646395 | Ground Loop | HYDRON MODULE | HXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646396 | Ground Loop | TETCO | TXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646397 | Ground Loop | GEOCOMFORT | GXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646398 | Ground Loop | HYDRON MODULE | HXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646399 | Ground Loop | TETCO | TXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646765 | Ground Loop | GEOCOMFORT | GCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | Yes
5646766 | Ground Loop | HYDRON MODULE | HCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | Yes
5646767 | Ground Loop | TETCO | TCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | Yes
5646768 | Ground Loop | GEOCOMFORT | GCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646769 | Ground Loop | HYDRON MODULE | HCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646770 | Ground Loop | TETCO | TCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646771 | Ground Loop | GEOCOMFORT | GCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646772 | Ground Loop | HYDRON MODULE | HCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646773 | Ground Loop | TETCO | TCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5699505 | Ground Loop | TRANE | VSVE0421 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85 | No
5699525 | Ground Loop | TRANE | VSVE0422 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85 | No
5699526 | Ground Loop | TRANE | VSVE0424 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85 | No
5699527 | Ground Loop | TRANE | VSVE0601 |  | 64600 | 18.3 | 50000 | 4 | 5.3833 | No
5699534 | Ground Loop | TRANE | VSVE0602 |  | 64600 | 18.3 | 50000 | 4 | 5.3833 | No
5699535 | Ground Loop | TRANE | VSVE0604 |  | 64600 | 18.3 | 50000 | 4 | 5.3833 | No
5699628 | Ground Loop | TRANE | VSHE0241 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833 | No
5699631 | Ground Loop | TRANE | VSHE0242 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833 | No
5699633 | Ground Loop | TRANE | VSHE0244 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833 | No
5699634 | Ground Loop | TRANE | VSHE0331 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417 | No
5699635 | Ground Loop | TRANE | VSHE0332 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417 | No
5699637 | Ground Loop | TRANE | VSHE0334 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417 | No
5699639 | Ground Loop | TRANE | VSHE0421 |  | 44600 | 22 | 31500 | 4.5 | 3.7167 | No
5699644 | Ground Loop | TRANE | VSHE0422 |  | 44600 | 22 | 31500 | 4.5 | 3.7167 | No
5699650 | Ground Loop | TRANE | VSHE0424 |  | 44600 | 22 | 31500 | 4.5 | 3.7167 | No
5699652 | Ground Loop | TRANE | VSHE0501 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667 | No
5699653 | Ground Loop | TRANE | VSHE0502 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667 | No
5699654 | Ground Loop | TRANE | VSHE0504 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667 | No
5699655 | Ground Loop | TRANE | VSHE0601 |  | 63200 | 17 | 50400 | 3.8 | 5.2667 | No
6501973 | Ground Loop | GEOSTAR | GBV/GBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501974 | Ground Loop | GEOSTAR | GBV/GBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501975 | Ground Loop | GEOSTAR | GBV/GBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501976 | Ground Loop | GEOSTAR | GBV/GBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
6501977 | Ground Loop | GEOSTAR | GBV/GBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501978 | Ground Loop | GEOSTAR | GBV/GBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501979 | Ground Loop | GEOSTAR | GBV/GBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
6501980 | Ground Loop | GEOSTAR | GBV/GBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501981 | Ground Loop | GEOSTAR | GBV/GBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501982 | Ground Loop | GEOSTAR | GBV/GBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
6501983 | Ground Loop | GEOSTAR | GBV/GBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501984 | Ground Loop | GEOSTAR | GBV/GBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501985 | Ground Loop | GEOSTAR | GBV/GBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
6501986 | Ground Loop | GEOSTAR | GBV/GBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501987 | Ground Loop | GEOSTAR | GBV/GBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501988 | Ground Loop | GEOSTAR | GBV/GBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501989 | Ground Loop | GEOSTAR | GBV/GBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501990 | Ground Loop | GEOSTAR | GBV/GBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501991 | Ground Loop | GEOSTAR | GBV/GBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501993 | Ground Loop | GEOSTAR | GBV/GBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6501994 | Ground Loop | GEOSTAR | GBV/GBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6501996 | Ground Loop | GEOSTAR | GBV/GBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6501997 | Ground Loop | GEOSTAR | GBV/GBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6501999 | Ground Loop | GEOSTAR | GBV/GBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6502000 | Ground Loop | GEOSTAR | GBV/GBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6502002 | Ground Loop | GEOSTAR | GBV/GBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502003 | Ground Loop | GEOSTAR | GBV/GBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502004 | Ground Loop | GEOSTAR | GBV/GBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502005 | Ground Loop | GEOSTAR | GBV/GBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502006 | Ground Loop | GEOSTAR | GBV/GBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502007 | Ground Loop | GEOSTAR | GBV/GBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
206346937 | Ground Loop | DAIKIN | WCCW*019*E***14* |  | 20600 | 19 | 14000 | 3.7 | 1.7167 | No
206346938 | Ground Loop | DAIKIN | WCCW*019*J***14* |  | 20600 | 19 | 14000 | 3.7 | 1.7167 | No
206346939 | Ground Loop | DAIKIN | WCCW*024*E***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
206346940 | Ground Loop | DAIKIN | WCCW*024*F***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
206346941 | Ground Loop | DAIKIN | WCCW*024*J***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
206346942 | Ground Loop | DAIKIN | WCCW*024*K***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
206346943 | Ground Loop | DAIKIN | WVFW*019*E***14 |  | 19700 | 19 | 13400 | 3.7 | 1.6417 | No
206346944 | Ground Loop | DAIKIN | WVFW*019*J***14 |  | 19700 | 19 | 13400 | 3.7 | 1.6417 | No
206346948 | Ground Loop | DAIKIN | WVFW*024*E***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
206346949 | Ground Loop | DAIKIN | WVFW*024*F***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
206346950 | Ground Loop | DAIKIN | WVFW*024*J***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
206346954 | Ground Loop | DAIKIN | WVFW*030*E***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
206346955 | Ground Loop | DAIKIN | WVFW*030*F***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
206346956 | Ground Loop | DAIKIN | WVFW*030*J***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
206346966 | Ground Loop | DAIKIN | WVFW*042*E***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
206346967 | Ground Loop | DAIKIN | WVFW*042*F***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
206346968 | Ground Loop | DAIKIN | WVFW*042*K***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
206346972 | Ground Loop | DAIKIN | WVFW*048*E***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
206346973 | Ground Loop | DAIKIN | WVFW*048*F***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
206346974 | Ground Loop | DAIKIN | WVFW*048*K***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
206346978 | Ground Loop | DAIKIN | WVFW*060*E***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
206346979 | Ground Loop | DAIKIN | WVFW*060*F***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
206346980 | Ground Loop | DAIKIN | WVFW*060*K***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
207335338 | Ground Loop | GEOSTAR | 111K038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | Yes
207335397 | Ground Loop | GeoSmart Energy | GT026**1*(1,4)*J |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335398 | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335399 | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335400 | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335401 | Ground Loop | GeoSmart Energy | GT072**1*(1,4)*J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335403 | Ground Loop | GeoSmart Energy | GS018**1*(1,4)*J |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
207335406 | Ground Loop | GeoSmart Energy | GS022**1*(1,4)*J |  | 19200 | 18.7 | 15000 | 4 | 1.6 | Yes
207335407 | Ground Loop | GeoSmart Energy | GS030**1*(0,3)*J |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | Yes
207335408 | Ground Loop | GeoSmart Energy | GS030**1*(1,4)*J |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
207335409 | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*K |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | Yes
207335410 | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*K |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | Yes
207335413 | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*K |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
207335414 | Ground Loop | GeoSmart Energy | GS060**1*(1,4)*K |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
207335415 | Ground Loop | GeoSmart Energy | GS060**1*0*K |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | Yes
207335416 | Ground Loop | GeoSmart Energy | GS070**1*(1,4)*J |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
207335514 | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
207335571 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****J |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
207335572 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(1,4)****J |  | 19200 | 18.7 | 15000 | 4 | 1.6 | Yes
207335573 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
207335574 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*K |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | Yes
207335575 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
207335576 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*K |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
207335577 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****K |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
207335578 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****J |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
207335579 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****J |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335580 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335581 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335582 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335583 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335584 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****H |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335585 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335586 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335587 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
216979849 | Ground Loop | HEIL | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979850 | Ground Loop | ARCOAIRE | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979851 | Ground Loop | KEEPRITE | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979852 | Ground Loop | TEMPSTAR | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979853 | Ground Loop | COMFORTMAKER | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979854 | Ground Loop | DAY & NIGHT | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979855 | Ground Loop | HEIL | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979856 | Ground Loop | ARCOAIRE | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979857 | Ground Loop | KEEPRITE | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979858 | Ground Loop | TEMPSTAR | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979859 | Ground Loop | COMFORTMAKER | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979860 | Ground Loop | DAY & NIGHT | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979861 | Ground Loop | HEIL | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979862 | Ground Loop | ARCOAIRE | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979863 | Ground Loop | KEEPRITE | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979864 | Ground Loop | TEMPSTAR | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979865 | Ground Loop | COMFORTMAKER | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979866 | Ground Loop | DAY & NIGHT | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979867 | Ground Loop | HEIL | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979868 | Ground Loop | ARCOAIRE | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979869 | Ground Loop | KEEPRITE | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979870 | Ground Loop | TEMPSTAR | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979871 | Ground Loop | COMFORTMAKER | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979872 | Ground Loop | DAY & NIGHT | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979873 | Ground Loop | HEIL | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979874 | Ground Loop | ARCOAIRE | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979875 | Ground Loop | KEEPRITE | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979876 | Ground Loop | TEMPSTAR | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979877 | Ground Loop | COMFORTMAKER | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979878 | Ground Loop | DAY & NIGHT | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979879 | Ground Loop | HEIL | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979880 | Ground Loop | ARCOAIRE | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979881 | Ground Loop | KEEPRITE | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979882 | Ground Loop | TEMPSTAR | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979883 | Ground Loop | COMFORTMAKER | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979884 | Ground Loop | DAY & NIGHT | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979885 | Ground Loop | HEIL | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216979886 | Ground Loop | ARCOAIRE | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979887 | Ground Loop | KEEPRITE | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979888 | Ground Loop | TEMPSTAR | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979889 | Ground Loop | COMFORTMAKER | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979890 | Ground Loop | DAY & NIGHT | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979891 | Ground Loop | HEIL | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979892 | Ground Loop | ARCOAIRE | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979893 | Ground Loop | KEEPRITE | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979894 | Ground Loop | TEMPSTAR | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979895 | Ground Loop | COMFORTMAKER | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979896 | Ground Loop | DAY & NIGHT | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
217014524 | Ground Loop | CARRIER | GCA72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014525 | Ground Loop | BRYANT | GCA72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
7487661 | Ground Loop | GEOCOMFORT | GYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | Yes
7487662 | Ground Loop | HYDRON MODULE | HYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | Yes
7487663 | Ground Loop | TETCO | TYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | Yes
7487664 | Ground Loop | TETCO | TYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487665 | Ground Loop | HYDRON MODULE | HYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487666 | Ground Loop | GEOCOMFORT | GYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487667 | Ground Loop | GEOCOMFORT | GYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487668 | Ground Loop | HYDRON MODULE | HYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487669 | Ground Loop | TETCO | TYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7499543 | Ground Loop | FHP | LM024-1CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7499546 | Ground Loop | FHP | LM024-2CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7499547 | Ground Loop | FHP | LM024-3CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7499548 | Ground Loop | FHP | LM024-4CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7499550 | Ground Loop | FHP | LM036-1VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7499552 | Ground Loop | FHP | LM036-2VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7499553 | Ground Loop | FHP | LM036-3VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7499554 | Ground Loop | FHP | LM036-4VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7499556 | Ground Loop | FHP | LM048-1VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7499559 | Ground Loop | FHP | LM048-3VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7499560 | Ground Loop | FHP | LM048-4VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7499562 | Ground Loop | FHP | LM060-1VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
5440573 | Ground Loop | GEOCOMFORT | GXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440574 | Ground Loop | HYDRON MODULE | HXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440575 | Ground Loop | TETCO | TXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440576 | Ground Loop | GEOCOMFORT | GXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440577 | Ground Loop | HYDRON MODULE | HXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440578 | Ground Loop | TETCO | TXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440703 | Ground Loop | GEOCOMFORT | GXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440704 | Ground Loop | HYDRON MODULE | HXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440705 | Ground Loop | TETCO | TXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440708 | Ground Loop | GEOCOMFORT | GXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440709 | Ground Loop | HYDRON MODULE | HXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440710 | Ground Loop | TETCO | TXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5599272 | Ground Loop | BOSCH-GEO | SM036-1CF/HZ/VT |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
5599275 | Ground Loop | BOSCH-GEO | SM060-1CF/HZ/VT |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
217037819 | Ground Loop | GeoSmart Energy | S5SZ060BD1 | S5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037821 | Ground Loop | GeoSmart Energy | S5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037822 | Ground Loop | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037823 | Ground Loop | GeoSmart Energy | S5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037824 | Ground Loop | GeoSmart Energy | S5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037826 | Ground Loop | GeoSmart Energy | S5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037827 | Ground Loop | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037828 | Ground Loop | GeoSmart Energy | S5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037829 | Ground Loop | GeoSmart Energy | S5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217351748 | Ground Loop | CARRIER | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351749 | Ground Loop | CARRIER | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351757 | Ground Loop | BRYANT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351758 | Ground Loop | BRYANT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351761 | Ground Loop | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351762 | Ground Loop | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351763 | Ground Loop | BRYANT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351765 | Ground Loop | BRYANT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351766 | Ground Loop | BRYANT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351768 | Ground Loop | BRYANT | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351769 | Ground Loop | BRYANT | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351770 | Ground Loop | BRYANT | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351771 | Ground Loop | BRYANT | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351772 | Ground Loop | BRYANT | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351774 | Ground Loop | BRYANT | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351775 | Ground Loop | BRYANT | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351776 | Ground Loop | BRYANT | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
7167540 | Ground Loop | CARRIER | 50PTD/H/V024***4/DA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7167541 | Ground Loop | CARRIER | 50PTD/H/V024***6/FA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7167542 | Ground Loop | CARRIER | 50PTD/H/V036***3/CA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7167543 | Ground Loop | CARRIER | 50PTD/H/V036***5/EA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7167544 | Ground Loop | CARRIER | 50PTD/H/V036***4/DA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7167545 | Ground Loop | CARRIER | 50PTD/H/V036***6/FA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7167546 | Ground Loop | CARRIER | 50PTD/H/V048***3/CA |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7167547 | Ground Loop | CARRIER | 50PTD/H/V048***5/EA |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7167548 | Ground Loop | CARRIER | 50PTD/H/V048***6/FA |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7167549 | Ground Loop | CARRIER | 50PTD/H/V060***3/CA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7167550 | Ground Loop | CARRIER | 50PTD/H/V060***5/EA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7167551 | Ground Loop | CARRIER | 50PTD/H/V060***6/FA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7170602 | Ground Loop | GEOCOMFORT | GVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | Yes
7170603 | Ground Loop | HYDRON MODULE | HVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | Yes
7170604 | Ground Loop | TETCO | TVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | Yes
206438719 | Ground Loop | BOSCH | EP009-1HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
216569714 | Ground Loop | GeoCool | GCHPV/H/D036BT**A*** |  | 39000 | 17.86 | 28500 | 4.2 | 3.25 | No
216621310 | Ground Loop | GEOSTAR | G5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216621311 | Ground Loop | GEOSTAR | G5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216621312 | Ground Loop | GEOSTAR | G5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216621313 | Ground Loop | GEOSTAR | G5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216621314 | Ground Loop | GEOSTAR | G5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216621315 | Ground Loop | GEOSTAR | G5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216621316 | Ground Loop | GEOSTAR | G5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216621317 | Ground Loop | GEOSTAR | G5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216621318 | Ground Loop | GEOSTAR | G5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216621319 | Ground Loop | GEOSTAR | G5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216621323 | Ground Loop | GEOSTAR | G5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216621324 | Ground Loop | GEOSTAR | G5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216621325 | Ground Loop | GEOSTAR | G5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621326 | Ground Loop | GEOSTAR | G5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621327 | Ground Loop | GEOSTAR | G5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621328 | Ground Loop | GEOSTAR | G5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621329 | Ground Loop | GEOSTAR | G5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621330 | Ground Loop | GEOSTAR | G5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621331 | Ground Loop | GEOSTAR | G5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621332 | Ground Loop | GEOSTAR | G5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621333 | Ground Loop | GEOSTAR | G5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216621334 | Ground Loop | GEOSTAR | G5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216621335 | Ground Loop | GEOSTAR | G5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216621336 | Ground Loop | GEOSTAR | G5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216621337 | Ground Loop | GEOSTAR | G5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621338 | Ground Loop | GEOSTAR | G5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621339 | Ground Loop | GEOSTAR | G5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621340 | Ground Loop | GEOSTAR | G5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621341 | Ground Loop | GEOSTAR | G5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621342 | Ground Loop | GEOSTAR | G5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621343 | Ground Loop | GEOSTAR | G5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621344 | Ground Loop | GEOSTAR | G5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621345 | Ground Loop | GEOSTAR | G5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621346 | Ground Loop | GEOSTAR | G5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621347 | Ground Loop | GEOSTAR | G5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621348 | Ground Loop | GEOSTAR | G5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621349 | Ground Loop | GEOSTAR | G5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621350 | Ground Loop | GEOSTAR | G5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621351 | Ground Loop | GEOSTAR | G5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621352 | Ground Loop | GEOSTAR | G5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621353 | Ground Loop | GEOSTAR | G5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621354 | Ground Loop | GEOSTAR | G5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621355 | Ground Loop | GEOSTAR | G5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216621356 | Ground Loop | GEOSTAR | G5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216621357 | Ground Loop | GEOSTAR | G5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216621358 | Ground Loop | GEOSTAR | G5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216621359 | Ground Loop | GEOSTAR | G5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
217967018 | Ground Loop | TRANE | VSHK024A |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167 | No
217967019 | Ground Loop | TRANE | VSVK024A |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917 | No
217967020 | Ground Loop | TRANE | VSHK033A |  | 33300 | 18.1 | 27700 | 4.1 | 2.775 | No
217967021 | Ground Loop | TRANE | VSVK033A |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417 | No
217967022 | Ground Loop | TRANE | VSHK042A |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167 | No
217967023 | Ground Loop | TRANE | VSVK042A |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417 | No
217967024 | Ground Loop | TRANE | VSHK050A |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417 | No
217967025 | Ground Loop | TRANE | VSVK050A |  | 50400 | 19.3 | 40400 | 4.3 | 4.2 | No
217967026 | Ground Loop | TRANE | VSHK060A |  | 61900 | 17 | 51400 | 3.9 | 5.1583 | No
217967027 | Ground Loop | TRANE | VSVK060A |  | 61200 | 17.9 | 49500 | 4.1 | 5.1 | No
217967028 | Ground Loop | TRANE | VSHK024B |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167 | No
217967029 | Ground Loop | TRANE | VSVK024B |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917 | No
217967030 | Ground Loop | TRANE | VSHK033B |  | 33300 | 18.1 | 27700 | 4.1 | 2.775 | No
217967031 | Ground Loop | TRANE | VSVK033B |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417 | No
217967032 | Ground Loop | TRANE | VSHK042B |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167 | No
217967033 | Ground Loop | TRANE | VSVK042B |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417 | No
217967034 | Ground Loop | TRANE | VSHK050B |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417 | No
217967035 | Ground Loop | TRANE | VSVK050B |  | 50400 | 19.3 | 40400 | 4.3 | 4.2 | No
217967036 | Ground Loop | TRANE | VSHK060B |  | 61900 | 17 | 51400 | 3.9 | 5.1583 | No
217967037 | Ground Loop | TRANE | VSVK060B |  | 61200 | 17.9 | 49500 | 4.1 | 5.1 | No
7519580 | Ground Loop | HYDRON MODULE | HVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519581 | Ground Loop | TETCO | TVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519582 | Ground Loop | GEOCOMFORT | GVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519583 | Ground Loop | HYDRON MODULE | HVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519584 | Ground Loop | TETCO | TVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519727 | Ground Loop | GEOCOMFORT | GVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | Yes
7519748 | Ground Loop | HYDRON MODULE | HVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | Yes
7519756 | Ground Loop | TETCO | TVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | Yes
7519769 | Ground Loop | GEOCOMFORT | GVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519770 | Ground Loop | HYDRON MODULE | HVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519771 | Ground Loop | TETCO | TVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519772 | Ground Loop | GEOCOMFORT | GVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519773 | Ground Loop | HYDRON MODULE | HVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519774 | Ground Loop | TETCO | TVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519775 | Ground Loop | GEOCOMFORT | GVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519776 | Ground Loop | HYDRON MODULE | HVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519777 | Ground Loop | TETCO | TVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7520238 | Ground Loop | GEOCOMFORT | GVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | Yes
7520239 | Ground Loop | HYDRON MODULE | HVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | Yes
7520240 | Ground Loop | TETCO | TVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | Yes
7520241 | Ground Loop | GEOCOMFORT | GVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520242 | Ground Loop | HYDRON MODULE | HVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520243 | Ground Loop | TETCO | TVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520244 | Ground Loop | TETCO | TVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520245 | Ground Loop | HYDRON MODULE | HVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520246 | Ground Loop | GEOCOMFORT | GVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520247 | Ground Loop | HYDRON MODULE | HVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520248 | Ground Loop | TETCO | TVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520249 | Ground Loop | GEOCOMFORT | GVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520250 | Ground Loop | GEOCOMFORT | GVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | Yes
7520251 | Ground Loop | HYDRON MODULE | HVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | Yes
7520252 | Ground Loop | TETCO | TVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | Yes
7520253 | Ground Loop | GEOCOMFORT | GVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520254 | Ground Loop | HYDRON MODULE | HVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520255 | Ground Loop | TETCO | TVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520256 | Ground Loop | GEOCOMFORT | GVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520257 | Ground Loop | HYDRON MODULE | HVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520258 | Ground Loop | TETCO | TVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520259 | Ground Loop | GEOCOMFORT | GVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520260 | Ground Loop | HYDRON MODULE | HVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520261 | Ground Loop | TETCO | TVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7523956 | Ground Loop | GEOCOMFORT | GVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | Yes
7523957 | Ground Loop | HYDRON MODULE | HVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | Yes
7523958 | Ground Loop | TETCO | TVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | Yes
7523959 | Ground Loop | GEOCOMFORT | GVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | No
7523960 | Ground Loop | HYDRON MODULE | HVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | No
7523961 | Ground Loop | TETCO | TVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | No
217642881 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642883 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642884 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642886 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
7410095 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
7410164 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
7410223 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
7410291 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
7410355 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
7410435 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
7410657 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
7410825 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
7410908 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
7411002 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
7411100 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7411231 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7411301 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
7411380 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7411778 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7411875 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
7411949 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
217351838 | Ground Loop | DAY & NIGHT | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351839 | Ground Loop | DAY & NIGHT | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351842 | Ground Loop | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351843 | Ground Loop | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351844 | Ground Loop | DAY & NIGHT | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351846 | Ground Loop | DAY & NIGHT | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351847 | Ground Loop | DAY & NIGHT | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351849 | Ground Loop | DAY & NIGHT | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351850 | Ground Loop | DAY & NIGHT | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351851 | Ground Loop | DAY & NIGHT | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351852 | Ground Loop | DAY & NIGHT | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351853 | Ground Loop | DAY & NIGHT | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351855 | Ground Loop | DAY & NIGHT | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351856 | Ground Loop | DAY & NIGHT | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351857 | Ground Loop | DAY & NIGHT | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351865 | Ground Loop | HEIL | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351866 | Ground Loop | HEIL | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351869 | Ground Loop | HEIL | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351870 | Ground Loop | HEIL | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351871 | Ground Loop | HEIL | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351873 | Ground Loop | HEIL | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351874 | Ground Loop | HEIL | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351876 | Ground Loop | HEIL | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351877 | Ground Loop | HEIL | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351878 | Ground Loop | HEIL | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351879 | Ground Loop | HEIL | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
6674620 | Ground Loop | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
6674621 | Ground Loop | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
6674622 | Ground Loop | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
6674623 | Ground Loop | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
6676515 | Ground Loop | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
6676516 | Ground Loop | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
6676518 | Ground Loop | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
6676519 | Ground Loop | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
6677645 | Ground Loop | BOSCH | LM048-1VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
6677682 | Ground Loop | BOSCH | LM048-3VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
6677754 | Ground Loop | BOSCH | LM048-4VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
6677875 | Ground Loop | BOSCH | LM060-1VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | No
6677876 | Ground Loop | BOSCH | LM060-3VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | No
6677878 | Ground Loop | BOSCH | LM060-4VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | No
203143790 | Ground Loop | TETCO | TVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203238019 | Ground Loop | BOSCH-GEO | BP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203238919 | Ground Loop | BOSCH-GEO | SM024-1VT/CFN-*****A |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167 | Yes
203238923 | Ground Loop | BOSCH-GEO | SM024-1HZC-*****A |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | No
203238926 | Ground Loop | BOSCH-GEO | SM024-1HZN-*****A |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | No
203253412 | Ground Loop | BOSCH | BP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203253413 | Ground Loop | BOSCH | SM024-1HZC-*****A |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | Yes
203253414 | Ground Loop | BOSCH | SM024-1HZC-*****C |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | Yes
203253415 | Ground Loop | BOSCH | SM024-1HZN-*****A |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | Yes
203253416 | Ground Loop | BOSCH | SM024-1HZN-*****C |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | Yes
203254061 | Ground Loop | BOSCH-GEO | SM070-1VT*-*****C |  | 71500 | 17.3 | 56000 | 3.7 | 5.9583 | Yes
203254465 | Ground Loop | BOSCH | SM070-1VT*******C |  | 71500 | 17.3 | 56000 | 3.7 | 5.9583 | Yes
203254606 | Ground Loop | CARRIER | GB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203254607 | Ground Loop | BRYANT | GB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254608 | Ground Loop | ARCOAIRE | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
213154474 | Ground Loop | GeoSmart Energy | GT038**1*1********L |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
213154475 | Ground Loop | GeoSmart Energy | GT049**1*1********L |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
213154476 | Ground Loop | GeoSmart Energy | GT064**1*1********L |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
213154477 | Ground Loop | GeoSmart Energy | GT072**1*1********L |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
213307834 | Ground Loop | GeoSmart Energy | QT038**1*(1,2)*****K |  | 36000 | 18.7 | 27400 | 3.9 | 3 | Yes
213307835 | Ground Loop | GeoSmart Energy | QT049**1*(1,2)*****J |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | Yes
213307837 | Ground Loop | GeoSmart Energy | QT072**1*1*****J |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | Yes
213502489 | Ground Loop | DAIKIN | WSMH007A1*G/J*T |  | 7400 | 18.8 | 5500 | 3.6 | 0.61667 | No
213502493 | Ground Loop | DAIKIN | WSMH007E1*G/J*T |  | 7600 | 19 | 5500 | 3.6 | 0.63333 | No
203265288 | Ground Loop | BOSCH-GEO | SM048-1VT/CFC-*****A |  | 51300 | 18.15 | 36900 | 3.9 | 4.275 | Yes
203265289 | Ground Loop | BOSCH-GEO | SM048-1VT/CFN-*****A |  | 51300 | 17.7 | 36900 | 3.6 | 4.275 | Yes
203265290 | Ground Loop | BOSCH-GEO | SM048-1HZC-*****A |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265291 | Ground Loop | BOSCH-GEO | SM048-1HZN-*****A |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203265529 | Ground Loop | BOSCH | SM048-1HZC-*****A |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265533 | Ground Loop | BOSCH | SM048-1HZC-*****C |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265538 | Ground Loop | BOSCH | SM048-1HZN-*****A |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203265540 | Ground Loop | BOSCH | SM048-1HZN-*****C |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203265973 | Ground Loop | CARRIER | GC048V/C**C***1**1 |  | 51300 | 18.15 | 36900 | 3.9 | 4.275 | Yes
203265976 | Ground Loop | BRYANT | GC048V/C**C***1*X1 |  | 51300 | 18.15 | 36900 | 3.9 | 4.275 | Yes
203265980 | Ground Loop | CARRIER | GC048V/C**N***1**1 |  | 51300 | 17.7 | 36900 | 3.6 | 4.275 | Yes
203265983 | Ground Loop | BRYANT | GC048V/C**N***1*X1 |  | 51300 | 17.7 | 36900 | 3.6 | 4.275 | Yes
203265987 | Ground Loop | CARRIER | GC048H**C***1**1 |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265989 | Ground Loop | BRYANT | GC048H**C***1*X1 |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265990 | Ground Loop | CARRIER | GC048H**N***1**1 |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203265991 | Ground Loop | BRYANT | GC048H**N***1*X1 |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203268807 | Ground Loop | BOSCH | SM060-1HZ*******C |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
203303751 | Ground Loop | BOSCH-GEO | BP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203303774 | Ground Loop | BOSCH | BP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303777 | Ground Loop | CARRIER | GB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203303778 | Ground Loop | BRYANT | GB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303779 | Ground Loop | HEIL | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203303780 | Ground Loop | ARCOAIRE | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303781 | Ground Loop | KEEPRITE | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303782 | Ground Loop | TEMPSTAR | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303783 | Ground Loop | COMFORTMAKER | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303784 | Ground Loop | DAY & NIGHT | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
211594122 | Ground Loop | TRANE | GEHG018A |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083 | No
211594123 | Ground Loop | TRANE | GEHG024A |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
211594124 | Ground Loop | TRANE | GEHG030A |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
211594125 | Ground Loop | TRANE | GEHG036A |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
211594129 | Ground Loop | TRANE | EXHG009A |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167 | No
211594130 | Ground Loop | TRANE | EXHG012A |  | 12300 | 19.5 | 9300 | 4 | 1.025 | No
211594131 | Ground Loop | TRANE | EXHG015A |  | 15800 | 19 | 12100 | 3.8 | 1.3167 | No
211594132 | Ground Loop | TRANE | EXHG018A |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333 | No
211594133 | Ground Loop | TRANE | EXHG024A |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
211594134 | Ground Loop | TRANE | EXHG030A |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
211594135 | Ground Loop | TRANE | EXHG036A |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
211594136 | Ground Loop | TRANE | EXHG042A |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
211594137 | Ground Loop | TRANE | EXHG048A |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
211594138 | Ground Loop | TRANE | EXHG060A |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
211594139 | Ground Loop | TRANE | EXHG070A |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
211594212 | Ground Loop | TRANE | DXHG024A |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
211594213 | Ground Loop | TRANE | DXHG036A |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
211594214 | Ground Loop | TRANE | DXHG048A |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
211594215 | Ground Loop | TRANE | DXHG060A |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
211594216 | Ground Loop | TRANE | DXHG070A |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
211594223 | Ground Loop | TRANE | GEHG0097 |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167 | No
211594224 | Ground Loop | TRANE | GEHG0127 |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083 | No
211594225 | Ground Loop | TRANE | GEHG0157 |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917 | No
211594226 | Ground Loop | TRANE | GEHG0187 |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083 | No
211594227 | Ground Loop | TRANE | GEHG024B |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
211594228 | Ground Loop | TRANE | GEHG0244 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
211594229 | Ground Loop | TRANE | GEHG0247 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
211594230 | Ground Loop | TRANE | GEHG030B |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
211594231 | Ground Loop | TRANE | GEHG0304 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
211594232 | Ground Loop | TRANE | GEHG0307 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
211594233 | Ground Loop | TRANE | GEHG036B |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
211594234 | Ground Loop | TRANE | GEHG0364 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
211594235 | Ground Loop | TRANE | GEHG0367 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
215415872 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415873 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415876 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415877 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415878 | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | Yes
215415879 | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | Yes
215415886 | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | Yes
215415887 | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | Yes
215415888 | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | Yes
215415889 | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | Yes
215415909 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | Yes
215415910 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | Yes
215415911 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667 | Yes
215415912 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667 | Yes
215415913 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083 | Yes
215415914 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083 | Yes
215415915 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | Yes
216726174 | Ground Loop | DAIKIN | WSRC007*A*G/J |  | 7400 | 19.4 | 4800 | 3.6 | 0.61667 | No
216726178 | Ground Loop | DAIKIN | WSRC009*A*G/J |  | 9100 | 18.9 | 6500 | 3.6 | 0.75833 | No
206185652 | Ground Loop | DAIKIN | WGCH048K1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185653 | Ground Loop | DAIKIN | WGCH048K1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
963507 | Ground Loop | WaterFurnace | NLV/NXV080T*3 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
963508 | Ground Loop | WaterFurnace | NLV/NXV080T*4 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
963509 | Ground Loop | WaterFurnace | NLV/NXV080T*5 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
963510 | Ground Loop | WaterFurnace | NLV/NXV095T*3 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
963511 | Ground Loop | WaterFurnace | NLV/NXV095T*4 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
963512 | Ground Loop | WaterFurnace | NLV/NXV095T*5 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
963513 | Ground Loop | WaterFurnace | NLV/NXV120T*3 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
963514 | Ground Loop | WaterFurnace | NLV/NXV120T*4 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
963515 | Ground Loop | WaterFurnace | NLV/NXV120T*5 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
1483426 | Ground Loop | BOSCH | BP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
1483428 | Ground Loop | BOSCH | BP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
1483429 | Ground Loop | BOSCH | BP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
202146929 | Ground Loop | HYDRON MODULE | HZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | No
202146930 | Ground Loop | TETCO | TZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | Yes
202146931 | Ground Loop | TETCO | TZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | No
202146932 | Ground Loop | TETCO | TZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | Yes
202146933 | Ground Loop | TETCO | TZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | No
202146936 | Ground Loop | GEOCOMFORT | GZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | Yes
202146939 | Ground Loop | HYDRON MODULE | HZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | Yes
202146942 | Ground Loop | TETCO | TZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | Yes
202146943 | Ground Loop | GEOCOMFORT | GZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | Yes
202146944 | Ground Loop | GEOCOMFORT | GZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146945 | Ground Loop | GEOCOMFORT | GZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146946 | Ground Loop | GEOCOMFORT | GZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146947 | Ground Loop | GEOCOMFORT | GZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146948 | Ground Loop | GEOCOMFORT | GZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | Yes
202146949 | Ground Loop | GEOCOMFORT | GZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146950 | Ground Loop | GEOCOMFORT | GZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146951 | Ground Loop | GEOCOMFORT | GZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146952 | Ground Loop | HYDRON MODULE | HZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | Yes
202146953 | Ground Loop | HYDRON MODULE | HZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
10272221 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10272222 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10298936 | Ground Loop | WaterFurnace | UVV/UVH036**0*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25 | No
10298937 | Ground Loop | WaterFurnace | UVV/UVH036**3*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25 | No
10298938 | Ground Loop | WaterFurnace | UVV/UVH036**4*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25 | No
10298941 | Ground Loop | WaterFurnace | UVV/UVH048**0*1 |  | 48000 | 20 | 38000 | 3.8 | 4 | No
10298942 | Ground Loop | WaterFurnace | UVV/UVH048**3*1 |  | 48000 | 20 | 38000 | 3.8 | 4 | No
10298943 | Ground Loop | WaterFurnace | UVV/UVH048**4*1 |  | 48000 | 20 | 38000 | 3.8 | 4 | No
10298944 | Ground Loop | WaterFurnace | UVV/UVH060**0*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667 | No
10298946 | Ground Loop | WaterFurnace | UVV/UVH060**3*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667 | No
10298947 | Ground Loop | WaterFurnace | UVV/UVH060**4*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667 | No
214839009 | Ground Loop | FHP | EC072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214839010 | Ground Loop | FHP | EC072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214839011 | Ground Loop | FHP | EC072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214839012 | Ground Loop | FHP | EC096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214839013 | Ground Loop | FHP | EC096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214839014 | Ground Loop | FHP | EC096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
202146873 | Ground Loop | GEOCOMFORT | GZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146874 | Ground Loop | GEOCOMFORT | GZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146875 | Ground Loop | GEOCOMFORT | GZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146876 | Ground Loop | HYDRON MODULE | HZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | Yes
202146877 | Ground Loop | HYDRON MODULE | HZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146878 | Ground Loop | HYDRON MODULE | HZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146879 | Ground Loop | HYDRON MODULE | HZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146880 | Ground Loop | TETCO | TZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | Yes
202146881 | Ground Loop | TETCO | TZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146882 | Ground Loop | TETCO | TZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146883 | Ground Loop | TETCO | TZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
207178493 | Ground Loop | GEOSTAR | 164J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207178495 | Ground Loop | GEOSTAR | 163J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207178496 | Ground Loop | GEOSTAR | 163J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207178497 | Ground Loop | GEOSTAR | 163J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207178498 | Ground Loop | GEOSTAR | 163J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207178499 | Ground Loop | GEOSTAR | 164J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207178500 | Ground Loop | GEOSTAR | 163J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207178519 | Ground Loop | GEOSTAR | 164H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207178520 | Ground Loop | GEOSTAR | 164H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207178521 | Ground Loop | GEOSTAR | 164H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207178522 | Ground Loop | GEOSTAR | 164H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207178525 | Ground Loop | GEOSTAR | 161/162J064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207178536 | Ground Loop | GEOSTAR | 163H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207198394 | Ground Loop | BOSCH | QV024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198395 | Ground Loop | BOSCH | QV024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198401 | Ground Loop | BOSCH | QV024-2HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198402 | Ground Loop | BOSCH | QV024-2HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198406 | Ground Loop | BOSCH | QV024-3HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198407 | Ground Loop | BOSCH | QV024-3HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198410 | Ground Loop | BOSCH | QV024-4HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198411 | Ground Loop | BOSCH | QV024-4HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198416 | Ground Loop | BOSCH | QV030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198417 | Ground Loop | BOSCH | QV030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198419 | Ground Loop | BOSCH | QV030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198420 | Ground Loop | BOSCH | QV030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198421 | Ground Loop | BOSCH | QV030-2HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198422 | Ground Loop | BOSCH | QV030-2HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198424 | Ground Loop | BOSCH | QV030-2VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198425 | Ground Loop | BOSCH | QV030-2VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198426 | Ground Loop | BOSCH | QV030-3HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198428 | Ground Loop | BOSCH | QV030-3HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198429 | Ground Loop | BOSCH | QV030-3VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198430 | Ground Loop | BOSCH | QV030-3VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198432 | Ground Loop | BOSCH | QV030-4HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198433 | Ground Loop | BOSCH | QV030-4HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198434 | Ground Loop | BOSCH | QV030-4VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198436 | Ground Loop | BOSCH | QV030-4VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198437 | Ground Loop | BOSCH | QV036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
214595688 | Ground Loop | AAON, Inc. | M2-007-2-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417 | No
214595689 | Ground Loop | AAON, Inc. | M2-007-2-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5 | No
214595690 | Ground Loop | AAON, Inc. | M2-007-3-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417 | No
214595691 | Ground Loop | AAON, Inc. | M2-007-3-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5 | No
214595692 | Ground Loop | AAON, Inc. | M2-007-4-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417 | No
214595693 | Ground Loop | AAON, Inc. | M2-007-4-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5 | No
207349379 | Ground Loop | WaterFurnace | NBV/NBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349380 | Ground Loop | WaterFurnace | NBV/NBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349381 | Ground Loop | WaterFurnace | NBV/NBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349382 | Ground Loop | WaterFurnace | NBV/NBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349383 | Ground Loop | WaterFurnace | NBV/NBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349384 | Ground Loop | WaterFurnace | NBV/NBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349385 | Ground Loop | WaterFurnace | NBV/NBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349386 | Ground Loop | WaterFurnace | NBV/NBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349387 | Ground Loop | WaterFurnace | NBV/NBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349388 | Ground Loop | WaterFurnace | NBV/NBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349389 | Ground Loop | WaterFurnace | NBV/NBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349390 | Ground Loop | WaterFurnace | NBV/NBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349391 | Ground Loop | WaterFurnace | NBV/NBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349392 | Ground Loop | WaterFurnace | NBV/NBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349393 | Ground Loop | WaterFurnace | NBV/NBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349394 | Ground Loop | WaterFurnace | NBV/NBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349395 | Ground Loop | WaterFurnace | NBV/NBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349396 | Ground Loop | WaterFurnace | NBV/NBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349397 | Ground Loop | WaterFurnace | NBV/NBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349398 | Ground Loop | WaterFurnace | NBV/NBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349399 | Ground Loop | WaterFurnace | NBV/NBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349400 | Ground Loop | WaterFurnace | NBV/NBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
206347002 | Ground Loop | DAIKIN | WCCW*030*E***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
206347003 | Ground Loop | DAIKIN | WCCW*030*F***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
206347004 | Ground Loop | DAIKIN | WCCW*030*J***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
206347005 | Ground Loop | DAIKIN | WCCW*030*K***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
206347006 | Ground Loop | DAIKIN | WCCW*036*E***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
206347007 | Ground Loop | DAIKIN | WCCW*036*F***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
206347008 | Ground Loop | DAIKIN | WCCW*036*J***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
206347009 | Ground Loop | DAIKIN | WCCW*036*K***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
206347010 | Ground Loop | DAIKIN | WCCW*042*E***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
206347011 | Ground Loop | DAIKIN | WCCW*042*F***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
206347012 | Ground Loop | DAIKIN | WCCW*042*K***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
206347013 | Ground Loop | DAIKIN | WCCW*048*E***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
206347014 | Ground Loop | DAIKIN | WCCW*048*F***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
206347015 | Ground Loop | DAIKIN | WCCW*048*K***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
206347016 | Ground Loop | DAIKIN | WCCW*060*E***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
206347017 | Ground Loop | DAIKIN | WCCW*060*F***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
206347018 | Ground Loop | DAIKIN | WCCW*060*K***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
206347036 | Ground Loop | DAIKIN | WCCW*015*J***14* |  | 16800 | 20.8 | 11500 | 3.8 | 1.4 | No
206347038 | Ground Loop | DAIKIN | WCCW*015*E***14* |  | 17200 | 20.8 | 11500 | 4 | 1.4333 | No
206422417 | Ground Loop | CENTURY | HBH/V015*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
206422418 | Ground Loop | COMFORT-AIRE | HBH/V015*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
206422419 | Ground Loop | CENTURY | HBH/V018*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
206422420 | Ground Loop | COMFORT-AIRE | HBH/V018*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
8738070 | Ground Loop | GEOCOMFORT | GVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738071 | Ground Loop | HYDRON MODULE | HVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738072 | Ground Loop | TETCO | TVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738073 | Ground Loop | GEOCOMFORT | GVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738074 | Ground Loop | HYDRON MODULE | HVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738075 | Ground Loop | TETCO | TVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738076 | Ground Loop | GEOCOMFORT | GVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738077 | Ground Loop | HYDRON MODULE | HVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738078 | Ground Loop | TETCO | TVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
203383888 | Ground Loop | CARRIER | 50PSV048***6/FA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383889 | Ground Loop | CARRIER | 50PSH048***3/CA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383890 | Ground Loop | CARRIER | 50PSH048***5/EA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383891 | Ground Loop | CARRIER | 50PSH048***6/FA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383892 | Ground Loop | FHP | EP018-1VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203383893 | Ground Loop | FHP | EP018-2VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203383894 | Ground Loop | FHP | EP018-1HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203383895 | Ground Loop | FHP | EP018-2HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203383896 | Ground Loop | FHP | EP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383897 | Ground Loop | FHP | EP042-3VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383898 | Ground Loop | FHP | EP042-4VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383899 | Ground Loop | FHP | EP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383900 | Ground Loop | FHP | EP042-3HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383901 | Ground Loop | FHP | EP042-4HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383902 | Ground Loop | FHP | EP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383903 | Ground Loop | FHP | EP048-3VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383904 | Ground Loop | FHP | EP048-4VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383905 | Ground Loop | FHP | EP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383906 | Ground Loop | FHP | EP048-3HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383907 | Ground Loop | FHP | EP048-4HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203459712 | Ground Loop | BOSCH-GEO | LM036-1CSC-*****B | LM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583 | No
203459725 | Ground Loop | FHP | LM036-1CSC-*****B | LM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583 | No
203459750 | Ground Loop | BOSCH | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 26200 | 17 | 17700 | 3.75 | 2.1833 | No
203459757 | Ground Loop | FHP | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 26200 | 17 | 17700 | 3.75 | 2.1833 | No
203466717 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
203471325 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
203490411 | Ground Loop | GeoSmart Energy | GTZ049*1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
203490420 | Ground Loop | GeoSmart Energy | GTZ049*1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
215837822 | Ground Loop | DAIKIN | WSSH024F3*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837824 | Ground Loop | DAIKIN | WSSH024J1*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837825 | Ground Loop | DAIKIN | WSSH024K3*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837831 | Ground Loop | DAIKIN | WSSH030F3*G/J*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
215837832 | Ground Loop | DAIKIN | WSSH030J1*G/J*T |  | 30600 | 21.15 | 21200 | 3.95 | 2.55 | No
215837833 | Ground Loop | DAIKIN | WSSH030K3*G/J*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
215837839 | Ground Loop | DAIKIN | WSSH030F3*G/J*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
215837840 | Ground Loop | DAIKIN | WSSH030J1*G/J*C |  | 30600 | 21.15 | 21200 | 3.95 | 2.55 | No
215837841 | Ground Loop | DAIKIN | WSSH030K3*G/J*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
215837847 | Ground Loop | DAIKIN | WSSH036F3*G/J*T |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583 | No
215837848 | Ground Loop | DAIKIN | WSSH036J1*G/J*T |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583 | No
215837850 | Ground Loop | DAIKIN | WSSH036K3*G/J*T |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583 | No
215837855 | Ground Loop | DAIKIN | WSSH036F3*G/J*C |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583 | No
215837856 | Ground Loop | DAIKIN | WSSH036J1*G/J*C |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583 | No
217754559 | Ground Loop | DAIKIN | WSMH036F1*G/J*P |  | 37800 | 18.18 | 30700 | 3.79 | 3.15 | No
217754560 | Ground Loop | DAIKIN | WSMH036K1*G/J*P |  | 37800 | 18.1 | 30700 | 3.79 | 3.15 | No
217754563 | Ground Loop | DAIKIN | WSMH036F1*G/J*T |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667 | No
217754564 | Ground Loop | DAIKIN | WSMH036K1*G/J*T |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667 | No
217754567 | Ground Loop | DAIKIN | WSMH036F1*G/J*C |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667 | No
217754568 | Ground Loop | DAIKIN | WSMH036K1*G/J*C |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667 | No
217754572 | Ground Loop | DAIKIN | WSMH042E1*G/J*P |  | 39900 | 17.5 | 32500 | 3.7 | 3.325 | No
217754573 | Ground Loop | DAIKIN | WSMH042F1*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325 | No
217754574 | Ground Loop | DAIKIN | WSMH042K1*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325 | No
217754578 | Ground Loop | DAIKIN | WSMH042E1*G/J*T |  | 40800 | 19.4 | 31600 | 3.8 | 3.4 | No
217754579 | Ground Loop | DAIKIN | WSMH042F1*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
217754580 | Ground Loop | DAIKIN | WSMH042K1*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
217754584 | Ground Loop | DAIKIN | WSMH042E1*G/J*C |  | 40800 | 19.4 | 31600 | 3.8 | 3.4 | No
217754585 | Ground Loop | DAIKIN | WSMH042F1*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
217754586 | Ground Loop | DAIKIN | WSMH042K1*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
217754591 | Ground Loop | DAIKIN | WSMH048E1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
217754592 | Ground Loop | DAIKIN | WSMH048F1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
217754593 | Ground Loop | DAIKIN | WSMH048K1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
217754594 | Ground Loop | DAIKIN | WSMH048L1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
217754598 | Ground Loop | DAIKIN | WSMH048E1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754599 | Ground Loop | DAIKIN | WSMH048F1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754600 | Ground Loop | DAIKIN | WSMH048K1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754604 | Ground Loop | DAIKIN | WSMH048E1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754605 | Ground Loop | DAIKIN | WSMH048F1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754606 | Ground Loop | DAIKIN | WSMH048K1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
202146884 | Ground Loop | GEOCOMFORT | GZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | Yes
202146885 | Ground Loop | GEOCOMFORT | GZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146886 | Ground Loop | GEOCOMFORT | GZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146887 | Ground Loop | HYDRON MODULE | HZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | Yes
202146888 | Ground Loop | HYDRON MODULE | HZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146889 | Ground Loop | HYDRON MODULE | HZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146890 | Ground Loop | TETCO | TZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | Yes
202146891 | Ground Loop | TETCO | TZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146892 | Ground Loop | TETCO | TZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146893 | Ground Loop | GEOCOMFORT | GZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | Yes
202146894 | Ground Loop | GEOCOMFORT | GZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146895 | Ground Loop | GEOCOMFORT | GZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146896 | Ground Loop | GEOCOMFORT | GZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146897 | Ground Loop | HYDRON MODULE | HZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | Yes
202146898 | Ground Loop | HYDRON MODULE | HZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146899 | Ground Loop | HYDRON MODULE | HZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146900 | Ground Loop | HYDRON MODULE | HZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146901 | Ground Loop | TETCO | TZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | Yes
202146902 | Ground Loop | TETCO | TZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146903 | Ground Loop | TETCO | TZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146913 | Ground Loop | GEOCOMFORT | GZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | Yes
202146914 | Ground Loop | GEOCOMFORT | GZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | No
202146915 | Ground Loop | GEOCOMFORT | GZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | Yes
202146916 | Ground Loop | HYDRON MODULE | HZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | Yes
202146917 | Ground Loop | HYDRON MODULE | HZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | No
202146918 | Ground Loop | HYDRON MODULE | HZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | Yes
202146919 | Ground Loop | TETCO | TZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | Yes
202146920 | Ground Loop | TETCO | TZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | No
202146921 | Ground Loop | TETCO | TZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | Yes
202146922 | Ground Loop | GEOCOMFORT | GZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | Yes
202146923 | Ground Loop | GEOCOMFORT | GZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | No
202146924 | Ground Loop | GEOCOMFORT | GZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | Yes
202146925 | Ground Loop | GEOCOMFORT | GZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | No
202146926 | Ground Loop | HYDRON MODULE | HZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | Yes
202146927 | Ground Loop | HYDRON MODULE | HZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | No
202146928 | Ground Loop | HYDRON MODULE | HZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | Yes
214606639 | Ground Loop | Dandelion Geo | DP1G072V3A1000S |  | 70000 | 17.5 | 61000 | 4.3 | 5.8333 | Yes
214771921 | Ground Loop | TRANE | GEVK009A |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333 | No
214771923 | Ground Loop | TRANE | GEVK015A |  | 15900 | 18.2 | 12500 | 3.85 | 1.325 | No
214771924 | Ground Loop | TRANE | GEVK018A |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417 | No
214771925 | Ground Loop | TRANE | GEVK024A |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214771926 | Ground Loop | TRANE | GEVK030A |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214771929 | Ground Loop | TRANE | GEVK048A |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214771930 | Ground Loop | TRANE | GEVK060A |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214771931 | Ground Loop | TRANE | EXVK009A |  | 9000 | 21.2 | 6100 | 3.91 | 0.75 | No
214771932 | Ground Loop | TRANE | EXVK012A |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167 | No
215893693 | Ground Loop | DUAL AIR | CFF024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | No
215893695 | Ground Loop | DUAL AIR | CFF031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | No
215893697 | Ground Loop | DUAL AIR | CFF036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | No
215893699 | Ground Loop | DUAL AIR | CFF041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | No
215893703 | Ground Loop | MIAMI HEAT PUMP | HPF024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | No
215893704 | Ground Loop | MIAMI HEAT PUMP | HPF031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | No
215893706 | Ground Loop | MIAMI HEAT PUMP | HPF036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | No
215893707 | Ground Loop | MIAMI HEAT PUMP | HPF041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | No
215893711 | Ground Loop | DUAL AIR | CFF049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833 | No
215893713 | Ground Loop | MIAMI HEAT PUMP | HPF049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833 | No
216014181 | Ground Loop | RHEEM | RPVV/H/D036D |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | Yes
216054107 | Ground Loop | WaterFurnace | W5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667 | Yes
216054108 | Ground Loop | WaterFurnace | W5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917 | Yes
216054109 | Ground Loop | WaterFurnace | W5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083 | Yes
216054110 | Ground Loop | WaterFurnace | W5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583 | Yes
216054475 | Ground Loop | GEOCOMFORT | GBS018* | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
216054476 | Ground Loop | GEOCOMFORT | GBT024* | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
216054477 | Ground Loop | GEOCOMFORT | GBT036* | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
216054478 | Ground Loop | GEOCOMFORT | GBT048* | EAD048 | 47800 | 17.3 | 41000 | 3.6 | 3.9833 | Yes
216054479 | Ground Loop | GEOCOMFORT | GVS009* |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | Yes
216054480 | Ground Loop | GEOCOMFORT | GVS012* |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167 | Yes
216054481 | Ground Loop | GEOCOMFORT | GVS018* |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | Yes
216054482 | Ground Loop | GEOCOMFORT | GVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
216054483 | Ground Loop | GEOCOMFORT | GVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
216054484 | Ground Loop | GEOCOMFORT | GVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
216054485 | Ground Loop | GEOCOMFORT | GVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
216054486 | Ground Loop | GEOCOMFORT | GVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917 | Yes
216054487 | Ground Loop | GEOCOMFORT | GYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
216054488 | Ground Loop | GEOCOMFORT | GYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083 | Yes
216054489 | Ground Loop | GEOCOMFORT | GYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325 | Yes
216054492 | Ground Loop | GEOCOMFORT | GZT024* |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | Yes
216054493 | Ground Loop | GEOCOMFORT | GZT030* |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | Yes
216054494 | Ground Loop | GEOCOMFORT | GZT036* |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | Yes
216054495 | Ground Loop | GEOCOMFORT | GZT042* |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | Yes
216625808 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625809 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625810 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625811 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625812 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625813 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625814 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625815 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625816 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625817 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625818 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625819 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625820 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625821 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625822 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625823 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625824 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625825 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625826 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625827 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625828 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625829 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625830 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625831 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625832 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625833 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625834 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625835 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625836 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625837 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625838 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625839 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625840 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625841 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625842 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625843 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625844 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625845 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625846 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625847 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625848 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625849 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625850 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625851 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625852 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625853 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625854 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625855 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625856 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625857 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625858 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625859 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625860 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625861 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625862 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625863 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215224301 | Ground Loop | BOSCH-GEO | RF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224302 | Ground Loop | BOSCH-GEO | RF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224305 | Ground Loop | BOSCH-GEO | RF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224306 | Ground Loop | BOSCH-GEO | RF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
217642897 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642898 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642899 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642900 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642901 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642902 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642903 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642911 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642912 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642913 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642914 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642915 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642916 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642917 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642918 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
8964161 | Ground Loop | BRYANT | GC060C/H/V******1*X1 + UI |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
8964162 | Ground Loop | CARRIER | GC060C/H/V******1**1 + UI |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
9008839 | Ground Loop | BOSCH | ES025-1CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
9008840 | Ground Loop | BOSCH | ES025-2CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
9009353 | Ground Loop | FHP | ES025-1CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
9009366 | Ground Loop | FHP | ES025-2CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
207198813 | Ground Loop | BOSCH | WQ024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198814 | Ground Loop | BOSCH | WQ024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198817 | Ground Loop | BOSCH | WQ030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198818 | Ground Loop | BOSCH | WQ030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198819 | Ground Loop | BOSCH | WQ030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198820 | Ground Loop | BOSCH | WQ030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198821 | Ground Loop | BOSCH | WQ036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198823 | Ground Loop | BOSCH | WQ036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
216743652 | Ground Loop | BOSCH | CP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216743653 | Ground Loop | BOSCH | CP048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216743654 | Ground Loop | BOSCH | CP048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216743655 | Ground Loop | BOSCH-GEO | RP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216743656 | Ground Loop | BOSCH | CP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216743657 | Ground Loop | BOSCH | CP060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216743658 | Ground Loop | BOSCH | CP060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216743659 | Ground Loop | BOSCH-GEO | RP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216743660 | Ground Loop | BOSCH | CP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216743661 | Ground Loop | BOSCH | CP060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216743662 | Ground Loop | BOSCH | CP060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216743663 | Ground Loop | BOSCH-GEO | RP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
216743664 | Ground Loop | BOSCH | CP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743665 | Ground Loop | BOSCH | CP070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743666 | Ground Loop | BOSCH | CP070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743671 | Ground Loop | BOSCH-GEO | RP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
216743672 | Ground Loop | BOSCH | CP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743673 | Ground Loop | BOSCH | CP070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743674 | Ground Loop | BOSCH | CP070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216759674 | Ground Loop | WaterFurnace | W7SZ042BV1**F | W7BM042BN1**2 | 41600 | 19.3 | 41400 | 3.8 | 3.4667 | Yes
216759816 | Ground Loop | WaterFurnace | W5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216759817 | Ground Loop | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216759818 | Ground Loop | WaterFurnace | W5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216759819 | Ground Loop | WaterFurnace | W5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216759821 | Ground Loop | GEOSTAR | G5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216759822 | Ground Loop | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216759823 | Ground Loop | GEOSTAR | G5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
4219430 | Ground Loop | NORDIC | RH55HACW-P-1T-*-SDE** |  | 44400 | 17 | 34700 | 3.6 | 3.7 | No
4219434 | Ground Loop | NORDIC | TF55HACW-P-1T-*-SDE** |  | 45400 | 17.1 | 35400 | 3.8 | 3.7833 | Yes
4219444 | Ground Loop | NORDIC | RS55HACW-P-1T-* | AH-55-P-1-***** | 45400 | 17 | 35600 | 3.8 | 3.7833 | Yes
4230311 | Ground Loop | DAIKIN | WCCW4015*E*01* |  | 16700 | 18.7 | 11400 | 3.7 | 1.3917 | No
214772079 | Ground Loop | TRANE | EXVK0244 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772080 | Ground Loop | TRANE | EXVK0247 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772081 | Ground Loop | TRANE | EXVK030B |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772082 | Ground Loop | TRANE | EXVK0304 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772083 | Ground Loop | TRANE | EXVK0307 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772084 | Ground Loop | TRANE | EXVK036B |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772085 | Ground Loop | TRANE | EXVK0364 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772086 | Ground Loop | TRANE | EXVK0367 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772087 | Ground Loop | TRANE | EXVK042B |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214772088 | Ground Loop | TRANE | EXVK0424 |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214772089 | Ground Loop | TRANE | EXVK048B |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214772090 | Ground Loop | TRANE | EXVK0484 |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214772091 | Ground Loop | TRANE | EXVK060B |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214772092 | Ground Loop | TRANE | EXVK0604 |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214772093 | Ground Loop | TRANE | EXVK070B |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772094 | Ground Loop | TRANE | EXVK0704 |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772095 | Ground Loop | TRANE | DXVK024A |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772096 | Ground Loop | TRANE | DXVK036A |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772097 | Ground Loop | TRANE | DXVK048A |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772098 | Ground Loop | TRANE | DXVK060A |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772099 | Ground Loop | TRANE | DXVK070A |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772101 | Ground Loop | TRANE | GEHK0097 |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333 | No
214772103 | Ground Loop | TRANE | GEHK0157 |  | 15900 | 18.2 | 12500 | 3.85 | 1.325 | No
214772104 | Ground Loop | TRANE | GEHK0187 |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417 | No
214772105 | Ground Loop | TRANE | GEHK024B |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772106 | Ground Loop | TRANE | GEHK0244 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772107 | Ground Loop | TRANE | GEHK0247 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772108 | Ground Loop | TRANE | GEHK030B |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772109 | Ground Loop | TRANE | GEHK0304 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772110 | Ground Loop | TRANE | GEHK0307 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772116 | Ground Loop | TRANE | GEHK048B |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214772117 | Ground Loop | TRANE | GEHK0484 |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214772118 | Ground Loop | TRANE | GEHK060B |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214772119 | Ground Loop | TRANE | GEHK0604 |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214772120 | Ground Loop | TRANE | EXHK0097 |  | 9000 | 21.2 | 6100 | 3.91 | 0.75 | No
214772121 | Ground Loop | TRANE | EXHK0127 |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167 | No
214772122 | Ground Loop | TRANE | EXHK0157 |  | 16200 | 18.7 | 11800 | 3.73 | 1.35 | No
214772123 | Ground Loop | TRANE | EXHK0187 |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417 | No
214772124 | Ground Loop | TRANE | EXHK024B |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772125 | Ground Loop | TRANE | EXHK0244 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772126 | Ground Loop | TRANE | EXHK0247 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772127 | Ground Loop | TRANE | EXHK030B |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772128 | Ground Loop | TRANE | EXHK0304 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772129 | Ground Loop | TRANE | EXHK0307 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772130 | Ground Loop | TRANE | EXHK036B |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772131 | Ground Loop | TRANE | EXHK0364 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772132 | Ground Loop | TRANE | EXHK0367 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772133 | Ground Loop | TRANE | EXHK042B |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214772134 | Ground Loop | TRANE | EXHK0424 |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
216419921 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
216419924 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
216419941 | Ground Loop | Whalen | WZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | Yes
216419946 | Ground Loop | Whalen | WZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | Yes
202146867 | Ground Loop | HYDRON MODULE | HZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146868 | Ground Loop | HYDRON MODULE | HZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146869 | Ground Loop | TETCO | TZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | Yes
202146870 | Ground Loop | TETCO | TZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146871 | Ground Loop | TETCO | TZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146872 | Ground Loop | GEOCOMFORT | GZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | Yes
207657665 | Ground Loop | ClimateMaster | TSL24 D |  | 26500 | 19.4 | 18500 | 3.6 | 2.2083 | No
207657667 | Ground Loop | ClimateMaster | TSL30 D |  | 29500 | 18.4 | 21000 | 3.7 | 2.4583 | No
207822807 | Ground Loop | HYDROTECH | HRCX30*-6 |  | 28000 | 18 | 20000 | 3.6 | 2.3333 | Yes
207822813 | Ground Loop | HYDROTECH | HRCX36*-6 |  | 34100 | 17.1 | 25000 | 3.6 | 2.8417 | Yes
208106952 | Ground Loop | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
208106953 | Ground Loop | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
208106954 | Ground Loop | 5 SERIES GEO-READY | NGV/NGH064*1*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
215224045 | Ground Loop | BOSCH | CF018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224046 | Ground Loop | BOSCH | CF018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224047 | Ground Loop | BOSCH | CF024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224048 | Ground Loop | BOSCH | CF024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224049 | Ground Loop | BOSCH | CF024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224050 | Ground Loop | BOSCH | CF024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
205973168 | Ground Loop | Enertech | ERE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175 | No
205973779 | Ground Loop | COMFORT-AIRE | HEV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
205973780 | Ground Loop | CENTURY | HEV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
4947178 | Ground Loop | TRANE | VSVE0241 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583 | No
4947179 | Ground Loop | TRANE | VSVE0242 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583 | No
4947180 | Ground Loop | TRANE | VSVE0244 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583 | No
4947183 | Ground Loop | TRANE | VSVE0331 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583 | No
4947184 | Ground Loop | TRANE | VSVE0332 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583 | No
4947185 | Ground Loop | TRANE | VSVE0334 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583 | No
4947240 | Ground Loop | TRANE | VSVE0501 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083 | No
4947241 | Ground Loop | TRANE | VSVE0502 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083 | No
4947242 | Ground Loop | TRANE | VSVE0504 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083 | No
5211514 | Ground Loop | DAIKIN | WGSV/WGSH007B*A |  | 8400 | 18.1 | 6200 | 3.9 | 0.7 | No
5211515 | Ground Loop | DAIKIN | WGSV/WGSH007B*E |  | 8400 | 18.1 | 6200 | 3.9 | 0.7 | No
5211516 | Ground Loop | DAIKIN | WGSV/WGSH007B*J |  | 8400 | 18.1 | 6200 | 3.9 | 0.7 | No
5220636 | Ground Loop | DAIKIN | WGSV/WGSH012B*A |  | 13300 | 18.1 | 10000 | 3.9 | 1.1083 | No
5220637 | Ground Loop | DAIKIN | WGSV/WGSH012B*E |  | 13300 | 18.1 | 10000 | 3.9 | 1.1083 | No
5220638 | Ground Loop | DAIKIN | WGSV/WGSH012B*J |  | 13300 | 17.2 | 10000 | 3.8 | 1.1083 | No
5220663 | Ground Loop | DAIKIN | WGSV/WGSH015B*E |  | 16000 | 21.2 | 11700 | 4.1 | 1.3333 | No
5220664 | Ground Loop | DAIKIN | WGSV/WGSH015B*J |  | 16000 | 19.1 | 11700 | 3.8 | 1.3333 | No
206900466 | Ground Loop | WaterFurnace | UDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900467 | Ground Loop | WaterFurnace | UDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900469 | Ground Loop | WaterFurnace | UDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900470 | Ground Loop | WaterFurnace | UDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900471 | Ground Loop | WaterFurnace | UDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900472 | Ground Loop | WaterFurnace | UDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900473 | Ground Loop | WaterFurnace | UDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900474 | Ground Loop | WaterFurnace | UDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900475 | Ground Loop | WaterFurnace | UDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900553 | Ground Loop | GEOSTAR | GDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900554 | Ground Loop | GEOSTAR | GDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900555 | Ground Loop | GEOSTAR | GDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900556 | Ground Loop | GEOSTAR | GDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900557 | Ground Loop | GEOSTAR | GDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900558 | Ground Loop | GEOSTAR | GDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900559 | Ground Loop | GEOSTAR | GDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900560 | Ground Loop | GEOSTAR | GDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900561 | Ground Loop | GEOSTAR | GDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
211594242 | Ground Loop | TRANE | EXHG0097 |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167 | No
211594243 | Ground Loop | TRANE | EXHG0127 |  | 12300 | 19.5 | 9300 | 4 | 1.025 | No
211594244 | Ground Loop | TRANE | EXHG0157 |  | 15800 | 19 | 12100 | 3.8 | 1.3167 | No
211594245 | Ground Loop | TRANE | EXHG0187 |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333 | No
211594246 | Ground Loop | TRANE | EXHG024B |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
211594247 | Ground Loop | TRANE | EXHG0244 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
211594248 | Ground Loop | TRANE | EXHG0247 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
211594249 | Ground Loop | TRANE | EXHG030B |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
211594250 | Ground Loop | TRANE | EXHG0304 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
211594251 | Ground Loop | TRANE | EXHG0307 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
211594252 | Ground Loop | TRANE | EXHG036B |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
211594253 | Ground Loop | TRANE | EXHG0364 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
211594254 | Ground Loop | TRANE | EXHG0367 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
211594255 | Ground Loop | TRANE | EXHG042B |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
211594256 | Ground Loop | TRANE | EXHG0424 |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
211594257 | Ground Loop | TRANE | EXHG048B |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
211594258 | Ground Loop | TRANE | EXHG0484 |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
211594259 | Ground Loop | TRANE | EXHG060B |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
211594260 | Ground Loop | TRANE | EXHG0604 |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
211594261 | Ground Loop | TRANE | EXHG070B |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
211594262 | Ground Loop | TRANE | EXHG0704 |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
211594263 | Ground Loop | TRANE | DXHG024B |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
211594264 | Ground Loop | TRANE | DXHG0244 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
211594265 | Ground Loop | TRANE | DXHG0247 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
211594266 | Ground Loop | TRANE | DXHG036B |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
211594267 | Ground Loop | TRANE | DXHG0364 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
211594268 | Ground Loop | TRANE | DXHG0367 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
211594269 | Ground Loop | TRANE | DXHG048B |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
211594270 | Ground Loop | TRANE | DXHG0484 |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
211594271 | Ground Loop | TRANE | DXHG060B |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
211594272 | Ground Loop | TRANE | DXHG0604 |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
211594273 | Ground Loop | TRANE | DXHG070B |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
211594274 | Ground Loop | TRANE | DXHG0704 |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
212428693 | Ground Loop | HYDROTECH | WSH6009A6* |  | 9500 | 18.9 | 6800 | 3.6 | 0.79167 | Yes
212428694 | Ground Loop | HYDROTECH | WSH6012A6* |  | 12000 | 18.2 | 8500 | 3.8 | 1 | Yes
212428695 | Ground Loop | HYDROTECH | WSH6018A6* |  | 19000 | 19 | 12000 | 3.6 | 1.5833 | Yes
212428696 | Ground Loop | HYDROTECH | WSH6024A6* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | Yes
212428697 | Ground Loop | HYDROTECH | WSH6030A6* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | Yes
8964157 | Ground Loop | BRYANT | GC036C/H/V******1*X1 + UI |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | Yes
8964158 | Ground Loop | CARRIER | GC036C/H/V******1**1 + UI |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | Yes
203993050 | Ground Loop | GEOSTAR | 111H049**1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
203993052 | Ground Loop | GEOSTAR | 111H072**1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
207083977 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083981 | Ground Loop | CARRIER | 50PCV036J/K*C/A5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083985 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202211042 | Ground Loop | WaterFurnace | URD038*0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211043 | Ground Loop | WaterFurnace | URD038*0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211044 | Ground Loop | WaterFurnace | URD038*0*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211045 | Ground Loop | WaterFurnace | URD038*3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211046 | Ground Loop | WaterFurnace | URD038*3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211047 | Ground Loop | WaterFurnace | URD038*3*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211048 | Ground Loop | WaterFurnace | URD049*0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211049 | Ground Loop | WaterFurnace | URD049*0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211050 | Ground Loop | WaterFurnace | URD049*0*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211051 | Ground Loop | WaterFurnace | URD049*3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211052 | Ground Loop | WaterFurnace | URD049*3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211053 | Ground Loop | WaterFurnace | URD049*3*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211054 | Ground Loop | WaterFurnace | URD064*0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211055 | Ground Loop | WaterFurnace | URD064*0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211056 | Ground Loop | WaterFurnace | URD064*0*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211057 | Ground Loop | WaterFurnace | URD064*3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211058 | Ground Loop | WaterFurnace | URD064*3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211059 | Ground Loop | WaterFurnace | URD064*3*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211060 | Ground Loop | WaterFurnace | URD072*0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211061 | Ground Loop | WaterFurnace | URD072*0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211062 | Ground Loop | WaterFurnace | URD072*0*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211063 | Ground Loop | WaterFurnace | URD072*3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211064 | Ground Loop | WaterFurnace | URD072*3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211065 | Ground Loop | WaterFurnace | URD072*3*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211066 | Ground Loop | WaterFurnace | URT096*3*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65 | No
202262237 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
202262238 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ042J1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
202272873 | Ground Loop | BOSCH-GEO | BP018-1VT*******C |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
7412057 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7412158 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
7412253 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7412381 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7412626 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7412712 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7412777 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7412856 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7412926 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7413034 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7413487 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7414142 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
7414232 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7414335 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7414470 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
7414553 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7414651 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7414828 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
7414896 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7415098 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7415209 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
7415301 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7415373 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7415455 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
7415878 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7416559 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7416688 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
7416782 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7416889 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7416979 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
7417060 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7417146 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7417250 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
7417329 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7417419 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7417586 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417698 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417776 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417867 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417918 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417992 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7418047 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7418154 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7418360 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418435 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418635 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418715 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418887 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418965 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7419321 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419403 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
202541572 | Ground Loop | BOSCH-GEO | BP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
202541573 | Ground Loop | BOSCH | BP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202541574 | Ground Loop | CARRIER | GB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
202541575 | Ground Loop | BRYANT | GB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202543170 | Ground Loop | CARRIER | GB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
202543171 | Ground Loop | BRYANT | GB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
205823050 | Ground Loop | OMEGA HEAT PUMP | VSHP060G |  | 18200 | 17.3 | 14000 | 3.6 | 1.5167 | No
4651870 | Ground Loop | GeoSmart Energy | ZS023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651873 | Ground Loop | GEOSTAR | ZS023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651874 | Ground Loop | GeoSmart Energy | ZS023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651882 | Ground Loop | GEOSTAR | ZS042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651883 | Ground Loop | GeoSmart Energy | ZS042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651888 | Ground Loop | GEOSTAR | ZS042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651889 | Ground Loop | GeoSmart Energy | ZS042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651894 | Ground Loop | GEOSTAR | ZS042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651895 | Ground Loop | GeoSmart Energy | ZS042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651936 | Ground Loop | GEOSTAR | ZS048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651937 | Ground Loop | GeoSmart Energy | ZS048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651942 | Ground Loop | GeoSmart Energy | ZS048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651943 | Ground Loop | GEOSTAR | ZS048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651948 | Ground Loop | GEOSTAR | ZS048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651949 | Ground Loop | GeoSmart Energy | ZS048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651954 | Ground Loop | GEOSTAR | ZS060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651955 | Ground Loop | GeoSmart Energy | ZS060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651966 | Ground Loop | GEOSTAR | ZS060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651967 | Ground Loop | GeoSmart Energy | ZS060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651972 | Ground Loop | GEOSTAR | ZS070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651973 | Ground Loop | GeoSmart Energy | ZS070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651978 | Ground Loop | GEOSTAR | ZS070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651979 | Ground Loop | GeoSmart Energy | ZS070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651984 | Ground Loop | GEOSTAR | ZS070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651985 | Ground Loop | GeoSmart Energy | ZS070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
215224539 | Ground Loop | FHP | CF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224540 | Ground Loop | FHP | CF024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224541 | Ground Loop | FHP | CF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224542 | Ground Loop | FHP | CF024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
3628355 | Ground Loop | WaterFurnace | USV/USH070**0*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
3628356 | Ground Loop | WaterFurnace | USV/USH070**3*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
3628357 | Ground Loop | WaterFurnace | USV/USH070**4*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
3628359 | Ground Loop | WaterFurnace | USV/USH060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3628360 | Ground Loop | WaterFurnace | USV/USH060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3628361 | Ground Loop | WaterFurnace | USV/USH060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3628363 | Ground Loop | WaterFurnace | USV/USH048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3628364 | Ground Loop | WaterFurnace | USV/USH048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3628365 | Ground Loop | WaterFurnace | USV/USH048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3628367 | Ground Loop | WaterFurnace | USV/USH042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3628368 | Ground Loop | WaterFurnace | USV/USH042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3628369 | Ground Loop | WaterFurnace | USV/USH042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3628403 | Ground Loop | WaterFurnace | USV/USH030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3628404 | Ground Loop | WaterFurnace | USV/USH030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3628405 | Ground Loop | WaterFurnace | USV/USH030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3628406 | Ground Loop | WaterFurnace | USV/USH030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3628407 | Ground Loop | WaterFurnace | USH023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3628408 | Ground Loop | WaterFurnace | USV/USH036**3*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
3628409 | Ground Loop | WaterFurnace | USV/USH036**0*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
3628410 | Ground Loop | WaterFurnace | USV/USH036**4*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
3628411 | Ground Loop | WaterFurnace | USH023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3628412 | Ground Loop | WaterFurnace | USH023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3628413 | Ground Loop | WaterFurnace | USH023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
216625864 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625865 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
207337469 | Ground Loop | GEOSTAR | 103H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337470 | Ground Loop | GEOSTAR | 103H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337471 | Ground Loop | GEOSTAR | 163H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337472 | Ground Loop | GEOSTAR | 163H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337473 | Ground Loop | GEOSTAR | 104H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337474 | Ground Loop | GEOSTAR | 104H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337475 | Ground Loop | GEOSTAR | 164H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337476 | Ground Loop | GEOSTAR | 164H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337477 | Ground Loop | GEOSTAR | 103J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207337478 | Ground Loop | GEOSTAR | 103J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207337479 | Ground Loop | GEOSTAR | 163J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207337480 | Ground Loop | GEOSTAR | 163J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207337481 | Ground Loop | GEOSTAR | 104J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207337482 | Ground Loop | GEOSTAR | 104J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207337483 | Ground Loop | GEOSTAR | 164J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207337484 | Ground Loop | GEOSTAR | 164J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207337485 | Ground Loop | GEOSTAR | 103J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337486 | Ground Loop | GEOSTAR | 103J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337487 | Ground Loop | GEOSTAR | 163J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337488 | Ground Loop | GEOSTAR | 163J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337489 | Ground Loop | GEOSTAR | 104H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337490 | Ground Loop | GEOSTAR | 104H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337491 | Ground Loop | GEOSTAR | 164H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337492 | Ground Loop | GEOSTAR | 164H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337493 | Ground Loop | GEOSTAR | 103J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337494 | Ground Loop | GEOSTAR | 103J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337495 | Ground Loop | GEOSTAR | 163J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337496 | Ground Loop | GEOSTAR | 163J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337497 | Ground Loop | GEOSTAR | 104H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337498 | Ground Loop | GEOSTAR | 104H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337499 | Ground Loop | GEOSTAR | 164H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337500 | Ground Loop | GEOSTAR | 164H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337509 | Ground Loop | GEOSTAR | 103H022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
6501898 | Ground Loop | GEOSTAR | GBV/GBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
6501899 | Ground Loop | GEOSTAR | GBV/GBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
6501900 | Ground Loop | GEOSTAR | GBV/GBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501901 | Ground Loop | GEOSTAR | GBV/GBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501902 | Ground Loop | GEOSTAR | GBV/GBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
6501903 | Ground Loop | GEOSTAR | GBV/GBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501904 | Ground Loop | GEOSTAR | GBV/GBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501905 | Ground Loop | GEOSTAR | GBV/GBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
6501906 | Ground Loop | GEOSTAR | GBV/GBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501907 | Ground Loop | GEOSTAR | GBV/GBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501908 | Ground Loop | GEOSTAR | GBV/GBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
6501909 | Ground Loop | GEOSTAR | GBV/GBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501910 | Ground Loop | GEOSTAR | GBV/GBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501911 | Ground Loop | GEOSTAR | GBV/GBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501912 | Ground Loop | GEOSTAR | GBV/GBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501913 | Ground Loop | GEOSTAR | GBV/GBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501914 | Ground Loop | GEOSTAR | GBV/GBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501915 | Ground Loop | GEOSTAR | GBV/GBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501916 | Ground Loop | GEOSTAR | GBV/GBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501917 | Ground Loop | GEOSTAR | GBV/GBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501918 | Ground Loop | GEOSTAR | GBV/GBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
6501919 | Ground Loop | GEOSTAR | GBV/GBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501920 | Ground Loop | GEOSTAR | GBV/GBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501921 | Ground Loop | GEOSTAR | GBV/GBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
6501922 | Ground Loop | GEOSTAR | GBV/GBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501923 | Ground Loop | GEOSTAR | GBV/GBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501924 | Ground Loop | GEOSTAR | GBV/GBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
6501925 | Ground Loop | GEOSTAR | GBV/GBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501926 | Ground Loop | GEOSTAR | GBV/GBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501927 | Ground Loop | GEOSTAR | GBV/GBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
6501928 | Ground Loop | GEOSTAR | GBV/GBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501929 | Ground Loop | GEOSTAR | GBV/GBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501930 | Ground Loop | GEOSTAR | GBV/GBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
6501931 | Ground Loop | GEOSTAR | GBV/GBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501932 | Ground Loop | GEOSTAR | GBV/GBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501933 | Ground Loop | GEOSTAR | GBV/GBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
6501934 | Ground Loop | GEOSTAR | GBV/GBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501935 | Ground Loop | GEOSTAR | GBV/GBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501936 | Ground Loop | GEOSTAR | GBV/GBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
6501937 | Ground Loop | GEOSTAR | GBV/GBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501938 | Ground Loop | GEOSTAR | GBV/GBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501939 | Ground Loop | GEOSTAR | GBV/GBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
6501940 | Ground Loop | GEOSTAR | GBV/GBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501941 | Ground Loop | GEOSTAR | GBV/GBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501942 | Ground Loop | GEOSTAR | GBV/GBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501943 | Ground Loop | GEOSTAR | GBV/GBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501944 | Ground Loop | GEOSTAR | GBV/GBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501945 | Ground Loop | GEOSTAR | GBV/GBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501946 | Ground Loop | GEOSTAR | GBV/GBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501947 | Ground Loop | GEOSTAR | GBV/GBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501948 | Ground Loop | GEOSTAR | GBV/GBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501949 | Ground Loop | GEOSTAR | GBV/GBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501951 | Ground Loop | GEOSTAR | GBV/GBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501952 | Ground Loop | GEOSTAR | GBV/GBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
9100359 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100361 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100362 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
207177460 | Ground Loop | TRANE | EXVG009A |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167 | No
207177461 | Ground Loop | TRANE | EXVG0097 |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167 | No
207177462 | Ground Loop | TRANE | EXVG012A |  | 12300 | 19.5 | 9300 | 4 | 1.025 | No
207177463 | Ground Loop | TRANE | EXVG0127 |  | 12300 | 19.5 | 9300 | 4 | 1.025 | No
207177464 | Ground Loop | TRANE | EXVG015A |  | 15800 | 19 | 12100 | 3.8 | 1.3167 | No
207177465 | Ground Loop | TRANE | EXVG0157 |  | 15800 | 19 | 12100 | 3.8 | 1.3167 | No
207177466 | Ground Loop | TRANE | EXVG018A |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333 | No
207177467 | Ground Loop | TRANE | EXVG0187 |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333 | No
207177468 | Ground Loop | TRANE | EXVG024A |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
207177469 | Ground Loop | TRANE | EXVG024B |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
207177470 | Ground Loop | TRANE | EXVG0244 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
207177471 | Ground Loop | TRANE | EXVG0247 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
207177472 | Ground Loop | TRANE | EXVG030A |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
207177473 | Ground Loop | TRANE | EXVG030B |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
207177474 | Ground Loop | TRANE | EXVG0304 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
207177475 | Ground Loop | TRANE | EXVG0307 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
207177476 | Ground Loop | TRANE | EXVG036A |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
207177477 | Ground Loop | TRANE | EXVG036B |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
207177478 | Ground Loop | TRANE | EXVG0364 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
207177479 | Ground Loop | TRANE | EXVG0367 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
207177480 | Ground Loop | TRANE | EXVG042A |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
207177481 | Ground Loop | TRANE | EXVG042B |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
207177482 | Ground Loop | TRANE | EXVG0424 |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
207177483 | Ground Loop | TRANE | EXVG048A |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
207177484 | Ground Loop | TRANE | EXVG048B |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
207177485 | Ground Loop | TRANE | EXVG0484 |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
207177486 | Ground Loop | TRANE | EXVG060A |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
207177487 | Ground Loop | TRANE | EXVG060B |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
207177488 | Ground Loop | TRANE | EXVG0604 |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
207177489 | Ground Loop | TRANE | EXVG070A |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
207177490 | Ground Loop | TRANE | EXVG070B |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
207177491 | Ground Loop | TRANE | EXVG0704 |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
207177492 | Ground Loop | TRANE | DXVG024A |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
207177493 | Ground Loop | TRANE | DXVG024B |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
207177494 | Ground Loop | TRANE | DXVG0244 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
207177495 | Ground Loop | TRANE | DXVG0247 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
207177496 | Ground Loop | TRANE | DXVG036A |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
207177497 | Ground Loop | TRANE | DXVG036B |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
207177498 | Ground Loop | TRANE | DXVG0364 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
207177499 | Ground Loop | TRANE | DXVG0367 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
207177500 | Ground Loop | TRANE | DXVG048A |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
207177501 | Ground Loop | TRANE | DXVG048B |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
207177502 | Ground Loop | TRANE | DXVG0484 |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
207177503 | Ground Loop | TRANE | DXVG060A |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
207177504 | Ground Loop | TRANE | DXVG060B |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
207177505 | Ground Loop | TRANE | DXVG0604 |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
207177506 | Ground Loop | TRANE | DXVG070A |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
207177507 | Ground Loop | TRANE | DXVG070B |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
207177508 | Ground Loop | TRANE | DXVG0704 |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
207178484 | Ground Loop | GEOSTAR | 163H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207178485 | Ground Loop | GEOSTAR | 164H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207178486 | Ground Loop | GEOSTAR | 164H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
214595625 | Ground Loop | AAON, Inc. | M2-004-3-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325 | No
214595629 | Ground Loop | AAON, Inc. | M2-004-4-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325 | No
216625696 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625697 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625698 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625699 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625700 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625701 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625702 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625703 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625704 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625705 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625706 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625707 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625708 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625709 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625710 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625711 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625712 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625713 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625714 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625715 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625716 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625717 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625718 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625719 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625720 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625721 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625722 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625723 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625724 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625725 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625726 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625727 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625728 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625729 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625730 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625731 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625732 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625733 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625734 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625735 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625736 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625737 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625738 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625739 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625740 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625741 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625742 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625743 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625744 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625745 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625746 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625747 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625750 | Ground Loop | GeoSmart Energy | S5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216625751 | Ground Loop | GeoSmart Energy | S5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
202330518 | Ground Loop | AAON, Inc. | M2-003-2-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917 | No
202330522 | Ground Loop | AAON, Inc. | M2-003-3-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917 | No
202330526 | Ground Loop | AAON, Inc. | M2-003-4-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917 | No
202330529 | Ground Loop | AAON, Inc. | M2-004-1-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667 | No
216739914 | Ground Loop | DAIKIN | WSNH024E1*G/J*C |  | 25300 | 18.5 | 17900 | 3.6 | 2.1083 | No
216739922 | Ground Loop | DAIKIN | WSNH030E1*G/J*C |  | 32100 | 18.3 | 23800 | 3.6 | 2.675 | No
216739930 | Ground Loop | DAIKIN | WSNH036E1*G/J*C |  | 35700 | 19.6 | 25500 | 3.6 | 2.975 | No
216739946 | Ground Loop | DAIKIN | WSNH060E1*G/J*C |  | 61200 | 17.3 | 49000 | 3.9 | 5.1 | No
216739947 | Ground Loop | DAIKIN | WSNH060F3*G/J*C |  | 61200 | 17 | 49000 | 3.9 | 5.1 | No
216739948 | Ground Loop | DAIKIN | WSNH060K3*G/J*C |  | 61200 | 17 | 49000 | 3.9 | 5.1 | No
216739957 | Ground Loop | DAIKIN | WSNV030E1*G/J*C |  | 31900 | 18.9 | 20500 | 3.6 | 2.6583 | No
216739965 | Ground Loop | DAIKIN | WSNV036E1*G/J*C |  | 37300 | 20.3 | 26100 | 3.8 | 3.1083 | No
216739966 | Ground Loop | DAIKIN | WSNV036F3*G/J*C |  | 37300 | 19.9 | 26100 | 3.8 | 3.1083 | No
216739967 | Ground Loop | DAIKIN | WSNV036J1*G/J*C |  | 37300 | 19.9 | 26100 | 3.8 | 3.1083 | No
216739968 | Ground Loop | DAIKIN | WSNV036K3*G/J*C |  | 37300 | 19.7 | 26100 | 3.7 | 3.1083 | No
9111997 | Ground Loop | BOSCH | SM024-1VT/CF*-*****B |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417 | No
9111998 | Ground Loop | BOSCH | SM036-1VT/CF*-*****B |  | 40200 | 21 | 28200 | 4.3 | 3.35 | No
9113111 | Ground Loop | BOSCH | SM048-1VT/CF*-*****B* |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167 | No
9113180 | Ground Loop | BOSCH | SM060-1VT/CF*-*****B |  | 63900 | 18.6 | 48600 | 4 | 5.325 | No
9113181 | Ground Loop | BOSCH | SM070-1VT/CF*-*****B |  | 71500 | 17.3 | 56000 | 3.8 | 5.9583 | No
9113182 | Ground Loop | BOSCH | SM024-1VT/CF*-*****B |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417 | Yes
9113183 | Ground Loop | BOSCH | SM036-1VT/CF*-*****B |  | 40200 | 21 | 28200 | 4.3 | 3.35 | Yes
9113184 | Ground Loop | BOSCH | SM048-1VT/CF*-*****B* |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167 | Yes
9113185 | Ground Loop | BOSCH | SM060-1VT/CF*-*****B |  | 63900 | 18.6 | 48600 | 4 | 5.325 | Yes
9113186 | Ground Loop | BOSCH | SM070-1VT/CF*-*****B |  | 71500 | 17.3 | 56000 | 3.8 | 5.9583 | Yes
9114306 | Ground Loop | GEOCOMFORT | GZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114307 | Ground Loop | HYDRON MODULE | HZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | Yes
9114308 | Ground Loop | TETCO | TZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | Yes
9114309 | Ground Loop | GEOCOMFORT | GZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114310 | Ground Loop | HYDRON MODULE | HZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114311 | Ground Loop | TETCO | TZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114312 | Ground Loop | GEOCOMFORT | GZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114313 | Ground Loop | HYDRON MODULE | HZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114314 | Ground Loop | TETCO | TZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
215415816 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)015A*VB |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415817 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)015A*VC |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415820 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)018A*VB |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415821 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)018A*VC |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415822 | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)024A*B |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | No
215415823 | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)024A*C |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | No
215415830 | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)048A*B |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | No
215415831 | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)048A*C |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | No
215415832 | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)060A*B |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | No
215415833 | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)060A*C |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | No
215415834 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415835 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415836 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415837 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415840 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415841 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415844 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
215415845 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
217754629 | Ground Loop | DAIKIN | WSMV024F1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
217754630 | Ground Loop | DAIKIN | WSMV024K1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
217754633 | Ground Loop | DAIKIN | WSMV024F1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
217754634 | Ground Loop | DAIKIN | WSMV024K1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
217754637 | Ground Loop | DAIKIN | WSMV024F1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
217754638 | Ground Loop | DAIKIN | WSMV024K1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
217754657 | Ground Loop | DAIKIN | WSMV036F1*G/J*T |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917 | No
217754658 | Ground Loop | DAIKIN | WSMV036K1*G/J*T |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917 | No
217754661 | Ground Loop | DAIKIN | WSMV036F1*G/J*C |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917 | No
217754662 | Ground Loop | DAIKIN | WSMV036K1*G/J*C |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917 | No
216739978 | Ground Loop | DAIKIN | WSNV048E1*G/J*C |  | 51100 | 19.5 | 35000 | 3.8 | 4.2583 | No
216739979 | Ground Loop | DAIKIN | WSNV048F3*G/J*C |  | 51100 | 19.1 | 35000 | 3.8 | 4.2583 | No
216739980 | Ground Loop | DAIKIN | WSNV048K3*G/J*C |  | 51100 | 19.1 | 35000 | 3.8 | 4.2583 | No
216739984 | Ground Loop | DAIKIN | WSNV060E1*G/J*C |  | 62200 | 17.8 | 46200 | 3.8 | 5.1833 | No
216739985 | Ground Loop | DAIKIN | WSNV060F3*G/J*C |  | 62200 | 17.4 | 46200 | 3.7 | 5.1833 | No
216739986 | Ground Loop | DAIKIN | WSNV060K3*G/J*C |  | 62200 | 17.4 | 46200 | 3.7 | 5.1833 | No
216743538 | Ground Loop | DAIKIN | WSNH048E1*G/J*C |  | 49100 | 18.8 | 38500 | 3.6 | 4.0917 | No
216743541 | Ground Loop | DAIKIN | WSNV024E1*G/J*C |  | 25100 | 18.8 | 18200 | 3.8 | 2.0917 | No
216743542 | Ground Loop | DAIKIN | WSNV024F3*G/J*C |  | 25100 | 18.4 | 18200 | 3.8 | 2.0917 | No
216743543 | Ground Loop | DAIKIN | WSNV024J1*G/J*C |  | 25100 | 18.4 | 18200 | 3.8 | 2.0917 | No
216743544 | Ground Loop | DAIKIN | WSNV024K3*G/J*C |  | 25100 | 18.2 | 18200 | 3.7 | 2.0917 | No
216743617 | Ground Loop | BOSCH-GEO | RP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216743618 | Ground Loop | BOSCH | CP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743619 | Ground Loop | BOSCH | CP024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743620 | Ground Loop | BOSCH | CP024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743621 | Ground Loop | BOSCH | CP024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743622 | Ground Loop | BOSCH-GEO | RP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216743623 | Ground Loop | BOSCH | CP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743624 | Ground Loop | BOSCH | CP024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743625 | Ground Loop | BOSCH | CP024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743626 | Ground Loop | BOSCH | CP024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743627 | Ground Loop | BOSCH-GEO | RP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216743628 | Ground Loop | BOSCH | CP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743629 | Ground Loop | BOSCH | CP024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743630 | Ground Loop | BOSCH | CP024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743631 | Ground Loop | BOSCH | CP024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743632 | Ground Loop | BOSCH-GEO | RP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216743633 | Ground Loop | BOSCH | CP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743634 | Ground Loop | BOSCH | CP024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743635 | Ground Loop | BOSCH | CP024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
7795914 | Ground Loop | GEOCOMFORT | GVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
7795915 | Ground Loop | HYDRON MODULE | HVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
7795916 | Ground Loop | TETCO | TVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
7795918 | Ground Loop | GEOCOMFORT | GVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795919 | Ground Loop | HYDRON MODULE | HVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795920 | Ground Loop | TETCO | TVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795921 | Ground Loop | GEOCOMFORT | GVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795922 | Ground Loop | HYDRON MODULE | HVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795923 | Ground Loop | TETCO | TVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795924 | Ground Loop | GEOCOMFORT | GVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795925 | Ground Loop | HYDRON MODULE | HVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795926 | Ground Loop | TETCO | TVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795943 | Ground Loop | GEOCOMFORT | GVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
7795944 | Ground Loop | HYDRON MODULE | HVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
7795945 | Ground Loop | TETCO | TVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
7795946 | Ground Loop | GEOCOMFORT | GVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795947 | Ground Loop | HYDRON MODULE | HVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795948 | Ground Loop | TETCO | TVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
212505504 | Ground Loop | AE Air | WSH6030AM* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
212505505 | Ground Loop | AE Air | WSH6060A6* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | Yes
212505506 | Ground Loop | AE Air | WSH6072A6* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | Yes
212505507 | Ground Loop | HYDROTECH | WSH6024AM* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | No
212505508 | Ground Loop | HYDROTECH | WSH6030AM* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
212505509 | Ground Loop | HYDROTECH | WSH6036AM* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | No
212505510 | Ground Loop | HYDROTECH | WSH6042AM* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | No
212505511 | Ground Loop | HYDROTECH | WSH6048AM* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | No
212505512 | Ground Loop | AE Air | WSH6024AM* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | No
212505513 | Ground Loop | AE Air | WSH6036AM* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | No
212505514 | Ground Loop | AE Air | WSH6042AM* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | No
212505515 | Ground Loop | AE Air | WSH6048AM* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | No
212508378 | Ground Loop | HYDROTECH | WSH6024AN* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | No
212508380 | Ground Loop | HYDROTECH | WSH6030AN* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
212508382 | Ground Loop | HYDROTECH | WSH6036AN* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | No
212508384 | Ground Loop | HYDROTECH | WSH6042AN* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | No
212508386 | Ground Loop | HYDROTECH | WSH6048AN* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | No
212508387 | Ground Loop | HYDROTECH | WSH6060AM* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | No
212508388 | Ground Loop | HYDROTECH | WSH6060AN* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | No
212508389 | Ground Loop | HYDROTECH | WSH6072AM* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | No
212508390 | Ground Loop | HYDROTECH | WSH6072AN* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | No
212508395 | Ground Loop | AE Air | WSH6024AN* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | No
212508397 | Ground Loop | AE Air | WSH6030AN* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
212508399 | Ground Loop | AE Air | WSH6036AN* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | No
212508401 | Ground Loop | AE Air | WSH6042AN* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | No
212508403 | Ground Loop | AE Air | WSH6048AN* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | No
212508404 | Ground Loop | AE Air | WSH6072AM* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | No
212508405 | Ground Loop | AE Air | WSH6072AN* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | No
212509300 | Ground Loop | AE Air | WSH6060AM* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | No
212509301 | Ground Loop | AE Air | WSH6060AN* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | No
217897469 | Ground Loop | CENTURY | MJN060A | MAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167 | Yes
217897470 | Ground Loop | COMFORT-AIRE | MJN060A | MAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167 | Yes
217903418 | Ground Loop | WaterFurnace | V5R036*S0**1* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903419 | Ground Loop | WaterFurnace | V5R036*S0**4* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903420 | Ground Loop | WaterFurnace | V5R036*S0**5* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903421 | Ground Loop | WaterFurnace | V5R048*S0**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903422 | Ground Loop | WaterFurnace | V5R048*S0**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903423 | Ground Loop | WaterFurnace | V5R048*S0**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903424 | Ground Loop | WaterFurnace | V5R060*S0**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903425 | Ground Loop | WaterFurnace | V5R060*S0**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903426 | Ground Loop | WaterFurnace | V5R060*S0**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903427 | Ground Loop | WaterFurnace | V5R072*S0**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903428 | Ground Loop | WaterFurnace | V5R072*S0**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903429 | Ground Loop | WaterFurnace | V5R072*S0**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903430 | Ground Loop | WaterFurnace | V5R036*S3**1* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903431 | Ground Loop | WaterFurnace | V5R036*S3**4* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903432 | Ground Loop | WaterFurnace | V5R036*S3**5* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903433 | Ground Loop | WaterFurnace | V5R036*S4**1* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903434 | Ground Loop | WaterFurnace | V5R036*S4**4* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903435 | Ground Loop | WaterFurnace | V5R036*S4**5* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903436 | Ground Loop | WaterFurnace | V5R048*S3**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903437 | Ground Loop | WaterFurnace | V5R048*S3**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903438 | Ground Loop | WaterFurnace | V5R048*S3**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903439 | Ground Loop | WaterFurnace | V5R048*S4**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903440 | Ground Loop | WaterFurnace | V5R048*S4**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903441 | Ground Loop | WaterFurnace | V5R048*S4**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903442 | Ground Loop | WaterFurnace | V5R060*S3**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903443 | Ground Loop | WaterFurnace | V5R060*S3**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903444 | Ground Loop | WaterFurnace | V5R060*S3**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903445 | Ground Loop | WaterFurnace | V5R060*S4**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903446 | Ground Loop | WaterFurnace | V5R060*S4**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903447 | Ground Loop | WaterFurnace | V5R060*S4**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903448 | Ground Loop | WaterFurnace | V5R072*S3**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903449 | Ground Loop | WaterFurnace | V5R072*S3**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903450 | Ground Loop | WaterFurnace | V5R072*S3**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903451 | Ground Loop | WaterFurnace | V5R072*S4**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903452 | Ground Loop | WaterFurnace | V5R072*S4**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903453 | Ground Loop | WaterFurnace | V5R072*S4**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903454 | Ground Loop | WaterFurnace | V5R036*D4**1* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903455 | Ground Loop | WaterFurnace | V5R036*D4**4* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903456 | Ground Loop | WaterFurnace | V5R036*D4**5* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903457 | Ground Loop | WaterFurnace | V5R048*D4**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903458 | Ground Loop | WaterFurnace | V5R048*D4**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
202330514 | Ground Loop | AAON, Inc. | M2-003-1-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917 | No
215399774 | Ground Loop | DAIKIN | WSMV015A1*G/J*T |  | 16300 | 21.12 | 11000 | 3.64 | 1.3583 | No
215399775 | Ground Loop | DAIKIN | WSMV015J1*G/J*T |  | 16300 | 21.12 | 11100 | 3.64 | 1.3583 | No
215399778 | Ground Loop | DAIKIN | WSMV015A1*G/J*C |  | 16300 | 21.12 | 11000 | 3.64 | 1.3583 | No
215399779 | Ground Loop | DAIKIN | WSMV015J1*G/J*C |  | 16300 | 21.12 | 11100 | 3.64 | 1.3583 | No
9100364 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100365 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100367 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100368 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
207177431 | Ground Loop | TRANE | GEVG009A |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167 | No
207177432 | Ground Loop | TRANE | GEVG0097 |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167 | No
207177433 | Ground Loop | TRANE | GEVG012A |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083 | No
207177434 | Ground Loop | TRANE | GEVG0127 |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083 | No
207177435 | Ground Loop | TRANE | GEVG015A |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917 | No
207177436 | Ground Loop | TRANE | GEVG0157 |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917 | No
207177437 | Ground Loop | TRANE | GEVG018A |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083 | No
207177438 | Ground Loop | TRANE | GEVG0187 |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083 | No
207177439 | Ground Loop | TRANE | GEVG024A |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
207177440 | Ground Loop | TRANE | GEVG024B |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
207177441 | Ground Loop | TRANE | GEVG0244 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
207177442 | Ground Loop | TRANE | GEVG0247 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
207177443 | Ground Loop | TRANE | GEVG030A |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
207177444 | Ground Loop | TRANE | GEVG030B |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
207177445 | Ground Loop | TRANE | GEVG0304 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
207177446 | Ground Loop | TRANE | GEVG0307 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
207177447 | Ground Loop | TRANE | GEVG036A |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
207177448 | Ground Loop | TRANE | GEVG036B |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
207177449 | Ground Loop | TRANE | GEVG0364 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
207177450 | Ground Loop | TRANE | GEVG0367 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
9011292 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
9032648 | Ground Loop | HYDROTECH | HRCX18*-6 |  | 18000 | 17.1 | 13000 | 3.6 | 1.5 | Yes
9033424 | Ground Loop | HYDROTECH | HRCX09*-6 |  | 10000 | 19 | 6800 | 3.6 | 0.83333 | Yes
9033758 | Ground Loop | HYDROTECH | HRCX24*-6 |  | 24000 | 19 | 17000 | 3.6 | 2 | Yes
9033759 | Ground Loop | HYDROTECH | HRCX12*-6 |  | 11800 | 18 | 8000 | 3.6 | 0.98333 | Yes
9035993 | Ground Loop | GEOCOMFORT | GZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | Yes
9035994 | Ground Loop | HYDRON MODULE | HZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | Yes
9035995 | Ground Loop | TETCO | TZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | Yes
9035996 | Ground Loop | GEOCOMFORT | GZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9035997 | Ground Loop | HYDRON MODULE | HZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9035998 | Ground Loop | TETCO | TZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9035999 | Ground Loop | GEOCOMFORT | GZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036000 | Ground Loop | HYDRON MODULE | HZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036001 | Ground Loop | TETCO | TZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036002 | Ground Loop | GEOCOMFORT | GZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036003 | Ground Loop | HYDRON MODULE | HZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036004 | Ground Loop | TETCO | TZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036975 | Ground Loop | GEOCOMFORT | GZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | Yes
9036998 | Ground Loop | HYDRON MODULE | HZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | Yes
9037017 | Ground Loop | TETCO | TZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | Yes
9037062 | Ground Loop | GEOCOMFORT | GZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037081 | Ground Loop | HYDRON MODULE | HZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037097 | Ground Loop | TETCO | TZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037137 | Ground Loop | GEOCOMFORT | GZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037158 | Ground Loop | HYDRON MODULE | HZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037175 | Ground Loop | TETCO | TZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037215 | Ground Loop | GEOCOMFORT | GZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037240 | Ground Loop | HYDRON MODULE | HZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037275 | Ground Loop | TETCO | TZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9038310 | Ground Loop | GEOCOMFORT | GZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | Yes
9038311 | Ground Loop | HYDRON MODULE | HZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | Yes
9038312 | Ground Loop | TETCO | TZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | Yes
9038313 | Ground Loop | GEOCOMFORT | GZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038314 | Ground Loop | HYDRON MODULE | HZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038315 | Ground Loop | TETCO | TZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038316 | Ground Loop | GEOCOMFORT | GZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038317 | Ground Loop | HYDRON MODULE | HZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038318 | Ground Loop | TETCO | TZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038319 | Ground Loop | GEOCOMFORT | GZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
217735445 | Ground Loop | DAIKIN | WSTV036J1*H*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583 | No
217752745 | Ground Loop | DAIKIN | WSTV024K1*H*C |  | 22400 | 17.45 | 17200 | 3.86 | 1.8667 | No
217752747 | Ground Loop | DAIKIN | WSTV030K1*H*C |  | 32200 | 18.9 | 20800 | 3.66 | 2.6833 | No
217752751 | Ground Loop | DAIKIN | WSTV042K1*H*C |  | 44800 | 18.96 | 27600 | 3.62 | 3.7333 | No
217752754 | Ground Loop | DAIKIN | WSTV048K1*H*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667 | No
217752755 | Ground Loop | DAIKIN | WSTV048L1*H*C |  | 52400 | 19.56 | 35200 | 3.78 | 4.3667 | No
217752758 | Ground Loop | DAIKIN | WSTV060K1*H*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583 | No
217752759 | Ground Loop | DAIKIN | WSTV060L1*H*C |  | 63100 | 19.01 | 46800 | 3.98 | 5.2583 | No
217752762 | Ground Loop | DAIKIN | WSTV070K1*H*C |  | 74600 | 18.62 | 56000 | 3.92 | 6.2167 | No
217752763 | Ground Loop | DAIKIN | WSTV070L1*H*C |  | 74600 | 18.43 | 56000 | 3.88 | 6.2167 | No
217754378 | Ground Loop | DAIKIN | WSSH024F1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217754379 | Ground Loop | DAIKIN | WSSH024K1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217754381 | Ground Loop | DAIKIN | WSSH024F1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217754382 | Ground Loop | DAIKIN | WSSH024K1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217754384 | Ground Loop | DAIKIN | WSSH030F1*H*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
217754385 | Ground Loop | DAIKIN | WSSH030K1*H*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
9910613 | Ground Loop | HYDRON MODULE | HZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910614 | Ground Loop | TETCO | TZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910620 | Ground Loop | GEOCOMFORT | GZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | Yes
9910621 | Ground Loop | HYDRON MODULE | HZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | Yes
9910622 | Ground Loop | TETCO | TZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | Yes
9910623 | Ground Loop | GEOCOMFORT | GZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910624 | Ground Loop | HYDRON MODULE | HZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910625 | Ground Loop | TETCO | TZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910626 | Ground Loop | GEOCOMFORT | GZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910627 | Ground Loop | HYDRON MODULE | HZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910628 | Ground Loop | TETCO | TZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910629 | Ground Loop | GEOCOMFORT | GZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910630 | Ground Loop | HYDRON MODULE | HZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910631 | Ground Loop | TETCO | TZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910636 | Ground Loop | GEOCOMFORT | GZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910637 | Ground Loop | HYDRON MODULE | HZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | Yes
9910638 | Ground Loop | TETCO | TZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | Yes
9910639 | Ground Loop | GEOCOMFORT | GZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910640 | Ground Loop | HYDRON MODULE | HZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910641 | Ground Loop | TETCO | TZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910642 | Ground Loop | GEOCOMFORT | GZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910643 | Ground Loop | HYDRON MODULE | HZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910644 | Ground Loop | TETCO | TZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910645 | Ground Loop | GEOCOMFORT | GZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910646 | Ground Loop | HYDRON MODULE | HZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910647 | Ground Loop | TETCO | TZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910648 | Ground Loop | GEOCOMFORT | GZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910649 | Ground Loop | HYDRON MODULE | HZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910650 | Ground Loop | TETCO | TZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910660 | Ground Loop | GEOCOMFORT | GZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | Yes
9910661 | Ground Loop | HYDRON MODULE | HZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | Yes
9910662 | Ground Loop | TETCO | TZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | Yes
9910663 | Ground Loop | GEOCOMFORT | GZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910664 | Ground Loop | HYDRON MODULE | HZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910665 | Ground Loop | TETCO | TZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910666 | Ground Loop | GEOCOMFORT | GZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910667 | Ground Loop | HYDRON MODULE | HZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910668 | Ground Loop | TETCO | TZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910672 | Ground Loop | GEOCOMFORT | GZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | Yes
9910673 | Ground Loop | HYDRON MODULE | HZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | Yes
9910674 | Ground Loop | TETCO | TZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | Yes
9910675 | Ground Loop | GEOCOMFORT | GZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910676 | Ground Loop | HYDRON MODULE | HZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910677 | Ground Loop | TETCO | TZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910678 | Ground Loop | GEOCOMFORT | GZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910679 | Ground Loop | HYDRON MODULE | HZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910680 | Ground Loop | TETCO | TZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910681 | Ground Loop | GEOCOMFORT | GZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910682 | Ground Loop | HYDRON MODULE | HZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910683 | Ground Loop | TETCO | TZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910696 | Ground Loop | GEOCOMFORT | GZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | Yes
9910697 | Ground Loop | HYDRON MODULE | HZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | Yes
9910698 | Ground Loop | TETCO | TZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | Yes
9910699 | Ground Loop | GEOCOMFORT | GZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910700 | Ground Loop | HYDRON MODULE | HZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910701 | Ground Loop | TETCO | TZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
4651271 | Ground Loop | WaterFurnace | USH023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651272 | Ground Loop | WaterFurnace | USH023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651273 | Ground Loop | WaterFurnace | USH023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651274 | Ground Loop | WaterFurnace | USH023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651339 | Ground Loop | WaterFurnace | USV/USH024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651340 | Ground Loop | WaterFurnace | USV/USH024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651341 | Ground Loop | WaterFurnace | USV/USH024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651342 | Ground Loop | WaterFurnace | USV/USH024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651403 | Ground Loop | WaterFurnace | USV/USH030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651404 | Ground Loop | WaterFurnace | USV/USH030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
215268334 | Ground Loop | WaterFurnace | V3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268335 | Ground Loop | WaterFurnace | V3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268336 | Ground Loop | WaterFurnace | V3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268337 | Ground Loop | WaterFurnace | V3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268338 | Ground Loop | WaterFurnace | V3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268339 | Ground Loop | WaterFurnace | V3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268340 | Ground Loop | WaterFurnace | V3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268348 | Ground Loop | WaterFurnace | V3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268349 | Ground Loop | WaterFurnace | V3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268350 | Ground Loop | WaterFurnace | V3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268351 | Ground Loop | WaterFurnace | V3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268352 | Ground Loop | WaterFurnace | V3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268353 | Ground Loop | WaterFurnace | V3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268354 | Ground Loop | WaterFurnace | V3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268355 | Ground Loop | WaterFurnace | V3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268356 | Ground Loop | WaterFurnace | V3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268357 | Ground Loop | WaterFurnace | V3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268358 | Ground Loop | WaterFurnace | V3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268359 | Ground Loop | WaterFurnace | V3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268365 | Ground Loop | WaterFurnace | V3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268366 | Ground Loop | WaterFurnace | V3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268367 | Ground Loop | WaterFurnace | V3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268368 | Ground Loop | WaterFurnace | V3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268369 | Ground Loop | WaterFurnace | V3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268664 | Ground Loop | WaterFurnace | V5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
215268665 | Ground Loop | WaterFurnace | V5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
215268666 | Ground Loop | WaterFurnace | V5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
215268667 | Ground Loop | WaterFurnace | V5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268668 | Ground Loop | WaterFurnace | V5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216743640 | Ground Loop | BOSCH | CP036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216743641 | Ground Loop | BOSCH | CP036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216743642 | Ground Loop | BOSCH-GEO | RP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216743643 | Ground Loop | BOSCH | CP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216743644 | Ground Loop | BOSCH | CP036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216743645 | Ground Loop | BOSCH | CP036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216743646 | Ground Loop | BOSCH | CP036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216743647 | Ground Loop | BOSCH-GEO | RP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216743648 | Ground Loop | BOSCH | CP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216743649 | Ground Loop | BOSCH | CP048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216743650 | Ground Loop | BOSCH | CP048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216743651 | Ground Loop | BOSCH-GEO | RP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
5220682 | Ground Loop | DAIKIN | WGSV/WGSH036B*F |  | 38500 | 22 | 26200 | 4.3 | 3.2083 | No
5220683 | Ground Loop | DAIKIN | WGSV/WGSH036B*J |  | 38500 | 22 | 26200 | 4.3 | 3.2083 | No
5220684 | Ground Loop | DAIKIN | WGSV/WGSH036B*K |  | 38500 | 22 | 26200 | 4.3 | 3.2083 | No
5220686 | Ground Loop | DAIKIN | WGSV/WGSH042B*E |  | 45500 | 20.2 | 31300 | 4 | 3.7917 | No
5220687 | Ground Loop | DAIKIN | WGSV/WGSH042B*F |  | 45500 | 20.2 | 31300 | 4 | 3.7917 | No
5220688 | Ground Loop | DAIKIN | WGSV/WGSH042B*K |  | 45500 | 20.2 | 31300 | 4 | 3.7917 | No
5220690 | Ground Loop | DAIKIN | WGSV/WGSH048B*E |  | 52700 | 19.9 | 36900 | 4 | 4.3917 | No
5220691 | Ground Loop | DAIKIN | WGSV/WGSH048B*F |  | 52700 | 19.9 | 36900 | 4 | 4.3917 | No
5220693 | Ground Loop | DAIKIN | WGSV/WGSH048B*K |  | 52700 | 19.9 | 36900 | 4 | 4.3917 | No
5220700 | Ground Loop | DAIKIN | WGSV/WGSH060B*E |  | 66300 | 20 | 46500 | 3.8 | 5.525 | No
5220701 | Ground Loop | DAIKIN | WGSV/WGSH060B*F |  | 66300 | 20 | 46500 | 3.8 | 5.525 | No
5220702 | Ground Loop | DAIKIN | WGSV/WGSH060B*K |  | 66300 | 20 | 46500 | 3.8 | 5.525 | No
5220703 | Ground Loop | DAIKIN | WGSV/WGSH070B*E |  | 75700 | 18 | 55800 | 3.7 | 6.3083 | No
5220704 | Ground Loop | DAIKIN | WGSV/WGSH070B*F |  | 75700 | 18 | 55800 | 3.7 | 6.3083 | No
5220705 | Ground Loop | DAIKIN | WGSV/WGSH070B*K |  | 75700 | 18 | 55800 | 3.7 | 6.3083 | No
5220707 | Ground Loop | DAIKIN | WGTV/WGTH026B*E |  | 27600 | 19.27 | 18100 | 4.1 | 2.3 | No
5220708 | Ground Loop | DAIKIN | WGTV/WGTH026B*F |  | 27600 | 19.27 | 18100 | 4.1 | 2.3 | No
5220709 | Ground Loop | DAIKIN | WGTV/WGTH026B*J |  | 27600 | 19.27 | 18100 | 4.1 | 2.3 | No
5220710 | Ground Loop | DAIKIN | WGTV/WGTH026B*K |  | 27600 | 19.27 | 18100 | 4.1 | 2.3 | No
5220933 | Ground Loop | DAIKIN | WGTV/WGTH032B*E |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167 | No
5220934 | Ground Loop | DAIKIN | WGTV/WGTH032B*F |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167 | No
5220935 | Ground Loop | DAIKIN | WGTV/WGTH032B*J |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167 | No
5220936 | Ground Loop | DAIKIN | WGTV/WGTH032B*K |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167 | No
5220980 | Ground Loop | DAIKIN | WGTV/WGTH038B*E |  | 40200 | 20.1 | 28100 | 4.2 | 3.35 | No
5220981 | Ground Loop | DAIKIN | WGTV/WGTH038B*F |  | 40200 | 20.1 | 28100 | 4.2 | 3.35 | No
5220982 | Ground Loop | DAIKIN | WGTV/WGTH038B*K |  | 40200 | 20.1 | 28100 | 4.2 | 3.35 | No
5220983 | Ground Loop | DAIKIN | WGTV/WGTH044B*E |  | 45900 | 19.8 | 31700 | 4 | 3.825 | No
5220984 | Ground Loop | DAIKIN | WGTV/WGTH044B*F |  | 45900 | 19.8 | 31700 | 4 | 3.825 | No
5220985 | Ground Loop | DAIKIN | WGTV/WGTH044B*K |  | 45900 | 19.8 | 31700 | 4 | 3.825 | No
5220987 | Ground Loop | DAIKIN | WGTV/WGTH049B*E |  | 50600 | 19.2 | 35900 | 4 | 4.2167 | No
5220988 | Ground Loop | DAIKIN | WGTV/WGTH049B*F |  | 50600 | 19.2 | 35900 | 4 | 4.2167 | No
5220989 | Ground Loop | DAIKIN | WGTV/WGTH049B*K |  | 50600 | 19.2 | 35900 | 4 | 4.2167 | No
5220990 | Ground Loop | DAIKIN | WGTV/WGTH064B*E |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917 | No
5220991 | Ground Loop | DAIKIN | WGTV/WGTH064B*F |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917 | No
5220992 | Ground Loop | DAIKIN | WGTV/WGTH064B*K |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917 | No
5295936 | Ground Loop | WaterFurnace | NBV/NBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
5295937 | Ground Loop | WaterFurnace | NBV/NBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
5295944 | Ground Loop | WaterFurnace | NBV/NBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
5295945 | Ground Loop | WaterFurnace | NBV/NBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
5295947 | Ground Loop | WaterFurnace | NBV/NBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
5295948 | Ground Loop | WaterFurnace | NBV/NBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
5295964 | Ground Loop | WaterFurnace | NBV/NBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
5295966 | Ground Loop | WaterFurnace | NBV/NBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
5295968 | Ground Loop | WaterFurnace | NBV/NBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
5295969 | Ground Loop | WaterFurnace | NBV/NBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
5295980 | Ground Loop | WaterFurnace | NBV/NBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
5295981 | Ground Loop | WaterFurnace | NBV/NBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
5295982 | Ground Loop | WaterFurnace | NBV/NBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
5295983 | Ground Loop | WaterFurnace | NBV/NBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
202434372 | Ground Loop | FHP | LV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434373 | Ground Loop | FHP | LV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434374 | Ground Loop | FHP | LV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434375 | Ground Loop | FHP | LV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434380 | Ground Loop | FHP | LV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434381 | Ground Loop | FHP | LV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
9910558 | Ground Loop | HYDRON MODULE | HZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910559 | Ground Loop | TETCO | TZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910564 | Ground Loop | GEOCOMFORT | GZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | Yes
9910565 | Ground Loop | HYDRON MODULE | HZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | Yes
9910566 | Ground Loop | TETCO | TZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | Yes
9910567 | Ground Loop | GEOCOMFORT | GZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910568 | Ground Loop | HYDRON MODULE | HZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910569 | Ground Loop | TETCO | TZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910570 | Ground Loop | GEOCOMFORT | GZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910571 | Ground Loop | HYDRON MODULE | HZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910572 | Ground Loop | TETCO | TZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910573 | Ground Loop | GEOCOMFORT | GZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910574 | Ground Loop | HYDRON MODULE | HZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910575 | Ground Loop | TETCO | TZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910576 | Ground Loop | GEOCOMFORT | GZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910577 | Ground Loop | HYDRON MODULE | HZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910578 | Ground Loop | TETCO | TZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910584 | Ground Loop | GEOCOMFORT | GZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | Yes
9910585 | Ground Loop | HYDRON MODULE | HZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | Yes
9910586 | Ground Loop | TETCO | TZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | Yes
9910587 | Ground Loop | GEOCOMFORT | GZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910588 | Ground Loop | HYDRON MODULE | HZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910589 | Ground Loop | TETCO | TZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910590 | Ground Loop | GEOCOMFORT | GZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910591 | Ground Loop | HYDRON MODULE | HZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910592 | Ground Loop | TETCO | TZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910593 | Ground Loop | GEOCOMFORT | GZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910594 | Ground Loop | HYDRON MODULE | HZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910595 | Ground Loop | TETCO | TZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910600 | Ground Loop | GEOCOMFORT | GZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | Yes
9910601 | Ground Loop | HYDRON MODULE | HZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | Yes
9910602 | Ground Loop | TETCO | TZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | Yes
9910603 | Ground Loop | GEOCOMFORT | GZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910604 | Ground Loop | HYDRON MODULE | HZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910605 | Ground Loop | TETCO | TZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910606 | Ground Loop | GEOCOMFORT | GZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910607 | Ground Loop | HYDRON MODULE | HZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910608 | Ground Loop | TETCO | TZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910609 | Ground Loop | GEOCOMFORT | GZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910610 | Ground Loop | HYDRON MODULE | HZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910611 | Ground Loop | TETCO | TZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910612 | Ground Loop | GEOCOMFORT | GZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
207198734 | Ground Loop | FHP | QV024-2HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198737 | Ground Loop | FHP | QV024-3HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198738 | Ground Loop | FHP | QV024-3HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198741 | Ground Loop | FHP | QV024-4HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198742 | Ground Loop | FHP | QV024-4HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198745 | Ground Loop | FHP | QV030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198746 | Ground Loop | FHP | QV030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198747 | Ground Loop | FHP | QV030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198748 | Ground Loop | FHP | QV030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198749 | Ground Loop | FHP | QV030-2HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198750 | Ground Loop | FHP | QV030-2HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198751 | Ground Loop | FHP | QV030-2VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198752 | Ground Loop | FHP | QV030-2VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198753 | Ground Loop | FHP | QV030-3HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198754 | Ground Loop | FHP | QV030-3HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198755 | Ground Loop | FHP | QV030-3VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198756 | Ground Loop | FHP | QV030-3VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198757 | Ground Loop | FHP | QV030-4HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198758 | Ground Loop | FHP | QV030-4HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198759 | Ground Loop | FHP | QV030-4VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198760 | Ground Loop | FHP | QV030-4VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198761 | Ground Loop | FHP | QV036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198763 | Ground Loop | FHP | QV036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198764 | Ground Loop | FHP | QV036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198765 | Ground Loop | FHP | QV036-2HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198767 | Ground Loop | FHP | QV036-2VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198768 | Ground Loop | FHP | QV036-2VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198769 | Ground Loop | FHP | QV036-3HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198771 | Ground Loop | FHP | QV036-3VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198772 | Ground Loop | FHP | QV036-3VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198773 | Ground Loop | FHP | QV036-4HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198775 | Ground Loop | FHP | QV036-4VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198776 | Ground Loop | FHP | QV036-4VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
216625542 | Ground Loop | GEOSTAR | G5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625543 | Ground Loop | GEOSTAR | G5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625616 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216625617 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216625618 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625619 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625620 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625621 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625622 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216625623 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216625624 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625625 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625626 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625627 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625628 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625629 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625630 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625631 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625632 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625633 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625634 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625635 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625636 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625637 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625638 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625639 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
201926779 | Ground Loop | WaterFurnace | URD064*4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
201926783 | Ground Loop | WaterFurnace | URD064*4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
201926787 | Ground Loop | WaterFurnace | URD064*4*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
201926799 | Ground Loop | WaterFurnace | URD072*4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
201926802 | Ground Loop | WaterFurnace | URD072*4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
201926804 | Ground Loop | WaterFurnace | URD072*4*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
201926809 | Ground Loop | WaterFurnace | URT096*4*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65 | No
201930362 | Ground Loop | GEOCOMFORT | GZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | Yes
202084059 | Ground Loop | GEOCOMFORT | GZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
202084060 | Ground Loop | HYDRON MODULE | HZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | Yes
202084061 | Ground Loop | HYDRON MODULE | HZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
202084062 | Ground Loop | TETCO | TZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | Yes
202084063 | Ground Loop | TETCO | TZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
202132024 | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-038-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175 | No
202132025 | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-050-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833 | No
202132026 | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-060-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15 | No
202146863 | Ground Loop | GEOCOMFORT | GZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | Yes
202146864 | Ground Loop | GEOCOMFORT | GZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146865 | Ground Loop | GEOCOMFORT | GZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146866 | Ground Loop | HYDRON MODULE | HZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | Yes
215224294 | Ground Loop | BOSCH-GEO | RF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
215224295 | Ground Loop | BOSCH-GEO | RF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
215224296 | Ground Loop | BOSCH-GEO | RF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
215224297 | Ground Loop | BOSCH-GEO | RF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
215224298 | Ground Loop | BOSCH-GEO | RF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
215224299 | Ground Loop | BOSCH-GEO | RF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | Yes
215224300 | Ground Loop | BOSCH-GEO | RF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | Yes
202434167 | Ground Loop | BOSCH | LV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434168 | Ground Loop | BOSCH | LV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434169 | Ground Loop | BOSCH | LV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434173 | Ground Loop | BOSCH | LV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434174 | Ground Loop | BOSCH | LV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434175 | Ground Loop | BOSCH | LV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
205901397 | Ground Loop | DUAL AIR | CFX049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833 | Yes
205901398 | Ground Loop | MIAMI HEAT PUMP | HPX049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833 | Yes
205961529 | Ground Loop | Johnson Controls | JRE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175 | No
217014536 | Ground Loop | COMFORTMAKER | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014537 | Ground Loop | DAY & NIGHT | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014544 | Ground Loop | HEIL | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014545 | Ground Loop | ARCOAIRE | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014546 | Ground Loop | KEEPRITE | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014547 | Ground Loop | TEMPSTAR | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014548 | Ground Loop | COMFORTMAKER | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014549 | Ground Loop | DAY & NIGHT | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217037791 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS024BD1 | Y5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037792 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | Y5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037793 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS048BD1 | Y5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037794 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS060BD1 | Y5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037796 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ024BD1 | Y5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037797 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | Y5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037798 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ048BD1 | Y5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037799 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ060BD1 | Y5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037801 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037802 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037803 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037804 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037806 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037807 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037808 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037809 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037811 | Ground Loop | GeoSmart Energy | S5SS024BD1 | S5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037812 | Ground Loop | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037813 | Ground Loop | GeoSmart Energy | S5SS048BD1 | S5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037814 | Ground Loop | GeoSmart Energy | S5SS060BD1 | S5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037816 | Ground Loop | GeoSmart Energy | S5SZ024BD1 | S5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037817 | Ground Loop | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037818 | Ground Loop | GeoSmart Energy | S5SZ048BD1 | S5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
206726863 | Ground Loop | HYDRON MODULE | HBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | No
206726864 | Ground Loop | TETCO | TBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
206726865 | Ground Loop | TETCO | TBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | No
206726878 | Ground Loop | GEOCOMFORT | GBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
206726879 | Ground Loop | HYDRON MODULE | HBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
206726880 | Ground Loop | TETCO | TBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
206726881 | Ground Loop | GEOCOMFORT | GBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | No
206726882 | Ground Loop | HYDRON MODULE | HBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | No
206726883 | Ground Loop | TETCO | TBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | No
4651405 | Ground Loop | WaterFurnace | USV/USH030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651407 | Ground Loop | WaterFurnace | USV/USH030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651417 | Ground Loop | WaterFurnace | USV/USH036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651418 | Ground Loop | WaterFurnace | USV/USH036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651419 | Ground Loop | WaterFurnace | USV/USH036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651420 | Ground Loop | WaterFurnace | USV/USH036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651530 | Ground Loop | WaterFurnace | USV/USH042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651532 | Ground Loop | WaterFurnace | USV/USH042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651533 | Ground Loop | WaterFurnace | USV/USH042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651546 | Ground Loop | WaterFurnace | USV/USH048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651547 | Ground Loop | WaterFurnace | USV/USH048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651548 | Ground Loop | WaterFurnace | USV/USH048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651574 | Ground Loop | WaterFurnace | USV/USH060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651575 | Ground Loop | WaterFurnace | USV/USH060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651576 | Ground Loop | WaterFurnace | USV/USH060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651577 | Ground Loop | WaterFurnace | USV/USH070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651578 | Ground Loop | WaterFurnace | USV/USH070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651579 | Ground Loop | WaterFurnace | USV/USH070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651610 | Ground Loop | GEOSTAR | ZS023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651611 | Ground Loop | GeoSmart Energy | ZS023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651614 | Ground Loop | GEOSTAR | ZS024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651615 | Ground Loop | GeoSmart Energy | ZS024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651618 | Ground Loop | GEOSTAR | ZS024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651619 | Ground Loop | GeoSmart Energy | ZS024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651622 | Ground Loop | GEOSTAR | ZS024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651623 | Ground Loop | GeoSmart Energy | ZS024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651626 | Ground Loop | GEOSTAR | ZS024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651627 | Ground Loop | GeoSmart Energy | ZS024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651630 | Ground Loop | GEOSTAR | ZS030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651631 | Ground Loop | GeoSmart Energy | ZS030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651634 | Ground Loop | GEOSTAR | ZS030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651635 | Ground Loop | GeoSmart Energy | ZS030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651639 | Ground Loop | GEOSTAR | ZS030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651640 | Ground Loop | GeoSmart Energy | ZS030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651644 | Ground Loop | GEOSTAR | ZS030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651645 | Ground Loop | GeoSmart Energy | ZS030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651657 | Ground Loop | GEOSTAR | ZS036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651658 | Ground Loop | GeoSmart Energy | ZS036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651665 | Ground Loop | GEOSTAR | ZS036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651666 | Ground Loop | GeoSmart Energy | ZS036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651726 | Ground Loop | GEOSTAR | ZS036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651727 | Ground Loop | GeoSmart Energy | ZS036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651732 | Ground Loop | GEOSTAR | ZS036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651733 | Ground Loop | GeoSmart Energy | ZS036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651865 | Ground Loop | GEOSTAR | ZS023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651866 | Ground Loop | GeoSmart Energy | ZS023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651869 | Ground Loop | GEOSTAR | ZS023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
202350498 | Ground Loop | AAON, Inc. | M2-014-2-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083 | No
202350499 | Ground Loop | AAON, Inc. | M2-014-2-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725 | No
5296014 | Ground Loop | WaterFurnace | NBV/NBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296015 | Ground Loop | WaterFurnace | NBV/NBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296225 | Ground Loop | WaterFurnace | NBV/NBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296226 | Ground Loop | WaterFurnace | NBV/NBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296227 | Ground Loop | WaterFurnace | NBV/NBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296228 | Ground Loop | WaterFurnace | NBV/NBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296229 | Ground Loop | WaterFurnace | NBV/NBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296230 | Ground Loop | WaterFurnace | NBV/NBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5315758 | Ground Loop | WaterFurnace | NBV/NBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315759 | Ground Loop | WaterFurnace | NBV/NBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315760 | Ground Loop | WaterFurnace | NBV/NBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315761 | Ground Loop | WaterFurnace | NBV/NBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315762 | Ground Loop | WaterFurnace | NBV/NBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315763 | Ground Loop | WaterFurnace | NBV/NBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315774 | Ground Loop | WaterFurnace | NBV/NBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
5315776 | Ground Loop | WaterFurnace | NBV/NBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
5315777 | Ground Loop | WaterFurnace | NBV/NBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
5315778 | Ground Loop | WaterFurnace | NBV/NBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
202434436 | Ground Loop | FHP | LV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434437 | Ground Loop | FHP | LV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434438 | Ground Loop | FHP | LV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434439 | Ground Loop | FHP | LV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434444 | Ground Loop | FHP | LV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434445 | Ground Loop | FHP | LV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434446 | Ground Loop | FHP | LV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434447 | Ground Loop | FHP | LV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
206185538 | Ground Loop | DAIKIN | WGCH019J1*G/J*T |  | 18300 | 17.6 | 13200 | 3.8 | 1.525 | No
206185539 | Ground Loop | DAIKIN | WGCH019J1*G/J*C |  | 18300 | 17.6 | 13200 | 3.8 | 1.525 | No
215851764 | Ground Loop | DAIKIN | WSTH030J1*G/J*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725 | No
215851765 | Ground Loop | DAIKIN | WSTH030K3*G/J*C |  | 32700 | 19.1 | 20600 | 3.64 | 2.725 | No
215851770 | Ground Loop | DAIKIN | WSTH036J1*G/J*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225 | No
215851772 | Ground Loop | DAIKIN | WSTH036K3*G/J*C |  | 38700 | 20.02 | 25900 | 3.64 | 3.225 | No
213614585 | Ground Loop | DAIKIN | WSCH015E1*G/J*T |  | 15600 | 19 | 11900 | 3.6 | 1.3 | No
213614586 | Ground Loop | DAIKIN | WSCH015E1*G/J*C |  | 15600 | 19 | 11900 | 3.6 | 1.3 | No
213710596 | Ground Loop | DAIKIN | WSSH007A1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625 | No
213710598 | Ground Loop | DAIKIN | WSSH007E1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625 | No
213710600 | Ground Loop | DAIKIN | WSSH007J1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625 | No
202434548 | Ground Loop | BOSCH | SV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434549 | Ground Loop | BOSCH | SV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434550 | Ground Loop | BOSCH | SV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434551 | Ground Loop | BOSCH | SV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434556 | Ground Loop | BOSCH | SV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434557 | Ground Loop | BOSCH | SV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434558 | Ground Loop | BOSCH | SV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434559 | Ground Loop | BOSCH | SV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
206185754 | Ground Loop | DAIKIN | WGCH015E1*G/J*P |  | 15100 | 18.1 | 11100 | 3.8 | 1.2583 | No
206185755 | Ground Loop | DAIKIN | WGCH015E1*G/J*T |  | 15300 | 19.9 | 10700 | 3.9 | 1.275 | No
206185756 | Ground Loop | DAIKIN | WGCH015E1*G/J*C |  | 15300 | 19.9 | 10700 | 3.9 | 1.275 | No
206185757 | Ground Loop | DAIKIN | WGCH019E1*G/J*C |  | 18300 | 19 | 13200 | 3.9 | 1.525 | No
216739972 | Ground Loop | DAIKIN | WSNV042E1*G/J*C |  | 44700 | 19.3 | 29000 | 3.6 | 3.725 | No
200083642 | Ground Loop | COMFORT-AIRE | HZV/H/D036B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | Yes
200083643 | Ground Loop | CENTURY | HZV/H/D036B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | Yes
200083644 | Ground Loop | COMFORT-AIRE | HZV/H/D024B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | Yes
200083645 | Ground Loop | CENTURY | HZV/H/D024B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | Yes
200083646 | Ground Loop | COMFORT-AIRE | HZV/H/D048B |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | Yes
200083647 | Ground Loop | CENTURY | HZV/H/D048B |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | Yes
200083648 | Ground Loop | COMFORT-AIRE | HZV/H/D060B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | Yes
200083649 | Ground Loop | CENTURY | HZV/H/D060B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | Yes
200083684 | Ground Loop | COMFORT-AIRE | HZS024B | WDG024**A-*B | 24700 | 17.7 | 18800 | 3.6 | 2.0583 | Yes
200083685 | Ground Loop | CENTURY | HZS024B | WDG024**A-*B | 24700 | 17.7 | 18800 | 3.6 | 2.0583 | Yes
200083686 | Ground Loop | COMFORT-AIRE | HZS024B | WDG024**B-*B | 25800 | 18.3 | 18700 | 3.8 | 2.15 | Yes
200083687 | Ground Loop | CENTURY | HZS024B | WDG024**B-*B | 25800 | 18.3 | 18700 | 3.8 | 2.15 | Yes
200083688 | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*A-B | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
200083689 | Ground Loop | CENTURY | HZS024B | MWG24*A-B | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
200083690 | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*C-B | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
200083691 | Ground Loop | CENTURY | HZS024B | MWG24*C-B | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
200083692 | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*B-B | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
200083693 | Ground Loop | CENTURY | HZS024B | MWG24*B-B | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
200083694 | Ground Loop | COMFORT-AIRE | HZS036B | MWG36**-B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | No
200083695 | Ground Loop | CENTURY | HZS036B | MWG36**-B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
200083696 | Ground Loop | COMFORT-AIRE | HZS036B | WDG036***-*B | 37700 | 17.8 | 26200 | 3.8 | 3.1417 | Yes
200083697 | Ground Loop | CENTURY | HZS036B | WDG036***-*B | 37700 | 17.8 | 26200 | 3.8 | 3.1417 | Yes
216772567 | Ground Loop | Enertech | EVS012* |  | 12625 | 18.2 | 9475 | 3.6 | 1.0521 | Yes
216772568 | Ground Loop | Enertech | EVS018* |  | 22275 | 24.1 | 15400 | 4.24 | 1.8562 | Yes
216772569 | Ground Loop | Enertech | EVT024* |  | 25775 | 20.5 | 19400 | 4.09 | 2.1479 | No
216772570 | Ground Loop | Enertech | EVT030* |  | 32900 | 19.8 | 24425 | 3.98 | 2.7417 | Yes
216772571 | Ground Loop | Enertech | EVT036* |  | 38450 | 18.8 | 29500 | 3.94 | 3.2042 | Yes
216772572 | Ground Loop | Enertech | EVT042* |  | 45900 | 19.4 | 32975 | 4.14 | 3.825 | Yes
216772573 | Ground Loop | Enertech | EVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917 | Yes
216772574 | Ground Loop | Enertech | EYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
216772575 | Ground Loop | Enertech | EYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083 | Yes
216772576 | Ground Loop | Enertech | EYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325 | Yes
216772579 | Ground Loop | Enertech | EZT024* |  | 26400 | 18.8 | 18400 | 3.9 | 2.2 | No
216772580 | Ground Loop | Enertech | EZT030* |  | 32625 | 17.6 | 24400 | 3.7 | 2.7188 | Yes
216772581 | Ground Loop | Enertech | EZT036* |  | 36725 | 18.9 | 28375 | 3.84 | 3.0604 | Yes
216772582 | Ground Loop | Enertech | EZT042* |  | 44750 | 18.8 | 32900 | 3.67 | 3.7292 | Yes
216772583 | Ground Loop | Enertech | EZT048* |  | 48700 | 17.3 | 36900 | 3.7 | 4.0583 | Yes
216772584 | Ground Loop | Enertech | EZT060* |  | 58875 | 17.4 | 44550 | 3.6 | 4.9062 | Yes
216772586 | Ground Loop | Enertech | EVS015* |  | 16725 | 24.1 | 11500 | 4.3 | 1.3938 | Yes
216772588 | Ground Loop | Enertech | EBT060* | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
216772590 | Ground Loop | Enertech | EVT060* |  | 60900 | 17.6 | 46700 | 3.8 | 5.075 | Yes
216772591 | Ground Loop | Enertech | EYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583 | Yes
216772592 | Ground Loop | Enertech | EZS015* |  | 14525 | 18.6 | 11200 | 3.9 | 1.2104 | Yes
216772593 | Ground Loop | Enertech | EZS017* |  | 17300 | 17 | 12825 | 3.61 | 1.4417 | Yes
216772594 | Ground Loop | Enertech | EZS018* |  | 20400 | 21.5 | 14100 | 3.86 | 1.7 | Yes
216772596 | Ground Loop | Enertech | EYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583 | Yes
215405064 | Ground Loop | DAIKIN | WSSV060E1*H*T |  | 66300 | 20 | 48800 | 4 | 5.525 | No
215405065 | Ground Loop | DAIKIN | WSSV060F3*H*T |  | 66300 | 19.8 | 48800 | 3.96 | 5.525 | No
215405066 | Ground Loop | DAIKIN | WSSV060K3*H*T |  | 66300 | 19.8 | 48800 | 3.92 | 5.525 | No
215405067 | Ground Loop | DAIKIN | WSSV060L3*H*T |  | 66300 | 19.4 | 48800 | 3.88 | 5.525 | No
215405068 | Ground Loop | DAIKIN | WSSV060E1*H*C |  | 66300 | 20 | 48800 | 4 | 5.525 | No
215405069 | Ground Loop | DAIKIN | WSSV060F3*H*C |  | 66300 | 19.8 | 48800 | 3.96 | 5.525 | No
206185640 | Ground Loop | DAIKIN | WGCH048E1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185641 | Ground Loop | DAIKIN | WGCH048E1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185646 | Ground Loop | DAIKIN | WGCH048F1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185647 | Ground Loop | DAIKIN | WGCH048F1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
202434484 | Ground Loop | BOSCH | SV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434485 | Ground Loop | BOSCH | SV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434486 | Ground Loop | BOSCH | SV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434487 | Ground Loop | BOSCH | SV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434492 | Ground Loop | BOSCH | SV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434493 | Ground Loop | BOSCH | SV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434494 | Ground Loop | BOSCH | SV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434495 | Ground Loop | BOSCH | SV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434500 | Ground Loop | BOSCH | SV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434501 | Ground Loop | BOSCH | SV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434502 | Ground Loop | BOSCH | SV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434503 | Ground Loop | BOSCH | SV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434508 | Ground Loop | BOSCH | SV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434509 | Ground Loop | BOSCH | SV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434510 | Ground Loop | BOSCH | SV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434511 | Ground Loop | BOSCH | SV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
217642975 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642976 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642977 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642978 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642979 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642980 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642981 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642982 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642983 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642984 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642990 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642991 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642992 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642993 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642994 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215400144 | Ground Loop | DAIKIN | WSMV048E1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215400145 | Ground Loop | DAIKIN | WSMV048F3*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215400148 | Ground Loop | DAIKIN | WSMV048E1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215400149 | Ground Loop | DAIKIN | WSMV048F3*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215400156 | Ground Loop | DAIKIN | WSMV060E1*G/J*T |  | 63500 | 17.8 | 46100 | 3.7 | 5.2917 | No
215400157 | Ground Loop | DAIKIN | WSMV060F3*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
215400160 | Ground Loop | DAIKIN | WSMV060E1*G/J*C |  | 63500 | 17.8 | 46100 | 3.7 | 5.2917 | No
215400161 | Ground Loop | DAIKIN | WSMV060F3*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
215400171 | Ground Loop | DAIKIN | WSSV012E1*H*T |  | 12200 | 20.4 | 8500 | 3.61 | 1.0167 | No
215400173 | Ground Loop | DAIKIN | WSSV015E1*H*T |  | 17000 | 23.75 | 10500 | 3.87 | 1.4167 | No
215400175 | Ground Loop | DAIKIN | WSSV015E1*H*C |  | 17000 | 23.75 | 10500 | 3.87 | 1.4167 | No
215400177 | Ground Loop | DAIKIN | WSSV019E1*H*T |  | 20600 | 20.96 | 14100 | 3.73 | 1.7167 | No
215400179 | Ground Loop | DAIKIN | WSSV019E1*H*C |  | 20600 | 20.96 | 14100 | 3.73 | 1.7167 | No
215400182 | Ground Loop | DAIKIN | WSSV024J1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215400183 | Ground Loop | DAIKIN | WSSV024K3*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215400186 | Ground Loop | DAIKIN | WSSV024J1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215400187 | Ground Loop | DAIKIN | WSSV024K3*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215400190 | Ground Loop | DAIKIN | WSSV030J1*H*T |  | 30200 | 20.49 | 20700 | 3.83 | 2.5167 | No
215400191 | Ground Loop | DAIKIN | WSSV030K3*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
215400194 | Ground Loop | DAIKIN | WSSV030J1*H*C |  | 30200 | 20.49 | 20700 | 3.83 | 2.5167 | No
215400195 | Ground Loop | DAIKIN | WSSV030K3*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
215400198 | Ground Loop | DAIKIN | WSSV036J1*H*T |  | 40500 | 20.65 | 27600 | 3.84 | 3.375 | No
215400199 | Ground Loop | DAIKIN | WSSV036K3*H*T |  | 40500 | 21.09 | 27600 | 3.83 | 3.375 | No
217351730 | Ground Loop | CARRIER | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351731 | Ground Loop | CARRIER | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351734 | Ground Loop | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351735 | Ground Loop | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351736 | Ground Loop | CARRIER | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351738 | Ground Loop | CARRIER | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351739 | Ground Loop | CARRIER | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351741 | Ground Loop | CARRIER | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351742 | Ground Loop | CARRIER | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351743 | Ground Loop | CARRIER | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351744 | Ground Loop | CARRIER | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351745 | Ground Loop | CARRIER | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351747 | Ground Loop | CARRIER | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217897457 | Ground Loop | CENTURY | MJN036A | MKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667 | Yes
217897458 | Ground Loop | COMFORT-AIRE | MJN036A | MKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667 | Yes
217897463 | Ground Loop | CENTURY | MJN024A | MAN024A | 23900 | 19 | 17900 | 4 | 1.9917 | Yes
217897464 | Ground Loop | COMFORT-AIRE | MJN024A | MAN024A | 23900 | 19 | 17900 | 4 | 1.9917 | Yes
217897465 | Ground Loop | CENTURY | MJN036A | MAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917 | Yes
217897466 | Ground Loop | COMFORT-AIRE | MJN036A | MAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917 | Yes
217897467 | Ground Loop | CENTURY | MJN048A | MAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833 | Yes
217897468 | Ground Loop | COMFORT-AIRE | MJN048A | MAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833 | Yes
202146985 | Ground Loop | TETCO | TZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146986 | Ground Loop | TETCO | TZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146987 | Ground Loop | TETCO | TZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146988 | Ground Loop | TETCO | TZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146989 | Ground Loop | TETCO | TZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | Yes
202146990 | Ground Loop | TETCO | TZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202146991 | Ground Loop | GEOCOMFORT | GZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | Yes
202146992 | Ground Loop | GEOCOMFORT | GZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202146993 | Ground Loop | GEOCOMFORT | GZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202146994 | Ground Loop | GEOCOMFORT | GZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202146995 | Ground Loop | GEOCOMFORT | GZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
215399839 | Ground Loop | DAIKIN | WSMV048L3*G/J*C |  | 49300 | 19.09 | 36000 | 3.75 | 4.1083 | No
215399846 | Ground Loop | DAIKIN | WSMV060K3*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
215399850 | Ground Loop | DAIKIN | WSMV060K3*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
215399858 | Ground Loop | DAIKIN | WSSV015A1*H*T |  | 17000 | 23.75 | 10400 | 3.77 | 1.4167 | No
215399859 | Ground Loop | DAIKIN | WSSV015J1*H*T |  | 17000 | 22.25 | 10500 | 3.77 | 1.4167 | No
215399862 | Ground Loop | DAIKIN | WSSV015A1*H*C |  | 17000 | 23.75 | 10400 | 3.77 | 1.4167 | No
215399863 | Ground Loop | DAIKIN | WSSV015J1*H*C |  | 17000 | 22.25 | 10500 | 3.77 | 1.4167 | No
215399865 | Ground Loop | DAIKIN | WSSV019J1*H*T |  | 20600 | 20.96 | 14100 | 3.63 | 1.7167 | No
215399867 | Ground Loop | DAIKIN | WSSV019J1*H*C |  | 20600 | 20.96 | 14100 | 3.63 | 1.7167 | No
215399870 | Ground Loop | DAIKIN | WSSV042J1*H*T |  | 44352 | 21.08 | 28710 | 3.88 | 3.696 | No
215399871 | Ground Loop | DAIKIN | WSSV042K3*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
215399874 | Ground Loop | DAIKIN | WSSV042J1*H*C |  | 44352 | 21.08 | 28710 | 3.88 | 3.696 | No
215399875 | Ground Loop | DAIKIN | WSSV042K3*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
215399878 | Ground Loop | DAIKIN | WSSV048K3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215399879 | Ground Loop | DAIKIN | WSSV048L3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215399882 | Ground Loop | DAIKIN | WSSV048K3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215399883 | Ground Loop | DAIKIN | WSSV048L3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
214771933 | Ground Loop | TRANE | EXVK015A |  | 16200 | 18.7 | 11800 | 3.73 | 1.35 | No
214771934 | Ground Loop | TRANE | EXVK018A |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417 | No
214771935 | Ground Loop | TRANE | EXVK024A |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214771936 | Ground Loop | TRANE | EXVK030A |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214771937 | Ground Loop | TRANE | EXVK036A |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214771938 | Ground Loop | TRANE | EXVK042A |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214771939 | Ground Loop | TRANE | EXVK048A |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
207335588 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335589 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****J |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335590 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335591 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335592 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335593 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
3706370 | Ground Loop | GEOSTAR | ZS018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
3706371 | Ground Loop | GEOSTAR | ZS023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3706373 | Ground Loop | GEOSTAR | ZS023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3706374 | Ground Loop | GEOSTAR | ZS023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3706375 | Ground Loop | GEOSTAR | ZS023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3706376 | Ground Loop | GEOSTAR | ZS024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3706377 | Ground Loop | GEOSTAR | ZS024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3706378 | Ground Loop | GEOSTAR | ZS024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3706379 | Ground Loop | GEOSTAR | ZS024**4*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3706380 | Ground Loop | GEOSTAR | ZS030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3706381 | Ground Loop | GEOSTAR | ZS030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3706382 | Ground Loop | GEOSTAR | ZS030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3706383 | Ground Loop | GEOSTAR | ZS030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3706391 | Ground Loop | GEOSTAR | ZS042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3706392 | Ground Loop | GEOSTAR | ZS042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3706393 | Ground Loop | GEOSTAR | ZS042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3706394 | Ground Loop | GEOSTAR | ZS048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3706395 | Ground Loop | GEOSTAR | ZS048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3706396 | Ground Loop | GEOSTAR | ZS048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3706397 | Ground Loop | GEOSTAR | ZS060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3706398 | Ground Loop | GEOSTAR | ZS060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3706399 | Ground Loop | GEOSTAR | ZS060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3811559 | Ground Loop | WaterFurnace | USV/USH024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3811671 | Ground Loop | WaterFurnace | USV/USH024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3811673 | Ground Loop | WaterFurnace | USV/USH024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
202147712 | Ground Loop | GEOCOMFORT | GZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147713 | Ground Loop | HYDRON MODULE | HZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147714 | Ground Loop | TETCO | TZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202434143 | Ground Loop | BOSCH | LV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434144 | Ground Loop | BOSCH | LV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434145 | Ground Loop | BOSCH | LV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434149 | Ground Loop | BOSCH | LV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434150 | Ground Loop | BOSCH | LV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434151 | Ground Loop | BOSCH | LV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434155 | Ground Loop | BOSCH | LV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434156 | Ground Loop | BOSCH | LV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434157 | Ground Loop | BOSCH | LV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434161 | Ground Loop | BOSCH | LV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434162 | Ground Loop | BOSCH | LV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434163 | Ground Loop | BOSCH | LV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
205767623 | Ground Loop | ClimateMaster | TCH/V015A*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
205767624 | Ground Loop | ClimateMaster | TRH/V015A*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
205767626 | Ground Loop | ClimateMaster | TES/P038B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
205780261 | Ground Loop | GEOSTAR | 111J038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
205782086 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ042J1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
205782087 | Ground Loop | GEOSTAR | 103J042**1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
205782239 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
205782240 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
205782241 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205782242 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST038**1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205782243 | Ground Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
205782244 | Ground Loop | GeoSmart Energy | GSZ042*1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
205782245 | Ground Loop | GeoSmart Energy | GTZ038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205782246 | Ground Loop | GeoSmart Energy | GTS038*1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
205782247 | Ground Loop | GeoSmart Energy | GTS038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205782567 | Ground Loop | YORK BY JOHNSON CONTROLS | YACT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
205782571 | Ground Loop | GeoSmart Energy | QT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
205788273 | Ground Loop | Johnson Controls | JSH/V/D018B B |  | 19500 | 18.4 | 14500 | 3.6 | 1.625 | No
205788274 | Ground Loop | SKYMARK | JSH/V/D018B C |  | 19500 | 18.4 | 14500 | 3.6 | 1.625 | No
205788275 | Ground Loop | Johnson Controls | JSH/V/D018B*K B |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833 | No
205788276 | Ground Loop | SKYMARK | JSH/V/D018B*K C |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833 | No
205788277 | Ground Loop | Johnson Controls | JSH/V/D024C B |  | 25300 | 18.9 | 19200 | 4 | 2.1083 | No
205788278 | Ground Loop | SKYMARK | JSH/V/D024C C |  | 25300 | 18.9 | 19200 | 4 | 2.1083 | No
205788279 | Ground Loop | Johnson Controls | JSH/V/D024C*K B |  | 25500 | 20.9 | 19100 | 4.2 | 2.125 | No
205788280 | Ground Loop | SKYMARK | JSH/V/D024C*K C |  | 25500 | 20.9 | 19100 | 4.2 | 2.125 | No
205788281 | Ground Loop | Johnson Controls | JSH/V/D030C B |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333 | No
205788282 | Ground Loop | SKYMARK | JSH/V/D030C C |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333 | No
205788283 | Ground Loop | Johnson Controls | JSH/V/D036C B |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583 | No
205788284 | Ground Loop | SKYMARK | JSH/V/D036C C |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583 | No
205788285 | Ground Loop | Johnson Controls | JSH/V/D036C*K B |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833 | No
205788286 | Ground Loop | SKYMARK | JSH/V/D036C*K C |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833 | No
205788287 | Ground Loop | Johnson Controls | JSH/V/D042C B |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417 | No
205788288 | Ground Loop | SKYMARK | JSH/V/D042C C |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417 | No
205788289 | Ground Loop | Johnson Controls | JSH/V/D042C*K B |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917 | Yes
205788290 | Ground Loop | SKYMARK | JSH/V/D042C*K C |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917 | Yes
205788293 | Ground Loop | Johnson Controls | JSH/V/D060C B |  | 63900 | 17.2 | 46900 | 3.7 | 5.325 | No
205788294 | Ground Loop | SKYMARK | JSH/V/D060C C |  | 63900 | 17.2 | 46900 | 3.7 | 5.325 | No
205823049 | Ground Loop | OMEGA HEAT PUMP | VSHP050G |  | 15000 | 18.5 | 10600 | 3.7 | 1.25 | No
202146996 | Ground Loop | GEOCOMFORT | GZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | Yes
202146997 | Ground Loop | GEOCOMFORT | GZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202146998 | Ground Loop | GEOCOMFORT | GZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202146999 | Ground Loop | GEOCOMFORT | GZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147000 | Ground Loop | HYDRON MODULE | HZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | Yes
202147001 | Ground Loop | HYDRON MODULE | HZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147002 | Ground Loop | HYDRON MODULE | HZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147003 | Ground Loop | HYDRON MODULE | HZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147004 | Ground Loop | HYDRON MODULE | HZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147005 | Ground Loop | HYDRON MODULE | HZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | Yes
202147006 | Ground Loop | HYDRON MODULE | HZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147007 | Ground Loop | HYDRON MODULE | HZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147008 | Ground Loop | HYDRON MODULE | HZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147009 | Ground Loop | TETCO | TZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | Yes
202147010 | Ground Loop | TETCO | TZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147011 | Ground Loop | TETCO | TZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147012 | Ground Loop | TETCO | TZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147013 | Ground Loop | TETCO | TZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147014 | Ground Loop | TETCO | TZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | Yes
202147015 | Ground Loop | TETCO | TZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147016 | Ground Loop | TETCO | TZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147017 | Ground Loop | TETCO | TZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147018 | Ground Loop | GEOCOMFORT | GZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | Yes
202147019 | Ground Loop | GEOCOMFORT | GZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147020 | Ground Loop | GEOCOMFORT | GZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147021 | Ground Loop | GEOCOMFORT | GZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147022 | Ground Loop | GEOCOMFORT | GZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | Yes
202147023 | Ground Loop | GEOCOMFORT | GZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147024 | Ground Loop | HYDRON MODULE | HZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | Yes
202147025 | Ground Loop | HYDRON MODULE | HZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147026 | Ground Loop | HYDRON MODULE | HZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147027 | Ground Loop | HYDRON MODULE | HZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147028 | Ground Loop | HYDRON MODULE | HZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | Yes
202147029 | Ground Loop | HYDRON MODULE | HZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147030 | Ground Loop | TETCO | TZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | Yes
202147031 | Ground Loop | TETCO | TZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147032 | Ground Loop | TETCO | TZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147033 | Ground Loop | TETCO | TZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147034 | Ground Loop | TETCO | TZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | Yes
202147035 | Ground Loop | TETCO | TZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147040 | Ground Loop | GEOCOMFORT | GZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | Yes
217897411 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
217897412 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
200083804 | Ground Loop | NORTHERN HEAT PUMP | RA-VE-061-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15 | No
200083805 | Ground Loop | NORTHSTAR SERIES | RA-VE-061-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15 | No
201756620 | Ground Loop | NORTHERN HEAT PUMP | RA-VE-041-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175 | No
201756621 | Ground Loop | NORTHSTAR SERIES | RA-VE-041-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175 | No
201756622 | Ground Loop | NORTHERN HEAT PUMP | RA-VE-053-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833 | No
201756623 | Ground Loop | NORTHSTAR SERIES | RA-VE-053-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833 | No
202434382 | Ground Loop | FHP | LV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434383 | Ground Loop | FHP | LV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434388 | Ground Loop | FHP | LV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434389 | Ground Loop | FHP | LV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434390 | Ground Loop | FHP | LV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434391 | Ground Loop | FHP | LV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434396 | Ground Loop | FHP | LV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434397 | Ground Loop | FHP | LV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434398 | Ground Loop | FHP | LV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434399 | Ground Loop | FHP | LV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
205996643 | Ground Loop | Johnson Controls | JEV/H/D026B B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | No
205996644 | Ground Loop | Johnson Controls | JEV/H/D038B B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | No
205996645 | Ground Loop | Johnson Controls | JEV/H/D049B B |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | No
205996646 | Ground Loop | Johnson Controls | JEV/H/D064B B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | No
206185518 | Ground Loop | DAIKIN | WGCH015A1*G/J*T |  | 15300 | 18 | 10700 | 3.6 | 1.275 | No
206185519 | Ground Loop | DAIKIN | WGCH015A1*G/J*C |  | 15300 | 18 | 10700 | 3.6 | 1.275 | No
206185527 | Ground Loop | DAIKIN | WGCH015J1*G/J*T |  | 14800 | 18 | 10500 | 3.6 | 1.2333 | No
206185528 | Ground Loop | DAIKIN | WGCH015J1*G/J*C |  | 14800 | 18 | 10500 | 3.6 | 1.2333 | No
206185532 | Ground Loop | DAIKIN | WGCH019E1*G/J*P |  | 18000 | 17.9 | 13600 | 3.8 | 1.5 | No
206185533 | Ground Loop | DAIKIN | WGCH019E1*G/J*T |  | 18300 | 19 | 13200 | 3.9 | 1.525 | No
217642948 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642959 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642960 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642961 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642962 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642963 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642964 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642965 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642973 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642974 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
9063210 | Ground Loop | DAIKIN | W.CCW.2.072.*.*.*.*.*.*.L |  | 80100 | 17.1 | 58700 | 3.75 | 6.675 | No
9100310 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100311 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100313 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100314 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100316 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100317 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100319 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100320 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100326 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
9100328 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
9100330 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
9100332 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
9100334 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100335 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100337 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100338 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100340 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100341 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100343 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100345 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100346 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100348 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100349 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100351 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100352 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100354 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100355 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100357 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100358 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
207348679 | Ground Loop | WaterFurnace | URS070*4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348680 | Ground Loop | WaterFurnace | URS070*4*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348681 | Ground Loop | WaterFurnace | URS060*0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348682 | Ground Loop | WaterFurnace | URS060*0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348683 | Ground Loop | WaterFurnace | URS060*0*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348684 | Ground Loop | WaterFurnace | URS060*3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348685 | Ground Loop | WaterFurnace | URS060*3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348686 | Ground Loop | WaterFurnace | URS060*3*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348687 | Ground Loop | WaterFurnace | URS060*4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348688 | Ground Loop | WaterFurnace | URS060*4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348689 | Ground Loop | WaterFurnace | URS060*4*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348707 | Ground Loop | WaterFurnace | URD038*0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348708 | Ground Loop | WaterFurnace | URD038*0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348709 | Ground Loop | WaterFurnace | URD038*0*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348710 | Ground Loop | WaterFurnace | URD038*3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348711 | Ground Loop | WaterFurnace | URD038*3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348712 | Ground Loop | WaterFurnace | URD038*3*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348713 | Ground Loop | WaterFurnace | URD038*4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348714 | Ground Loop | WaterFurnace | URD038*4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348715 | Ground Loop | WaterFurnace | URD038*4*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348716 | Ground Loop | WaterFurnace | URD049*0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348717 | Ground Loop | WaterFurnace | URD049*0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348718 | Ground Loop | WaterFurnace | URD049*0*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348719 | Ground Loop | WaterFurnace | URD049*3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348720 | Ground Loop | WaterFurnace | URD049*3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348721 | Ground Loop | WaterFurnace | URD049*3*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348722 | Ground Loop | WaterFurnace | URD049*4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348723 | Ground Loop | WaterFurnace | URD049*4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348724 | Ground Loop | WaterFurnace | URD049*4*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348725 | Ground Loop | WaterFurnace | URD064*0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348726 | Ground Loop | WaterFurnace | URD064*0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348727 | Ground Loop | WaterFurnace | URD064*0*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348728 | Ground Loop | WaterFurnace | URD064*3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348729 | Ground Loop | WaterFurnace | URD064*3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348730 | Ground Loop | WaterFurnace | URD064*3*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348731 | Ground Loop | WaterFurnace | URD064*4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348732 | Ground Loop | WaterFurnace | URD064*4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348733 | Ground Loop | WaterFurnace | URD064*4*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348734 | Ground Loop | WaterFurnace | URD072*0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348735 | Ground Loop | WaterFurnace | URD072*0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348736 | Ground Loop | WaterFurnace | URD072*0*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348737 | Ground Loop | WaterFurnace | URD072*3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348738 | Ground Loop | WaterFurnace | URD072*3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348739 | Ground Loop | WaterFurnace | URD072*3*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348740 | Ground Loop | WaterFurnace | URD072*4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348741 | Ground Loop | WaterFurnace | URD072*4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348742 | Ground Loop | WaterFurnace | URD072*4*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
205767489 | Ground Loop | ClimateMaster | TSH/V/D018B |  | 19500 | 18.4 | 14500 | 3.6 | 1.625 | No
205767490 | Ground Loop | ClimateMaster | TSH/V/D018B*K |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833 | No
215224810 | Ground Loop | HEIL | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224811 | Ground Loop | ARCOAIRE | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224812 | Ground Loop | KEEPRITE | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224813 | Ground Loop | TEMPSTAR | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224814 | Ground Loop | COMFORTMAKER | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224815 | Ground Loop | DAY & NIGHT | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224816 | Ground Loop | HEIL | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224817 | Ground Loop | ARCOAIRE | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224818 | Ground Loop | KEEPRITE | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224819 | Ground Loop | TEMPSTAR | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224820 | Ground Loop | COMFORTMAKER | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224821 | Ground Loop | DAY & NIGHT | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224822 | Ground Loop | HEIL | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224823 | Ground Loop | ARCOAIRE | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224824 | Ground Loop | KEEPRITE | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224825 | Ground Loop | TEMPSTAR | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224826 | Ground Loop | COMFORTMAKER | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224827 | Ground Loop | DAY & NIGHT | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224828 | Ground Loop | HEIL | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224829 | Ground Loop | ARCOAIRE | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224830 | Ground Loop | KEEPRITE | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224831 | Ground Loop | TEMPSTAR | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224832 | Ground Loop | COMFORTMAKER | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224833 | Ground Loop | DAY & NIGHT | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
206438871 | Ground Loop | CARRIER | 50PSH/V009***3/CA* |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438872 | Ground Loop | CARRIER | 50PSH/V009***4/DA* |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438873 | Ground Loop | CARRIER | 50PSH/V012***3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438874 | Ground Loop | CARRIER | 50PSH/V015***3/CA* |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438875 | Ground Loop | CARRIER | 50PSH/V015***4/DA* |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438876 | Ground Loop | CARRIER | 50PSH/V030***4/DA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438877 | Ground Loop | CARRIER | 50PSH/V030***6/FA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438878 | Ground Loop | CARRIER | 50PSH/V030***5/EA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438879 | Ground Loop | CARRIER | 50PSH/V030***3/CA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438880 | Ground Loop | CARRIER | 50PSH/V060***6/FA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438881 | Ground Loop | CARRIER | 50PSH/V060***5/EA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438882 | Ground Loop | CARRIER | 50PSH/V060***3/CA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438883 | Ground Loop | CARRIER | 50PSH/V070***3/CA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438884 | Ground Loop | CARRIER | 50PSH/V070***5/EA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438885 | Ground Loop | CARRIER | 50PSH/V070***6/FA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438903 | Ground Loop | CARRIER | 50PSV012**C3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438904 | Ground Loop | CARRIER | 50PSH012**C3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
214067581 | Ground Loop | GeoSmart Energy | GBV/GBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067582 | Ground Loop | GeoSmart Energy | GBV/GBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067584 | Ground Loop | GeoSmart Energy | GBV/GBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214067585 | Ground Loop | GeoSmart Energy | GBV/GBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214067586 | Ground Loop | GeoSmart Energy | GBV/GBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214067587 | Ground Loop | GeoSmart Energy | GBV/GBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214067588 | Ground Loop | GeoSmart Energy | GBV/GBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
214067589 | Ground Loop | GeoSmart Energy | GBV/GBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214067590 | Ground Loop | GeoSmart Energy | GBV/GBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214067591 | Ground Loop | GeoSmart Energy | GBV/GBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
214067592 | Ground Loop | GeoSmart Energy | GBV/GBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214067593 | Ground Loop | GeoSmart Energy | GBV/GBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214067594 | Ground Loop | GeoSmart Energy | GBV/GBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
215837857 | Ground Loop | DAIKIN | WSSH036K3*G/J*C |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583 | No
215837863 | Ground Loop | DAIKIN | WSSH042F3*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837865 | Ground Loop | DAIKIN | WSSH042J1*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837866 | Ground Loop | DAIKIN | WSSH042K3*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837873 | Ground Loop | DAIKIN | WSSH042F3*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837874 | Ground Loop | DAIKIN | WSSH042J1*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837876 | Ground Loop | DAIKIN | WSSH042K3*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837882 | Ground Loop | DAIKIN | WSSH048F3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837883 | Ground Loop | DAIKIN | WSSH048K3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837884 | Ground Loop | DAIKIN | WSSH048L3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837891 | Ground Loop | DAIKIN | WSSH048F3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837892 | Ground Loop | DAIKIN | WSSH048K3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837893 | Ground Loop | DAIKIN | WSSH048L3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837917 | Ground Loop | DAIKIN | WSSH070F3*G/J*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
215837919 | Ground Loop | DAIKIN | WSSH070K3*G/J*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
215837926 | Ground Loop | DAIKIN | WSSH070F3*G/J*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
215837927 | Ground Loop | DAIKIN | WSSH070K3*G/J*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
215851758 | Ground Loop | DAIKIN | WSTH024J1*G/J*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917 | No
215851759 | Ground Loop | DAIKIN | WSTH024K3*G/J*C |  | 25100 | 19.32 | 17200 | 3.8 | 2.0917 | No
216726189 | Ground Loop | DAIKIN | WSRC007*E*G/J |  | 7100 | 19.4 | 4700 | 3.6 | 0.59167 | No
216726191 | Ground Loop | DAIKIN | WSRC009*E*G/J |  | 9100 | 18.1 | 6500 | 3.6 | 0.75833 | No
216726195 | Ground Loop | DAIKIN | WSRC015*E*G/J |  | 15400 | 18.9 | 11200 | 3.6 | 1.2833 | No
214844588 | Ground Loop | WaterFurnace | W7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083 | Yes
214844645 | Ground Loop | WaterFurnace | W7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833 | Yes
214844646 | Ground Loop | WaterFurnace | W7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75 | Yes
215223494 | Ground Loop | WaterFurnace | V5AV084*D4**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
215223500 | Ground Loop | WaterFurnace | V5AV084*D3**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
215223501 | Ground Loop | WaterFurnace | V5AV084*D5**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
215224027 | Ground Loop | BOSCH | CF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224028 | Ground Loop | BOSCH | CF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224029 | Ground Loop | BOSCH | CF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224030 | Ground Loop | BOSCH | CF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224031 | Ground Loop | BOSCH | CF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224032 | Ground Loop | BOSCH | CF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224033 | Ground Loop | BOSCH | CF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224034 | Ground Loop | BOSCH | CF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224035 | Ground Loop | BOSCH | CF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224036 | Ground Loop | BOSCH | CF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224037 | Ground Loop | BOSCH | CF007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224038 | Ground Loop | BOSCH | CF007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224039 | Ground Loop | BOSCH | CF009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224040 | Ground Loop | BOSCH | CF009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224041 | Ground Loop | BOSCH | CF012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224042 | Ground Loop | BOSCH | CF012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224043 | Ground Loop | BOSCH | CF015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224044 | Ground Loop | BOSCH | CF015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
201907610 | Ground Loop | WaterFurnace | URS036*0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907611 | Ground Loop | WaterFurnace | URS036*0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907612 | Ground Loop | WaterFurnace | URS036*0*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907613 | Ground Loop | WaterFurnace | URS036*3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907614 | Ground Loop | WaterFurnace | URS036*3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907615 | Ground Loop | WaterFurnace | URS036*3*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907616 | Ground Loop | WaterFurnace | URS036*4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907617 | Ground Loop | WaterFurnace | URS036*4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907618 | Ground Loop | WaterFurnace | URS036*4*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214823446 | Ground Loop | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | Yes
217903460 | Ground Loop | WaterFurnace | V5R060*D4**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903461 | Ground Loop | WaterFurnace | V5R060*D4**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903462 | Ground Loop | WaterFurnace | V5R060*D4**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903463 | Ground Loop | WaterFurnace | V5R072*D4**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903464 | Ground Loop | WaterFurnace | V5R072*D4**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903465 | Ground Loop | WaterFurnace | V5R072*D4**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903466 | Ground Loop | WaterFurnace | V5R096*T4**5* |  | 88100 | 18 | 69900 | 3.8 | 7.3417 | No
217903467 | Ground Loop | WaterFurnace | V5R120*T4**5* |  | 119400 | 17.7 | 92000 | 3.8 | 9.95 | No
217903468 | Ground Loop | WaterFurnace | V5R036*D0**1* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903469 | Ground Loop | WaterFurnace | V5R036*D0**4* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903470 | Ground Loop | WaterFurnace | V5R036*D0**5* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903471 | Ground Loop | WaterFurnace | V5R036*D3**1* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903472 | Ground Loop | WaterFurnace | V5R036*D3**4* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903473 | Ground Loop | WaterFurnace | V5R036*D3**5* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903474 | Ground Loop | WaterFurnace | V5R048*D0**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903475 | Ground Loop | WaterFurnace | V5R048*D0**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903476 | Ground Loop | WaterFurnace | V5R048*D0**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903477 | Ground Loop | WaterFurnace | V5R048*D3**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903478 | Ground Loop | WaterFurnace | V5R048*D3**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903479 | Ground Loop | WaterFurnace | V5R048*D3**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903480 | Ground Loop | WaterFurnace | V5R060*D0**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903481 | Ground Loop | WaterFurnace | V5R060*D0**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903482 | Ground Loop | WaterFurnace | V5R060*D0**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903483 | Ground Loop | WaterFurnace | V5R060*D3**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903484 | Ground Loop | WaterFurnace | V5R060*D3**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903485 | Ground Loop | WaterFurnace | V5R060*D3**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903486 | Ground Loop | WaterFurnace | V5R072*D0**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903487 | Ground Loop | WaterFurnace | V5R072*D0**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
209180330 | Ground Loop | HYDROTECH | WSV6018B* |  | 18000 | 17.2 | 13500 | 3.6 | 1.5 | Yes
209180331 | Ground Loop | HYDROTECH | WSV6036B* |  | 37000 | 18 | 28000 | 3.6 | 3.0833 | Yes
209180332 | Ground Loop | HYDROTECH | WSV6042B* |  | 42000 | 18.5 | 30000 | 3.6 | 3.5 | Yes
209180334 | Ground Loop | HYDROTECH | WSV6048B* |  | 51000 | 17.7 | 37000 | 3.6 | 4.25 | Yes
209180335 | Ground Loop | AE Air | WSV6018B* |  | 18000 | 17.2 | 13500 | 3.6 | 1.5 | Yes
209180336 | Ground Loop | AE Air | WSV6036B* |  | 37000 | 18 | 28000 | 3.6 | 3.0833 | Yes
209180337 | Ground Loop | AE Air | WSV6042B* |  | 42000 | 18.5 | 30000 | 3.6 | 3.5 | Yes
209180338 | Ground Loop | AE Air | WSV6048B* |  | 51000 | 17.7 | 37000 | 3.6 | 4.25 | Yes
209323637 | Ground Loop | HYDROTECH | WSV6009B* |  | 10000 | 19 | 7500 | 3.7 | 0.83333 | Yes
209323638 | Ground Loop | AE Air | WSV6009B* |  | 10000 | 19 | 7500 | 3.7 | 0.83333 | Yes
209945912 | Ground Loop | WaterFurnace | NBV/NBH009**0*6 |  | 9800 | 17.1 | 7800 | 3.6 | 0.81667 | No
209945913 | Ground Loop | WaterFurnace | NBV/NBH009**2*6 |  | 9800 | 17.1 | 7800 | 3.6 | 0.81667 | No
209945914 | Ground Loop | WaterFurnace | NBV/NBH012**0*6 |  | 12200 | 17.1 | 9500 | 3.6 | 1.0167 | No
209945915 | Ground Loop | WaterFurnace | NBV/NBH012**2*6 |  | 12200 | 17.1 | 9500 | 3.6 | 1.0167 | No
210286836 | Ground Loop | Energy Catalyst | DHHP036TV | DHHP036TV | 37500 | 17 | 29300 | 4.3 | 3.125 | Yes
210286837 | Ground Loop | Energy Catalyst | DHHP036TH | DHHP036TH | 37500 | 17 | 29300 | 4.3 | 3.125 | Yes
215400087 | Ground Loop | DAIKIN | WSMV019E1*G/J*T |  | 20600 | 20.26 | 15100 | 3.69 | 1.7167 | No
215400089 | Ground Loop | DAIKIN | WSMV019E1*G/J*C |  | 20600 | 20.26 | 15100 | 3.69 | 1.7167 | No
215400092 | Ground Loop | DAIKIN | WSMV024E1*G/J*P |  | 25500 | 19.55 | 18900 | 3.72 | 2.125 | No
215400093 | Ground Loop | DAIKIN | WSMV024F3*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
215400096 | Ground Loop | DAIKIN | WSMV024E1*G/J*T |  | 25600 | 20.91 | 18600 | 3.87 | 2.1333 | No
215400097 | Ground Loop | DAIKIN | WSMV024F3*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215400100 | Ground Loop | DAIKIN | WSMV024E1*G/J*C |  | 25600 | 20.91 | 18600 | 3.87 | 2.1333 | No
215400101 | Ground Loop | DAIKIN | WSMV024F3*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
217351904 | Ground Loop | KEEPRITE | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351905 | Ground Loop | KEEPRITE | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351906 | Ground Loop | KEEPRITE | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351907 | Ground Loop | KEEPRITE | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351909 | Ground Loop | KEEPRITE | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351910 | Ground Loop | KEEPRITE | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351911 | Ground Loop | KEEPRITE | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351919 | Ground Loop | TEMPSTAR | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351920 | Ground Loop | TEMPSTAR | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351923 | Ground Loop | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351924 | Ground Loop | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351925 | Ground Loop | TEMPSTAR | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351927 | Ground Loop | TEMPSTAR | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351928 | Ground Loop | TEMPSTAR | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351930 | Ground Loop | TEMPSTAR | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351931 | Ground Loop | TEMPSTAR | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351932 | Ground Loop | TEMPSTAR | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351933 | Ground Loop | TEMPSTAR | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351934 | Ground Loop | TEMPSTAR | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351936 | Ground Loop | TEMPSTAR | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351937 | Ground Loop | TEMPSTAR | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351938 | Ground Loop | TEMPSTAR | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
8738031 | Ground Loop | GEOCOMFORT | GVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
8738032 | Ground Loop | HYDRON MODULE | HVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
8738033 | Ground Loop | TETCO | TVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
8738034 | Ground Loop | GEOCOMFORT | GVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738035 | Ground Loop | HYDRON MODULE | HVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738036 | Ground Loop | TETCO | TVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738037 | Ground Loop | GEOCOMFORT | GVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738038 | Ground Loop | HYDRON MODULE | HVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738039 | Ground Loop | TETCO | TVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738051 | Ground Loop | GEOCOMFORT | GVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | Yes
8738052 | Ground Loop | HYDRON MODULE | HVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | Yes
8738053 | Ground Loop | TETCO | TVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | Yes
8738054 | Ground Loop | GEOCOMFORT | GVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738055 | Ground Loop | HYDRON MODULE | HVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738056 | Ground Loop | TETCO | TVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738057 | Ground Loop | GEOCOMFORT | GVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738058 | Ground Loop | HYDRON MODULE | HVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738059 | Ground Loop | TETCO | TVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738060 | Ground Loop | GEOCOMFORT | GVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738061 | Ground Loop | HYDRON MODULE | HVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738062 | Ground Loop | TETCO | TVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738067 | Ground Loop | GEOCOMFORT | GVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | Yes
8738068 | Ground Loop | HYDRON MODULE | HVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | Yes
8738069 | Ground Loop | TETCO | TVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | Yes
203337768 | Ground Loop | BOSCH-GEO | CE025-1VT/HZ/CF*-*****B |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
203337769 | Ground Loop | BOSCH | CE025-1VT/HZ/CF*-*****B |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337770 | Ground Loop | CARRIER | GP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
203337771 | Ground Loop | BRYANT | GP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337772 | Ground Loop | HEIL | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
203337773 | Ground Loop | ARCOAIRE | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337774 | Ground Loop | KEEPRITE | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337775 | Ground Loop | TEMPSTAR | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337776 | Ground Loop | COMFORTMAKER | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337777 | Ground Loop | DAY & NIGHT | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203343532 | Ground Loop | BOSCH-GEO | SM024-1CS*******A | SM024-1AV/AH*-*****A | 26200 | 17 | 17700 | 3.75 | 2.1833 | Yes
203343535 | Ground Loop | BOSCH | SM024-1CS*******A | SM024-1AV/AH*-*****A | 26200 | 17 | 17700 | 3.75 | 2.1833 | Yes
213502573 | Ground Loop | DAIKIN | WSCH042E1*G/J*P |  | 39900 | 17.5 | 32500 | 3.7 | 3.325 | No
213502574 | Ground Loop | DAIKIN | WSCH042E1*G/J*T |  | 40800 | 19.4 | 31600 | 3.8 | 3.4 | No
213502575 | Ground Loop | DAIKIN | WSCH042E1*G/J*C |  | 40800 | 19.4 | 31600 | 3.8 | 3.4 | No
213502579 | Ground Loop | DAIKIN | WSCH048E1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
213502580 | Ground Loop | DAIKIN | WSCH048E1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
213502581 | Ground Loop | DAIKIN | WSCH048E1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
213614501 | Ground Loop | DAIKIN | WSCH015A1*G/J*T |  | 15600 | 19 | 11900 | 3.6 | 1.3 | No
213614502 | Ground Loop | DAIKIN | WSCH015A1*G/J*C |  | 15600 | 19 | 11900 | 3.6 | 1.3 | No
213614506 | Ground Loop | DAIKIN | WSCH015J1*G/J*P |  | 15500 | 18 | 11900 | 3.6 | 1.2917 | No
213614507 | Ground Loop | DAIKIN | WSCH015J1*G/J*T |  | 15500 | 18.7 | 12000 | 3.8 | 1.2917 | No
213614508 | Ground Loop | DAIKIN | WSCH015J1*G/J*C |  | 15500 | 18.7 | 12000 | 3.8 | 1.2917 | No
217754475 | Ground Loop | DAIKIN | WSTH024E1*H*C |  | 25100 | 19.92 | 17200 | 3.92 | 2.0917 | No
217754476 | Ground Loop | DAIKIN | WSTH024F1*H*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917 | No
217754479 | Ground Loop | DAIKIN | WSTH030E1*H*C |  | 32700 | 19.69 | 20600 | 3.75 | 2.725 | No
217754480 | Ground Loop | DAIKIN | WSTH030F1*H*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725 | No
217754483 | Ground Loop | DAIKIN | WSTH036E1*H*C |  | 38700 | 20.64 | 25900 | 3.75 | 3.225 | No
217754484 | Ground Loop | DAIKIN | WSTH036F1*H*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225 | No
217754487 | Ground Loop | DAIKIN | WSTH042E1*H*C |  | 45900 | 20.06 | 28400 | 3.7 | 3.825 | No
217754488 | Ground Loop | DAIKIN | WSTH042F1*H*C |  | 45900 | 19.66 | 28400 | 3.63 | 3.825 | No
217754491 | Ground Loop | DAIKIN | WSTH048E1*H*C |  | 49300 | 19.59 | 36300 | 3.87 | 4.1083 | No
217754492 | Ground Loop | DAIKIN | WSTH048F1*H*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083 | No
217754495 | Ground Loop | DAIKIN | WSTH060E1*H*C |  | 61600 | 19 | 44200 | 3.7 | 5.1333 | No
217754496 | Ground Loop | DAIKIN | WSTH060F1*H*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333 | No
213087558 | Ground Loop | WaterFurnace | NDS049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
213087559 | Ground Loop | WaterFurnace | NDS049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
213087562 | Ground Loop | WaterFurnace | NDS064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
213087563 | Ground Loop | WaterFurnace | NDS064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
213154439 | Ground Loop | GeoSmart Energy | GTS026*1******K | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
213154440 | Ground Loop | GeoSmart Energy | GTS026*1******K | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
213154441 | Ground Loop | GeoSmart Energy | GTS049*1******K | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
213154442 | Ground Loop | GeoSmart Energy | GTS049*1******K | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
213154445 | Ground Loop | GeoSmart Energy | GTS064*1******K | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
213154446 | Ground Loop | GeoSmart Energy | GTS064*1******K | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
213154447 | Ground Loop | GeoSmart Energy | GTS038*1******K | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
213154448 | Ground Loop | GeoSmart Energy | GTS038*1******K | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
213154454 | Ground Loop | GeoSmart Energy | GTZ026*1******K | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
213154455 | Ground Loop | GeoSmart Energy | GTZ026*1******K | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
213154456 | Ground Loop | GeoSmart Energy | GTZ038*1******K | SAH036* | 36000 | 19 | 27900 | 4 | 3 | Yes
213154457 | Ground Loop | GeoSmart Energy | GTZ038*1******K | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
213154458 | Ground Loop | GeoSmart Energy | GTZ049*1******K | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
213154459 | Ground Loop | GeoSmart Energy | GTZ049*1******K | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
213154460 | Ground Loop | GeoSmart Energy | GTZ064*1******K | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
213154461 | Ground Loop | GeoSmart Energy | GTZ064*1******K | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
213154465 | Ground Loop | GeoSmart Energy | GS018**1*1********L |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
213154466 | Ground Loop | GeoSmart Energy | GS022**1*1********L |  | 19200 | 18.7 | 15000 | 4 | 1.6 | Yes
213154467 | Ground Loop | GeoSmart Energy | GS030**1*1********L |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
213154468 | Ground Loop | GeoSmart Energy | GS036**1*1********L |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | Yes
213154469 | Ground Loop | GeoSmart Energy | GS042**1*1********L |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
213154470 | Ground Loop | GeoSmart Energy | GS048**1*1********L |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
213154471 | Ground Loop | GeoSmart Energy | GS060**1*1********L |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
213154472 | Ground Loop | GeoSmart Energy | GS070**1*1********L |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
213154473 | Ground Loop | GeoSmart Energy | GT026**1*1********L |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
202146954 | Ground Loop | HYDRON MODULE | HZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146955 | Ground Loop | HYDRON MODULE | HZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146956 | Ground Loop | HYDRON MODULE | HZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146957 | Ground Loop | HYDRON MODULE | HZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | Yes
202146958 | Ground Loop | HYDRON MODULE | HZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146959 | Ground Loop | HYDRON MODULE | HZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146960 | Ground Loop | HYDRON MODULE | HZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146961 | Ground Loop | TETCO | TZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | Yes
202146962 | Ground Loop | TETCO | TZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146963 | Ground Loop | TETCO | TZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146964 | Ground Loop | TETCO | TZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146965 | Ground Loop | TETCO | TZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146966 | Ground Loop | TETCO | TZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | Yes
202146967 | Ground Loop | TETCO | TZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146968 | Ground Loop | TETCO | TZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146969 | Ground Loop | TETCO | TZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146970 | Ground Loop | GEOCOMFORT | GZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | Yes
202146971 | Ground Loop | GEOCOMFORT | GZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146972 | Ground Loop | GEOCOMFORT | GZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146973 | Ground Loop | GEOCOMFORT | GZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146974 | Ground Loop | GEOCOMFORT | GZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146975 | Ground Loop | GEOCOMFORT | GZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | Yes
202146976 | Ground Loop | GEOCOMFORT | GZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202146977 | Ground Loop | HYDRON MODULE | HZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | Yes
202146978 | Ground Loop | HYDRON MODULE | HZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146979 | Ground Loop | HYDRON MODULE | HZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146980 | Ground Loop | HYDRON MODULE | HZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146981 | Ground Loop | HYDRON MODULE | HZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146982 | Ground Loop | HYDRON MODULE | HZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | Yes
202146983 | Ground Loop | HYDRON MODULE | HZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202146984 | Ground Loop | TETCO | TZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | Yes
204835632 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
204835633 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205129920 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
205129921 | Ground Loop | GEOSTAR | 103J036**1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
205145424 | Ground Loop | GEOCOMFORT | GVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
205145425 | Ground Loop | GEOCOMFORT | GVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145426 | Ground Loop | GEOCOMFORT | GVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145427 | Ground Loop | HYDRON MODULE | HVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
205145428 | Ground Loop | HYDRON MODULE | HVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145429 | Ground Loop | HYDRON MODULE | HVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145430 | Ground Loop | TETCO | TVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
205145431 | Ground Loop | TETCO | TVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145432 | Ground Loop | TETCO | TVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145433 | Ground Loop | GEOCOMFORT | GVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
205145434 | Ground Loop | GEOCOMFORT | GVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145435 | Ground Loop | GEOCOMFORT | GVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145436 | Ground Loop | HYDRON MODULE | HVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
205145437 | Ground Loop | HYDRON MODULE | HVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145438 | Ground Loop | HYDRON MODULE | HVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145439 | Ground Loop | TETCO | TVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145527 | Ground Loop | GEOCOMFORT | GVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145528 | Ground Loop | HYDRON MODULE | HVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145529 | Ground Loop | TETCO | TVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145530 | Ground Loop | TETCO | TVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
205145531 | Ground Loop | TETCO | TVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
216625471 | Ground Loop | GEOSTAR | G5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625472 | Ground Loop | GEOSTAR | G5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625473 | Ground Loop | GEOSTAR | G5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625474 | Ground Loop | GEOSTAR | G5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625475 | Ground Loop | GEOSTAR | G5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625476 | Ground Loop | GEOSTAR | G5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625477 | Ground Loop | GEOSTAR | G5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625478 | Ground Loop | GEOSTAR | G5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625479 | Ground Loop | GEOSTAR | G5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625480 | Ground Loop | GEOSTAR | G5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625481 | Ground Loop | GEOSTAR | G5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625482 | Ground Loop | GEOSTAR | G5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625483 | Ground Loop | GEOSTAR | G5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625484 | Ground Loop | GEOSTAR | G5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625485 | Ground Loop | GEOSTAR | G5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625486 | Ground Loop | GEOSTAR | G5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625487 | Ground Loop | GEOSTAR | G5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625488 | Ground Loop | GEOSTAR | G5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625489 | Ground Loop | GEOSTAR | G5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625490 | Ground Loop | GEOSTAR | G5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625491 | Ground Loop | GEOSTAR | G5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625492 | Ground Loop | GEOSTAR | G5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625493 | Ground Loop | GEOSTAR | G5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625494 | Ground Loop | GEOSTAR | G5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625495 | Ground Loop | GEOSTAR | G5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625496 | Ground Loop | GEOSTAR | G5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625497 | Ground Loop | GEOSTAR | G5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625498 | Ground Loop | GEOSTAR | G5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625499 | Ground Loop | GEOSTAR | G5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625500 | Ground Loop | GEOSTAR | G5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625501 | Ground Loop | GEOSTAR | G5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625502 | Ground Loop | GEOSTAR | G5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625503 | Ground Loop | GEOSTAR | G5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625504 | Ground Loop | GEOSTAR | G5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625505 | Ground Loop | GEOSTAR | G5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625506 | Ground Loop | GEOSTAR | G5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625507 | Ground Loop | GEOSTAR | G5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
9910702 | Ground Loop | GEOCOMFORT | GZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910703 | Ground Loop | HYDRON MODULE | HZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910704 | Ground Loop | TETCO | TZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910708 | Ground Loop | GEOCOMFORT | GZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | Yes
9910709 | Ground Loop | HYDRON MODULE | HZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | Yes
9910710 | Ground Loop | TETCO | TZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | Yes
9910711 | Ground Loop | GEOCOMFORT | GZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910712 | Ground Loop | HYDRON MODULE | HZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910713 | Ground Loop | TETCO | TZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910714 | Ground Loop | GEOCOMFORT | GZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910715 | Ground Loop | HYDRON MODULE | HZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910716 | Ground Loop | TETCO | TZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910717 | Ground Loop | GEOCOMFORT | GZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910718 | Ground Loop | HYDRON MODULE | HZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910719 | Ground Loop | TETCO | TZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910752 | Ground Loop | GEOCOMFORT | GZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | Yes
9910753 | Ground Loop | HYDRON MODULE | HZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | Yes
9910754 | Ground Loop | TETCO | TZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | Yes
9910755 | Ground Loop | GEOCOMFORT | GZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910756 | Ground Loop | HYDRON MODULE | HZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910757 | Ground Loop | TETCO | TZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910758 | Ground Loop | GEOCOMFORT | GZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910759 | Ground Loop | HYDRON MODULE | HZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910760 | Ground Loop | TETCO | TZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910764 | Ground Loop | GEOCOMFORT | GZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | Yes
9910765 | Ground Loop | HYDRON MODULE | HZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | Yes
9910766 | Ground Loop | TETCO | TZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | Yes
9910767 | Ground Loop | GEOCOMFORT | GZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910768 | Ground Loop | HYDRON MODULE | HZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910769 | Ground Loop | TETCO | TZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910770 | Ground Loop | GEOCOMFORT | GZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910771 | Ground Loop | HYDRON MODULE | HZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910772 | Ground Loop | TETCO | TZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910773 | Ground Loop | GEOCOMFORT | GZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910774 | Ground Loop | HYDRON MODULE | HZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910775 | Ground Loop | TETCO | TZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910780 | Ground Loop | GEOCOMFORT | GZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | Yes
9910781 | Ground Loop | HYDRON MODULE | HZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | Yes
9910782 | Ground Loop | TETCO | TZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | Yes
9910783 | Ground Loop | GEOCOMFORT | GZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910784 | Ground Loop | HYDRON MODULE | HZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910785 | Ground Loop | TETCO | TZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910786 | Ground Loop | GEOCOMFORT | GZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910787 | Ground Loop | HYDRON MODULE | HZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910788 | Ground Loop | TETCO | TZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
203495469 | Ground Loop | GEOSTAR | 101/102J049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
203495470 | Ground Loop | GEOSTAR | 103J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
203495474 | Ground Loop | GEOSTAR | 103J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
207083919 | Ground Loop | CARRIER | 50PCV024J/K*N/J5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083921 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083923 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083925 | Ground Loop | CARRIER | 50PCV024J/K*C/A6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083927 | Ground Loop | CARRIER | 50PCV024J/K*N/J6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083961 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083965 | Ground Loop | CARRIER | 50PCV036J/K*C/A3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083969 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083973 | Ground Loop | CARRIER | 50PCV036J/K*C/A4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
215310891 | Ground Loop | GEOSTAR | G7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083 | Yes
215310892 | Ground Loop | GEOSTAR | G7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833 | Yes
215310893 | Ground Loop | GEOSTAR | G7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75 | Yes
215310990 | Ground Loop | GeoSmart Energy | S7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083 | Yes
215310991 | Ground Loop | GeoSmart Energy | S7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833 | Yes
215310992 | Ground Loop | GeoSmart Energy | S7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75 | Yes
216802003 | Ground Loop | CARRIER | 50WT*036***5*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216802004 | Ground Loop | CARRIER | 50WT*036***5*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216802005 | Ground Loop | CARRIER | 50WT*036***6*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216802006 | Ground Loop | CARRIER | 50WT*036***6*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216802007 | Ground Loop | CARRIER | 50WT*048***3*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216802008 | Ground Loop | CARRIER | 50WT*048***3*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216802009 | Ground Loop | CARRIER | 50WT*048***5*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216802010 | Ground Loop | CARRIER | 50WT*048***5*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216802011 | Ground Loop | CARRIER | 50WT*048***6*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216802012 | Ground Loop | CARRIER | 50WT*048***6*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216802013 | Ground Loop | CARRIER | 50WT*060***3*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216802014 | Ground Loop | CARRIER | 50WT*060***3*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216802015 | Ground Loop | CARRIER | 50WT*060***5*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216802016 | Ground Loop | CARRIER | 50WT*060***5*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216802017 | Ground Loop | CARRIER | 50WT*060***6*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216802018 | Ground Loop | CARRIER | 50WT*060***6*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216802019 | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**3*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216802021 | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**3*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216802023 | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**5*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216802025 | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**5*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
215866226 | Ground Loop | ClimateMaster | SMS15A*L |  | 14800 | 17.5 | 11000 | 3.6 | 1.2333 | No
215866227 | Ground Loop | ClimateMaster | SMT15A*L |  | 15400 | 18.8 | 11000 | 3.7 | 1.2833 | No
215866229 | Ground Loop | ClimateMaster | SMT18A*L |  | 18900 | 17.8 | 13500 | 3.6 | 1.575 | No
215866231 | Ground Loop | ClimateMaster | SMT24A*L |  | 25900 | 20.5 | 18000 | 3.7 | 2.1583 | No
215866233 | Ground Loop | ClimateMaster | SMT30A*L |  | 30000 | 19 | 22300 | 3.7 | 2.5 | No
215866540 | Ground Loop | DAIKIN | WSTH048E1*G/J*C |  | 49300 | 19.59 | 36300 | 3.87 | 4.1083 | No
215866541 | Ground Loop | DAIKIN | WSTH048F3*G/J*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083 | No
215866542 | Ground Loop | DAIKIN | WSTV024E1*G/J*C |  | 22400 | 17.99 | 17200 | 3.98 | 1.8667 | No
215866543 | Ground Loop | DAIKIN | WSTV024F3*G/J*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667 | No
215866544 | Ground Loop | DAIKIN | WSTV048E1*G/J*C |  | 52400 | 20.17 | 35200 | 3.9 | 4.3667 | No
215866545 | Ground Loop | DAIKIN | WSTV048F3*G/J*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667 | No
217754758 | Ground Loop | DAIKIN | WSCH048F1*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
217754759 | Ground Loop | DAIKIN | WSCH048K1*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
217754762 | Ground Loop | DAIKIN | WSCH048F1*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
217754763 | Ground Loop | DAIKIN | WSCH048K1*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
10318061 | Ground Loop | GEOSTAR | 103H070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10318062 | Ground Loop | GeoSmart Energy | GSZ070*1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10346237 | Ground Loop | GEOCOMFORT | GZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
5699656 | Ground Loop | TRANE | VSHE0602 |  | 63200 | 17 | 50400 | 3.8 | 5.2667 | No
5699657 | Ground Loop | TRANE | VSHE0604 |  | 63200 | 17 | 50400 | 3.8 | 5.2667 | No
6501887 | Ground Loop | GEOSTAR | GBV/GBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
6501888 | Ground Loop | GEOSTAR | GBV/GBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
6501889 | Ground Loop | GEOSTAR | GBV/GBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
6501890 | Ground Loop | GEOSTAR | GBV/GBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
6501891 | Ground Loop | GEOSTAR | GBV/GBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
6501892 | Ground Loop | GEOSTAR | GBV/GBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
6501894 | Ground Loop | GEOSTAR | GBV/GBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
6501895 | Ground Loop | GEOSTAR | GBV/GBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
6501897 | Ground Loop | GEOSTAR | GBV/GBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
202434652 | Ground Loop | CARRIER | 50PCV024J/K*C3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434653 | Ground Loop | CARRIER | 50PCV024J/K*C5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434654 | Ground Loop | CARRIER | 50PCV024J/K*C6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434655 | Ground Loop | CARRIER | 50PCV024J/K*C4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434660 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434661 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434662 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434663 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434668 | Ground Loop | CARRIER | 50PCV024J/K*N3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434669 | Ground Loop | CARRIER | 50PCV024J/K*N5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434670 | Ground Loop | CARRIER | 50PCV024J/K*N6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434671 | Ground Loop | CARRIER | 50PCV024J/K*N4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434676 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434677 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434678 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434679 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
206194171 | Ground Loop | Johnson Controls | JSH/V/D030C*K B |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333 | Yes
206194172 | Ground Loop | SKYMARK | JSH/V/D030C*K C |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333 | Yes
206194173 | Ground Loop | Johnson Controls | JSH/V/D048C*K B |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167 | No
206194174 | Ground Loop | SKYMARK | JSH/V/D048C*K C |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167 | No
206194175 | Ground Loop | Johnson Controls | JSH/V/D060C*K B |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667 | No
206194176 | Ground Loop | SKYMARK | JSH/V/D060C*K C |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667 | No
216801990 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**4*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801991 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**5*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801992 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**5*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801993 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**5*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801994 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**5*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801995 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**6*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801996 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**6*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801997 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**6*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801998 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**6*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801999 | Ground Loop | CARRIER | 50WT*036***3*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216802000 | Ground Loop | CARRIER | 50WT*036***3*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216802001 | Ground Loop | CARRIER | 50WT*036***4*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216802002 | Ground Loop | CARRIER | 50WT*036***4*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
207083897 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083899 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083901 | Ground Loop | CARRIER | 50PCV024J/K*C/A3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083903 | Ground Loop | CARRIER | 50PCV024J/K*N/J3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083905 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083907 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083909 | Ground Loop | CARRIER | 50PCV024J/K*C/A4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083911 | Ground Loop | CARRIER | 50PCV024J/K*N/J4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083913 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083915 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083917 | Ground Loop | CARRIER | 50PCV024J/K*C/A5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
215837703 | Ground Loop | DAIKIN | WSMH030F3*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
215837704 | Ground Loop | DAIKIN | WSMH030J1*G/J*T |  | 29500 | 19.36 | 21900 | 3.76 | 2.4583 | No
215837705 | Ground Loop | DAIKIN | WSMH030K3*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
215837711 | Ground Loop | DAIKIN | WSMH030F3*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
215837712 | Ground Loop | DAIKIN | WSMH030J1*G/J*C |  | 29500 | 19.36 | 21900 | 3.76 | 2.4583 | No
215837714 | Ground Loop | DAIKIN | WSMH030K3*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
215837719 | Ground Loop | DAIKIN | WSMH036F3*G/J*P |  | 37800 | 18.18 | 30700 | 3.79 | 3.15 | No
215837721 | Ground Loop | DAIKIN | WSMH036J1*G/J*P |  | 37800 | 17.73 | 30700 | 3.8 | 3.15 | No
10316662 | Ground Loop | GEOSTAR | 104H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316663 | Ground Loop | GeoSmart Energy | GTS064*1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316664 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316666 | Ground Loop | GEOSTAR | 104H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316667 | Ground Loop | GeoSmart Energy | GTS064*1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10318010 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10318016 | Ground Loop | GeoSmart Energy | GSZ022*1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10318017 | Ground Loop | GEOSTAR | 103H022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
10318018 | Ground Loop | GeoSmart Energy | GSZ022*1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
10318019 | Ground Loop | GEOSTAR | 103H022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10318020 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10318021 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10318022 | Ground Loop | GEOSTAR | 103H030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
10318023 | Ground Loop | GeoSmart Energy | GSZ030*1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10318024 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10318025 | Ground Loop | GeoSmart Energy | GSZ030*1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
10318026 | Ground Loop | GEOSTAR | 103H030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10318045 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10318046 | Ground Loop | GeoSmart Energy | GSZ048*1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10318047 | Ground Loop | GEOSTAR | 103H048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
10318048 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10318049 | Ground Loop | GeoSmart Energy | GSZ048*1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10318050 | Ground Loop | GEOSTAR | 103H048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
10318051 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10318052 | Ground Loop | GeoSmart Energy | GSZ060*1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10318054 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10318055 | Ground Loop | GeoSmart Energy | GSZ060*1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
10318056 | Ground Loop | GEOSTAR | 103H060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
10318060 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
216802027 | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**6*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216802029 | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**6*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216979809 | Ground Loop | CARRIER | GCA24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979810 | Ground Loop | BRYANT | GCA24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979811 | Ground Loop | CARRIER | GCA24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979812 | Ground Loop | BRYANT | GCA24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979813 | Ground Loop | CARRIER | GCA24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979814 | Ground Loop | BRYANT | GCA24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979815 | Ground Loop | CARRIER | GCA24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979816 | Ground Loop | BRYANT | GCA24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979817 | Ground Loop | CARRIER | GCA36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979818 | Ground Loop | BRYANT | GCA36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979819 | Ground Loop | CARRIER | GCA36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216979820 | Ground Loop | BRYANT | GCA36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979821 | Ground Loop | CARRIER | GCA48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979822 | Ground Loop | BRYANT | GCA48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979823 | Ground Loop | CARRIER | GCA48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979824 | Ground Loop | BRYANT | GCA48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979825 | Ground Loop | CARRIER | GCA60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979826 | Ground Loop | BRYANT | GCA60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979827 | Ground Loop | CARRIER | GCA60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979828 | Ground Loop | BRYANT | GCA60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979837 | Ground Loop | HEIL | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979838 | Ground Loop | ARCOAIRE | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979839 | Ground Loop | KEEPRITE | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979840 | Ground Loop | TEMPSTAR | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979841 | Ground Loop | COMFORTMAKER | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979842 | Ground Loop | DAY & NIGHT | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979843 | Ground Loop | HEIL | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979844 | Ground Loop | ARCOAIRE | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
7419527 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419618 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419733 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419797 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7421327 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421397 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421438 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421969 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421970 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421971 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
7421972 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421973 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421974 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
7421975 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421976 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421977 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
7421980 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421989 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421999 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
7422020 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422043 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422058 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422072 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422083 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422093 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422134 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422147 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422187 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422202 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422225 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422234 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422268 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422280 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422290 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422299 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422309 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
206900571 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900572 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900573 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900574 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900575 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900576 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900577 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900578 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900579 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206438720 | Ground Loop | BOSCH | EP009-2HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438721 | Ground Loop | BOSCH | EP012-0HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438723 | Ground Loop | BOSCH | EP012-0VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438725 | Ground Loop | BOSCH | EP012-1HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438727 | Ground Loop | BOSCH | EP012-1VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438729 | Ground Loop | BOSCH | EP012-2HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438731 | Ground Loop | BOSCH | EP012-2VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438733 | Ground Loop | BOSCH | EP015-2HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438734 | Ground Loop | BOSCH | EP030-1HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438735 | Ground Loop | BOSCH | EP030-2HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438736 | Ground Loop | BOSCH | EP030-3HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438737 | Ground Loop | BOSCH | EP030-4HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438738 | Ground Loop | BOSCH | EP060-3HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438739 | Ground Loop | BOSCH | EP060-4HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438740 | Ground Loop | BOSCH | EP070-3HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438741 | Ground Loop | BOSCH | EP070-4HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438761 | Ground Loop | BOSCH | EP012-1HZ/VT*-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438762 | Ground Loop | BOSCH | EP015-1HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438763 | Ground Loop | BOSCH | EP060-1HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438764 | Ground Loop | BOSCH | EP070-1HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
9100370 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100371 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100373 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100374 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100377 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100378 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100380 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100381 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100383 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100384 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100390 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100391 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100393 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100394 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100396 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100397 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100400 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100401 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100403 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
217967038 | Ground Loop | TRANE | VSHK0244 |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167 | No
217967039 | Ground Loop | TRANE | VSVK0244 |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917 | No
217967040 | Ground Loop | TRANE | VSHK0334 |  | 33300 | 18.1 | 27700 | 4.1 | 2.775 | No
217967041 | Ground Loop | TRANE | VSVK0334 |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417 | No
217967042 | Ground Loop | TRANE | VSHK0424 |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167 | No
217967043 | Ground Loop | TRANE | VSVK0424 |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417 | No
217967044 | Ground Loop | TRANE | VSHK0504 |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417 | No
217967045 | Ground Loop | TRANE | VSVK0504 |  | 50400 | 19.3 | 40400 | 4.3 | 4.2 | No
217967046 | Ground Loop | TRANE | VSHK0604 |  | 61900 | 17 | 51400 | 3.9 | 5.1583 | No
217967047 | Ground Loop | TRANE | VSVK0604 |  | 61200 | 17.9 | 49500 | 4.1 | 5.1 | No
201864513 | Ground Loop | GEOCOMFORT | GZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864514 | Ground Loop | HYDRON MODULE | HZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864515 | Ground Loop | TETCO | TZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864519 | Ground Loop | GEOCOMFORT | GZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864521 | Ground Loop | HYDRON MODULE | HZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864523 | Ground Loop | TETCO | TZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
214841657 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
214841658 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
214841660 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
214841662 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
202350500 | Ground Loop | AAON, Inc. | M2-014-3-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083 | No
202350501 | Ground Loop | AAON, Inc. | M2-014-3-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725 | No
202350502 | Ground Loop | AAON, Inc. | M2-014-4-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083 | No
202350503 | Ground Loop | AAON, Inc. | M2-014-4-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725 | No
205767566 | Ground Loop | ClimateMaster | TSL15 A |  | 15400 | 17.7 | 11500 | 3.6 | 1.2833 | No
205767567 | Ground Loop | ClimateMaster | TSL15 B |  | 15400 | 19.2 | 11000 | 3.7 | 1.2833 | No
205767571 | Ground Loop | ClimateMaster | TSL24 B |  | 26500 | 19.4 | 18500 | 3.6 | 2.2083 | No
205767573 | Ground Loop | ClimateMaster | TSL30 B |  | 29500 | 18.4 | 21000 | 3.7 | 2.4583 | No
205767582 | Ground Loop | ClimateMaster | TES/P038B | TAH038C | 37700 | 17.8 | 26200 | 3.8 | 3.1417 | Yes
205767586 | Ground Loop | ClimateMaster | TES/P026B | TAH026C***A* | 24700 | 17.7 | 18800 | 3.6 | 2.0583 | Yes
205767587 | Ground Loop | ClimateMaster | TES/P026B | TAH026C***B* | 25800 | 18.3 | 18700 | 3.8 | 2.15 | Yes
205767588 | Ground Loop | ClimateMaster | TES/P026B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
205767589 | Ground Loop | ClimateMaster | TES/P026B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
205767592 | Ground Loop | ClimateMaster | TRE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175 | No
205767606 | Ground Loop | ClimateMaster | VEV/H/D0930 |  | 24000 | 24.3 | 30000 | 3.6 | 2 | Yes
217351880 | Ground Loop | HEIL | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351882 | Ground Loop | HEIL | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351883 | Ground Loop | HEIL | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351884 | Ground Loop | HEIL | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
8735477 | Ground Loop | GEOCOMFORT | GVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | Yes
8735495 | Ground Loop | HYDRON MODULE | HVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | Yes
8735512 | Ground Loop | TETCO | TVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | Yes
8735538 | Ground Loop | GEOCOMFORT | GVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735552 | Ground Loop | HYDRON MODULE | HVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735567 | Ground Loop | TETCO | TVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735607 | Ground Loop | GEOCOMFORT | GVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735711 | Ground Loop | HYDRON MODULE | HVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735721 | Ground Loop | TETCO | TVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735754 | Ground Loop | GEOCOMFORT | GVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735767 | Ground Loop | HYDRON MODULE | HVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735778 | Ground Loop | TETCO | TVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735903 | Ground Loop | GEOCOMFORT | GVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | Yes
8735904 | Ground Loop | HYDRON MODULE | HVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | Yes
8735905 | Ground Loop | TETCO | TVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | Yes
8735906 | Ground Loop | GEOCOMFORT | GVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735907 | Ground Loop | HYDRON MODULE | HVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735908 | Ground Loop | TETCO | TVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735909 | Ground Loop | GEOCOMFORT | GVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735910 | Ground Loop | HYDRON MODULE | HVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735911 | Ground Loop | TETCO | TVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8737970 | Ground Loop | GEOCOMFORT | GVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | Yes
8737971 | Ground Loop | HYDRON MODULE | HVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | Yes
8737972 | Ground Loop | TETCO | TVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | Yes
8737973 | Ground Loop | GEOCOMFORT | GVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737974 | Ground Loop | HYDRON MODULE | HVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737975 | Ground Loop | TETCO | TVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737976 | Ground Loop | GEOCOMFORT | GVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737977 | Ground Loop | HYDRON MODULE | HVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737978 | Ground Loop | TETCO | TVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
202147041 | Ground Loop | GEOCOMFORT | GZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147042 | Ground Loop | GEOCOMFORT | GZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147047 | Ground Loop | HYDRON MODULE | HZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | Yes
202147048 | Ground Loop | HYDRON MODULE | HZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147049 | Ground Loop | HYDRON MODULE | HZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147054 | Ground Loop | TETCO | TZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | Yes
202147055 | Ground Loop | TETCO | TZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147056 | Ground Loop | TETCO | TZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147061 | Ground Loop | GEOCOMFORT | GZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | Yes
202147062 | Ground Loop | GEOCOMFORT | GZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147067 | Ground Loop | HYDRON MODULE | HZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | Yes
202147068 | Ground Loop | HYDRON MODULE | HZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147073 | Ground Loop | TETCO | TZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | Yes
202147074 | Ground Loop | TETCO | TZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147690 | Ground Loop | GEOCOMFORT | GZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202147691 | Ground Loop | HYDRON MODULE | HZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202147692 | Ground Loop | TETCO | TZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202147693 | Ground Loop | TETCO | TZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202147697 | Ground Loop | GEOCOMFORT | GZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | No
202147698 | Ground Loop | HYDRON MODULE | HZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | No
202147699 | Ground Loop | TETCO | TZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | No
202147700 | Ground Loop | GEOCOMFORT | GZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | No
202147701 | Ground Loop | HYDRON MODULE | HZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | No
202147702 | Ground Loop | TETCO | TZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | No
202147703 | Ground Loop | GEOCOMFORT | GZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147704 | Ground Loop | GEOCOMFORT | GZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147705 | Ground Loop | HYDRON MODULE | HZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147706 | Ground Loop | HYDRON MODULE | HZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147707 | Ground Loop | TETCO | TZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147708 | Ground Loop | TETCO | TZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202835053 | Ground Loop | BOSCH | SM036-1HZ*-*****C |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | Yes
202835056 | Ground Loop | BOSCH | SM024-1VT*-*****C |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417 | Yes
202835057 | Ground Loop | BOSCH | SM060-1VT*-*****C |  | 63900 | 18.6 | 48600 | 4 | 5.325 | Yes
202836307 | Ground Loop | BOSCH | SM036-1VT*-*****C |  | 40200 | 21 | 28200 | 4.3 | 3.35 | Yes
202836309 | Ground Loop | BOSCH | SM048-1VT*-*****C |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167 | Yes
202434716 | Ground Loop | CARRIER | 50PCV036J/K*C3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434717 | Ground Loop | CARRIER | 50PCV036J/K*C5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434718 | Ground Loop | CARRIER | 50PCV036J/K*C6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434719 | Ground Loop | CARRIER | 50PCV036J/K*C4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434724 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434725 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434726 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434727 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
206342117 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*3 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
206342118 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*4 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
206342119 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*5 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
206342120 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
206342121 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
206342122 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
206342123 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*3 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
206342124 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*5 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
206342125 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*4 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
206346929 | Ground Loop | DAIKIN | WVFW*024*K***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
206346930 | Ground Loop | DAIKIN | WVFW*030*K***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
215811946 | Ground Loop | HYDROTECH | WSV6009D* |  | 9800 | 19 | 6800 | 3.7 | 0.81667 | No
215811947 | Ground Loop | AE Air | WSV6009D* |  | 9800 | 19 | 6800 | 3.7 | 0.81667 | No
215811948 | Ground Loop | HYDROTECH | WSV6012D* |  | 12500 | 19 | 9000 | 3.6 | 1.0417 | No
215811950 | Ground Loop | AE Air | WSV6012D* |  | 12500 | 19 | 9000 | 3.6 | 1.0417 | No
215811951 | Ground Loop | HYDROTECH | WSV6018D* |  | 18000 | 17.2 | 13000 | 3.6 | 1.5 | No
215811952 | Ground Loop | AE Air | WSV6018D* |  | 18000 | 17.2 | 13000 | 3.6 | 1.5 | No
215811953 | Ground Loop | HYDROTECH | WSV6024D* |  | 23000 | 18 | 17500 | 3.6 | 1.9167 | No
215811954 | Ground Loop | AE Air | WSV6024D* |  | 23000 | 18 | 17500 | 3.6 | 1.9167 | No
215811955 | Ground Loop | HYDROTECH | WSV6030D* |  | 28000 | 17.5 | 19900 | 3.6 | 2.3333 | No
215811957 | Ground Loop | AE Air | WSV6030D* |  | 28000 | 17.5 | 19900 | 3.6 | 2.3333 | No
215811958 | Ground Loop | HYDROTECH | WSV6036D* |  | 37000 | 18 | 28000 | 3.6 | 3.0833 | No
215811959 | Ground Loop | AE Air | WSV6036D* |  | 37000 | 18 | 28000 | 3.6 | 3.0833 | No
215811960 | Ground Loop | HYDROTECH | WSV6042D* |  | 42000 | 18 | 30000 | 3.6 | 3.5 | No
215811961 | Ground Loop | AE Air | WSV6042D* |  | 42000 | 18 | 30000 | 3.6 | 3.5 | No
215815841 | Ground Loop | HYDROTECH | WSV6060D* |  | 63000 | 18 | 42500 | 3.6 | 5.25 | No
215815842 | Ground Loop | AE Air | WSV6060D* |  | 63000 | 18 | 42500 | 3.6 | 5.25 | No
215815843 | Ground Loop | HYDROTECH | WSV6072D* |  | 73000 | 17.9 | 52000 | 3.6 | 6.0833 | No
215815844 | Ground Loop | AE Air | WSV6072D* |  | 73000 | 17.9 | 52000 | 3.6 | 6.0833 | No
217735435 | Ground Loop | DAIKIN | WSTH024J1*H*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917 | No
217735437 | Ground Loop | DAIKIN | WSTH030J1*H*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725 | No
217735439 | Ground Loop | DAIKIN | WSTH036J1*H*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225 | No
217735441 | Ground Loop | DAIKIN | WSTV024J1*H*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667 | No
217735443 | Ground Loop | DAIKIN | WSTV030J1*H*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833 | No
205767513 | Ground Loop | ClimateMaster | TSH/V/D024C |  | 25300 | 18.9 | 19200 | 4 | 2.1083 | Yes
205767514 | Ground Loop | ClimateMaster | TSH/V/D024C*K |  | 25500 | 20.9 | 19100 | 4.2 | 2.125 | Yes
205767515 | Ground Loop | ClimateMaster | TSH/V/D030C |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333 | Yes
205767516 | Ground Loop | ClimateMaster | TSH/V/D030C*K |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333 | Yes
205767517 | Ground Loop | ClimateMaster | TSH/V/D036C |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583 | Yes
205767518 | Ground Loop | ClimateMaster | TSH/V/D036C*K |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833 | Yes
205767519 | Ground Loop | ClimateMaster | TSH/V/D042C |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417 | Yes
205767520 | Ground Loop | ClimateMaster | TSH/V/D042C*K |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917 | Yes
205767521 | Ground Loop | ClimateMaster | TSH/V/D048C*K |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167 | Yes
205767522 | Ground Loop | ClimateMaster | TSH/V/D060C |  | 63900 | 17.2 | 46900 | 3.7 | 5.325 | Yes
205767523 | Ground Loop | ClimateMaster | TSH/V/D060C*K |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667 | Yes
205767525 | Ground Loop | ClimateMaster | TSH/V/D070C*K |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833 | Yes
205767532 | Ground Loop | ClimateMaster | TSM15 B |  | 15500 | 18.8 | 11000 | 3.6 | 1.2917 | No
205767538 | Ground Loop | ClimateMaster | TSM30 B |  | 29000 | 17.6 | 22200 | 3.6 | 2.4167 | No
205767541 | Ground Loop | ClimateMaster | TCH/V018A*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
205767548 | Ground Loop | ClimateMaster | TRH/V018A*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
205767559 | Ground Loop | ClimateMaster | TZV/H060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
202350417 | Ground Loop | AAON, Inc. | RN-009-2-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425 | No
202350418 | Ground Loop | AAON, Inc. | RN-009-3-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425 | No
202350419 | Ground Loop | AAON, Inc. | RN-009-4-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425 | No
202350429 | Ground Loop | AAON, Inc. | RN-011-2-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417 | No
202350430 | Ground Loop | AAON, Inc. | RN-011-3-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417 | No
202350431 | Ground Loop | AAON, Inc. | RN-011-4-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417 | No
215415916 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | Yes
215415917 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | Yes
215415918 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | Yes
215415919 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | No
215415920 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | No
215415921 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667 | No
215415922 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667 | No
215415923 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083 | No
215415924 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083 | No
215415925 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | No
215415926 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | No
215415927 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | No
215415928 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | No
217531660 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)006A |  | 6300 | 20 | 4400 | 3.6 | 0.525 | Yes
217531661 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)009A |  | 9700 | 19 | 7000 | 3.7 | 0.80833 | Yes
217531662 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)012A |  | 12400 | 19.5 | 9200 | 3.6 | 1.0333 | Yes
217531663 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)018A |  | 20100 | 19.5 | 14500 | 4.1 | 1.675 | Yes
8740368 | Ground Loop | GEOCOMFORT | GVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | Yes
8740369 | Ground Loop | HYDRON MODULE | HVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | Yes
8740370 | Ground Loop | TETCO | TVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | Yes
8740371 | Ground Loop | GEOCOMFORT | GVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740372 | Ground Loop | HYDRON MODULE | HVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740373 | Ground Loop | TETCO | TVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740374 | Ground Loop | GEOCOMFORT | GVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740375 | Ground Loop | HYDRON MODULE | HVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740376 | Ground Loop | TETCO | TVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8791878 | Ground Loop | GEOSTAR | 101/102H060**1*(1,4)***** |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
8791879 | Ground Loop | GeoSmart Energy | GS060**1*(1,4)********H |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
8791880 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****H |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
8791883 | Ground Loop | GEOSTAR | 101/102H060**1*0***** |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
8791884 | Ground Loop | GeoSmart Energy | GS060**1*0********H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
8791885 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*0****H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
10435614 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10435615 | Ground Loop | GEOSTAR | 103H070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | Yes
10435616 | Ground Loop | GeoSmart Energy | GSZ070*1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | Yes
10447649 | Ground Loop | RHEEM | RPVS/EC025 | RCFL-HM2417 | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
10447650 | Ground Loop | RHEEM | RPVS/EC025 | RCFL-HM2621 | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
10447662 | Ground Loop | RHEEM | RPVS/EC036 | RCFL-HM38** | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
217212068 | Ground Loop | FHP | CP036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217212070 | Ground Loop | FHP | CP036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
217212071 | Ground Loop | FHP | CP036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217212072 | Ground Loop | FHP | CP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
217212073 | Ground Loop | FHP | CP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
217212074 | Ground Loop | FHP | CP048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
217212076 | Ground Loop | FHP | CP048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
217212077 | Ground Loop | FHP | CP048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
217212078 | Ground Loop | FHP | CP048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
217212079 | Ground Loop | FHP | CP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
217212080 | Ground Loop | FHP | CP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
217212082 | Ground Loop | FHP | CP060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
217212083 | Ground Loop | FHP | CP060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
217212084 | Ground Loop | FHP | CP060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
217212085 | Ground Loop | FHP | CP060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
217212086 | Ground Loop | FHP | CP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212089 | Ground Loop | FHP | CP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212091 | Ground Loop | FHP | CP070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212094 | Ground Loop | FHP | CP070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212097 | Ground Loop | FHP | CP070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212099 | Ground Loop | FHP | CP070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212102 | Ground Loop | BOSCH | RP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
217212103 | Ground Loop | BOSCH | RP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
217212105 | Ground Loop | BOSCH | RP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
217212106 | Ground Loop | BOSCH | RP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
217212107 | Ground Loop | BOSCH | RP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
217212108 | Ground Loop | BOSCH | RP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
217212109 | Ground Loop | BOSCH | RP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
217212111 | Ground Loop | BOSCH | RP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
217212112 | Ground Loop | BOSCH | RP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
217212113 | Ground Loop | BOSCH | RP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
217212114 | Ground Loop | BOSCH | RP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217212116 | Ground Loop | BOSCH | RP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
215400079 | Ground Loop | DAIKIN | WSMV015E1*G/J*P |  | 16100 | 20.21 | 11200 | 3.65 | 1.3417 | No
215400081 | Ground Loop | DAIKIN | WSMV015E1*G/J*T |  | 16300 | 21.12 | 11100 | 3.74 | 1.3583 | No
215400083 | Ground Loop | DAIKIN | WSMV015E1*G/J*C |  | 16300 | 21.12 | 11100 | 3.74 | 1.3583 | No
217351071 | Ground Loop | BOSCH | CP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | No
217351072 | Ground Loop | BOSCH | CP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | No
217351073 | Ground Loop | BOSCH | CP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | No
217351074 | Ground Loop | BOSCH | CP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | No
217351075 | Ground Loop | BOSCH | CP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | No
217351076 | Ground Loop | BOSCH | CP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | No
217351077 | Ground Loop | BOSCH | CP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | No
217351078 | Ground Loop | BOSCH | CP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | No
217351079 | Ground Loop | BOSCH | CP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | No
217351080 | Ground Loop | BOSCH | CP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | No
217351082 | Ground Loop | BOSCH | CP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | No
217351083 | Ground Loop | BOSCH | CP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | No
217351084 | Ground Loop | BOSCH | CP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3 | No
217351087 | Ground Loop | BOSCH-GEO | RP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | Yes
217351088 | Ground Loop | BOSCH-GEO | RP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | Yes
217351089 | Ground Loop | BOSCH-GEO | RP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | Yes
217351090 | Ground Loop | BOSCH-GEO | RP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | Yes
217351091 | Ground Loop | BOSCH-GEO | RP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | Yes
217351092 | Ground Loop | BOSCH-GEO | RP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | Yes
217351093 | Ground Loop | BOSCH-GEO | RP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | Yes
217351094 | Ground Loop | BOSCH-GEO | RP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | Yes
217351095 | Ground Loop | BOSCH-GEO | RP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | Yes
217351096 | Ground Loop | BOSCH-GEO | RP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | Yes
217351098 | Ground Loop | BOSCH-GEO | RP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | Yes
217351099 | Ground Loop | BOSCH-GEO | RP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | Yes
217351100 | Ground Loop | BOSCH-GEO | RP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3 | Yes
217351103 | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351104 | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351107 | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351108 | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351109 | Ground Loop | GEO-THERMAL SPLIT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351111 | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351112 | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351114 | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
7499565 | Ground Loop | FHP | LM060-3VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7499566 | Ground Loop | FHP | LM060-4VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7499702 | Ground Loop | BOSCH | SM036-1CF/HZ/VT |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | Yes
7519546 | Ground Loop | GEOCOMFORT | GVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | No
7519547 | Ground Loop | HYDRON MODULE | HVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | No
7519548 | Ground Loop | TETCO | TVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | No
7519549 | Ground Loop | GEOCOMFORT | GVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519550 | Ground Loop | HYDRON MODULE | HVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519551 | Ground Loop | TETCO | TVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519552 | Ground Loop | GEOCOMFORT | GVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519553 | Ground Loop | HYDRON MODULE | HVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519554 | Ground Loop | TETCO | TVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519555 | Ground Loop | GEOCOMFORT | GVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519556 | Ground Loop | HYDRON MODULE | HVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519557 | Ground Loop | TETCO | TVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519558 | Ground Loop | GEOCOMFORT | GVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519559 | Ground Loop | HYDRON MODULE | HVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519560 | Ground Loop | TETCO | TVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519561 | Ground Loop | GEOCOMFORT | GVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519562 | Ground Loop | HYDRON MODULE | HVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519563 | Ground Loop | TETCO | TVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519564 | Ground Loop | GEOCOMFORT | GVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519565 | Ground Loop | HYDRON MODULE | HVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519566 | Ground Loop | TETCO | TVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519567 | Ground Loop | GEOCOMFORT | GVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519568 | Ground Loop | HYDRON MODULE | HVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519569 | Ground Loop | TETCO | TVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519570 | Ground Loop | GEOCOMFORT | GVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519571 | Ground Loop | HYDRON MODULE | HVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519572 | Ground Loop | TETCO | TVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519573 | Ground Loop | GEOCOMFORT | GVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
5315780 | Ground Loop | WaterFurnace | NBV/NBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315781 | Ground Loop | WaterFurnace | NBV/NBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315782 | Ground Loop | WaterFurnace | NBV/NBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315783 | Ground Loop | WaterFurnace | NBV/NBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315784 | Ground Loop | WaterFurnace | NBV/NBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315785 | Ground Loop | WaterFurnace | NBV/NBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5316500 | Ground Loop | WaterFurnace | NBV/NBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316501 | Ground Loop | WaterFurnace | NBV/NBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316502 | Ground Loop | WaterFurnace | NBV/NBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316503 | Ground Loop | WaterFurnace | NBV/NBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316504 | Ground Loop | WaterFurnace | NBV/NBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316505 | Ground Loop | WaterFurnace | NBV/NBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316510 | Ground Loop | WaterFurnace | NBV/NBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316511 | Ground Loop | WaterFurnace | NBV/NBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316512 | Ground Loop | WaterFurnace | NBV/NBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316513 | Ground Loop | WaterFurnace | NBV/NBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316514 | Ground Loop | WaterFurnace | NBV/NBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316515 | Ground Loop | WaterFurnace | NBV/NBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316516 | Ground Loop | WaterFurnace | NBV/NBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5317193 | Ground Loop | WaterFurnace | NBV/NBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317194 | Ground Loop | WaterFurnace | NBV/NBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317195 | Ground Loop | WaterFurnace | NBV/NBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317196 | Ground Loop | WaterFurnace | NBV/NBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317197 | Ground Loop | WaterFurnace | NBV/NBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317198 | Ground Loop | WaterFurnace | NBV/NBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317199 | Ground Loop | WaterFurnace | NBV/NBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317200 | Ground Loop | WaterFurnace | NBV/NBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317201 | Ground Loop | WaterFurnace | NBV/NBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317202 | Ground Loop | WaterFurnace | NBV/NBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317203 | Ground Loop | WaterFurnace | NBV/NBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317205 | Ground Loop | WaterFurnace | NBV/NBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317206 | Ground Loop | WaterFurnace | NBV/NBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317207 | Ground Loop | WaterFurnace | NBV/NBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317209 | Ground Loop | WaterFurnace | NBV/NBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317210 | Ground Loop | WaterFurnace | NBV/NBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317211 | Ground Loop | WaterFurnace | NBV/NBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317270 | Ground Loop | WaterFurnace | NBV/NBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317328 | Ground Loop | WaterFurnace | NBV/NBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317329 | Ground Loop | WaterFurnace | NBV/NBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317330 | Ground Loop | WaterFurnace | NBV/NBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317331 | Ground Loop | WaterFurnace | NBV/NBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317332 | Ground Loop | WaterFurnace | NBV/NBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317333 | Ground Loop | WaterFurnace | NBV/NBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317334 | Ground Loop | WaterFurnace | NBV/NBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317335 | Ground Loop | WaterFurnace | NBV/NBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5339321 | Ground Loop | TTHERM GEO | TVA-036-1* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175 | No
5339322 | Ground Loop | TTHERM GEO | TVA-048-1* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833 | No
5339323 | Ground Loop | TTHERM GEO | TVA-060-1* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15 | No
217014528 | Ground Loop | CARRIER | GCA72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014529 | Ground Loop | BRYANT | GCA72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014532 | Ground Loop | HEIL | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014533 | Ground Loop | ARCOAIRE | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014534 | Ground Loop | KEEPRITE | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014535 | Ground Loop | TEMPSTAR | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
207657660 | Ground Loop | ClimateMaster | TSL15 A/C |  | 15400 | 17.7 | 11500 | 3.6 | 1.2833 | No
207657661 | Ground Loop | ClimateMaster | TSL15 D |  | 15400 | 19.2 | 11000 | 3.7 | 1.2833 | No
216625752 | Ground Loop | GeoSmart Energy | S5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625753 | Ground Loop | GeoSmart Energy | S5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625754 | Ground Loop | GeoSmart Energy | S5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625755 | Ground Loop | GeoSmart Energy | S5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625756 | Ground Loop | GeoSmart Energy | S5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216625757 | Ground Loop | GeoSmart Energy | S5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216625758 | Ground Loop | GeoSmart Energy | S5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625759 | Ground Loop | GeoSmart Energy | S5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625760 | Ground Loop | GeoSmart Energy | S5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625761 | Ground Loop | GeoSmart Energy | S5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625762 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625763 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625764 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625765 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625766 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625767 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625768 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625769 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625770 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625771 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625772 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625773 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625774 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625775 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625776 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625777 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625778 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625779 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625780 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625781 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625782 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625783 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625784 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625785 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625786 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625787 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625788 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625789 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625790 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625791 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625792 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625793 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625794 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625795 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625796 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625797 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625798 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625799 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625800 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625801 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625802 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625803 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625804 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625805 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625806 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625807 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268725 | Ground Loop | WaterFurnace | V5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268726 | Ground Loop | WaterFurnace | V5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268727 | Ground Loop | WaterFurnace | V5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268728 | Ground Loop | WaterFurnace | V5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268729 | Ground Loop | WaterFurnace | V5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268730 | Ground Loop | WaterFurnace | V5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268731 | Ground Loop | WaterFurnace | V5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268732 | Ground Loop | WaterFurnace | V5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268733 | Ground Loop | WaterFurnace | V5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268734 | Ground Loop | WaterFurnace | V5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
213714597 | Ground Loop | DAIKIN | WSSH070E1*H*T |  | 73300 | 19.73 | 53600 | 3.64 | 6.1083 | No
213714598 | Ground Loop | DAIKIN | WSSH070E1*H*C |  | 73300 | 19.73 | 53600 | 3.64 | 6.1083 | No
214063740 | Ground Loop | GeoSmart Energy | GBV/GBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
214063741 | Ground Loop | GeoSmart Energy | GBV/GBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
214063742 | Ground Loop | GeoSmart Energy | GBV/GBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
214063743 | Ground Loop | GeoSmart Energy | GBV/GBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
214063744 | Ground Loop | GeoSmart Energy | GBV/GBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
214063745 | Ground Loop | GeoSmart Energy | GBV/GBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
214063747 | Ground Loop | GeoSmart Energy | GBV/GBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214063748 | Ground Loop | GeoSmart Energy | GBV/GBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214063750 | Ground Loop | GeoSmart Energy | GBV/GBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214063751 | Ground Loop | GeoSmart Energy | GBV/GBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214063752 | Ground Loop | GeoSmart Energy | GBV/GBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
214063753 | Ground Loop | GeoSmart Energy | GBV/GBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214063754 | Ground Loop | GeoSmart Energy | GBV/GBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214063755 | Ground Loop | GeoSmart Energy | GBV/GBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
214063756 | Ground Loop | GeoSmart Energy | GBV/GBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214063757 | Ground Loop | GeoSmart Energy | GBV/GBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214063758 | Ground Loop | GeoSmart Energy | GBV/GBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214063759 | Ground Loop | GeoSmart Energy | GBV/GBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214063760 | Ground Loop | GeoSmart Energy | GBV/GBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214063761 | Ground Loop | GeoSmart Energy | GBV/GBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214063762 | Ground Loop | GeoSmart Energy | GBV/GBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
214063763 | Ground Loop | GeoSmart Energy | GBV/GBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214063764 | Ground Loop | GeoSmart Energy | GBV/GBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214063765 | Ground Loop | GeoSmart Energy | GBV/GBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
214063766 | Ground Loop | GeoSmart Energy | GBV/GBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214063767 | Ground Loop | GeoSmart Energy | GBV/GBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214063768 | Ground Loop | GeoSmart Energy | GBV/GBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
214063769 | Ground Loop | GeoSmart Energy | GBV/GBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214063770 | Ground Loop | GeoSmart Energy | GBV/GBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214063771 | Ground Loop | GeoSmart Energy | GBV/GBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
214063772 | Ground Loop | GeoSmart Energy | GBV/GBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214063773 | Ground Loop | GeoSmart Energy | GBV/GBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214063774 | Ground Loop | GeoSmart Energy | GBV/GBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063775 | Ground Loop | GeoSmart Energy | GBV/GBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063776 | Ground Loop | GeoSmart Energy | GBV/GBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063777 | Ground Loop | GeoSmart Energy | GBV/GBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063778 | Ground Loop | GeoSmart Energy | GBV/GBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214063779 | Ground Loop | GeoSmart Energy | GBV/GBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214063780 | Ground Loop | GeoSmart Energy | GBV/GBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214063781 | Ground Loop | GeoSmart Energy | GBV/GBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214063782 | Ground Loop | GeoSmart Energy | GBV/GBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
214063783 | Ground Loop | GeoSmart Energy | GBV/GBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
215837780 | Ground Loop | DAIKIN | WSMH048F3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837781 | Ground Loop | DAIKIN | WSMH048K3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837783 | Ground Loop | DAIKIN | WSMH048L3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837814 | Ground Loop | DAIKIN | WSSH024F3*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837815 | Ground Loop | DAIKIN | WSSH024J1*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837817 | Ground Loop | DAIKIN | WSSH024K3*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
216419947 | Ground Loop | Whalen | WZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | Yes
216439574 | Ground Loop | GeoSmart Energy | S5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667 | Yes
216439575 | Ground Loop | GeoSmart Energy | S5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917 | Yes
216439576 | Ground Loop | GeoSmart Energy | S5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083 | Yes
216439577 | Ground Loop | GeoSmart Energy | S5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583 | Yes
216508982 | Ground Loop | ClimateMaster | SJ/PN024A | SKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975 | Yes
216508983 | Ground Loop | ClimateMaster | SJ/PN036A | SKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667 | Yes
217897413 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
217897414 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
217897417 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
217897418 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
217897421 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
217897422 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
217897449 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
217897450 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
217897453 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
217897454 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
217897455 | Ground Loop | CENTURY | MJN024A | MKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975 | Yes
217897456 | Ground Loop | COMFORT-AIRE | MJN024A | MKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975 | Yes
215224089 | Ground Loop | BOSCH | CF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224090 | Ground Loop | BOSCH | CF024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224091 | Ground Loop | BOSCH | CF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224092 | Ground Loop | BOSCH | CF024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
214771940 | Ground Loop | TRANE | EXVK060A |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214771941 | Ground Loop | TRANE | EXVK070A |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214771943 | Ground Loop | TRANE | GEHK009A |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333 | No
214771945 | Ground Loop | TRANE | GEHK015A |  | 15900 | 18.2 | 12500 | 3.85 | 1.325 | No
214771946 | Ground Loop | TRANE | GEHK018A |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417 | No
214771947 | Ground Loop | TRANE | GEHK024A |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214771948 | Ground Loop | TRANE | GEHK030A |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214771951 | Ground Loop | TRANE | GEHK048A |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214771952 | Ground Loop | TRANE | GEHK060A |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214771953 | Ground Loop | TRANE | EXHK009A |  | 9000 | 21.2 | 6100 | 3.91 | 0.75 | No
214771954 | Ground Loop | TRANE | EXHK012A |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167 | No
214771955 | Ground Loop | TRANE | EXHK015A |  | 16200 | 18.7 | 11800 | 3.73 | 1.35 | No
214771956 | Ground Loop | TRANE | EXHK018A |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417 | No
214771957 | Ground Loop | TRANE | EXHK024A |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214771958 | Ground Loop | TRANE | EXHK030A |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214771959 | Ground Loop | TRANE | EXHK036A |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214771960 | Ground Loop | TRANE | EXHK042A |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214771961 | Ground Loop | TRANE | EXHK048A |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214771962 | Ground Loop | TRANE | EXHK060A |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214771963 | Ground Loop | TRANE | EXHK070A |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772055 | Ground Loop | TRANE | GEVK0097 |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333 | No
214772057 | Ground Loop | TRANE | GEVK0157 |  | 15900 | 18.2 | 12500 | 3.85 | 1.325 | No
214772058 | Ground Loop | TRANE | GEVK0187 |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417 | No
214772059 | Ground Loop | TRANE | GEVK024B |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772060 | Ground Loop | TRANE | GEVK0244 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772061 | Ground Loop | TRANE | GEVK0247 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772062 | Ground Loop | TRANE | GEVK030B |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772063 | Ground Loop | TRANE | GEVK0304 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772064 | Ground Loop | TRANE | GEVK0307 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
5220666 | Ground Loop | DAIKIN | WGSV/WGSH019B*E |  | 18700 | 18.7 | 13800 | 4.1 | 1.5583 | No
5220667 | Ground Loop | DAIKIN | WGSV/WGSH019B*J |  | 18700 | 18.7 | 13800 | 4.1 | 1.5583 | No
5220670 | Ground Loop | DAIKIN | WGSV/WGSH024B*E |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917 | No
5220671 | Ground Loop | DAIKIN | WGSV/WGSH024B*F |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917 | No
212428698 | Ground Loop | HYDROTECH | WSH6036A6* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | Yes
212428699 | Ground Loop | HYDROTECH | WSH6042A6* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | Yes
212428700 | Ground Loop | HYDROTECH | WSH6048A6* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | Yes
212428701 | Ground Loop | AE Air | WSH6009A6* |  | 9500 | 18.9 | 6800 | 3.6 | 0.79167 | Yes
212428702 | Ground Loop | AE Air | WSH6012A6* |  | 12000 | 18.2 | 8500 | 3.8 | 1 | Yes
212428703 | Ground Loop | AE Air | WSH6018A6* |  | 19000 | 19 | 12000 | 3.6 | 1.5833 | Yes
212428704 | Ground Loop | AE Air | WSH6024A6* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | Yes
212428705 | Ground Loop | AE Air | WSH6030A6* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | Yes
212428706 | Ground Loop | AE Air | WSH6036A6* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | Yes
212428707 | Ground Loop | AE Air | WSH6042A6* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | Yes
212428708 | Ground Loop | AE Air | WSH6048A6* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | Yes
212505502 | Ground Loop | HYDROTECH | WSH6060A6* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | Yes
212505503 | Ground Loop | HYDROTECH | WSH6072A6* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | Yes
202679205 | Ground Loop | BOSCH-GEO | SM036-1CSC-*****B | SM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583 | Yes
202679208 | Ground Loop | BOSCH | SM036-1CSC-*****B | SM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583 | Yes
202729320 | Ground Loop | HEIL | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
202729321 | Ground Loop | ARCOAIRE | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729322 | Ground Loop | KEEPRITE | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729323 | Ground Loop | TEMPSTAR | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729324 | Ground Loop | COMFORTMAKER | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
215837601 | Ground Loop | DAIKIN | WSCH048F3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837603 | Ground Loop | DAIKIN | WSCH048K3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837604 | Ground Loop | DAIKIN | WSCH048L3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837610 | Ground Loop | DAIKIN | WSCH048F3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837611 | Ground Loop | DAIKIN | WSCH048K3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837613 | Ground Loop | DAIKIN | WSCH048L3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
217754387 | Ground Loop | DAIKIN | WSSH030F1*H*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
217754388 | Ground Loop | DAIKIN | WSSH030K1*H*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
217754390 | Ground Loop | DAIKIN | WSSH036F1*H*T |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583 | No
217754391 | Ground Loop | DAIKIN | WSSH036K1*H*T |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583 | No
217754393 | Ground Loop | DAIKIN | WSSH036F1*H*C |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583 | No
217754394 | Ground Loop | DAIKIN | WSSH036K1*H*C |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583 | No
217754396 | Ground Loop | DAIKIN | WSSH042F1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217754397 | Ground Loop | DAIKIN | WSSH042K1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217754399 | Ground Loop | DAIKIN | WSSH042F1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217754400 | Ground Loop | DAIKIN | WSSH042K1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217754402 | Ground Loop | DAIKIN | WSSH048F1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754403 | Ground Loop | DAIKIN | WSSH048K1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754404 | Ground Loop | DAIKIN | WSSH048L1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754406 | Ground Loop | DAIKIN | WSSH048F1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754407 | Ground Loop | DAIKIN | WSSH048K1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754408 | Ground Loop | DAIKIN | WSSH048L1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754418 | Ground Loop | DAIKIN | WSSH070F1*H*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
217754419 | Ground Loop | DAIKIN | WSSH070K1*H*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
217754422 | Ground Loop | DAIKIN | WSSH070F1*H*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
217754423 | Ground Loop | DAIKIN | WSSH070K1*H*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
217754426 | Ground Loop | DAIKIN | WSSV024F1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
217754427 | Ground Loop | DAIKIN | WSSV024K1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
217754429 | Ground Loop | DAIKIN | WSSV024F1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
217754430 | Ground Loop | DAIKIN | WSSV024K1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
217754432 | Ground Loop | DAIKIN | WSSV030F1*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
217754433 | Ground Loop | DAIKIN | WSSV030K1*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
217754435 | Ground Loop | DAIKIN | WSSV030F1*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
217754436 | Ground Loop | DAIKIN | WSSV030K1*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
217754438 | Ground Loop | DAIKIN | WSSV036F1*H*T |  | 40500 | 21.18 | 27600 | 3.83 | 3.375 | No
217754439 | Ground Loop | DAIKIN | WSSV036K1*H*T |  | 40500 | 21.09 | 27600 | 3.83 | 3.375 | No
217754441 | Ground Loop | DAIKIN | WSSV036F1*H*C |  | 40500 | 21.18 | 27600 | 3.83 | 3.375 | No
202350444 | Ground Loop | AAON, Inc. | M2-007-2-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7 | No
202350445 | Ground Loop | AAON, Inc. | M2-007-2-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583 | No
202350446 | Ground Loop | AAON, Inc. | M2-007-2-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417 | No
202350447 | Ground Loop | AAON, Inc. | M2-007-2-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5 | No
202350448 | Ground Loop | AAON, Inc. | M2-007-3-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7 | No
202350449 | Ground Loop | AAON, Inc. | M2-007-3-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583 | No
202350450 | Ground Loop | AAON, Inc. | M2-007-3-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417 | No
202350451 | Ground Loop | AAON, Inc. | M2-007-3-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5 | No
202350452 | Ground Loop | AAON, Inc. | M2-007-4-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7 | No
202350453 | Ground Loop | AAON, Inc. | M2-007-4-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583 | No
202350454 | Ground Loop | AAON, Inc. | M2-007-4-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417 | No
202350455 | Ground Loop | AAON, Inc. | M2-007-4-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5 | No
4236565 | Ground Loop | DAIKIN | WVFW1030*E***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583 | No
4236634 | Ground Loop | DAIKIN | WVFW1030*F***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583 | No
4236635 | Ground Loop | DAIKIN | WVFW1030*J***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583 | No
4504310 | Ground Loop | BOSCH-GEO | BP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
4509712 | Ground Loop | BOSCH-GEO | BP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
4510474 | Ground Loop | BOSCH-GEO | BP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
4547265 | Ground Loop | DUAL AIR | CFX024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | Yes
4547266 | Ground Loop | DUAL AIR | CFX031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | Yes
4547267 | Ground Loop | DUAL AIR | CFX036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | Yes
4547268 | Ground Loop | DUAL AIR | CFX041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | Yes
4547869 | Ground Loop | MIAMI HEAT PUMP | HPX024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | Yes
4547870 | Ground Loop | MIAMI HEAT PUMP | HPX031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | Yes
4547871 | Ground Loop | MIAMI HEAT PUMP | HPX036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | Yes
4547872 | Ground Loop | MIAMI HEAT PUMP | HPX041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | Yes
215827089 | Ground Loop | DAIKIN | WSLH120F1*G/J |  | 123000 | 17.1 | 90000 | 3.7 | 10.25 | No
215827090 | Ground Loop | DAIKIN | WSLH120K1*G/J |  | 123000 | 17.1 | 90000 | 3.6 | 10.25 | No
215827091 | Ground Loop | DAIKIN | WSLH120L1*G/J |  | 123000 | 17.1 | 90000 | 3.6 | 10.25 | No
215827092 | Ground Loop | DAIKIN | WSLV072F1*G/J |  | 77000 | 19 | 53000 | 3.7 | 6.4167 | No
215827094 | Ground Loop | DAIKIN | WSLV072K1*G/J |  | 77000 | 19 | 53000 | 3.7 | 6.4167 | No
215827096 | Ground Loop | DAIKIN | WSLV072L1*G/J |  | 77000 | 19 | 53000 | 3.6 | 6.4167 | No
215827098 | Ground Loop | DAIKIN | WSLV096F1*G/J |  | 99500 | 19.4 | 74100 | 3.9 | 8.2917 | No
215827100 | Ground Loop | DAIKIN | WSLV096K1*G/J |  | 99500 | 19.4 | 74100 | 3.9 | 8.2917 | No
215827102 | Ground Loop | DAIKIN | WSLV096L1*G/J |  | 99500 | 18.7 | 74100 | 3.7 | 8.2917 | No
217752403 | Ground Loop | ClimateMaster | SL(A/*)*06A |  | 6300 | 20.5 | 4600 | 3.6 | 0.525 | No
217752677 | Ground Loop | DAIKIN | WSSH024J1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217752679 | Ground Loop | DAIKIN | WSSH024J1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217752681 | Ground Loop | DAIKIN | WSSH030J1*H*T |  | 30600 | 21.15 | 21200 | 3.95 | 2.55 | No
217752683 | Ground Loop | DAIKIN | WSSH030J1*H*C |  | 30600 | 21.15 | 21200 | 3.95 | 2.55 | No
217752685 | Ground Loop | DAIKIN | WSSH036J1*H*T |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583 | No
217752687 | Ground Loop | DAIKIN | WSSH036J1*H*C |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583 | No
217752689 | Ground Loop | DAIKIN | WSSH042J1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217752691 | Ground Loop | DAIKIN | WSSH042J1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
9910542 | Ground Loop | TETCO | TZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | Yes
9910543 | Ground Loop | GEOCOMFORT | GZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | No
9910544 | Ground Loop | HYDRON MODULE | HZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | No
9910545 | Ground Loop | TETCO | TZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | No
9910548 | Ground Loop | GEOCOMFORT | GZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | Yes
9910549 | Ground Loop | HYDRON MODULE | HZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | Yes
9910550 | Ground Loop | TETCO | TZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | Yes
9910551 | Ground Loop | GEOCOMFORT | GZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910552 | Ground Loop | HYDRON MODULE | HZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910553 | Ground Loop | TETCO | TZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910554 | Ground Loop | GEOCOMFORT | GZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910555 | Ground Loop | HYDRON MODULE | HZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910556 | Ground Loop | TETCO | TZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910557 | Ground Loop | GEOCOMFORT | GZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
216625508 | Ground Loop | GEOSTAR | G5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625509 | Ground Loop | GEOSTAR | G5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625510 | Ground Loop | GEOSTAR | G5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625511 | Ground Loop | GEOSTAR | G5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625512 | Ground Loop | GEOSTAR | G5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625513 | Ground Loop | GEOSTAR | G5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625514 | Ground Loop | GEOSTAR | G5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625515 | Ground Loop | GEOSTAR | G5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625516 | Ground Loop | GEOSTAR | G5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625517 | Ground Loop | GEOSTAR | G5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625518 | Ground Loop | GEOSTAR | G5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625519 | Ground Loop | GEOSTAR | G5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625520 | Ground Loop | GEOSTAR | G5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625521 | Ground Loop | GEOSTAR | G5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625522 | Ground Loop | GEOSTAR | G5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625523 | Ground Loop | GEOSTAR | G5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625524 | Ground Loop | GEOSTAR | G5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625525 | Ground Loop | GEOSTAR | G5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625526 | Ground Loop | GEOSTAR | G5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625527 | Ground Loop | GEOSTAR | G5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625528 | Ground Loop | GEOSTAR | G5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625529 | Ground Loop | GEOSTAR | G5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625530 | Ground Loop | GEOSTAR | G5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625531 | Ground Loop | GEOSTAR | G5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625532 | Ground Loop | GEOSTAR | G5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625533 | Ground Loop | GEOSTAR | G5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625534 | Ground Loop | GEOSTAR | G5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625535 | Ground Loop | GEOSTAR | G5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
208450079 | Ground Loop | AE Air | HRCX18*-6 |  | 18000 | 17.1 | 13000 | 3.6 | 1.5 | Yes
208450080 | Ground Loop | AE Air | HRCX09*-6 |  | 10000 | 19 | 6800 | 3.6 | 0.83333 | Yes
208450081 | Ground Loop | AE Air | HRCX24*-6 |  | 24000 | 19 | 17000 | 3.6 | 2 | Yes
208450082 | Ground Loop | AE Air | HRCX12*-6 |  | 11800 | 18 | 8000 | 3.6 | 0.98333 | Yes
208450083 | Ground Loop | AE Air | HRCX30*-6 |  | 28000 | 18 | 20000 | 3.6 | 2.3333 | Yes
208450084 | Ground Loop | AE Air | HRCX36*-6 |  | 34100 | 17.1 | 25000 | 3.6 | 2.8417 | Yes
208556796 | Ground Loop | GEOCOMFORT | GRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125 | Yes
208556798 | Ground Loop | HYDRON MODULE | HRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125 | Yes
208556799 | Ground Loop | TETCO | TRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125 | Yes
208556801 | Ground Loop | GEOCOMFORT | GRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15 | No
208556804 | Ground Loop | HYDRON MODULE | HRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15 | Yes
208556806 | Ground Loop | TETCO | TRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15 | Yes
208556808 | Ground Loop | GEOCOMFORT | GRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417 | Yes
208556810 | Ground Loop | HYDRON MODULE | HRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417 | Yes
208556812 | Ground Loop | TETCO | TRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417 | Yes
215224293 | Ground Loop | BOSCH-GEO | RF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
216054496 | Ground Loop | GEOCOMFORT | GZT048* |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | Yes
216054499 | Ground Loop | GEOCOMFORT | GVS015* |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | Yes
3628414 | Ground Loop | WaterFurnace | USV/USH018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
3628415 | Ground Loop | WaterFurnace | USV/USH018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
3628416 | Ground Loop | WaterFurnace | USV/USH015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
3628417 | Ground Loop | WaterFurnace | USV/USH015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
7422322 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7423168 | Ground Loop | WaterFurnace | NBV/NBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7423169 | Ground Loop | GEOSTAR | GBV/GBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7423171 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7487652 | Ground Loop | GEOCOMFORT | GYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | Yes
7487653 | Ground Loop | HYDRON MODULE | HYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | Yes
7487654 | Ground Loop | TETCO | TYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | Yes
7487655 | Ground Loop | TETCO | TYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487656 | Ground Loop | GEOCOMFORT | GYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487657 | Ground Loop | HYDRON MODULE | HYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487658 | Ground Loop | HYDRON MODULE | HYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487659 | Ground Loop | GEOCOMFORT | GYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487660 | Ground Loop | TETCO | TYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
206608717 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048J1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
206608718 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048J1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
206608719 | Ground Loop | GEOSTAR | 103J048**1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
215224477 | Ground Loop | FHP | CF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224478 | Ground Loop | FHP | CF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224479 | Ground Loop | FHP | CF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224480 | Ground Loop | FHP | CF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224481 | Ground Loop | FHP | CF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224482 | Ground Loop | FHP | CF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224483 | Ground Loop | FHP | CF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224484 | Ground Loop | FHP | CF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224485 | Ground Loop | FHP | CF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224486 | Ground Loop | FHP | CF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224487 | Ground Loop | FHP | CF007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224488 | Ground Loop | FHP | CF007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224489 | Ground Loop | FHP | CF009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224490 | Ground Loop | FHP | CF009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224491 | Ground Loop | FHP | CF012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224492 | Ground Loop | FHP | CF012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224493 | Ground Loop | FHP | CF015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224494 | Ground Loop | FHP | CF015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224495 | Ground Loop | FHP | CF018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224496 | Ground Loop | FHP | CF018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224497 | Ground Loop | FHP | CF024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224498 | Ground Loop | FHP | CF024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224499 | Ground Loop | FHP | CF024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224500 | Ground Loop | FHP | CF024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
5295984 | Ground Loop | WaterFurnace | NBV/NBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295985 | Ground Loop | WaterFurnace | NBV/NBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295986 | Ground Loop | WaterFurnace | NBV/NBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295987 | Ground Loop | WaterFurnace | NBV/NBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295988 | Ground Loop | WaterFurnace | NBV/NBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295989 | Ground Loop | WaterFurnace | NBV/NBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295990 | Ground Loop | WaterFurnace | NBV/NBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295991 | Ground Loop | WaterFurnace | NBV/NBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295992 | Ground Loop | WaterFurnace | NBV/NBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
5295993 | Ground Loop | WaterFurnace | NBV/NBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
5295994 | Ground Loop | WaterFurnace | NBV/NBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
5295995 | Ground Loop | WaterFurnace | NBV/NBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
5295996 | Ground Loop | WaterFurnace | NBV/NBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5295997 | Ground Loop | WaterFurnace | NBV/NBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5295998 | Ground Loop | WaterFurnace | NBV/NBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5295999 | Ground Loop | WaterFurnace | NBV/NBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296000 | Ground Loop | WaterFurnace | NBV/NBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296001 | Ground Loop | WaterFurnace | NBV/NBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296002 | Ground Loop | WaterFurnace | NBV/NBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296003 | Ground Loop | WaterFurnace | NBV/NBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296004 | Ground Loop | WaterFurnace | NBV/NBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
5296005 | Ground Loop | WaterFurnace | NBV/NBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
5296006 | Ground Loop | WaterFurnace | NBV/NBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
5296007 | Ground Loop | WaterFurnace | NBV/NBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
5296008 | Ground Loop | WaterFurnace | NBV/NBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296009 | Ground Loop | WaterFurnace | NBV/NBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296010 | Ground Loop | WaterFurnace | NBV/NBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296011 | Ground Loop | WaterFurnace | NBV/NBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296012 | Ground Loop | WaterFurnace | NBV/NBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296013 | Ground Loop | WaterFurnace | NBV/NBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067595 | Ground Loop | GeoSmart Energy | GBV/GBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214067596 | Ground Loop | GeoSmart Energy | GBV/GBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214067597 | Ground Loop | GeoSmart Energy | GBV/GBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214067598 | Ground Loop | GeoSmart Energy | GBV/GBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214067600 | Ground Loop | GeoSmart Energy | GBV/GBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214067601 | Ground Loop | GeoSmart Energy | GBV/GBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214067603 | Ground Loop | GeoSmart Energy | GBV/GBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214067604 | Ground Loop | GeoSmart Energy | GBV/GBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214067606 | Ground Loop | GeoSmart Energy | GBV/GBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067607 | Ground Loop | GeoSmart Energy | GBV/GBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067608 | Ground Loop | GeoSmart Energy | GBV/GBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067609 | Ground Loop | GeoSmart Energy | GBV/GBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067866 | Ground Loop | GeoSmart Energy | GBV/GBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067867 | Ground Loop | GeoSmart Energy | GBV/GBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067871 | Ground Loop | GeoSmart Energy | GBV/GBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067872 | Ground Loop | GeoSmart Energy | GBV/GBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214390535 | Ground Loop | Dandelion Geo | DP1G060V3A1000S |  | 62000 | 17 | 53000 | 4.5 | 5.1667 | Yes
214437585 | Ground Loop | Dandelion Geo | DP1G036V3A1000S |  | 39200 | 19.8 | 31000 | 4.6 | 3.2667 | Yes
214437586 | Ground Loop | Dandelion Geo | DP1G048V3A1000S |  | 51500 | 18.8 | 41500 | 4.4 | 4.2917 | Yes
207198824 | Ground Loop | BOSCH | WQ036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207200558 | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207200565 | Ground Loop | GeoSmart Energy | GS060**1*(1,4)*H |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207200566 | Ground Loop | GeoSmart Energy | GS060**1*0*H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
5615034 | Ground Loop | DAIKIN | WCCW5030*E*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625 | No
5615035 | Ground Loop | DAIKIN | WCCW5030*F*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625 | No
5615036 | Ground Loop | DAIKIN | WCCW5030*J*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625 | No
5615037 | Ground Loop | DAIKIN | WCCW5030*K*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625 | No
5615042 | Ground Loop | DAIKIN | WCCW5036*E*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15 | No
5615043 | Ground Loop | DAIKIN | WCCW5036*F*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15 | No
5615044 | Ground Loop | DAIKIN | WCCW5036*J*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15 | No
5615045 | Ground Loop | DAIKIN | WCCW5036*K*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15 | No
5615050 | Ground Loop | DAIKIN | WCCW5042*E*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083 | No
5615051 | Ground Loop | DAIKIN | WCCW5042*F*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083 | No
5615052 | Ground Loop | DAIKIN | WCCW5042*K*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083 | No
5615053 | Ground Loop | DAIKIN | WCCW5042*L*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083 | No
5646343 | Ground Loop | GEOCOMFORT | GXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | Yes
5646344 | Ground Loop | HYDRON MODULE | HXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | Yes
5646345 | Ground Loop | TETCO | TXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | Yes
5646346 | Ground Loop | GEOCOMFORT | GXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646347 | Ground Loop | HYDRON MODULE | HXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646348 | Ground Loop | TETCO | TXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646349 | Ground Loop | GEOCOMFORT | GXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646350 | Ground Loop | HYDRON MODULE | HXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646351 | Ground Loop | TETCO | TXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646371 | Ground Loop | GEOCOMFORT | GXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | Yes
5646372 | Ground Loop | HYDRON MODULE | HXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | Yes
5646373 | Ground Loop | TETCO | TXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | Yes
5646374 | Ground Loop | GEOCOMFORT | GXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646375 | Ground Loop | HYDRON MODULE | HXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646376 | Ground Loop | TETCO | TXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646377 | Ground Loop | GEOCOMFORT | GXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646378 | Ground Loop | HYDRON MODULE | HXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646379 | Ground Loop | TETCO | TXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646381 | Ground Loop | GEOCOMFORT | GCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | Yes
5646382 | Ground Loop | HYDRON MODULE | HCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | Yes
5646383 | Ground Loop | TETCO | TCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | Yes
5646384 | Ground Loop | GEOCOMFORT | GCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646385 | Ground Loop | HYDRON MODULE | HCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646386 | Ground Loop | TETCO | TCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646387 | Ground Loop | GEOCOMFORT | GCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
4230745 | Ground Loop | DAIKIN | WCCW4019*E*01* |  | 22600 | 17.3 | 14700 | 3.6 | 1.8833 | No
4230747 | Ground Loop | DAIKIN | WCCW4019*J*01* |  | 22600 | 17.3 | 14700 | 3.6 | 1.8833 | No
4233405 | Ground Loop | DAIKIN | WVFW1042*E***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833 | No
4233406 | Ground Loop | DAIKIN | WVFW1042*F***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833 | No
4233407 | Ground Loop | DAIKIN | WVFW1042*K***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833 | No
4233408 | Ground Loop | DAIKIN | WVFW1042*L***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833 | No
215268318 | Ground Loop | WaterFurnace | V3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268320 | Ground Loop | WaterFurnace | V3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268321 | Ground Loop | WaterFurnace | V3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268323 | Ground Loop | WaterFurnace | V3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
204031803 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
204031812 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
213710604 | Ground Loop | DAIKIN | WSSH009A1*H*T |  | 9500 | 21 | 7000 | 3.91 | 0.79167 | No
213710605 | Ground Loop | DAIKIN | WSSH009E1*H*T |  | 9500 | 21 | 7000 | 3.91 | 0.79167 | No
213710611 | Ground Loop | DAIKIN | WSSH012A1*H*T |  | 12200 | 20.1 | 9100 | 3.9 | 1.0167 | No
213710613 | Ground Loop | DAIKIN | WSSH012E1*H*T |  | 12000 | 20.3 | 9100 | 3.9 | 1 | No
213710616 | Ground Loop | DAIKIN | WSSH012J1*H*T |  | 12200 | 19 | 9100 | 3.8 | 1.0167 | No
213710620 | Ground Loop | DAIKIN | WSSH015A1*H*T |  | 17100 | 23.7 | 11000 | 3.9 | 1.425 | No
213710622 | Ground Loop | DAIKIN | WSSH015A1*H*C |  | 17100 | 23.7 | 11000 | 3.9 | 1.425 | No
213710624 | Ground Loop | DAIKIN | WSSH015E1*H*T |  | 17100 | 23.69 | 11000 | 3.9 | 1.425 | No
213710625 | Ground Loop | DAIKIN | WSSH015E1*H*C |  | 17100 | 23.69 | 11000 | 3.9 | 1.425 | No
213710629 | Ground Loop | DAIKIN | WSSH015J1*H*T |  | 17000 | 22 | 10900 | 3.9 | 1.4167 | No
213710630 | Ground Loop | DAIKIN | WSSH015J1*H*C |  | 17000 | 22 | 10900 | 3.9 | 1.4167 | No
213710633 | Ground Loop | DAIKIN | WSSH019E1*H*T |  | 20700 | 21.1 | 14100 | 3.8 | 1.725 | No
213710634 | Ground Loop | DAIKIN | WSSH019E1*H*C |  | 20700 | 21.1 | 14100 | 3.8 | 1.725 | No
213710638 | Ground Loop | DAIKIN | WSSH019J1*H*T |  | 20700 | 21.1 | 14100 | 3.8 | 1.725 | No
213710639 | Ground Loop | DAIKIN | WSSH019J1*H*C |  | 20700 | 21.1 | 14100 | 3.8 | 1.725 | No
213710641 | Ground Loop | DAIKIN | WSSH024E1*H*T |  | 25700 | 21.7 | 16900 | 4 | 2.1417 | No
213710643 | Ground Loop | DAIKIN | WSSH024E1*H*C |  | 25700 | 21.7 | 16900 | 4 | 2.1417 | No
213710645 | Ground Loop | DAIKIN | WSSH030E1*H*T |  | 30600 | 22.5 | 21200 | 4.2 | 2.55 | No
213710646 | Ground Loop | DAIKIN | WSSH030E1*H*C |  | 30600 | 22.5 | 21200 | 4.2 | 2.55 | No
213710648 | Ground Loop | DAIKIN | WSSH036E1*H*T |  | 40300 | 22 | 27600 | 3.7 | 3.3583 | No
213710650 | Ground Loop | DAIKIN | WSSH036E1*H*C |  | 40300 | 22 | 27600 | 3.7 | 3.3583 | No
213710652 | Ground Loop | DAIKIN | WSSH042E1*H*T |  | 44000 | 21.7 | 29000 | 3.9 | 3.6667 | No
213710653 | Ground Loop | DAIKIN | WSSH042E1*H*C |  | 44000 | 21.7 | 29000 | 3.9 | 3.6667 | No
213710655 | Ground Loop | DAIKIN | WSSH048E1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
213710657 | Ground Loop | DAIKIN | WSSH048E1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837722 | Ground Loop | DAIKIN | WSMH036K3*G/J*P |  | 37800 | 18.1 | 30700 | 3.79 | 3.15 | No
215837728 | Ground Loop | DAIKIN | WSMH036F3*G/J*T |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667 | No
215837730 | Ground Loop | DAIKIN | WSMH036J1*G/J*T |  | 38000 | 18.77 | 30000 | 3.9 | 3.1667 | No
215837731 | Ground Loop | DAIKIN | WSMH036K3*G/J*T |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667 | No
215837737 | Ground Loop | DAIKIN | WSMH036F3*G/J*C |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667 | No
215837739 | Ground Loop | DAIKIN | WSMH036J1*G/J*C |  | 38000 | 18.77 | 30000 | 3.9 | 3.1667 | No
215837740 | Ground Loop | DAIKIN | WSMH036K3*G/J*C |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667 | No
215837744 | Ground Loop | DAIKIN | WSMH042F3*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325 | No
215837746 | Ground Loop | DAIKIN | WSMH042K3*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325 | No
215837750 | Ground Loop | DAIKIN | WSMH042F3*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
215837751 | Ground Loop | DAIKIN | WSMH042K3*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
215837756 | Ground Loop | DAIKIN | WSMH042F3*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
215837757 | Ground Loop | DAIKIN | WSMH042K3*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
215837763 | Ground Loop | DAIKIN | WSMH048F3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
215837764 | Ground Loop | DAIKIN | WSMH048K3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
215837766 | Ground Loop | DAIKIN | WSMH048L3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
215837771 | Ground Loop | DAIKIN | WSMH048F3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837773 | Ground Loop | DAIKIN | WSMH048K3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837774 | Ground Loop | DAIKIN | WSMH048L3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754499 | Ground Loop | DAIKIN | WSTH070E1*H*C |  | 75600 | 19.03 | 52200 | 3.66 | 6.3 | No
217754503 | Ground Loop | DAIKIN | WSTV024E1*H*C |  | 22400 | 17.99 | 17200 | 3.98 | 1.8667 | No
217754504 | Ground Loop | DAIKIN | WSTV024F1*H*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667 | No
217754507 | Ground Loop | DAIKIN | WSTV030E1*H*C |  | 32200 | 19.48 | 20800 | 3.78 | 2.6833 | No
217754508 | Ground Loop | DAIKIN | WSTV030F1*H*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833 | No
217754511 | Ground Loop | DAIKIN | WSTV036E1*H*C |  | 39100 | 21.12 | 25600 | 3.68 | 3.2583 | No
217754512 | Ground Loop | DAIKIN | WSTV036F1*H*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583 | No
217754515 | Ground Loop | DAIKIN | WSTV042E1*H*C |  | 44800 | 19.54 | 27600 | 3.74 | 3.7333 | No
217754516 | Ground Loop | DAIKIN | WSTV042F1*H*C |  | 44800 | 19.15 | 27600 | 3.66 | 3.7333 | No
217754519 | Ground Loop | DAIKIN | WSTV048E1*H*C |  | 52400 | 20.17 | 35200 | 3.9 | 4.3667 | No
217754520 | Ground Loop | DAIKIN | WSTV048F1*H*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667 | No
217754523 | Ground Loop | DAIKIN | WSTV060E1*H*C |  | 63100 | 19.6 | 46800 | 4.1 | 5.2583 | No
217754524 | Ground Loop | DAIKIN | WSTV060F1*H*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583 | No
217754527 | Ground Loop | DAIKIN | WSTV070E1*H*C |  | 74600 | 19 | 56000 | 4 | 6.2167 | No
217754528 | Ground Loop | DAIKIN | WSTV070F1*H*C |  | 74600 | 18.62 | 56000 | 3.92 | 6.2167 | No
217754535 | Ground Loop | DAIKIN | WSMH024F1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
217754536 | Ground Loop | DAIKIN | WSMH024K1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
217754539 | Ground Loop | DAIKIN | WSMH024F1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
217754540 | Ground Loop | DAIKIN | WSMH024K1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
217754543 | Ground Loop | DAIKIN | WSMH024F1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
217754544 | Ground Loop | DAIKIN | WSMH024K1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
217754547 | Ground Loop | DAIKIN | WSMH030F1*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333 | No
217754548 | Ground Loop | DAIKIN | WSMH030K1*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333 | No
217351121 | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351122 | Ground Loop | GEO-THERMAL SPLIT | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351671 | Ground Loop | BOSCH | RP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | Yes
217351672 | Ground Loop | BOSCH | RP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | Yes
217351673 | Ground Loop | BOSCH | RP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | Yes
217351674 | Ground Loop | BOSCH | RP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | Yes
217351675 | Ground Loop | BOSCH | RP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | Yes
217351676 | Ground Loop | BOSCH | RP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | Yes
217351677 | Ground Loop | BOSCH | RP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | Yes
217351678 | Ground Loop | BOSCH | RP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | Yes
217351679 | Ground Loop | BOSCH | RP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | Yes
217351680 | Ground Loop | BOSCH | RP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | Yes
217351682 | Ground Loop | BOSCH | RP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | Yes
217351683 | Ground Loop | BOSCH | RP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | Yes
217351684 | Ground Loop | BOSCH | RP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3 | Yes
217351692 | Ground Loop | FHP | CP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | No
217351693 | Ground Loop | FHP | CP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | No
217351694 | Ground Loop | FHP | CP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | No
217351695 | Ground Loop | FHP | CP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | No
217351696 | Ground Loop | FHP | CP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | No
217351697 | Ground Loop | FHP | CP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | No
217351698 | Ground Loop | FHP | CP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | No
217351699 | Ground Loop | FHP | CP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | No
217351700 | Ground Loop | FHP | CP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | No
217351701 | Ground Loop | FHP | CP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | No
217351703 | Ground Loop | FHP | CP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | No
217351704 | Ground Loop | FHP | CP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | No
217351705 | Ground Loop | FHP | CP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3 | No
216625640 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625641 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625642 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625643 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625644 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
214772135 | Ground Loop | TRANE | EXHK048B |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214772136 | Ground Loop | TRANE | EXHK0484 |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214772137 | Ground Loop | TRANE | EXHK060B |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214772138 | Ground Loop | TRANE | EXHK0604 |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214772139 | Ground Loop | TRANE | EXHK070B |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772140 | Ground Loop | TRANE | EXHK0704 |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772141 | Ground Loop | TRANE | DXHK024A |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772142 | Ground Loop | TRANE | DXHK036A |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772143 | Ground Loop | TRANE | DXHK048A |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772144 | Ground Loop | TRANE | DXHK060A |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772145 | Ground Loop | TRANE | DXHK070A |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772146 | Ground Loop | TRANE | DXVK024B |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772147 | Ground Loop | TRANE | DXVK0244 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772148 | Ground Loop | TRANE | DXVK036B |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772149 | Ground Loop | TRANE | DXVK0364 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772150 | Ground Loop | TRANE | DXVK048B |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772151 | Ground Loop | TRANE | DXVK0484 |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772152 | Ground Loop | TRANE | DXVK060B |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772153 | Ground Loop | TRANE | DXVK0604 |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772154 | Ground Loop | TRANE | DXVK070B |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772155 | Ground Loop | TRANE | DXVK0704 |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772156 | Ground Loop | TRANE | DXHK024B |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772157 | Ground Loop | TRANE | DXHK0244 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772158 | Ground Loop | TRANE | DXHK036B |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772159 | Ground Loop | TRANE | DXHK0364 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772160 | Ground Loop | TRANE | DXHK048B |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772161 | Ground Loop | TRANE | DXHK0484 |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772162 | Ground Loop | TRANE | DXHK060B |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772163 | Ground Loop | TRANE | DXHK0604 |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772164 | Ground Loop | TRANE | DXHK070B |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772165 | Ground Loop | TRANE | DXHK0704 |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772166 | Ground Loop | TRANE | DXVK0247 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772167 | Ground Loop | TRANE | DXVK0367 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772168 | Ground Loop | TRANE | DXHK0247 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772169 | Ground Loop | TRANE | DXHK0367 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214773312 | Ground Loop | TRANE | GEVK090 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667 | No
214776121 | Ground Loop | TRANE | GEVK120 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85 | No
214776125 | Ground Loop | TRANE | GEVK0904 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667 | No
214776126 | Ground Loop | TRANE | GEVK0908 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667 | No
214776135 | Ground Loop | TRANE | GEVK1203 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85 | No
214776136 | Ground Loop | TRANE | GEVK1208 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85 | No
10346238 | Ground Loop | HYDRON MODULE | HZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346239 | Ground Loop | TETCO | TZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346240 | Ground Loop | GEOCOMFORT | GZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346241 | Ground Loop | HYDRON MODULE | HZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346242 | Ground Loop | TETCO | TZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346243 | Ground Loop | GEOCOMFORT | GZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346244 | Ground Loop | HYDRON MODULE | HZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346245 | Ground Loop | TETCO | TZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346246 | Ground Loop | GEOCOMFORT | GZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346247 | Ground Loop | HYDRON MODULE | HZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346248 | Ground Loop | TETCO | TZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346253 | Ground Loop | GEOCOMFORT | GZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | Yes
10346254 | Ground Loop | HYDRON MODULE | HZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | Yes
10346255 | Ground Loop | TETCO | TZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | Yes
10346256 | Ground Loop | GEOCOMFORT | GZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346257 | Ground Loop | HYDRON MODULE | HZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346258 | Ground Loop | TETCO | TZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346259 | Ground Loop | GEOCOMFORT | GZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346260 | Ground Loop | HYDRON MODULE | HZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346261 | Ground Loop | TETCO | TZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10384616 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ070H1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | Yes
206194177 | Ground Loop | Johnson Controls | JSH/V/D070C*K B |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833 | No
206194178 | Ground Loop | SKYMARK | JSH/V/D070C*K C |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833 | No
206199262 | Ground Loop | RHEEM | RPVV/H/D026D |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | Yes
206199264 | Ground Loop | RHEEM | RPVV/H/D049D |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | Yes
206199265 | Ground Loop | RHEEM | RPVV/H/D064D |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | Yes
206223145 | Ground Loop | ClimateMaster | TRT060D |  | 64500 | 17.9 | 46000 | 3.7 | 5.375 | No
206223146 | Ground Loop | CENTURY | HZS024B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
206223147 | Ground Loop | COMFORT-AIRE | HZS024B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
206223148 | Ground Loop | CENTURY | HZS024B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
206223149 | Ground Loop | COMFORT-AIRE | HZS024B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
206223150 | Ground Loop | CENTURY | HZS036B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
206223151 | Ground Loop | COMFORT-AIRE | HZS036B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
206229666 | Ground Loop | BOSCH | EP024-1HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229667 | Ground Loop | BOSCH | EP024-2HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229668 | Ground Loop | BOSCH | EP024-3HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229669 | Ground Loop | BOSCH | EP024-4HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229674 | Ground Loop | FHP | EP024-1HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229675 | Ground Loop | FHP | EP024-2HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229676 | Ground Loop | FHP | EP024-3HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229677 | Ground Loop | FHP | EP024-4HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229682 | Ground Loop | CARRIER | 50PSH/V024**C3/CA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229683 | Ground Loop | CARRIER | 50PSH/V024**C4/DA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229684 | Ground Loop | CARRIER | 50PSH/V024**C5/EA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229685 | Ground Loop | CARRIER | 50PSH/V024**C6/FA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
215400104 | Ground Loop | DAIKIN | WSMV030E1*G/J*P |  | 29500 | 19.36 | 21300 | 3.62 | 2.4583 | No
215400108 | Ground Loop | DAIKIN | WSMV030E1*G/J*T |  | 29800 | 19.77 | 21500 | 3.65 | 2.4833 | No
215400112 | Ground Loop | DAIKIN | WSMV030E1*G/J*C |  | 29800 | 19.77 | 21500 | 3.65 | 2.4833 | No
215400116 | Ground Loop | DAIKIN | WSMV036E1*G/J*P |  | 37600 | 19.36 | 28000 | 3.69 | 3.1333 | No
215400120 | Ground Loop | DAIKIN | WSMV036E1*G/J*T |  | 37500 | 19.9 | 28000 | 3.82 | 3.125 | No
215400121 | Ground Loop | DAIKIN | WSMV036F3*G/J*T |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917 | No
215400124 | Ground Loop | DAIKIN | WSMV036E1*G/J*C |  | 37500 | 19.9 | 28000 | 3.82 | 3.125 | No
215400125 | Ground Loop | DAIKIN | WSMV036F3*G/J*C |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917 | No
215400132 | Ground Loop | DAIKIN | WSMV042E1*G/J*T |  | 43000 | 19.86 | 30000 | 3.66 | 3.5833 | No
215400136 | Ground Loop | DAIKIN | WSMV042E1*G/J*C |  | 43000 | 19.86 | 30000 | 3.66 | 3.5833 | No
215400140 | Ground Loop | DAIKIN | WSMV048E1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
215400141 | Ground Loop | DAIKIN | WSMV048F3*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
208556818 | Ground Loop | GEOCOMFORT | GRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417 | Yes
208556821 | Ground Loop | HYDRON MODULE | HRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417 | Yes
208556822 | Ground Loop | TETCO | TRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417 | Yes
208556825 | Ground Loop | GEOCOMFORT | GRT048 | EED048 | 49800 | 17.4 | 38200 | 3.8 | 4.15 | Yes
208556827 | Ground Loop | HYDRON MODULE | HRT048 | EED048 | 49800 | 17.4 | 38200 | 3.8 | 4.15 | Yes
208556829 | Ground Loop | TETCO | TRT048 | EED060 | 49800 | 17.4 | 38200 | 3.8 | 4.15 | Yes
208556831 | Ground Loop | GEOCOMFORT | GRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333 | Yes
208556832 | Ground Loop | HYDRON MODULE | HRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333 | Yes
208556834 | Ground Loop | TETCO | TRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333 | Yes
208771547 | Ground Loop | HYDROTECH | WSV6012B* |  | 12500 | 19 | 9000 | 3.6 | 1.0417 | Yes
208771548 | Ground Loop | HYDROTECH | WSV6024B* |  | 24000 | 18 | 17500 | 3.6 | 2 | Yes
208771549 | Ground Loop | HYDROTECH | WSV6030B* |  | 33500 | 17.5 | 25000 | 3.6 | 2.7917 | Yes
208856966 | Ground Loop | HYDROTECH | WSV6060B* |  | 63000 | 18 | 42500 | 3.6 | 5.25 | Yes
208856967 | Ground Loop | HYDROTECH | WSV6072B* |  | 73500 | 18 | 52000 | 3.6 | 6.125 | Yes
208856972 | Ground Loop | AE Air | WSV6012B* |  | 12500 | 19 | 9000 | 3.6 | 1.0417 | Yes
208856973 | Ground Loop | AE Air | WSV6024B* |  | 24000 | 18 | 17500 | 3.6 | 2 | Yes
208856974 | Ground Loop | AE Air | WSV6030B* |  | 33500 | 17.5 | 25000 | 3.6 | 2.7917 | Yes
208856975 | Ground Loop | AE Air | WSV6060B* |  | 63000 | 18 | 42500 | 3.6 | 5.25 | Yes
208856976 | Ground Loop | AE Air | WSV6072B* |  | 73500 | 18 | 52000 | 3.6 | 6.125 | Yes
217903488 | Ground Loop | WaterFurnace | V5R072*D0**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903489 | Ground Loop | WaterFurnace | V5R072*D3**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903490 | Ground Loop | WaterFurnace | V5R072*D3**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903491 | Ground Loop | WaterFurnace | V5R072*D3**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903492 | Ground Loop | WaterFurnace | V5R096*T3**5* |  | 88100 | 18 | 69900 | 3.8 | 7.3417 | No
217903493 | Ground Loop | WaterFurnace | V5R120*T3**5* |  | 119400 | 17.7 | 92000 | 3.8 | 9.95 | No
207312016 | Ground Loop | WaterFurnace | SDV049J1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | Yes
207312018 | Ground Loop | WaterFurnace | SDV072J1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | Yes
207312019 | Ground Loop | WaterFurnace | SDV038K1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3 | Yes
207312171 | Ground Loop | WaterFurnace | NDV/NDH026J1*(1,4) |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207312172 | Ground Loop | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207312173 | Ground Loop | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207312174 | Ground Loop | WaterFurnace | NDV/NDH072J1*(1,4) |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207312176 | Ground Loop | WaterFurnace | NDV/NDH064K1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207312224 | Ground Loop | WaterFurnace | NSV/NSH018J1*(1,4) |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
207312225 | Ground Loop | WaterFurnace | NSV/NSH030J1*(1,4) |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
207312226 | Ground Loop | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | Yes
207312227 | Ground Loop | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
207312228 | Ground Loop | WaterFurnace | NSV/NSH048K1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
207312229 | Ground Loop | WaterFurnace | NSV/NSH060K1*(1,4)* |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
207312230 | Ground Loop | WaterFurnace | NSV/NSH070J1*(1,4) |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
207312265 | Ground Loop | WaterFurnace | NSV/NSH030J1*(0,3) |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | Yes
207312266 | Ground Loop | WaterFurnace | NSV/NSH036K1*(0,3) |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | Yes
207312269 | Ground Loop | WaterFurnace | NSV/NSH060K1*0* |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | Yes
207312271 | Ground Loop | WaterFurnace | NSV/NSH022J1*(1,4) |  | 19200 | 18.7 | 15000 | 4 | 1.6 | Yes
215268735 | Ground Loop | WaterFurnace | V5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
215268736 | Ground Loop | WaterFurnace | V5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
215268737 | Ground Loop | WaterFurnace | V5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268738 | Ground Loop | WaterFurnace | V5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268739 | Ground Loop | WaterFurnace | V5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268740 | Ground Loop | WaterFurnace | V5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268741 | Ground Loop | WaterFurnace | V5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268742 | Ground Loop | WaterFurnace | V5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268743 | Ground Loop | WaterFurnace | V5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268744 | Ground Loop | WaterFurnace | V5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268745 | Ground Loop | WaterFurnace | V5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268746 | Ground Loop | WaterFurnace | V5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268747 | Ground Loop | WaterFurnace | V5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268748 | Ground Loop | WaterFurnace | V5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268749 | Ground Loop | WaterFurnace | V5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268750 | Ground Loop | WaterFurnace | V5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268751 | Ground Loop | WaterFurnace | V5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268752 | Ground Loop | WaterFurnace | V5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268753 | Ground Loop | WaterFurnace | V5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268754 | Ground Loop | WaterFurnace | V5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268755 | Ground Loop | WaterFurnace | V5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268756 | Ground Loop | WaterFurnace | V5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268757 | Ground Loop | WaterFurnace | V5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268758 | Ground Loop | WaterFurnace | V5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268759 | Ground Loop | WaterFurnace | V5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268760 | Ground Loop | WaterFurnace | V5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268761 | Ground Loop | WaterFurnace | V5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268762 | Ground Loop | WaterFurnace | V5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268763 | Ground Loop | WaterFurnace | V5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268764 | Ground Loop | WaterFurnace | V5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268765 | Ground Loop | WaterFurnace | V5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268766 | Ground Loop | WaterFurnace | V5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268767 | Ground Loop | WaterFurnace | V5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268768 | Ground Loop | WaterFurnace | V5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268769 | Ground Loop | WaterFurnace | V5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268770 | Ground Loop | WaterFurnace | V5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268771 | Ground Loop | WaterFurnace | V5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268772 | Ground Loop | WaterFurnace | V5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268773 | Ground Loop | WaterFurnace | V5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268774 | Ground Loop | WaterFurnace | V5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268775 | Ground Loop | WaterFurnace | V5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268776 | Ground Loop | WaterFurnace | V5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268777 | Ground Loop | WaterFurnace | V5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268778 | Ground Loop | WaterFurnace | V5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268779 | Ground Loop | WaterFurnace | V5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268780 | Ground Loop | WaterFurnace | V5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
202434117 | Ground Loop | BOSCH | LV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434119 | Ground Loop | BOSCH | LV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434121 | Ground Loop | BOSCH | LV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434123 | Ground Loop | BOSCH | LV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434125 | Ground Loop | BOSCH | LV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434127 | Ground Loop | BOSCH | LV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
215224679 | Ground Loop | BOSCH | RF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
215224680 | Ground Loop | BOSCH | RF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
215224681 | Ground Loop | BOSCH | RF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
215224682 | Ground Loop | BOSCH | RF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
215224683 | Ground Loop | BOSCH | RF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
215224684 | Ground Loop | BOSCH | RF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
215224685 | Ground Loop | BOSCH | RF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | Yes
215224686 | Ground Loop | BOSCH | RF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | Yes
215224687 | Ground Loop | BOSCH | RF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224688 | Ground Loop | BOSCH | RF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224691 | Ground Loop | BOSCH | RF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224692 | Ground Loop | BOSCH | RF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224782 | Ground Loop | CARRIER | GBA18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224783 | Ground Loop | BRYANT | GBA18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224784 | Ground Loop | CARRIER | GBA18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224785 | Ground Loop | BRYANT | GBA18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224786 | Ground Loop | CARRIER | GBA24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224787 | Ground Loop | BRYANT | GBA24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224788 | Ground Loop | CARRIER | GBA24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224789 | Ground Loop | BRYANT | GBA24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
216743636 | Ground Loop | BOSCH | CP024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743637 | Ground Loop | BOSCH-GEO | RP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216743638 | Ground Loop | BOSCH | CP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216743639 | Ground Loop | BOSCH | CP036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
202443461 | Ground Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
202443462 | Ground Loop | GeoSmart Energy | GSZ042*1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
202443463 | Ground Loop | GeoSmart Energy | GTZ038*1*J | SAH038* | 36000 | 19 | 27900 | 4 | 3 | No
202443470 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
202443471 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
202443472 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
202443473 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST038**1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3 | Yes
6501954 | Ground Loop | GEOSTAR | GBV/GBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501955 | Ground Loop | GEOSTAR | GBV/GBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501957 | Ground Loop | GEOSTAR | GBV/GBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501958 | Ground Loop | GEOSTAR | GBV/GBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501961 | Ground Loop | GEOSTAR | GBV/GBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501962 | Ground Loop | GEOSTAR | GBV/GBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501964 | Ground Loop | GEOSTAR | GBV/GBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501965 | Ground Loop | GEOSTAR | GBV/GBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501967 | Ground Loop | GEOSTAR | GBV/GBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501968 | Ground Loop | GEOSTAR | GBV/GBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501970 | Ground Loop | GEOSTAR | GBV/GBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501971 | Ground Loop | GEOSTAR | GBV/GBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501972 | Ground Loop | GEOSTAR | GBV/GBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207200576 | Ground Loop | GeoSmart Energy | GTZ026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207200577 | Ground Loop | GeoSmart Energy | GTZ026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
207200578 | Ground Loop | GeoSmart Energy | GTS026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207200579 | Ground Loop | GeoSmart Energy | GTS026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207200580 | Ground Loop | GeoSmart Energy | GTS049*1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207200581 | Ground Loop | GeoSmart Energy | GTS049*1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207200582 | Ground Loop | GeoSmart Energy | GTS064*1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207200583 | Ground Loop | GeoSmart Energy | GTS064*1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207200586 | Ground Loop | GeoSmart Energy | GSZ022*1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
207200587 | Ground Loop | GeoSmart Energy | GSZ022*1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
207200588 | Ground Loop | GeoSmart Energy | GSZ030*1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
207200589 | Ground Loop | GeoSmart Energy | GSZ030*1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
207200590 | Ground Loop | GeoSmart Energy | GSZ048*1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
207200591 | Ground Loop | GeoSmart Energy | GSZ048*1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
207200592 | Ground Loop | GeoSmart Energy | GSZ060*1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
207200593 | Ground Loop | GeoSmart Energy | GSZ060*1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
207200594 | Ground Loop | GeoSmart Energy | GSZ070*1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207200596 | Ground Loop | GeoSmart Energy | GSZ070*1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | Yes
207200598 | Ground Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
207200599 | Ground Loop | GeoSmart Energy | GSZ042*1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
207200600 | Ground Loop | GeoSmart Energy | GTZ038*1*J | SAH038* | 36000 | 19 | 27900 | 4 | 3 | No
207200601 | Ground Loop | GeoSmart Energy | GTZ049*1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207200602 | Ground Loop | GeoSmart Energy | GTZ049*1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
207200603 | Ground Loop | GeoSmart Energy | GTS064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207200604 | Ground Loop | GeoSmart Energy | GTS064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
207200605 | Ground Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
207200606 | Ground Loop | GeoSmart Energy | GSZ042*1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
207200607 | Ground Loop | GeoSmart Energy | GTZ038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
217193306 | Ground Loop | WaterFurnace | V7A(V/H)024*V0**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125 | No
217193307 | Ground Loop | WaterFurnace | V7A(V/H)036*V0**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25 | No
217193308 | Ground Loop | WaterFurnace | V7A(V/H)048*V0**1* |  | 48000 | 20 | 38000 | 3.8 | 4 | No
217193309 | Ground Loop | WaterFurnace | V7A(V/H)060*V0**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083 | No
217193552 | Ground Loop | WaterFurnace | V7A(V/H)024*V3**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125 | No
217193553 | Ground Loop | WaterFurnace | V7A(V/H)024*V4**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125 | No
217193554 | Ground Loop | WaterFurnace | V7A(V/H)036*V3**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25 | No
217193555 | Ground Loop | WaterFurnace | V7A(V/H)036*V4**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25 | No
217193556 | Ground Loop | WaterFurnace | V7A(V/H)048*V3**1* |  | 48000 | 20 | 38000 | 3.8 | 4 | No
217193557 | Ground Loop | WaterFurnace | V7A(V/H)048*V4**1* |  | 48000 | 20 | 38000 | 3.8 | 4 | No
217193558 | Ground Loop | WaterFurnace | V7A(V/H)060*V3**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083 | No
217193559 | Ground Loop | WaterFurnace | V7A(V/H)060*V4**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083 | No
217212043 | Ground Loop | FHP | CP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212044 | Ground Loop | FHP | CP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212045 | Ground Loop | FHP | CP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212046 | Ground Loop | FHP | CP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212048 | Ground Loop | FHP | CP024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212049 | Ground Loop | FHP | CP024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212050 | Ground Loop | FHP | CP024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212051 | Ground Loop | FHP | CP024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212052 | Ground Loop | FHP | CP024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212054 | Ground Loop | FHP | CP024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212055 | Ground Loop | FHP | CP024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212056 | Ground Loop | FHP | CP024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212057 | Ground Loop | FHP | CP024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212059 | Ground Loop | FHP | CP024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212060 | Ground Loop | FHP | CP024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212061 | Ground Loop | FHP | CP024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212062 | Ground Loop | FHP | CP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
217212064 | Ground Loop | FHP | CP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217212065 | Ground Loop | FHP | CP036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
217212066 | Ground Loop | FHP | CP036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217212067 | Ground Loop | FHP | CP036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
7795949 | Ground Loop | GEOCOMFORT | GVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795950 | Ground Loop | HYDRON MODULE | HVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795951 | Ground Loop | TETCO | TVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795952 | Ground Loop | GEOCOMFORT | GVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795953 | Ground Loop | HYDRON MODULE | HVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795954 | Ground Loop | TETCO | TVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
8000290 | Ground Loop | GEOCOOL | GCHP01024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | No
8000291 | Ground Loop | GEOCOOL | GCHP01031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | No
8000292 | Ground Loop | GEOCOOL | GCHP01036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | No
8000293 | Ground Loop | GEOCOOL | GCHP01041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | No
8077723 | Ground Loop | GEOCOMFORT | GYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | Yes
8077724 | Ground Loop | HYDRON MODULE | HYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | Yes
8077725 | Ground Loop | TETCO | TYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | Yes
8077726 | Ground Loop | GEOCOMFORT | GYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077727 | Ground Loop | HYDRON MODULE | HYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077728 | Ground Loop | TETCO | TYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077729 | Ground Loop | GEOCOMFORT | GYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077730 | Ground Loop | HYDRON MODULE | HYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077731 | Ground Loop | TETCO | TYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077735 | Ground Loop | GEOCOMFORT | GYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | Yes
8077736 | Ground Loop | HYDRON MODULE | HYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | Yes
8077737 | Ground Loop | TETCO | TYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | Yes
8077738 | Ground Loop | GEOCOMFORT | GYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077739 | Ground Loop | HYDRON MODULE | HYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077740 | Ground Loop | TETCO | TYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077741 | Ground Loop | GEOCOMFORT | GYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077742 | Ground Loop | HYDRON MODULE | HYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077743 | Ground Loop | TETCO | TYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
205767612 | Ground Loop | ClimateMaster | TZV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
205767615 | Ground Loop | ClimateMaster | QEV/H/D0930 |  | 24000 | 24.3 | 30000 | 3.6 | 2 | Yes
205767616 | Ground Loop | ClimateMaster | TYV/H060B |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | No
215268669 | Ground Loop | WaterFurnace | V5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268670 | Ground Loop | WaterFurnace | V5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268671 | Ground Loop | WaterFurnace | V5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268672 | Ground Loop | WaterFurnace | V5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268673 | Ground Loop | WaterFurnace | V5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268675 | Ground Loop | WaterFurnace | V5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
215268676 | Ground Loop | WaterFurnace | V5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
215268677 | Ground Loop | WaterFurnace | V5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
215268678 | Ground Loop | WaterFurnace | V5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
215268679 | Ground Loop | WaterFurnace | V5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
215268680 | Ground Loop | WaterFurnace | V5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
215268681 | Ground Loop | WaterFurnace | V5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
215268682 | Ground Loop | WaterFurnace | V5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268683 | Ground Loop | WaterFurnace | V5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268684 | Ground Loop | WaterFurnace | V5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268685 | Ground Loop | WaterFurnace | V5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268686 | Ground Loop | WaterFurnace | V5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268687 | Ground Loop | WaterFurnace | V5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268688 | Ground Loop | WaterFurnace | V5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268689 | Ground Loop | WaterFurnace | V5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268690 | Ground Loop | WaterFurnace | V5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268691 | Ground Loop | WaterFurnace | V5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268692 | Ground Loop | WaterFurnace | V5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268693 | Ground Loop | WaterFurnace | V5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268694 | Ground Loop | WaterFurnace | V5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268695 | Ground Loop | WaterFurnace | V5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268696 | Ground Loop | WaterFurnace | V5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268697 | Ground Loop | WaterFurnace | V5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268698 | Ground Loop | WaterFurnace | V5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268699 | Ground Loop | WaterFurnace | V5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268700 | Ground Loop | WaterFurnace | V5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268701 | Ground Loop | WaterFurnace | V5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268702 | Ground Loop | WaterFurnace | V5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268703 | Ground Loop | WaterFurnace | V5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268704 | Ground Loop | WaterFurnace | V5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268705 | Ground Loop | WaterFurnace | V5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268706 | Ground Loop | WaterFurnace | V5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268707 | Ground Loop | WaterFurnace | V5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268708 | Ground Loop | WaterFurnace | V5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268709 | Ground Loop | WaterFurnace | V5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268710 | Ground Loop | WaterFurnace | V5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268711 | Ground Loop | WaterFurnace | V5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268712 | Ground Loop | WaterFurnace | V5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268713 | Ground Loop | WaterFurnace | V5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268714 | Ground Loop | WaterFurnace | V5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268715 | Ground Loop | WaterFurnace | V5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268716 | Ground Loop | WaterFurnace | V5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268717 | Ground Loop | WaterFurnace | V5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268718 | Ground Loop | WaterFurnace | V5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268719 | Ground Loop | WaterFurnace | V5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268720 | Ground Loop | WaterFurnace | V5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268721 | Ground Loop | WaterFurnace | V5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268722 | Ground Loop | WaterFurnace | V5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268723 | Ground Loop | WaterFurnace | V5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268724 | Ground Loop | WaterFurnace | V5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216759824 | Ground Loop | GEOSTAR | G5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216759826 | Ground Loop | WaterFurnace | W5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216759827 | Ground Loop | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216759828 | Ground Loop | WaterFurnace | W5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216759829 | Ground Loop | WaterFurnace | W5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216759831 | Ground Loop | GEOSTAR | G5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | No
216759832 | Ground Loop | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | No
216759833 | Ground Loop | GEOSTAR | G5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | No
216759834 | Ground Loop | GEOSTAR | G5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | No
216767321 | Ground Loop | TETCO | TVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
213502525 | Ground Loop | DAIKIN | WSMH015A1*G/J*P |  | 16000 | 20.1 | 12100 | 4 | 1.3333 | No
213502526 | Ground Loop | DAIKIN | WSMH015A1*G/J*T |  | 16300 | 21.1 | 11800 | 4.1 | 1.3583 | No
213502527 | Ground Loop | DAIKIN | WSMH015A1*G/J*C |  | 16300 | 21.1 | 11800 | 4.1 | 1.3583 | No
213502531 | Ground Loop | DAIKIN | WSMH015E1*G/J*P |  | 16000 | 20.1 | 12300 | 4 | 1.3333 | No
213502532 | Ground Loop | DAIKIN | WSMH015E1*G/J*T |  | 16300 | 21.1 | 12000 | 4.1 | 1.3583 | No
213502533 | Ground Loop | DAIKIN | WSMH015E1*G/J*C |  | 16300 | 21.1 | 12000 | 4.1 | 1.3583 | No
213502537 | Ground Loop | DAIKIN | WSMH015J1*G/J*P |  | 16000 | 18.9 | 12300 | 3.9 | 1.3333 | No
213502538 | Ground Loop | DAIKIN | WSMH015J1*G/J*T |  | 16300 | 19.9 | 12000 | 4 | 1.3583 | No
213502539 | Ground Loop | DAIKIN | WSMH015J1*G/J*C |  | 16300 | 19.9 | 12000 | 4 | 1.3583 | No
213502543 | Ground Loop | DAIKIN | WSMH019E1*G/J*P |  | 20500 | 18.8 | 15600 | 3.8 | 1.7083 | No
213502544 | Ground Loop | DAIKIN | WSMH019E1*G/J*T |  | 20700 | 19.5 | 15300 | 3.9 | 1.725 | No
213502545 | Ground Loop | DAIKIN | WSMH019E1*G/J*C |  | 20700 | 19.5 | 15300 | 3.9 | 1.725 | No
213502549 | Ground Loop | DAIKIN | WSMH019J1*G/J*P |  | 20500 | 18.8 | 15600 | 3.7 | 1.7083 | No
213502550 | Ground Loop | DAIKIN | WSMH019J1*G/J*T |  | 20700 | 19.5 | 15300 | 3.8 | 1.725 | No
213502551 | Ground Loop | DAIKIN | WSMH019J1*G/J*C |  | 20700 | 19.5 | 15300 | 3.8 | 1.725 | No
213502555 | Ground Loop | DAIKIN | WSMH024E1*G/J*P |  | 25600 | 19.2 | 18400 | 3.9 | 2.1333 | No
213502556 | Ground Loop | DAIKIN | WSMH024E1*G/J*T |  | 25800 | 20.5 | 18200 | 3.9 | 2.15 | No
213502557 | Ground Loop | DAIKIN | WSMH024E1*G/J*C |  | 25800 | 20.5 | 18200 | 3.9 | 2.15 | No
213502561 | Ground Loop | DAIKIN | WSMH030E1*G/J*P |  | 29200 | 19 | 22200 | 3.8 | 2.4333 | No
213502562 | Ground Loop | DAIKIN | WSMH030E1*G/J*T |  | 29500 | 20.6 | 21900 | 4 | 2.4583 | No
213502563 | Ground Loop | DAIKIN | WSMH030E1*G/J*C |  | 29500 | 20.6 | 21900 | 4 | 2.4583 | No
213502567 | Ground Loop | DAIKIN | WSMH036E1*G/J*P |  | 37800 | 18.8 | 30700 | 3.9 | 3.15 | No
213502568 | Ground Loop | DAIKIN | WSMH036E1*G/J*T |  | 38000 | 19.9 | 30000 | 4 | 3.1667 | No
213502569 | Ground Loop | DAIKIN | WSMH036E1*G/J*C |  | 38000 | 19.9 | 30000 | 4 | 3.1667 | No
215824878 | Ground Loop | ICE AIR LLC | 8VSHPGE09**C |  | 11000 | 21.3 | 6500 | 3.64 | 0.91667 | No
215824879 | Ground Loop | ICE AIR LLC | 8VSHPGE12**C |  | 13800 | 20.1 | 9000 | 3.7 | 1.15 | No
215824880 | Ground Loop | ICE AIR LLC | 8VSHPGE15**C |  | 15000 | 17.5 | 10500 | 3.7 | 1.25 | No
215824881 | Ground Loop | ICE AIR LLC | 8VSHPGE18**C |  | 19500 | 18.7 | 13400 | 3.63 | 1.625 | No
215824882 | Ground Loop | ICE AIR LLC | 8VSHPGE24**C |  | 24800 | 18.4 | 17000 | 3.66 | 2.0667 | No
215824883 | Ground Loop | ICE AIR LLC | 8VSHPGE30**C |  | 30000 | 17.3 | 21900 | 3.6 | 2.5 | No
215824884 | Ground Loop | ICE AIR LLC | 8VSHPGE06**C |  | 8800 | 19.6 | 5800 | 3.6 | 0.73333 | No
215827077 | Ground Loop | DAIKIN | WSLH072F1*G/J |  | 73500 | 18 | 53600 | 3.6 | 6.125 | No
215827078 | Ground Loop | DAIKIN | WSLH072K1*G/J |  | 73500 | 18 | 53600 | 3.6 | 6.125 | No
215827083 | Ground Loop | DAIKIN | WSLH096F1*G/J |  | 98000 | 17.9 | 72000 | 3.6 | 8.1667 | No
215827084 | Ground Loop | DAIKIN | WSLH096K1*G/J |  | 98000 | 17.9 | 72000 | 3.6 | 8.1667 | No
203372397 | Ground Loop | HEIL | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
203372398 | Ground Loop | ARCOAIRE | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372399 | Ground Loop | KEEPRITE | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372400 | Ground Loop | TEMPSTAR | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372401 | Ground Loop | COMFORTMAKER | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372402 | Ground Loop | DAY & NIGHT | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372403 | Ground Loop | HEIL | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
203372404 | Ground Loop | ARCOAIRE | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372405 | Ground Loop | KEEPRITE | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372406 | Ground Loop | TEMPSTAR | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372407 | Ground Loop | COMFORTMAKER | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372408 | Ground Loop | DAY & NIGHT | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372993 | Ground Loop | BOSCH | SM060-1HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
203380957 | Ground Loop | BOSCH | EP018-1VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203380958 | Ground Loop | BOSCH | EP018-2VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203380959 | Ground Loop | BOSCH | EP018-1HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203380960 | Ground Loop | BOSCH | EP018-2HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203380963 | Ground Loop | BOSCH | EP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203380964 | Ground Loop | BOSCH | EP042-3VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203380965 | Ground Loop | BOSCH | EP042-4VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203380966 | Ground Loop | BOSCH | EP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203380967 | Ground Loop | BOSCH | EP042-3HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203380968 | Ground Loop | BOSCH | EP042-4HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203380969 | Ground Loop | BOSCH | EP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203380970 | Ground Loop | BOSCH | EP048-3VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203380971 | Ground Loop | BOSCH | EP048-4VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203380972 | Ground Loop | BOSCH | EP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203380973 | Ground Loop | BOSCH | EP048-3HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203380974 | Ground Loop | BOSCH | EP048-4HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383876 | Ground Loop | CARRIER | 50PSV018***3/CA |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203383877 | Ground Loop | CARRIER | 50PSV018***4/DA |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203383878 | Ground Loop | CARRIER | 50PSH018***3/CA |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203383879 | Ground Loop | CARRIER | 50PSH018***4/DA |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203383880 | Ground Loop | CARRIER | 50PSV042***3/CA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383881 | Ground Loop | CARRIER | 50PSV042***5/EA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383882 | Ground Loop | CARRIER | 50PSV042***6/FA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383883 | Ground Loop | CARRIER | 50PSH042***3/CA |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383884 | Ground Loop | CARRIER | 50PSH042***5/EA |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383885 | Ground Loop | CARRIER | 50PSH042***6/FA |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383886 | Ground Loop | CARRIER | 50PSV048***3/CA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383887 | Ground Loop | CARRIER | 50PSV048***5/EA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
202147709 | Ground Loop | GEOCOMFORT | GZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147710 | Ground Loop | HYDRON MODULE | HZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147711 | Ground Loop | TETCO | TZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
215224599 | Ground Loop | CARRIER | 50WD*007***3*(A-H)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224600 | Ground Loop | CARRIER | 50WD*007***3*(J-R)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224601 | Ground Loop | CARRIER | 50WD*007***4*(A-H)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224602 | Ground Loop | CARRIER | 50WD*007***4*(J-R)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224603 | Ground Loop | CARRIER | 50WD*009***3*(A-H)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224604 | Ground Loop | CARRIER | 50WD*009***3*(J-R)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224605 | Ground Loop | CARRIER | 50WD*009***4*(A-H)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224606 | Ground Loop | CARRIER | 50WD*009***4*(J-R)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224607 | Ground Loop | CARRIER | 50WD*012***3*(A-H)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224608 | Ground Loop | CARRIER | 50WD*012***3*(J-R)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224609 | Ground Loop | CARRIER | 50WD*012***4*(A-H)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224610 | Ground Loop | CARRIER | 50WD*012***4*(J-R)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224611 | Ground Loop | CARRIER | 50WD*015***3*(A-H)** |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224612 | Ground Loop | CARRIER | 50WD*015***3*(J-R)** |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
217351811 | Ground Loop | COMFORTMAKER | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351812 | Ground Loop | COMFORTMAKER | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351815 | Ground Loop | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351816 | Ground Loop | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351817 | Ground Loop | COMFORTMAKER | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351819 | Ground Loop | COMFORTMAKER | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351820 | Ground Loop | COMFORTMAKER | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351822 | Ground Loop | COMFORTMAKER | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351823 | Ground Loop | COMFORTMAKER | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351824 | Ground Loop | COMFORTMAKER | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351825 | Ground Loop | COMFORTMAKER | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351826 | Ground Loop | COMFORTMAKER | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351828 | Ground Loop | COMFORTMAKER | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351829 | Ground Loop | COMFORTMAKER | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351830 | Ground Loop | COMFORTMAKER | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
216767322 | Ground Loop | TETCO | TVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
216767323 | Ground Loop | TETCO | TVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
216767324 | Ground Loop | TETCO | TVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
216767325 | Ground Loop | TETCO | TVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917 | Yes
216767326 | Ground Loop | TETCO | TYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
216767327 | Ground Loop | TETCO | TYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083 | Yes
216767328 | Ground Loop | TETCO | TYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325 | Yes
216767329 | Ground Loop | TETCO | TVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
216767330 | Ground Loop | TETCO | TYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583 | Yes
216767332 | Ground Loop | TETCO | TYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583 | Yes
216767333 | Ground Loop | HYDRON MODULE | HVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
216767334 | Ground Loop | HYDRON MODULE | HVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
216767335 | Ground Loop | HYDRON MODULE | HVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
216767336 | Ground Loop | HYDRON MODULE | HVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
216767337 | Ground Loop | HYDRON MODULE | HVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917 | Yes
216767338 | Ground Loop | HYDRON MODULE | HYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
216767339 | Ground Loop | HYDRON MODULE | HYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083 | Yes
216767340 | Ground Loop | HYDRON MODULE | HYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325 | Yes
216767341 | Ground Loop | HYDRON MODULE | HVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
216767342 | Ground Loop | HYDRON MODULE | HYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583 | Yes
216767344 | Ground Loop | HYDRON MODULE | HYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583 | Yes
216772562 | Ground Loop | Enertech | EBS018* | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
216772563 | Ground Loop | Enertech | EBT024* | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
216772564 | Ground Loop | Enertech | EBT036* | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
216772565 | Ground Loop | Enertech | EBT048* | EAD048 | 47800 | 17.3 | 41000 | 3.6 | 3.9833 | Yes
7022707 | Ground Loop | GeoSmart Energy | ZS060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
7022708 | Ground Loop | GEOSTAR | ZS060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
7167375 | Ground Loop | BRYANT | GB024H/V******1*X1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
7167376 | Ground Loop | CARRIER | GB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
7167377 | Ground Loop | BRYANT | GB030H/V******1*X1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
7167378 | Ground Loop | CARRIER | GB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
7167538 | Ground Loop | CARRIER | 50PTD/H/V024***3/CA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7167539 | Ground Loop | CARRIER | 50PTD/H/V024***5/EA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
207323881 | Ground Loop | WaterFurnace | NDZ026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
207323882 | Ground Loop | WaterFurnace | NDZ026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
207323883 | Ground Loop | WaterFurnace | NDS026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207323884 | Ground Loop | WaterFurnace | NDS026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207323885 | Ground Loop | WaterFurnace | NDZ038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207323886 | Ground Loop | WaterFurnace | NDZ038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207323887 | Ground Loop | WaterFurnace | NDS038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207323888 | Ground Loop | WaterFurnace | NDZ049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
207323889 | Ground Loop | WaterFurnace | NDZ049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
207323890 | Ground Loop | WaterFurnace | NDS049H1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207323891 | Ground Loop | WaterFurnace | NDS049H1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
214823447 | Ground Loop | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | Yes
214823448 | Ground Loop | GeoSmart Energy | S5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | Yes
214823449 | Ground Loop | GeoSmart Energy | S5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | Yes
214823450 | Ground Loop | GeoSmart Energy | S5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | Yes
214823451 | Ground Loop | GeoSmart Energy | S5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | Yes
214823480 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | Yes
214823481 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | Yes
214823482 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | Yes
214823484 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | Yes
214823485 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | Yes
214823486 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | Yes
214823487 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | Yes
214823488 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | Yes
214837733 | Ground Loop | BOSCH | EC072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837734 | Ground Loop | BOSCH | EC072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837735 | Ground Loop | BOSCH | EC072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837736 | Ground Loop | BOSCH | EC096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837737 | Ground Loop | BOSCH | EC096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837738 | Ground Loop | BOSCH | EC096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837742 | Ground Loop | CARRIER | 50H/VQP072***3C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837743 | Ground Loop | CARRIER | 50H/VQP072***5C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837744 | Ground Loop | CARRIER | 50H/VQP072***6C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837745 | Ground Loop | CARRIER | 50H/VQP096***3C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837746 | Ground Loop | CARRIER | 50H/VQP096***5C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837747 | Ground Loop | CARRIER | 50H/VQP096***6C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
216569713 | Ground Loop | GeoCool | GCHPV/H/D024BT**A*** |  | 26400 | 17.95 | 19000 | 4.2 | 2.2 | No
206438781 | Ground Loop | FHP | EP009-1HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438782 | Ground Loop | FHP | EP009-2HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438783 | Ground Loop | FHP | EP012-1HZ/VT*-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438784 | Ground Loop | FHP | EP015-1HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438785 | Ground Loop | FHP | EP015-2HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438786 | Ground Loop | FHP | EP030-2HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438787 | Ground Loop | FHP | EP030-4HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438788 | Ground Loop | FHP | EP030-3HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438789 | Ground Loop | FHP | EP030-1HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438790 | Ground Loop | FHP | EP060-4HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438791 | Ground Loop | FHP | EP060-3HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438792 | Ground Loop | FHP | EP060-1HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438793 | Ground Loop | FHP | EP070-1HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438794 | Ground Loop | FHP | EP070-3HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438795 | Ground Loop | FHP | EP070-4HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438813 | Ground Loop | FHP | EP012-1VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438814 | Ground Loop | FHP | EP012-1HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438817 | Ground Loop | FHP | EP012-0VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438818 | Ground Loop | FHP | EP012-2VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438819 | Ground Loop | FHP | EP012-0HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438820 | Ground Loop | FHP | EP012-2HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
7170606 | Ground Loop | GEOCOMFORT | GVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | Yes
7170607 | Ground Loop | HYDRON MODULE | HVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | Yes
7170608 | Ground Loop | TETCO | TVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | Yes
7170609 | Ground Loop | GEOCOMFORT | GVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | Yes
7170610 | Ground Loop | HYDRON MODULE | HVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | Yes
7170611 | Ground Loop | TETCO | TVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | Yes
7170612 | Ground Loop | GEOCOMFORT | GVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | Yes
7170613 | Ground Loop | HYDRON MODULE | HVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | Yes
7170614 | Ground Loop | TETCO | TVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | Yes
10581121 | Ground Loop | GEOSTAR | 107H064**1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083 | No
207323892 | Ground Loop | WaterFurnace | NDZ064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
207323893 | Ground Loop | WaterFurnace | NDZ064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
207323894 | Ground Loop | WaterFurnace | NDS064H1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207323895 | Ground Loop | WaterFurnace | NDS064H1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207323900 | Ground Loop | WaterFurnace | NDS038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207323901 | Ground Loop | WaterFurnace | NSZ022H1* | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
207323902 | Ground Loop | WaterFurnace | NSZ030H1* | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
207323903 | Ground Loop | WaterFurnace | NSZ036J1* | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
207323904 | Ground Loop | WaterFurnace | NSZ042J1* | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
207323905 | Ground Loop | WaterFurnace | NSZ048J1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
207323906 | Ground Loop | WaterFurnace | NSZ048J1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
207323907 | Ground Loop | WaterFurnace | NSZ060J1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
207323908 | Ground Loop | WaterFurnace | NSZ060J1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
207323909 | Ground Loop | WaterFurnace | NSZ070H1* | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207323910 | Ground Loop | WaterFurnace | NSZ022H1* | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
207323911 | Ground Loop | WaterFurnace | NSZ030H1* | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
207323912 | Ground Loop | WaterFurnace | NSZ036J1* | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
207323913 | Ground Loop | WaterFurnace | NSZ042J1* | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
207323914 | Ground Loop | WaterFurnace | NSZ070H1* | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207335135 | Ground Loop | GEOSTAR | 101/102J018**1*(1,4)***** |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
207335136 | Ground Loop | GEOSTAR | 101/102J030**1*(1,4)***** |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
207335137 | Ground Loop | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | Yes
207335138 | Ground Loop | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
207335139 | Ground Loop | GEOSTAR | 101/102K048**1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
207335140 | Ground Loop | GEOSTAR | 101/102K060**1*(1,4)****** |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
207335141 | Ground Loop | GEOSTAR | 101/102J070**1*(1,4)***** |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
207335142 | Ground Loop | GEOSTAR | 101/102J026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335143 | Ground Loop | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335144 | Ground Loop | GEOSTAR | 101/102K049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335145 | Ground Loop | GEOSTAR | 101/102K064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335146 | Ground Loop | GEOSTAR | 101/102J072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335147 | Ground Loop | GEOSTAR | 161/162K064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335247 | Ground Loop | GEOSTAR | 101/102J022**1*(1,4)***** |  | 19200 | 18.7 | 19200 | 4 | 1.6 | Yes
207335249 | Ground Loop | GEOSTAR | 161/162J026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335251 | Ground Loop | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335253 | Ground Loop | GEOSTAR | 161/162K049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335255 | Ground Loop | GEOSTAR | 161/162J072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335335 | Ground Loop | GEOSTAR | 111J049**1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | Yes
207335337 | Ground Loop | GEOSTAR | 111J072**1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | Yes
8332268 | Ground Loop | GEOCOMFORT | GYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
8332358 | Ground Loop | HYDRON MODULE | HYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
8332380 | Ground Loop | TETCO | TYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
8332431 | Ground Loop | GEOCOMFORT | GYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332452 | Ground Loop | HYDRON MODULE | HYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332472 | Ground Loop | TETCO | TYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332525 | Ground Loop | GEOCOMFORT | GYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332545 | Ground Loop | HYDRON MODULE | HYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332563 | Ground Loop | TETCO | TYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8560797 | Ground Loop | 5 SERIES | NSV/NSH060H1*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
8560805 | Ground Loop | 5 SERIES | NSV/NSH060H1*(1,4) |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
8560913 | Ground Loop | GEOCOMFORT | GVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | Yes
8560914 | Ground Loop | HYDRON MODULE | HVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | Yes
8560915 | Ground Loop | TETCO | TVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | Yes
8560916 | Ground Loop | GEOCOMFORT | GVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560917 | Ground Loop | HYDRON MODULE | HVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560918 | Ground Loop | TETCO | TVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560919 | Ground Loop | GEOCOMFORT | GVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560920 | Ground Loop | HYDRON MODULE | HVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560921 | Ground Loop | TETCO | TVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560930 | Ground Loop | GEOCOMFORT | GVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167 | Yes
8560931 | Ground Loop | HYDRON MODULE | HVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167 | Yes
8560932 | Ground Loop | TETCO | TVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167 | Yes
8560938 | Ground Loop | GEOCOMFORT | GVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | Yes
8560939 | Ground Loop | HYDRON MODULE | HVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | Yes
8560940 | Ground Loop | TETCO | TVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | Yes
8560941 | Ground Loop | GEOCOMFORT | GVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | No
8560942 | Ground Loop | HYDRON MODULE | HVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | No
8560943 | Ground Loop | TETCO | TVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | No
8560946 | Ground Loop | GEOCOMFORT | GVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | Yes
8560947 | Ground Loop | HYDRON MODULE | HVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | Yes
8560948 | Ground Loop | TETCO | TVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | Yes
8560949 | Ground Loop | GEOCOMFORT | GVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | No
8560950 | Ground Loop | HYDRON MODULE | HVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | No
8560951 | Ground Loop | TETCO | TVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | No
203113890 | Ground Loop | GEOSTAR | 103J042**1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
203113892 | Ground Loop | GEOSTAR | 103J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
203113894 | Ground Loop | GEOSTAR | 104J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
203143108 | Ground Loop | GEOCOMFORT | GVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | Yes
203143111 | Ground Loop | GEOCOMFORT | GVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143114 | Ground Loop | GEOCOMFORT | GVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143119 | Ground Loop | GEOCOMFORT | GVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143124 | Ground Loop | HYDRON MODULE | HVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | Yes
203143129 | Ground Loop | HYDRON MODULE | HVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143133 | Ground Loop | HYDRON MODULE | HVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143138 | Ground Loop | HYDRON MODULE | HVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143143 | Ground Loop | TETCO | TVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | Yes
203143148 | Ground Loop | TETCO | TVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143153 | Ground Loop | TETCO | TVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143157 | Ground Loop | TETCO | TVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143746 | Ground Loop | GEOCOMFORT | GVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | Yes
203143749 | Ground Loop | GEOCOMFORT | GVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143752 | Ground Loop | GEOCOMFORT | GVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143764 | Ground Loop | HYDRON MODULE | HVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | Yes
203143767 | Ground Loop | HYDRON MODULE | HVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143770 | Ground Loop | HYDRON MODULE | HVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143781 | Ground Loop | TETCO | TVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | Yes
203143785 | Ground Loop | TETCO | TVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
217351115 | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351116 | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351117 | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351118 | Ground Loop | GEO-THERMAL SPLIT | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351120 | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
203254609 | Ground Loop | HEIL | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254610 | Ground Loop | KEEPRITE | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254611 | Ground Loop | TEMPSTAR | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254612 | Ground Loop | COMFORTMAKER | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254614 | Ground Loop | DAY & NIGHT | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254620 | Ground Loop | BRYANT | GC024V/C**N***1*X1 |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167 | Yes
203254624 | Ground Loop | BRYANT | GC024H**C***1*X1 |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | Yes
203254626 | Ground Loop | BRYANT | GC024H**N***1*X1 |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | Yes
203254744 | Ground Loop | CARRIER | GC024V/C**N***1**1 |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167 | Yes
203254748 | Ground Loop | CARRIER | GC024H**C***1**1 |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | Yes
203254752 | Ground Loop | CARRIER | GC024H**N***1**1 |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | Yes
203260718 | Ground Loop | BOSCH-GEO | SM024-1VT/CFC******A |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167 | Yes
203260866 | Ground Loop | CARRIER | GC024V/C**C***1**1 + UI |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167 | Yes
203260867 | Ground Loop | BRYANT | GC024V/C**C***1*X1 + UI |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167 | Yes
202667081 | Ground Loop | BOSCH-GEO | BP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
206726680 | Ground Loop | WaterFurnace | UVV/UVH024**0*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125 | No
206726691 | Ground Loop | WaterFurnace | UVV/UVH024**3*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125 | No
206726692 | Ground Loop | WaterFurnace | UVV/UVH024**4*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125 | No
206726812 | Ground Loop | GEOCOMFORT | GBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | Yes
206726813 | Ground Loop | GEOCOMFORT | GBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
206726814 | Ground Loop | HYDRON MODULE | HBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | Yes
206726815 | Ground Loop | HYDRON MODULE | HBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
206726816 | Ground Loop | TETCO | TBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | Yes
206726817 | Ground Loop | TETCO | TBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
206726818 | Ground Loop | GEOCOMFORT | GBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
206726819 | Ground Loop | GEOCOMFORT | GBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | No
206726820 | Ground Loop | HYDRON MODULE | HBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
206726821 | Ground Loop | HYDRON MODULE | HBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | No
206726822 | Ground Loop | TETCO | TBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
206726823 | Ground Loop | TETCO | TBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | No
206726824 | Ground Loop | GEOCOMFORT | GBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | Yes
206726825 | Ground Loop | GEOCOMFORT | GBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
206726826 | Ground Loop | HYDRON MODULE | HBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | Yes
206726827 | Ground Loop | HYDRON MODULE | HBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
206726828 | Ground Loop | TETCO | TBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | Yes
206726829 | Ground Loop | TETCO | TBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
206726830 | Ground Loop | GEOCOMFORT | GBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
206726831 | Ground Loop | GEOCOMFORT | GBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | No
206726832 | Ground Loop | HYDRON MODULE | HBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
206726833 | Ground Loop | HYDRON MODULE | HBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | No
206726834 | Ground Loop | TETCO | TBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
206726835 | Ground Loop | TETCO | TBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | No
206726836 | Ground Loop | GEOCOMFORT | GBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | Yes
206726837 | Ground Loop | GEOCOMFORT | GBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | Yes
206726838 | Ground Loop | HYDRON MODULE | HBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | Yes
206726839 | Ground Loop | HYDRON MODULE | HBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | Yes
206726840 | Ground Loop | TETCO | TBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | Yes
206726841 | Ground Loop | TETCO | TBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | Yes
206726842 | Ground Loop | GEOCOMFORT | GBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
206726843 | Ground Loop | GEOCOMFORT | GBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | No
206726844 | Ground Loop | HYDRON MODULE | HBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
206726845 | Ground Loop | HYDRON MODULE | HBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | No
206726846 | Ground Loop | TETCO | TBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
206726847 | Ground Loop | TETCO | TBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | No
206726848 | Ground Loop | GEOCOMFORT | GBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | Yes
206726849 | Ground Loop | HYDRON MODULE | HBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | Yes
206726850 | Ground Loop | TETCO | TBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | Yes
206726851 | Ground Loop | GEOCOMFORT | GBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
206726852 | Ground Loop | HYDRON MODULE | HBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
206726853 | Ground Loop | TETCO | TBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
206726854 | Ground Loop | GEOCOMFORT | GBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | Yes
206726855 | Ground Loop | GEOCOMFORT | GBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
206726856 | Ground Loop | HYDRON MODULE | HBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | Yes
206726857 | Ground Loop | HYDRON MODULE | HBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
206726858 | Ground Loop | TETCO | TBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | Yes
206726859 | Ground Loop | TETCO | TBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
206726860 | Ground Loop | GEOCOMFORT | GBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
206726861 | Ground Loop | GEOCOMFORT | GBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | No
206726862 | Ground Loop | HYDRON MODULE | HBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
211594119 | Ground Loop | TRANE | GEHG009A |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167 | No
211594120 | Ground Loop | TRANE | GEHG012A |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083 | No
211594121 | Ground Loop | TRANE | GEHG015A |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917 | No
3706350 | Ground Loop | GEOSTAR | ZS015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
3706351 | Ground Loop | GEOSTAR | ZS015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
3706369 | Ground Loop | GEOSTAR | ZS018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
216714623 | Ground Loop | GEOSTAR | G3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714624 | Ground Loop | GEOSTAR | G3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714625 | Ground Loop | GEOSTAR | G3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714626 | Ground Loop | GEOSTAR | G3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714627 | Ground Loop | GEOSTAR | G3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714636 | Ground Loop | GEOSTAR | G3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714637 | Ground Loop | GEOSTAR | G3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714638 | Ground Loop | GEOSTAR | G3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714639 | Ground Loop | GEOSTAR | G3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714640 | Ground Loop | GEOSTAR | G3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714641 | Ground Loop | GEOSTAR | G3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714642 | Ground Loop | GEOSTAR | G3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714643 | Ground Loop | GEOSTAR | G3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714644 | Ground Loop | GEOSTAR | G3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714645 | Ground Loop | GEOSTAR | G3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714646 | Ground Loop | GEOSTAR | G3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714647 | Ground Loop | GEOSTAR | G3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714648 | Ground Loop | GEOSTAR | G3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714649 | Ground Loop | GEOSTAR | G3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714656 | Ground Loop | GEOSTAR | G3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714657 | Ground Loop | GEOSTAR | G3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714658 | Ground Loop | GEOSTAR | G3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714659 | Ground Loop | GEOSTAR | G3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714660 | Ground Loop | GEOSTAR | G3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714661 | Ground Loop | GEOSTAR | G3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
202326797 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
202326829 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
202328436 | Ground Loop | BOSCH | BP018-1VT*******C |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
10259035 | Ground Loop | GEOCOMFORT | GZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | Yes
10259036 | Ground Loop | HYDRON MODULE | HZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | Yes
10259037 | Ground Loop | TETCO | TZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | Yes
10259038 | Ground Loop | GEOCOMFORT | GZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | No
10259039 | Ground Loop | HYDRON MODULE | HZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | No
10259040 | Ground Loop | TETCO | TZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | No
10259044 | Ground Loop | GEOCOMFORT | GZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | Yes
10259045 | Ground Loop | HYDRON MODULE | HZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | Yes
10259046 | Ground Loop | TETCO | TZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | Yes
10259047 | Ground Loop | GEOCOMFORT | GZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | No
10259048 | Ground Loop | HYDRON MODULE | HZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | No
10259049 | Ground Loop | TETCO | TZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | No
10259054 | Ground Loop | GEOCOMFORT | GZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | Yes
10259055 | Ground Loop | HYDRON MODULE | HZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | Yes
10259056 | Ground Loop | TETCO | TZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | Yes
10259057 | Ground Loop | GEOCOMFORT | GZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | No
10259058 | Ground Loop | HYDRON MODULE | HZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | No
10259059 | Ground Loop | TETCO | TZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | No
10259062 | Ground Loop | GEOCOMFORT | GZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | Yes
10259063 | Ground Loop | HYDRON MODULE | HZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | Yes
10259064 | Ground Loop | TETCO | TZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | Yes
10259065 | Ground Loop | GEOCOMFORT | GZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | No
10259066 | Ground Loop | HYDRON MODULE | HZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | No
10259067 | Ground Loop | TETCO | TZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | No
10271778 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10271930 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
10271959 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ022H1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10271961 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ022H1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
10271981 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ030H1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10271985 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ030H1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
10272006 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048H1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10272008 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048H1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
10272012 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060H1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10272014 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060H1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
10272021 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ070H1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10272215 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10272216 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10272219 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10272220 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
9100404 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100417 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100431 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9105364 | Ground Loop | GEOCOMFORT | GVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6 | Yes
9105366 | Ground Loop | HYDRON MODULE | HVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6 | Yes
9105367 | Ground Loop | TETCO | TVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6 | Yes
204272856 | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
204272857 | Ground Loop | GeoSmart Energy | GTS064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204272858 | Ground Loop | GeoSmart Energy | GTS064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204272859 | Ground Loop | GeoSmart Energy | GTZ064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204272860 | Ground Loop | GeoSmart Energy | GTZ064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204272890 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
204272892 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204272893 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204276830 | Ground Loop | GEOSTAR | 104J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
204276831 | Ground Loop | GEOSTAR | 103J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
204278291 | Ground Loop | WaterFurnace | SDV038J1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
204346746 | Ground Loop | GeoCool | GCHPV/H/D024T**A*** |  | 27000 | 17.95 | 18500 | 4.2 | 2.25 | No
204346873 | Ground Loop | GeoCool | GCHPV/H/D036T**A*** |  | 39000 | 17.86 | 26900 | 4.4 | 3.25 | No
207178492 | Ground Loop | GEOSTAR | 163J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
214841676 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
214841678 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
214841679 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
214841680 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
214841682 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
214841684 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
214841698 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
214841700 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
214841701 | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | Yes
214841705 | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | Yes
214841706 | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | Yes
214841707 | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | No
214841711 | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | No
214841712 | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | No
5615049 | Ground Loop | DAIKIN | WCCW5036*K*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
5615054 | Ground Loop | DAIKIN | WCCW5042*E*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
5615055 | Ground Loop | DAIKIN | WCCW5042*F*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
5615056 | Ground Loop | DAIKIN | WCCW5042*K*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
5615061 | Ground Loop | DAIKIN | WCCW5048*E*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
5615062 | Ground Loop | DAIKIN | WCCW5048*F*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
5615063 | Ground Loop | DAIKIN | WCCW5048*K*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
207200622 | Ground Loop | GeoSmart Energy | QT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
207200623 | Ground Loop | GeoSmart Energy | QT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
207200624 | Ground Loop | GeoSmart Energy | VI048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
202330283 | Ground Loop | AAON, Inc. | WH-018-1-H-ACAC-C0-10-200-A |  | 17300 | 19.2 | 13300 | 4.7 | 1.4417 | No
202330284 | Ground Loop | AAON, Inc. | WH-018-A-H-ACAC-C0-10-200-A |  | 17300 | 19.2 | 13300 | 4.7 | 1.4417 | No
6580833 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
5696567 | Ground Loop | 5 SERIES | NSV/NSH022G1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5708463 | Ground Loop | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5708493 | Ground Loop | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5708550 | Ground Loop | GEOSTAR | 101/102A022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5708623 | Ground Loop | GeoSmart Energy | GS022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5731224 | Ground Loop | BARD | GTC36S2-A | GTA3600UD1AA+GTB1-A | 38400 | 17.3 | 29600 | 4 | 3.2 | No
6581203 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
207699058 | Ground Loop | UNILUX VHP | UVHP-08-G |  | 26613 | 17.38 | 18707 | 3.61 | 2.2178 | No
5505441 | Ground Loop | BARD | GTC36S2-A | HE37942D175B2505AW/HE37942D210B2505AW | 38500 | 19.3 | 27000 | 4.1 | 3.2083 | No
5612204 | Ground Loop | GeoSmart Energy | VI048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
5613676 | Ground Loop | GEOSTAR | 141/142A048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
205993127 | Ground Loop | HYDRON MODULE | HBT036 | HED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
205993128 | Ground Loop | HYDRON MODULE | HBT036 | HAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075 | No
205993129 | Ground Loop | TETCO | TBT036 | TED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
205993130 | Ground Loop | TETCO | TBT036 | TAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075 | No
205993131 | Ground Loop | GEOCOMFORT | GBT036*2 | GED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
205993132 | Ground Loop | GEOCOMFORT | GBT036*2 | GAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075 | No
205993133 | Ground Loop | HYDRON MODULE | HBT036*2 | HED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
10268245 | Ground Loop | HYDRON MODULE | HBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268246 | Ground Loop | TETCO | TBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268247 | Ground Loop | GEOCOMFORT | GBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268248 | Ground Loop | HYDRON MODULE | HBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268249 | Ground Loop | TETCO | TBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268250 | Ground Loop | GEOCOMFORT | GBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268251 | Ground Loop | HYDRON MODULE | HBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
202607207 | Ground Loop | WHALEN | VP-A-0814-*DD |  | 24000 | 17.1 | 17000 | 3.8 | 2 | No
202607208 | Ground Loop | WHALEN | VP-A-1004-*DD |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833 | No
8849312 | Ground Loop | 5 SERIES | NDV/NDH026H1*(1,4) |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5341546 | Ground Loop | DAIKIN | WVFW1019*E***04 |  | 19700 | 19 | 13400 | 3.7 | 1.6417 | No
5341628 | Ground Loop | DAIKIN | WVFW1019*J***04 |  | 19700 | 19 | 13400 | 3.7 | 1.6417 | No
5317927 | Ground Loop | GEOCOMFORT | GRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225 | No
10268252 | Ground Loop | TETCO | TBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268253 | Ground Loop | GEOCOMFORT | GBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268254 | Ground Loop | HYDRON MODULE | HBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268255 | Ground Loop | TETCO | TBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268260 | Ground Loop | GEOCOMFORT | GBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268261 | Ground Loop | HYDRON MODULE | HBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268262 | Ground Loop | TETCO | TBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
202391450 | Ground Loop | CARRIER | 50PSV012**C4/DA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391451 | Ground Loop | CARRIER | 50PSH012**C0/BA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391452 | Ground Loop | CARRIER | 50PSH012**C4/DA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
8106144 | Ground Loop | TRANE | DXVF0704 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
8106145 | Ground Loop | TRANE | DXVF0708 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
8247563 | Ground Loop | TRANE | DXHF0601 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
8247564 | Ground Loop | TRANE | DXHF0602 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
8247571 | Ground Loop | TRANE | DXHF0603 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
8247572 | Ground Loop | TRANE | DXHF0604 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
8247573 | Ground Loop | TRANE | DXHF0608 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
202330427 | Ground Loop | AAON, Inc. | WV-048-A-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083 | No
202330428 | Ground Loop | AAON, Inc. | WV-048-A-H-DCAC-C0-10-D00-A |  | 49800 | 17.5 | 44900 | 3.9 | 4.15 | No
202330429 | Ground Loop | AAON, Inc. | WV-048-3-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083 | No
205993162 | Ground Loop | GEOCOMFORT | GBT024*2 | GAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917 | No
205993163 | Ground Loop | HYDRON MODULE | HBT024*2 | HED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
205993164 | Ground Loop | HYDRON MODULE | HBT024*2 | HAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917 | No
205993165 | Ground Loop | TETCO | TBT024*2 | TED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
205993166 | Ground Loop | TETCO | TBT024*2 | TAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917 | No
10581116 | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT064**1*1******H |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083 | No
10581118 | Ground Loop | GEOSTAR | 107H026**1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667 | No
10581119 | Ground Loop | GEOSTAR | 107H038**1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833 | No
10581120 | Ground Loop | GEOSTAR | 107H049**1*1 |  | 50400 | 19 | 38000 | 4 | 4.2 | No
203466716 | Ground Loop | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
203470607 | Ground Loop | 5 SERIES | NSV/NSH048J1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
203490410 | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
8560787 | Ground Loop | 5 SERIES | NSV/NSH030H1*(0,3) |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
8560799 | Ground Loop | 5 SERIES | NSV/NSH018H1*(1,4) |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
8560800 | Ground Loop | 5 SERIES | NSV/NSH022H1*(1,4) |  | 19200 | 18.7 | 15000 | 4 | 1.6 | No
202350416 | Ground Loop | AAON, Inc. | RN-009-4-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583 | No
202350426 | Ground Loop | AAON, Inc. | RN-011-2-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775 | No
202350427 | Ground Loop | AAON, Inc. | RN-011-3-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775 | No
202350428 | Ground Loop | AAON, Inc. | RN-011-4-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775 | No
7167555 | Ground Loop | CARRIER | 50PSH/V024***5/EA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7167556 | Ground Loop | CARRIER | 50PSH/V024***6/FA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
5343140 | Ground Loop | DAIKIN | WVFW1024*E***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
5343141 | Ground Loop | DAIKIN | WVFW1024*F***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
5343142 | Ground Loop | DAIKIN | WVFW1024*J***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
5343146 | Ground Loop | DAIKIN | WVFW1030*E***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
205993134 | Ground Loop | HYDRON MODULE | HBT036*2 | HAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075 | No
205993135 | Ground Loop | TETCO | TBT036*2 | TED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
205993136 | Ground Loop | TETCO | TBT036*2 | TAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075 | No
205993137 | Ground Loop | GEOCOMFORT | GBT048 | GED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
205993138 | Ground Loop | GEOCOMFORT | GBT048 | GAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917 | No
205993139 | Ground Loop | HYDRON MODULE | HBT048 | HED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
205993140 | Ground Loop | HYDRON MODULE | HBT048 | HAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917 | No
203362373 | Ground Loop | WHALEN | VP-H-0814-*DD |  | 24000 | 17.1 | 17000 | 3.8 | 2 | No
203362374 | Ground Loop | WHALEN | VP-H-1004-*DD |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833 | No
8789598 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
8791888 | Ground Loop | GEOSTAR | 101/102H070**1*(1,4)***** |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
8791889 | Ground Loop | GeoSmart Energy | GS070**1*(1,4)********H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
8791890 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7499460 | Ground Loop | FHP | EP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7499461 | Ground Loop | FHP | EP024-2HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7499463 | Ground Loop | FHP | EP024-3HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7499464 | Ground Loop | FHP | EP024-4HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7499465 | Ground Loop | FHP | EP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7499466 | Ground Loop | FHP | EP030-2HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7499467 | Ground Loop | FHP | EP030-3HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
214855048 | Ground Loop | WHALEN | CASH*018AD**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
214855049 | Ground Loop | WHALEN | CASV*018AB**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
214855050 | Ground Loop | WHALEN | CASV*018AD**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
214855051 | Ground Loop | WHALEN | CASH*024AB**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855052 | Ground Loop | WHALEN | CASH*024AD**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855053 | Ground Loop | WHALEN | CASH*024AJ**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855054 | Ground Loop | WHALEN | CASH*024AM**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
207200560 | Ground Loop | GeoSmart Energy | GS018**1*(1,4)*H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
207200563 | Ground Loop | GeoSmart Energy | GS030**1*(0,3)*H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
207200564 | Ground Loop | GeoSmart Energy | GS030**1*(1,4)*H |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
207200567 | Ground Loop | GeoSmart Energy | GS070**1*(1,4)*H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
206315256 | Ground Loop | WHALEN | CASV*018AD**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
206599757 | Ground Loop | 5 SERIES | NSV/NSH060J1*0* |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
206599760 | Ground Loop | 5 SERIES | NSV/NSH060J1*(1,4)* |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
206599762 | Ground Loop | GEOSTAR | 101/102J060**1*0****** |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
206599765 | Ground Loop | GEOSTAR | 101/102J060**1*(1,4)****** |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6965882 | Ground Loop | TRANE | EXVF0061 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675 | No
207334458 | Ground Loop | WaterFurnace | NDP026H1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667 | No
207334459 | Ground Loop | WaterFurnace | NDP038H1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833 | No
207334460 | Ground Loop | WaterFurnace | NDP049H1*1 |  | 50400 | 19 | 38000 | 4 | 4.2 | No
207334462 | Ground Loop | WaterFurnace | NDP064H1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083 | No
5677855 | Ground Loop | BARD | QW2S2-A |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333 | No
5677856 | Ground Loop | BARD | QW2S2-B |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333 | No
5677857 | Ground Loop | BARD | QW2S2-C |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333 | No
202330323 | Ground Loop | AAON, Inc. | WH-048-1-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083 | No
5296259 | Ground Loop | TRANE | EXVF0421 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296260 | Ground Loop | TRANE | EXVF0422 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296261 | Ground Loop | TRANE | EXVF0423 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296262 | Ground Loop | TRANE | EXVF0424 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296263 | Ground Loop | TRANE | EXVF0488 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
205782568 | Ground Loop | YORK BY JOHNSON CONTROLS | YACT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
205782570 | Ground Loop | YORK BY JOHNSON CONTROLS | YACT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
205782572 | Ground Loop | GeoSmart Energy | QT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
205782574 | Ground Loop | GeoSmart Energy | QT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
10268203 | Ground Loop | TETCO | TBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268204 | Ground Loop | GEOCOMFORT | GBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268205 | Ground Loop | HYDRON MODULE | HBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268206 | Ground Loop | TETCO | TBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268207 | Ground Loop | GEOCOMFORT | GBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268208 | Ground Loop | HYDRON MODULE | HBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268209 | Ground Loop | TETCO | TBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
202443457 | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202443458 | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
202443459 | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
202443460 | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
8786558 | Ground Loop | GeoSmart Energy | GS018**1*(1,4)********H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
8786559 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214855069 | Ground Loop | WHALEN | CASH*036AJ**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855070 | Ground Loop | WHALEN | CASH*036AM**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855071 | Ground Loop | WHALEN | CASV*036AB**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855072 | Ground Loop | WHALEN | CASV*036AD**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855073 | Ground Loop | WHALEN | CASV*036AJ**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855074 | Ground Loop | WHALEN | CASV*036AM**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
6966789 | Ground Loop | TRANE | EXVF0127 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917 | No
205993155 | Ground Loop | GEOCOMFORT | GBT024 | GED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
205993156 | Ground Loop | GEOCOMFORT | GBT024 | GAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917 | No
205993157 | Ground Loop | HYDRON MODULE | HBT024 | HED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
205993158 | Ground Loop | HYDRON MODULE | HBT024 | HAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917 | No
205993159 | Ground Loop | TETCO | TBT024 | TED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
205993160 | Ground Loop | TETCO | TBT024 | TAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917 | No
205993161 | Ground Loop | GEOCOMFORT | GBT024*2 | GED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
10445242 | Ground Loop | WaterFurnace | SDV049H1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
10445244 | Ground Loop | WaterFurnace | SDV072H1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
10581108 | Ground Loop | 5 SERIES | NDP026H1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667 | No
10268140 | Ground Loop | HYDRON MODULE | HBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268141 | Ground Loop | TETCO | TBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268198 | Ground Loop | GEOCOMFORT | GBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268199 | Ground Loop | HYDRON MODULE | HBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268200 | Ground Loop | TETCO | TBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268201 | Ground Loop | GEOCOMFORT | GBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268202 | Ground Loop | HYDRON MODULE | HBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
8786547 | Ground Loop | GEOSTAR | 101/102H072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
8786548 | Ground Loop | GeoSmart Energy | GT072**1*(1,4)********H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
8786549 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
8786557 | Ground Loop | GEOSTAR | 101/102H018**1*(1,4)***** |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
7499468 | Ground Loop | FHP | EP030-4HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7499480 | Ground Loop | FHP | EP060-1HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7499482 | Ground Loop | FHP | EP060-3HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7499483 | Ground Loop | FHP | EP060-4HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7499484 | Ground Loop | FHP | EP070-1HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
7499485 | Ground Loop | FHP | EP070-3HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
7499487 | Ground Loop | FHP | EP070-4HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
214855062 | Ground Loop | WHALEN | CASH*030AM**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855063 | Ground Loop | WHALEN | CASV*030AB**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855064 | Ground Loop | WHALEN | CASV*030AD**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855065 | Ground Loop | WHALEN | CASV*030AJ**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855066 | Ground Loop | WHALEN | CASV*030AM**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855067 | Ground Loop | WHALEN | CASH*036AB**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855068 | Ground Loop | WHALEN | CASH*036AD**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
6965885 | Ground Loop | TRANE | EXVF0062 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675 | No
6965888 | Ground Loop | TRANE | EXVF0067 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675 | No
6966727 | Ground Loop | TRANE | EXVF0121 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917 | No
6966753 | Ground Loop | TRANE | EXVF0122 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917 | No
207178494 | Ground Loop | GEOSTAR | 161/162J049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5343215 | Ground Loop | DAIKIN | WVFW1060*E***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
5343216 | Ground Loop | DAIKIN | WVFW1060*F***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
5343217 | Ground Loop | DAIKIN | WVFW1060*K***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
205288519 | Ground Loop | BARD | QW2S3DA |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833 | No
205288520 | Ground Loop | BARD | QW2S3DB |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833 | No
205288643 | Ground Loop | BARD | QW2S3DC |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833 | No
5296247 | Ground Loop | TRANE | EXVF0241 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125 | No
5296248 | Ground Loop | TRANE | EXVF0242 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125 | No
5296249 | Ground Loop | TRANE | EXVF0247 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125 | No
4230441 | Ground Loop | DAIKIN | WCCW4015*J*04* |  | 16800 | 20.8 | 11500 | 3.8 | 1.4 | No
4230746 | Ground Loop | DAIKIN | WCCW4019*E*04* |  | 22600 | 18.4 | 14800 | 3.8 | 1.8833 | No
4230748 | Ground Loop | DAIKIN | WCCW4019*J*04* |  | 22600 | 18.4 | 14800 | 3.8 | 1.8833 | No
4230750 | Ground Loop | DAIKIN | WCCW4024*E*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1 | No
4230752 | Ground Loop | DAIKIN | WCCW4024*F*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1 | No
4230754 | Ground Loop | DAIKIN | WCCW4024*J*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1 | No
4231098 | Ground Loop | DAIKIN | WCCW4024*K*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1 | No
202901193 | Ground Loop | WHALEN | VD-A-0801-*DA |  | 24500 | 17.5 | 17000 | 4 | 2.0417 | No
202350521 | Ground Loop | AAON, Inc. | WV-036-2-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2 | No
202350524 | Ground Loop | AAON, Inc. | WV-048-1-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083 | No
202350526 | Ground Loop | AAON, Inc. | WV-048-2-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083 | No
202330763 | Ground Loop | WHALEN | CASH*024AJ**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330764 | Ground Loop | WHALEN | CASV*024AJ**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330765 | Ground Loop | WHALEN | CASH*024AM**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330766 | Ground Loop | WHALEN | CASV*024AM**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330767 | Ground Loop | WHALEN | CASH*030AJ**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330768 | Ground Loop | WHALEN | CASV*030AJ**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330769 | Ground Loop | WHALEN | CASH*030AM**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330573 | Ground Loop | AAON, Inc. | WH-006-B-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333 | No
202330574 | Ground Loop | AAON, Inc. | WH-006-1-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333 | No
202330282 | Ground Loop | AAON, Inc. | WH-018-A-H-ACAC-C0-10-100-A |  | 17600 | 17.6 | 13500 | 4.4 | 1.4667 | No
5343170 | Ground Loop | DAIKIN | WVFW1048*E***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
5343172 | Ground Loop | DAIKIN | WVFW1048*F***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
5343173 | Ground Loop | DAIKIN | WVFW1048*K***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
5295950 | Ground Loop | TRANE | EXHF0301 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475 | No
5295951 | Ground Loop | TRANE | EXHF0302 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475 | No
5295952 | Ground Loop | TRANE | EXHF0307 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475 | No
5295953 | Ground Loop | TRANE | EXHF0361 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295954 | Ground Loop | TRANE | EXHF0362 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295955 | Ground Loop | TRANE | EXHF0367 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295956 | Ground Loop | TRANE | EXHF0363 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
10268263 | Ground Loop | GEOCOMFORT | GBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268264 | Ground Loop | HYDRON MODULE | HBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268265 | Ground Loop | TETCO | TBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268268 | Ground Loop | GEOCOMFORT | GBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268269 | Ground Loop | HYDRON MODULE | HBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268270 | Ground Loop | TETCO | TBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268271 | Ground Loop | GEOCOMFORT | GBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
8105933 | Ground Loop | TRANE | DXHF0703 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105934 | Ground Loop | TRANE | DXHF0704 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105935 | Ground Loop | TRANE | DXHF0708 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105950 | Ground Loop | TRANE | DXVF0241 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
8105955 | Ground Loop | TRANE | DXVF0242 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
8105956 | Ground Loop | TRANE | DXVF0243 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
8105960 | Ground Loop | TRANE | DXVF0244 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
7167343 | Ground Loop | CARRIER | 50PSH/V024***4/DA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7167344 | Ground Loop | CARRIER | 50PSH/V030***4/DA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7167345 | Ground Loop | CARRIER | 50PSH/V030***6/FA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7167346 | Ground Loop | CARRIER | 50PSH/V030***5/EA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7167347 | Ground Loop | CARRIER | 50PSH/V030***3/CA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7167357 | Ground Loop | CARRIER | 50PSH/V060***6/FA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7167358 | Ground Loop | CARRIER | 50PSH/V060***5/EA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
5296264 | Ground Loop | TRANE | EXVF0428 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296265 | Ground Loop | TRANE | EXVF0481 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
5296266 | Ground Loop | TRANE | EXVF0482 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
5296267 | Ground Loop | TRANE | EXVF0483 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
5296268 | Ground Loop | TRANE | EXVF0484 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
205993113 | Ground Loop | GEOCOMFORT | GBS018 | GED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
205993114 | Ground Loop | GEOCOMFORT | GBS018 | GAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85 | No
205993115 | Ground Loop | HYDRON MODULE | HBS018 | HED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
205993116 | Ground Loop | HYDRON MODULE | HBS018 | HAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85 | No
205993117 | Ground Loop | TETCO | TBS018 | TED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
205993118 | Ground Loop | TETCO | TBS018 | TAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85 | No
205993119 | Ground Loop | GEOCOMFORT | GBS018*2 | GED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
202330748 | Ground Loop | WHALEN | CASH*036AD**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330749 | Ground Loop | WHALEN | CASV*036AD**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
207699054 | Ground Loop | UNILUX VHP | UVHP-03-G |  | 9900 | 17.22 | 7452 | 3.65 | 0.825 | No
207699055 | Ground Loop | UNILUX VHP | UVHP-04-G |  | 13040 | 17.32 | 10273 | 3.62 | 1.0867 | No
207699056 | Ground Loop | UNILUX VHP | UVHP-05-G |  | 15724 | 17.2 | 11705 | 3.61 | 1.3103 | No
207699057 | Ground Loop | UNILUX VHP | UVHP-06-G |  | 19621 | 17.3 | 15106 | 3.62 | 1.6351 | No
205993179 | Ground Loop | GEOCOMFORT | GBT060 | GAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917 | No
205993180 | Ground Loop | HYDRON MODULE | HBT060 | HAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917 | No
205993181 | Ground Loop | TETCO | TBT060 | TAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917 | No
205993182 | Ground Loop | GEOCOMFORT | GBT060*2 | GAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917 | No
10443577 | Ground Loop | GEOCOMFORT | GBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443578 | Ground Loop | HYDRON MODULE | HBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443579 | Ground Loop | TETCO | TBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443580 | Ground Loop | GEOCOMFORT | GBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443581 | Ground Loop | HYDRON MODULE | HBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443582 | Ground Loop | TETCO | TBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443583 | Ground Loop | GEOCOMFORT | GBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
203490416 | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
203494005 | Ground Loop | GEOSTAR | 101/102J048**1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
4219442 | Ground Loop | NORDIC | RS25HACW-P-1T-* | AH-25-P-1-***** | 24800 | 17 | 18300 | 3.6 | 2.0667 | No
4230439 | Ground Loop | DAIKIN | WCCW4015*E*04* |  | 17200 | 20.8 | 11500 | 4 | 1.4333 | No
203113882 | Ground Loop | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
203113887 | Ground Loop | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
202358913 | Ground Loop | DAIKIN | WCCW5019*E*04* |  | 20600 | 19 | 14000 | 3.7 | 1.7167 | No
202358915 | Ground Loop | DAIKIN | WCCW5019*J*04* |  | 20600 | 19 | 14000 | 3.7 | 1.7167 | No
202358917 | Ground Loop | DAIKIN | WCCW5024*E*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
202358919 | Ground Loop | DAIKIN | WCCW5024*F*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
202358921 | Ground Loop | DAIKIN | WCCW5024*J*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
202358923 | Ground Loop | DAIKIN | WCCW5024*K*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
202391369 | Ground Loop | AQUARIUS | EP012-1VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
8105926 | Ground Loop | TRANE | DXHF0481 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105927 | Ground Loop | TRANE | DXHF0482 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105928 | Ground Loop | TRANE | DXHF0483 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105929 | Ground Loop | TRANE | DXHF0484 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105930 | Ground Loop | TRANE | DXHF0488 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105931 | Ground Loop | TRANE | DXHF0701 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105932 | Ground Loop | TRANE | DXHF0702 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
7499450 | Ground Loop | FHP | EP009-1HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
7499451 | Ground Loop | FHP | EP009-2HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
7499453 | Ground Loop | FHP | EP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
7499455 | Ground Loop | FHP | EP015-1HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
7499456 | Ground Loop | FHP | EP015-2HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
214855055 | Ground Loop | WHALEN | CASV*024AB**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855056 | Ground Loop | WHALEN | CASV*024AD**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855057 | Ground Loop | WHALEN | CASV*024AJ**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855058 | Ground Loop | WHALEN | CASV*024AM**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855059 | Ground Loop | WHALEN | CASH*030AB**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855060 | Ground Loop | WHALEN | CASH*030AD**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855061 | Ground Loop | WHALEN | CASH*030AJ**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330347 | Ground Loop | AAON, Inc. | WV-009-B-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667 | No
202330348 | Ground Loop | AAON, Inc. | WV-009-1-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667 | No
202330349 | Ground Loop | AAON, Inc. | WV-009-A-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667 | No
202330350 | Ground Loop | AAON, Inc. | WV-012-B-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125 | No
202330351 | Ground Loop | AAON, Inc. | WV-012-1-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125 | No
202330352 | Ground Loop | AAON, Inc. | WV-012-A-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125 | No
5343147 | Ground Loop | DAIKIN | WVFW1030*F***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
5343148 | Ground Loop | DAIKIN | WVFW1030*J***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
5317936 | Ground Loop | GEOCOMFORT | GRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5317937 | Ground Loop | HYDRON MODULE | HRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5317938 | Ground Loop | TETCO | TRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5295943 | Ground Loop | TRANE | EXHF0241 |  | 24700 | 18 | 17900 | 3.6 | 2.0583 | No
5295946 | Ground Loop | TRANE | EXHF0242 |  | 24700 | 18 | 17900 | 3.6 | 2.0583 | No
5295949 | Ground Loop | TRANE | EXHF0247 |  | 24700 | 18 | 17900 | 3.6 | 2.0583 | No
3919848 | Ground Loop | AQUARIUS | EP009-1HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
3919850 | Ground Loop | AQUARIUS | EP009-2HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
3919853 | Ground Loop | AQUARIUS | EP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
3919854 | Ground Loop | AQUARIUS | EP015-1HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
3919855 | Ground Loop | AQUARIUS | EP015-2HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
3919884 | Ground Loop | AQUARIUS | EP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
3919931 | Ground Loop | AQUARIUS | EP024-2HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
202391437 | Ground Loop | FHP | EP012-2HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391438 | Ground Loop | FHP | EP012-0HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391439 | Ground Loop | FHP | EP012-2VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391440 | Ground Loop | FHP | EP012-0VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
8105973 | Ground Loop | TRANE | DXVF0481 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105974 | Ground Loop | TRANE | DXVF0482 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105975 | Ground Loop | TRANE | DXVF0483 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105976 | Ground Loop | TRANE | DXVF0484 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105977 | Ground Loop | TRANE | DXVF0488 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105978 | Ground Loop | TRANE | DXVF0601 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
214813285 | Ground Loop | ARCADIAN | AVHP-03-G |  | 9900 | 17.22 | 7452 | 3.65 | 0.825 | No
214813286 | Ground Loop | ARCADIAN | AVHP-04-G |  | 13040 | 17.32 | 10273 | 3.62 | 1.0867 | No
214813287 | Ground Loop | ARCADIAN | AVHP-05-G |  | 15724 | 17.2 | 11705 | 3.61 | 1.3103 | No
214813288 | Ground Loop | ARCADIAN | AVHP-06-G |  | 19621 | 17.3 | 15106 | 3.62 | 1.6351 | No
214813289 | Ground Loop | ARCADIAN | AVHP-08-G |  | 26613 | 17.38 | 18707 | 3.61 | 2.2178 | No
214813290 | Ground Loop | ARCADIAN | AVHP-10-G |  | 31947 | 17.27 | 21202 | 3.62 | 2.6622 | No
202330391 | Ground Loop | AAON, Inc. | WV-036-2-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05 | No
202330392 | Ground Loop | AAON, Inc. | WV-036-3-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05 | No
5343160 | Ground Loop | DAIKIN | WVFW1042*E***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
5343161 | Ground Loop | DAIKIN | WVFW1042*F***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
5343162 | Ground Loop | DAIKIN | WVFW1042*K***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
10443497 | Ground Loop | HYDRON MODULE | HBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443498 | Ground Loop | TETCO | TBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443499 | Ground Loop | GEOCOMFORT | GBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443500 | Ground Loop | HYDRON MODULE | HBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443501 | Ground Loop | TETCO | TBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443502 | Ground Loop | GEOCOMFORT | GBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443503 | Ground Loop | HYDRON MODULE | HBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
3920503 | Ground Loop | AQUARIUS | EP070-1HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
3920504 | Ground Loop | AQUARIUS | EP070-3HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
3920505 | Ground Loop | AQUARIUS | EP070-4HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
202350093 | Ground Loop | 5 SERIES | NSV/NSH036J1*(0,3) |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
202350095 | Ground Loop | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
202350096 | Ground Loop | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7167359 | Ground Loop | CARRIER | 50PSH/V060***3/CA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7167360 | Ground Loop | CARRIER | 50PSH/V070***3/CA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
7167361 | Ground Loop | CARRIER | 50PSH/V070***5/EA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
7167362 | Ground Loop | CARRIER | 50PSH/V070***6/FA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
202330339 | Ground Loop | AAON, Inc. | WH-036-A-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667 | No
202330340 | Ground Loop | AAON, Inc. | WH-036-3-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667 | No
202330343 | Ground Loop | AAON, Inc. | WH-048-A-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667 | No
202330344 | Ground Loop | AAON, Inc. | WH-048-3-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667 | No
206315249 | Ground Loop | WHALEN | CASH*015AB**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
206315250 | Ground Loop | WHALEN | CASV*015AB**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
206315251 | Ground Loop | WHALEN | CASH*015AD**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
206315252 | Ground Loop | WHALEN | CASV*015AD**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
206315253 | Ground Loop | WHALEN | CASH*018AB**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
206315254 | Ground Loop | WHALEN | CASV*018AB**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
206315255 | Ground Loop | WHALEN | CASH*018AD**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
205993148 | Ground Loop | TETCO | TBT048*2 | TAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917 | No
205993149 | Ground Loop | GEOCOMFORT | GBT060 | GED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
205993150 | Ground Loop | HYDRON MODULE | HBT060 | HED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
205993151 | Ground Loop | TETCO | TBT060 | TED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
205993152 | Ground Loop | GEOCOMFORT | GBT060*2 | GED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
205993153 | Ground Loop | HYDRON MODULE | HBT060*2 | HED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
205993154 | Ground Loop | TETCO | TBT060*2 | TED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
204031802 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
203363320 | Ground Loop | WILLIAMS | EW009H1D*A |  | 24000 | 17.1 | 17000 | 3.8 | 2 | No
202330770 | Ground Loop | WHALEN | CASV*030AM**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330771 | Ground Loop | WHALEN | CASH*036AJ**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330772 | Ground Loop | WHALEN | CASV*036AJ**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330773 | Ground Loop | WHALEN | CASH*036AM**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330774 | Ground Loop | WHALEN | CASV*036AM**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330741 | Ground Loop | WHALEN | CASV*024AD**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330742 | Ground Loop | WHALEN | CASH*030AB**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330743 | Ground Loop | WHALEN | CASV*030AB**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330744 | Ground Loop | WHALEN | CASH*030AD**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330745 | Ground Loop | WHALEN | CASV*030AD**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330746 | Ground Loop | WHALEN | CASH*036AB**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330747 | Ground Loop | WHALEN | CASV*036AB**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
6936993 | Ground Loop | BARD | GTC60S2-A | HE49948D210B2705AW | 63000 | 18.8 | 48000 | 4.05 | 5.25 | No
205993183 | Ground Loop | HYDRON MODULE | HBT060*2 | HAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917 | No
205993184 | Ground Loop | TETCO | TBT060*2 | TAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917 | No
10443584 | Ground Loop | HYDRON MODULE | HBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443585 | Ground Loop | TETCO | TBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443586 | Ground Loop | GEOCOMFORT | GBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443587 | Ground Loop | HYDRON MODULE | HBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443588 | Ground Loop | TETCO | TBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
204031808 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
203363090 | Ground Loop | WILLIAMS | EW010H1D*A |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833 | No
9850157 | Ground Loop | DAIKIN | WVFW1024*K***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
9850202 | Ground Loop | DAIKIN | WVFW1030*K***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
202391370 | Ground Loop | AQUARIUS | EP012-1HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391373 | Ground Loop | AQUARIUS | EP012-0VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391374 | Ground Loop | AQUARIUS | EP012-2VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391375 | Ground Loop | AQUARIUS | EP012-0HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391376 | Ground Loop | AQUARIUS | EP012-2HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
8105965 | Ground Loop | TRANE | DXVF0247 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
8105966 | Ground Loop | TRANE | DXVF0248 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
202330575 | Ground Loop | AAON, Inc. | WH-006-A-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333 | No
202330576 | Ground Loop | AAON, Inc. | WV-006-B-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525 | No
202330577 | Ground Loop | AAON, Inc. | WV-006-1-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525 | No
202330578 | Ground Loop | AAON, Inc. | WV-006-A-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525 | No
202330738 | Ground Loop | WHALEN | CASH*024AB**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330739 | Ground Loop | WHALEN | CASV*024AB**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330740 | Ground Loop | WHALEN | CASH*024AD**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
207348743 | Ground Loop | WaterFurnace | URT096*3*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65 | No
207348744 | Ground Loop | WaterFurnace | URT096*4*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65 | No
201846902 | Ground Loop | GEOSTAR | 111H038**1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
5360714 | Ground Loop | BARD | GTC36S2-A | GTADP-3642-* | 39500 | 18.3 | 29000 | 4.2 | 3.2917 | No
5360715 | Ground Loop | BARD | GTC48S2-A | GTADP-4860-C | 51500 | 18.6 | 37000 | 3.9 | 4.2917 | No
5360791 | Ground Loop | BARD | GTC60S2-A | GTADP-4860-C | 63000 | 18.8 | 48000 | 4.05 | 5.25 | No
5440741 | Ground Loop | 7 SERIES | NVV/NVH048A1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
205993120 | Ground Loop | GEOCOMFORT | GBS018*2 | GAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85 | No
205993121 | Ground Loop | HYDRON MODULE | HBS018*2 | HED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
205993122 | Ground Loop | HYDRON MODULE | HBS018*2 | HAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85 | No
205993123 | Ground Loop | TETCO | TBS018*2 | TED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
205993124 | Ground Loop | TETCO | TBS018*2 | TAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85 | No
205993125 | Ground Loop | GEOCOMFORT | GBT036 | GED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
205993126 | Ground Loop | GEOCOMFORT | GBT036 | GAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075 | No
8786527 | Ground Loop | GEOSTAR | 101/102H026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
8786528 | Ground Loop | GeoSmart Energy | GT026**1*(1,4)********H |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
8786529 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****H |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
202350506 | Ground Loop | AAON, Inc. | WH-036-1-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667 | No
202350507 | Ground Loop | AAON, Inc. | WH-036-2-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667 | No
202350510 | Ground Loop | AAON, Inc. | WH-048-1-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667 | No
214855043 | Ground Loop | WHALEN | CASH*015AB**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
214855044 | Ground Loop | WHALEN | CASH*015AD**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
214855045 | Ground Loop | WHALEN | CASV*015AB**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
214855046 | Ground Loop | WHALEN | CASV*015AD**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
214855047 | Ground Loop | WHALEN | CASH*018AB**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
6945298 | Ground Loop | BARD | GTC48S2-A | HE49948D210B2705AW | 51500 | 18.6 | 37000 | 3.9 | 4.2917 | No
10443504 | Ground Loop | TETCO | TBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443509 | Ground Loop | GEOCOMFORT | GBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443510 | Ground Loop | HYDRON MODULE | HBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443511 | Ground Loop | TETCO | TBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443512 | Ground Loop | GEOCOMFORT | GBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443513 | Ground Loop | HYDRON MODULE | HBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443514 | Ground Loop | TETCO | TBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
5295957 | Ground Loop | TRANE | EXHF0368 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295958 | Ground Loop | TRANE | EXHF0364 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295959 | Ground Loop | TRANE | EXHF0421 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
5295961 | Ground Loop | TRANE | EXHF0422 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
5295963 | Ground Loop | TRANE | EXHF0423 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
5295965 | Ground Loop | TRANE | EXHF0424 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
5295967 | Ground Loop | TRANE | EXHF0428 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
10268272 | Ground Loop | HYDRON MODULE | HBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268273 | Ground Loop | TETCO | TBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268274 | Ground Loop | GEOCOMFORT | GBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268275 | Ground Loop | HYDRON MODULE | HBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268276 | Ground Loop | TETCO | TBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268277 | Ground Loop | GEOCOMFORT | GBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268278 | Ground Loop | HYDRON MODULE | HBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
9951968 | Ground Loop | BARD | GV27S3AA |  | 26600 | 18.1 | 20200 | 4.1 | 2.2167 | No
9951969 | Ground Loop | BARD | GV38S3AA |  | 38500 | 17.1 | 31400 | 4.05 | 3.2083 | No
9951970 | Ground Loop | BARD | GV51S3AA |  | 49500 | 17.1 | 39500 | 3.75 | 4.125 | No
202350511 | Ground Loop | AAON, Inc. | WH-048-2-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667 | No
202350515 | Ground Loop | AAON, Inc. | WV-024-1-H-DCAC-C0-10-D00-A |  | 26900 | 18.1 | 16700 | 3.82 | 2.2417 | No
202350519 | Ground Loop | AAON, Inc. | WV-036-1-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2 | No
207699059 | Ground Loop | UNILUX VHP | UVHP-10-G |  | 31947 | 17.27 | 21202 | 3.62 | 2.6622 | No
202330305 | Ground Loop | AAON, Inc. | WH-036-1-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833 | No
202330306 | Ground Loop | AAON, Inc. | WH-036-A-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833 | No
202330307 | Ground Loop | AAON, Inc. | WH-036-1-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667 | No
202330308 | Ground Loop | AAON, Inc. | WH-036-A-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667 | No
202330309 | Ground Loop | AAON, Inc. | WH-036-2-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833 | No
202330271 | Ground Loop | AAON, Inc. | WH-009-B-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775 | No
202330272 | Ground Loop | AAON, Inc. | WH-009-1-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775 | No
202330273 | Ground Loop | AAON, Inc. | WH-009-A-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775 | No
205993141 | Ground Loop | TETCO | TBT048 | TED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
205993142 | Ground Loop | TETCO | TBT048 | TAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917 | No
205993143 | Ground Loop | GEOCOMFORT | GBT048*2 | GED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
205993144 | Ground Loop | GEOCOMFORT | GBT048*2 | GAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917 | No
205993145 | Ground Loop | HYDRON MODULE | HBT048*2 | HED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
205993146 | Ground Loop | HYDRON MODULE | HBT048*2 | HAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917 | No
205993147 | Ground Loop | TETCO | TBT048*2 | TED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
5295970 | Ground Loop | TRANE | EXHF0481 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
5295971 | Ground Loop | TRANE | EXHF0482 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
5295972 | Ground Loop | TRANE | EXHF0483 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
5295973 | Ground Loop | TRANE | EXHF0484 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
5295974 | Ground Loop | TRANE | EXHF0488 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
10268279 | Ground Loop | TETCO | TBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10318053 | Ground Loop | GEOSTAR | 103H060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10443493 | Ground Loop | GEOCOMFORT | GBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443494 | Ground Loop | HYDRON MODULE | HBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443495 | Ground Loop | TETCO | TBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443496 | Ground Loop | GEOCOMFORT | GBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
3920297 | Ground Loop | AQUARIUS | EP030-2HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
3920298 | Ground Loop | AQUARIUS | EP030-4HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
3920299 | Ground Loop | AQUARIUS | EP030-3HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
3920300 | Ground Loop | AQUARIUS | EP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
3920500 | Ground Loop | AQUARIUS | EP060-4HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
3920501 | Ground Loop | AQUARIUS | EP060-3HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
3920502 | Ground Loop | AQUARIUS | EP060-1HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
202923075 | Ground Loop | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
203113881 | Ground Loop | GEOSTAR | 101/102J036**1*(0,3)***** |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
202391443 | Ground Loop | FHP | EP012-1HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391444 | Ground Loop | FHP | EP012-1VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391445 | Ground Loop | CARRIER | 50PSV012**C3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391446 | Ground Loop | CARRIER | 50PSH012**C3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391449 | Ground Loop | CARRIER | 50PSV012**C0/BA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
8105979 | Ground Loop | TRANE | DXVF0602 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105980 | Ground Loop | TRANE | DXVF0603 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105981 | Ground Loop | TRANE | DXVF0604 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105982 | Ground Loop | TRANE | DXVF0608 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105983 | Ground Loop | TRANE | DXVF0701 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
8105984 | Ground Loop | TRANE | DXVF0702 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
8105985 | Ground Loop | TRANE | DXVF0703 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
202330403 | Ground Loop | AAON, Inc. | WV-048-1-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083 | No
202330404 | Ground Loop | AAON, Inc. | WV-048-A-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083 | No
202330407 | Ground Loop | AAON, Inc. | WV-048-2-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083 | No
202330408 | Ground Loop | AAON, Inc. | WV-048-3-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083 | No
202330387 | Ground Loop | AAON, Inc. | WV-036-1-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05 | No
202330388 | Ground Loop | AAON, Inc. | WV-036-A-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05 | No
202330310 | Ground Loop | AAON, Inc. | WH-036-3-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833 | No
202330311 | Ground Loop | AAON, Inc. | WH-036-2-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667 | No
202330312 | Ground Loop | AAON, Inc. | WH-036-3-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667 | No
202330328 | Ground Loop | AAON, Inc. | WH-048-3-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083 | No
5296250 | Ground Loop | TRANE | EXVF0301 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333 | No
5296251 | Ground Loop | TRANE | EXVF0302 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333 | No
5296252 | Ground Loop | TRANE | EXVF0307 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333 | No
10268233 | Ground Loop | GEOCOMFORT | GBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268234 | Ground Loop | HYDRON MODULE | HBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268235 | Ground Loop | TETCO | TBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268236 | Ground Loop | GEOCOMFORT | GBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268237 | Ground Loop | HYDRON MODULE | HBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268238 | Ground Loop | TETCO | TBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268244 | Ground Loop | GEOCOMFORT | GBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
202443465 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202443466 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
202443468 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
202443469 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
8105913 | Ground Loop | TRANE | DXHF0248 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
202330418 | Ground Loop | AAON, Inc. | WV-024-A-H-DCAC-C0-10-D00-A |  | 26900 | 18.1 | 16700 | 3.82 | 2.2417 | No
202330422 | Ground Loop | AAON, Inc. | WV-036-A-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2 | No
202330424 | Ground Loop | AAON, Inc. | WV-036-3-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2 | No
7167334 | Ground Loop | CARRIER | 50PSH/V009***3/CA |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
7167335 | Ground Loop | CARRIER | 50PSH/V009***4/DA |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
7167337 | Ground Loop | CARRIER | 50PSH/V012***3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
7167338 | Ground Loop | CARRIER | 50PSH/V015***3/CA |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
7167339 | Ground Loop | CARRIER | 50PSH/V015***4/DA |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
7167342 | Ground Loop | CARRIER | 50PSH/V024***3/CA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7076986 | Ground Loop | AQUARIUS | EP024-3HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7076987 | Ground Loop | AQUARIUS | EP024-4HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
5932336 | Ground Loop | GEOCOMFORT | GRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5932337 | Ground Loop | HYDRON MODULE | HRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5932338 | Ground Loop | TETCO | TRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5932368 | Ground Loop | GEOCOMFORT | GRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5932380 | Ground Loop | HYDRON MODULE | HRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5932381 | Ground Loop | TETCO | TRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5615038 | Ground Loop | DAIKIN | WCCW5030*E*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
5615039 | Ground Loop | DAIKIN | WCCW5030*F*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
5615040 | Ground Loop | DAIKIN | WCCW5030*J*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
5615041 | Ground Loop | DAIKIN | WCCW5030*K*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
5615046 | Ground Loop | DAIKIN | WCCW5036*E*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
5615047 | Ground Loop | DAIKIN | WCCW5036*F*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
5615048 | Ground Loop | DAIKIN | WCCW5036*J*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
207200570 | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
207200571 | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207200572 | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
207200574 | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
202330277 | Ground Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-100-A |  | 14700 | 18.2 | 11100 | 4.8 | 1.225 | No
202330278 | Ground Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-100-A |  | 14700 | 18.2 | 11100 | 4.8 | 1.225 | No
202330279 | Ground Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 14700 | 19.9 | 10900 | 5.2 | 1.225 | No
202330280 | Ground Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 14700 | 19.9 | 10900 | 5.2 | 1.225 | No
202330281 | Ground Loop | AAON, Inc. | WH-018-1-H-ACAC-C0-10-100-A |  | 17600 | 17.6 | 13500 | 4.4 | 1.4667 | No
207178526 | Ground Loop | GEOSTAR | 161/162H026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207178527 | Ground Loop | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207178547 | Ground Loop | GEOSTAR | 161/162H072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207200554 | Ground Loop | GeoSmart Energy | GT026**1*(1,4)*H |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207200555 | Ground Loop | GeoSmart Energy | GT072**1*(1,4)*H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207200556 | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207200557 | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207337519 | Ground Loop | GEOSTAR | 103H060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
207337520 | Ground Loop | GEOSTAR | 103H060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
5615068 | Ground Loop | DAIKIN | WCCW5060*E*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
5615069 | Ground Loop | DAIKIN | WCCW5060*F*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
5615070 | Ground Loop | DAIKIN | WCCW5060*K*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
5317928 | Ground Loop | HYDRON MODULE | HRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225 | No
5317929 | Ground Loop | TETCO | TRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225 | No
5317930 | Ground Loop | GEOCOMFORT | GRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5317931 | Ground Loop | HYDRON MODULE | HRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5317932 | Ground Loop | TETCO | TRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
203363068 | Ground Loop | WILLIAMS | EW009A1D*A |  | 24000 | 17.1 | 17000 | 3.8 | 2 | No
203363069 | Ground Loop | WILLIAMS | EW010A1D*A |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833 | No
8789586 | Ground Loop | GEOSTAR | 101/102H022**1*(1,4)***** |  | 19200 | 18.7 | 15500 | 4 | 1.6 | No
8789591 | Ground Loop | GEOSTAR | 101/102H030**1*(0,3)***** |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
8789592 | Ground Loop | GeoSmart Energy | GS030**1*(0,3)********H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
8789593 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
8789596 | Ground Loop | GEOSTAR | 101/102H030**1*(1,4)***** |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
8789597 | Ground Loop | GeoSmart Energy | GS030**1*(1,4)********H |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
8103479 | Ground Loop | TRANE | DXHF0241 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
8105907 | Ground Loop | TRANE | DXHF0242 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
8105909 | Ground Loop | TRANE | DXHF0243 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
8105911 | Ground Loop | TRANE | DXHF0244 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
8105912 | Ground Loop | TRANE | DXHF0247 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
202330324 | Ground Loop | AAON, Inc. | WH-048-A-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083 | No
202330327 | Ground Loop | AAON, Inc. | WH-048-2-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083 | No
10581109 | Ground Loop | 5 SERIES | NDP038H1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833 | No
10581110 | Ground Loop | 5 SERIES | NDP049H1*1 |  | 50400 | 19 | 38000 | 4 | 4.2 | No
10581111 | Ground Loop | 5 SERIES | NDP064H1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083 | No
10581113 | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT026**1*1******H |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667 | No
10581114 | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833 | No
10581115 | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT049**1*1******H |  | 50400 | 19 | 38000 | 4 | 4.2 | No
10206404 | Ground Loop | BARD | GTC36S2-A | HE37942D210B2505AW | 39500 | 18.3 | 29000 | 4.2 | 3.2917 | No
10206405 | Ground Loop | BARD | GTC36S2-A | HE37942D175B2505AW | 39500 | 18.3 | 29000 | 4.2 | 3.2917 | No
10268136 | Ground Loop | GEOCOMFORT | GBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268137 | Ground Loop | HYDRON MODULE | HBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268138 | Ground Loop | TETCO | TBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268139 | Ground Loop | GEOCOMFORT | GBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
8560801 | Ground Loop | 5 SERIES | NSV/NSH030H1*(1,4) |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
8560806 | Ground Loop | 5 SERIES | NSV/NSH070H1*(1,4) |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
8570181 | Ground Loop | 5 SERIES | NDV/NDH072H1*(1,4) |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202350098 | Ground Loop | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202350414 | Ground Loop | AAON, Inc. | RN-009-2-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583 | No
202350415 | Ground Loop | AAON, Inc. | RN-009-3-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583 | No

## Residential GSHP
[6 empty] | Water Loop Heat Pump |  |  |  |  | Ground Water Heat Pump |  |  |  |  | Ground Loop Heat Pump |  |  |  |  | Direct Geoexchange Heat Pump
AHRI Certified Reference Number | Brand Name | AHRI Type | Program Type | Outdoor Unit Model Number | Indoor Unit Model Number(s) | Full Load WLHP Cooling Capacity (Btuh) | Full Load WLHP Cooling EER (Btuh/watt) | Full Load WLHP Heating COP | Full Load WLHP Heating Capacity (Btuh) | WLHP Tonnage | Full Load GWHP Cooling Capacity (Btuh) | Full Load GWHP Cooling EER (Btuh/watt) | Full Load GWHP Heating COP | Full Load GWHP Heating Capacity (Btuh) | GWHP Tonnage | Full Load GLHP Cooling Capacity (Btuh) | Full Load GLHP Cooling EER (Btuh/watt) | Full Load GLHP Heating COP | Full Load GLHP Heating Capacity (Btuh) | GLHP Tonnage | Refrigerant Type | Full Load DGX Cooling Capacity (Btuh) | Full Load DGX Cooling EER (Btuh/watt) | Full Load DGX Heating COP | Full Load DGX Heating Capacity (Btuh) | DGX Tonnage
203105868 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-36C1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-410A | 38000 | 19.1 | 3.9 | 38000 | 3.1667
203105870 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-42C1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-410A | 44000 | 21 | 3.9 | 44000 | 3.6667
203105871 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 51500 | 19.8 | 4 | 51500 | 4.2917
203105874 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-54C1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-410A | 56000 | 19.1 | 3.8 | 56000 | 4.6667
203105877 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-60C1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-410A | 61500 | 19.1 | 3.6 | 61500 | 5.125
203470614 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 33600 | 20.1 | 3.6 | 33600 | 2.8
203470620 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-24C1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-410A | 25400 | 19.1 | 3.9 | 25400 | 2.1167
203470621 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-30C1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-410A | 31600 | 20.1 | 3.9 | 31600 | 2.6333
204494956 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-36C1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-410A | 38000 | 19.1 | 3.9 | 38000 | 3.1667
204494957 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-42C1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-410A | 44000 | 19.1 | 3.9 | 44000 | 3.6667
204494958 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 51500 | 19.8 | 4 | 51500 | 4.2917
204494959 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-54C1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-410A | 56000 | 19.1 | 3.8 | 56000 | 4.6667
204494960 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-60C1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-410A | 61500 | 19.1 | 3.6 | 61500 | 5.125
216720848 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-24D1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-454B | 24000 | 19.1 | 3.9 | 24000 | 2
216720849 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-30D1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-454B | 31600 | 20.1 | 3.9 | 31600 | 2.6333
216720850 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 38000 | 22 | 3.9 | 38000 | 3.1667
216720851 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 44000 | 19.1 | 3.9 | 44000 | 3.6667
216720852 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 51500 | 21 | 4.1 | 51500 | 4.2917
216720853 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-54D1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-454B | 56000 | 19.1 | 3.8 | 56000 | 4.6667
216720854 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 61500 | 19.1 | 4 | 61500 | 5.125
216720855 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-24D1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-454B | 16100 | 20.1 | 4.3 | 16100 | 1.3417
216720856 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-30D1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-454B | 20100 | 20.1 | 4.3 | 20100 | 1.675
216720857 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.1 | 24100 | 2.0083
216720858 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.5 | 32200 | 2.6833
216720859 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.6 | 40200 | 3.35
216720860 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.4 | 24100 | 2.0083
216720861 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.4 | 32200 | 2.6833
216720862 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.4 | 40200 | 3.35
216720863 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.4 | 24100 | 2.0083
216720864 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.4 | 32200 | 2.6833
216720865 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.6 | 40200 | 3.35
216720866 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 4.3 | 28100 | 2.3417
216720867 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 3.9 | 28100 | 2.3417
216720868 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 3.9 | 28100 | 2.3417
8224172 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SC-018-1C | AVS-018-* | [15 empty] | R-410A | 18000 | 17.1 | 3.6 | 18000 | 1.5
8229033 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SD-018-1C | AVS-018-* | [15 empty] | R-410A | 18000 | 17.1 | 3.6 | 18000 | 1.5
8229034 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SDH-018-1C | AVS-018-* | [15 empty] | R-410A | 18000 | 17.1 | 3.6 | 18000 | 1.5
8229035 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SDH-024-1C | AVS-024-* | [15 empty] | R-410A | 24000 | 17.1 | 3.6 | 24000 | 2
8229036 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SD-024-1C | AVS-024-* | [15 empty] | R-410A | 24000 | 17.1 | 3.6 | 24000 | 2
8229037 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SC-024-1C | AVS-024-* | [15 empty] | R-410A | 24000 | 17.1 | 3.6 | 24000 | 2
8229041 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SDH-036-1C | AVS-036-* | [15 empty] | R-410A | 36000 | 17.1 | 3.6 | 36000 | 3
8229042 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SD-036-1C | AVS-036-* | [15 empty] | R-410A | 36000 | 17.1 | 3.6 | 36000 | 3
8229043 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SC-036-1C | AVS-036-* | [15 empty] | R-410A | 36000 | 17.1 | 3.6 | 36000 | 3
201841510 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | PSC-024-1C | AVS-024-* | [15 empty] | R-410A | 18000 | 25 | 4.3 | 18000 | 1.5
201841515 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-018-1C | HVA-018-* | [15 empty] | R-410A | 18000 | 16 | 3.6 | 18000 | 1.5
201841516 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-024-1C | HVA-024-* | [15 empty] | R-410A | 24000 | 16 | 3.6 | 24000 | 2
201841517 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-030-1C | HVA-030-* | [15 empty] | R-410A | 30000 | 16 | 3.6 | 30000 | 2.5
201841518 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-036-1C | HVA-036-* | [15 empty] | R-410A | 36000 | 16 | 3.6 | 36000 | 3
201841519 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-042-1C | HVA-042-* | [15 empty] | R-410A | 42000 | 16 | 3.6 | 42000 | 3.5
201841520 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-048-1C | HVA-048-* | [15 empty] | R-410A | 48000 | 16 | 3.6 | 48000 | 4
201841521 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-054-1C | HVA-054-* | [15 empty] | R-410A | 54000 | 16 | 3.6 | 54000 | 4.5
201841522 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-060-1C | HVA-060-* | [15 empty] | R-410A | 60000 | 16 | 3.6 | 60000 | 5
201902854 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-24C1-CP1-*-* | AH-024-*-*-* | [15 empty] | R-410A | 18000 | 25 | 4.3 | 18000 | 1.5
201902855 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-36C1-CP1-*-* | AH-036-*-*-* | [15 empty] | R-410A | 28000 | 23 | 4.1 | 28000 | 2.3333
201902856 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-48C1-CP1-*-* | AH-048-*-*-* | [15 empty] | R-410A | 40000 | 23 | 4.1 | 40000 | 3.3333
201902857 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-60C1-CP1-*-* | AH-060-*-*-* | [15 empty] | R-410A | 49000 | 23 | 4.1 | 49000 | 4.0833
201902862 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-30C1-CP1-*-* | AH-030-*-*-* | [15 empty] | R-410A | 23000 | 25 | 4.3 | 23000 | 1.9167
201902863 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-36C1-CP1-*-* | AH-036-*-*-* | [15 empty] | R-410A | 28000 | 25 | 4.3 | 28000 | 2.3333
201902864 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-48C1-CP1-*-* | AH-048-*-*-* | [15 empty] | R-410A | 40000 | 25 | 4.3 | 40000 | 3.3333
201902865 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-24C1-*-* | AH-024-*-*-* | [15 empty] | R-410A | 24000 | 21 | 3.6 | 24000 | 2
201902866 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-24C1-CP1-*-* | AH-024-*-*-* | [15 empty] | R-410A | 24000 | 20.9 | 4 | 24000 | 2
201902867 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-30C1-CP1-*-* | AH-030-*-*-* | [15 empty] | R-410A | 30000 | 21 | 4 | 30000 | 2.5
201902868 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-30C1-*-* | AH-030-*-*-* | [15 empty] | R-410A | 30000 | 19.1 | 3.6 | 30000 | 2.5
201902869 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-36C1-*-* | AH-036-*-*-* | [15 empty] | R-410A | 36000 | 19.1 | 3.6 | 36000 | 3
201902870 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-36C1-CP1-*-* | AH-036-*-*-* | [15 empty] | R-410A | 36000 | 20.9 | 4 | 36000 | 3
201902871 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-42C1-CP1-*-* | AH-042-*-*-* | [15 empty] | R-410A | 42000 | 21 | 4 | 42000 | 3.5
201902872 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-42C1-*-* | AH-042-*-*-* | [15 empty] | R-410A | 42000 | 19.1 | 3.6 | 42000 | 3.5
201902873 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-48C1-*-* | AH-048-*-*-* | [15 empty] | R-410A | 48000 | 19.1 | 3.6 | 48000 | 4
201902874 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-48C1-CP1-*-* | AH-048-*-*-* | [15 empty] | R-410A | 48000 | 20.9 | 4 | 48000 | 4
201902875 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-60C1-*-* | AH-060-*-*-* | [15 empty] | R-410A | 60000 | 19.1 | 3.6 | 60000 | 5
201902876 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-60C1-CP1-*-* | AH-060-*-*-* | [15 empty] | R-410A | 60000 | 20.9 | 4 | 60000 | 5
201977884 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-54C1-*-* | AH-054-*-*-* | [15 empty] | R-410A | 54000 | 19.1 | 3.6 | 54000 | 4.5
201977885 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-54C1-CP1-*-* | AH-054-*-*-* | [15 empty] | R-410A | 54000 | 21 | 4 | 54000 | 4.5
201978151 | Test Brand 01 | HRCU-DGX-C | Direct Expansion Refrigerant | TEST MODEL | TEST MODEL | [15 empty] | R-407C | 20000 | 24 | 5 | 20000 | 1.6667
203105865 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-24C1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-410A | 24000 | 19.1 | 3.8 | 24000 | 2
203105866 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-30C1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-410A | 30000 | 19.1 | 3.8 | 30000 | 2.5
203470619 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-24C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 24000 | 19.1 | 3.6 | 24000 | 2
206374296 | Test Brand 01 | HRCU-DGX-C | Direct Expansion Refrigerant | TEST11922-1 | TEST MODEL | [15 empty] | R-32 | 20000 | 24 | 5 | 20000 | 1.6667
217607067 | BRAND_01 | HRCU-DGX-CB | Direct Expansion Refrigerant | MZ-TEST-ESPASS | AH-MZ-TEST-ESMIN | [15 empty] | R-454B | 24100 | 30 | 4.4 | 24100 | 2.0083
217730044 | BRAND_01 | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-36C1-CP*-*-* | S33-40LEWH-4500 | [15 empty] | R-410A | 38000 | 19.1 | 3.9 | 38000 | 3.1667
206438907 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV012**C0/BA* | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438908 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV012**C4/DA* | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438909 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH012**C0/BA* | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438910 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH012**C4/DA* | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438911 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV012**N0/BA* | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438912 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV012**N4/DA* | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438913 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH012**N0/BA* | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438914 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH012**N4/DA* | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206570649 | 7 SERIES | WBAHP | Water-to-Air and Brine-to-Air | NVV/NVH036C1*(1,2) |  | 32300 | 17.7 | 5.3 | 51000 | 2.6917 | 38000 | 31.2 | 4.5 | 41700 | 3.1667 | 35800 | 21.6 | 3.5 | 32900 | 2.9833
215415748 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)042A*VB | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
215415749 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)042A*VC | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
215415750 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)048A*B | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215415751 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)048A*C | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215415752 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)048A*VB | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
215415753 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)048A*VC | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
215415770 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)015A*B | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
215415771 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)015A*C | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
215415772 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)015A*VB | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
215415773 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)015A*VC | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
215415774 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)018A*B | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
215415775 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)018A*C | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
215415776 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)018A*VB | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
215415777 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)018A*VC | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
215415778 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)024A*B | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
215415779 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)024A*C | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
215415780 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)024A*VB | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
215415781 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)024A*VC | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
215415784 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)030A*VB | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
215415785 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)030A*VC | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
215415788 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)036A*VB | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
215415789 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)036A*VC | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
215415792 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)042A*VB | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
215415793 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)042A*VC | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
215415794 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*B | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215415795 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*C | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215415796 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*VB | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
215415797 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*VC | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
217351892 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS024SR*C******1 | F(C,T)MA5*36**** | [5 empty] | 28200 | 24.2 | 4.9 | 23400 | 2.35 | 26000 | 18.5 | 4.1 | 18800 | 2.1667
217351893 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS024SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 27600 | 23.7 | 4.8 | 23000 | 2.3 | 25400 | 18.1 | 4 | 18400 | 2.1167
217351894 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*36**** | [5 empty] | 40000 | 21.7 | 4.6 | 36600 | 3.3333 | 36800 | 16.9 | 3.7 | 28200 | 3.0667
217351895 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 39000 | 21.3 | 4.5 | 35800 | 3.25 | 36000 | 16.6 | 3.7 | 27600 | 3
217351896 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 41000 | 22.8 | 4.8 | 34800 | 3.4167 | 39000 | 18.5 | 3.7 | 27400 | 3.25
217351897 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 40500 | 22.3 | 4.7 | 34200 | 3.375 | 38000 | 18.1 | 3.7 | 26800 | 3.1667
217351898 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 52000 | 21.5 | 4.6 | 46500 | 4.3333 | 48500 | 17.1 | 4 | 37800 | 4.0417
217351899 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 51000 | 21 | 4.5 | 45500 | 4.25 | 47500 | 16.7 | 3.9 | 37000 | 3.9583
217351900 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*C******1 | F(C,T)MA5*60**** | [5 empty] | 63500 | 21.7 | 4.4 | 60000 | 5.2917 | 60500 | 17.6 | 3.7 | 47000 | 5.0417
217351901 | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*N******1 | F(C,T)MA5*60**** | [5 empty] | 62500 | 21.3 | 4.3 | 59000 | 5.2083 | 59500 | 17.3 | 3.7 | 46000 | 4.9583
217351903 | KEEPRITE | WBAHP-C | Water-to-Air and Brine-to-Air | HS024SR*C******1 | EAM5*2*M*** | [5 empty] | 27200 | 24.8 | 4.5 | 23900 | 2.2667 | 25900 | 17.5 | 3.8 | 18900 | 2.1583
216687113 | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SS024BD1 | W5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216687114 | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SS036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216687115 | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SS048BD1 | W5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216687116 | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SS060BD1 | W5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216687118 | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SZ024BD1 | W5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216687119 | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SZ036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216687120 | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SZ048BD1 | W5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216687121 | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SZ060BD1 | W5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216687731 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SS024BD1 | G5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216687732 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SS036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216687733 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SS048BD1 | G5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216687734 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SS060BD1 | G5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216687736 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SZ024BD1 | G5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216687737 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SZ036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216687738 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SZ048BD1 | G5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216687739 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SZ060BD1 | G5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216714606 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)006*R0**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
216714607 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)006*R2**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
216714612 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)015*R0**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
216714613 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)015*R0**4 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
216714614 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)015*R2**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
216714615 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)015*R2**4 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
216714620 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S0**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714621 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S0**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714622 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S2**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
207337510 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H022**1 | SRAA026* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207337511 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H030**1 | SAH030* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207337512 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H030**1 | SRAA026* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207337513 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J036**1 | SAH036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207337514 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J036**1 | SRAA036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
214839280 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-1HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839281 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-1VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839282 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-3HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839283 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-3VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839284 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-4HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839285 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-4VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
215400201 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036K3*B*C |  | 39000 | 18.32 | 5.34 | 44100 | 3.25
215400204 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042E1*B*T |  | 43000 | 18.36 | 5.43 | 47600 | 3.5833
215400205 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F3*B*T |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
215400208 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042E1*B*C |  | 43000 | 18.36 | 5.43 | 47600 | 3.5833
215400209 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F3*B*C |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
215400212 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048E1*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400213 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F3*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400216 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048E1*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400217 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F3*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400220 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060E1*B*T |  | 64000 | 17.4 | 5.3 | 78000 | 5.3333
215400221 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F3*B*T |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
215400222 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060E1*B*C |  | 64000 | 17.4 | 5.3 | 78000 | 5.3333
215400223 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F3*B*C |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
215402546 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV007E1*B*T |  | 7100 | 17.99 | 5.49 | 8100 | 0.59167
215402548 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV009E1*B*T |  | 9200 | 17.49 | 4.98 | 11000 | 0.76667
215402550 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024E1*B*T |  | 24400 | 18.37 | 5.79 | 28000 | 2.0333
215402551 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F3*B*T |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
215402554 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024E1*B*C |  | 24400 | 18.37 | 5.79 | 28000 | 2.0333
215402555 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F3*B*C |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
215402558 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030E1*B*T |  | 29200 | 19.17 | 5.67 | 34500 | 2.4333
215402559 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F3*B*T |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
215402562 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030E1*B*C |  | 29200 | 19.17 | 5.67 | 34500 | 2.4333
215402563 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F3*B*C |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
215402566 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036E1*B*T |  | 39000 | 19.02 | 5.35 | 44100 | 3.25
215402567 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036F3*B*T |  | 39000 | 18.4 | 5.34 | 44100 | 3.25
215402570 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036E1*B*C |  | 39000 | 19.02 | 5.35 | 44100 | 3.25
215402571 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036F3*B*C |  | 39000 | 18.4 | 5.34 | 44100 | 3.25
217351779 | BRYANT | WBWHP | Water-to-Water and Brine-to-Water | GW024WA********1 |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351780 | BRYANT | WBWHP | Water-to-Water and Brine-to-Water | GW036WA********1 | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351781 | BRYANT | WBWHP | Water-to-Water and Brine-to-Water | GW048WA********1 | [6 empty] | 44000 | 21.5 | 4.25 | 50000 | 3.6667 | 42500 | 16.9 | 3.46 | 39500 | 3.5417
217351782 | BRYANT | WBWHP | Water-to-Water and Brine-to-Water | GW060WA********1 | [6 empty] | 55000 | 20.7 | 3.96 | 59500 | 4.5833 | 51500 | 15.9 | 3.16 | 47500 | 4.2917
217351784 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS024SR*C******1 | F(C,T)MA5*36**** | [5 empty] | 28200 | 24.2 | 4.9 | 23400 | 2.35 | 26000 | 18.5 | 4.1 | 18800 | 2.1667
217351785 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS024SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 27600 | 23.7 | 4.8 | 23000 | 2.3 | 25400 | 18.1 | 4 | 18400 | 2.1167
217351786 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*36**** | [5 empty] | 40000 | 21.7 | 4.6 | 36600 | 3.3333 | 36800 | 16.9 | 3.7 | 28200 | 3.0667
217351787 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 39000 | 21.3 | 4.5 | 35800 | 3.25 | 36000 | 16.6 | 3.7 | 27600 | 3
217351788 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 41000 | 22.8 | 4.8 | 34800 | 3.4167 | 39000 | 18.5 | 3.7 | 27400 | 3.25
217351789 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 40500 | 22.3 | 4.7 | 34200 | 3.375 | 38000 | 18.1 | 3.7 | 26800 | 3.1667
217351790 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 52000 | 21.5 | 4.6 | 46500 | 4.3333 | 48500 | 17.1 | 4 | 37800 | 4.0417
217351791 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 51000 | 21 | 4.5 | 45500 | 4.25 | 47500 | 16.7 | 3.9 | 37000 | 3.9583
217351792 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*C******1 | F(C,T)MA5*60**** | [5 empty] | 63500 | 21.7 | 4.4 | 60000 | 5.2917 | 60500 | 17.6 | 3.7 | 47000 | 5.0417
217351793 | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*N******1 | F(C,T)MA5*60**** | [5 empty] | 62500 | 21.3 | 4.3 | 59000 | 5.2083 | 59500 | 17.3 | 3.7 | 46000 | 4.9583
217351795 | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS024SR*C******1 | EAM5*2*M*** | [5 empty] | 27200 | 24.8 | 4.5 | 23900 | 2.2667 | 25900 | 17.5 | 3.8 | 18900 | 2.1583
217351796 | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS024SR*N******1 | EAM5*2*M*** | [5 empty] | 26700 | 24.3 | 4.4 | 23400 | 2.225 | 25400 | 17.1 | 3.7 | 18500 | 2.1167
217351797 | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS036SR*C******1 | EAM5*3*M*** | [5 empty] | 40300 | 22.8 | 4.4 | 34500 | 3.3583 | 37400 | 17.7 | 3.6 | 27600 | 3.1167
217351798 | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS036SR*N******1 | EAM5*3*M*** | [5 empty] | 39500 | 22.3 | 4.3 | 33800 | 3.2917 | 36600 | 17.4 | 3.6 | 27100 | 3.05
217351799 | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS048SR*C******1 | EAM5*4*M*** | [5 empty] | 54600 | 22.3 | 4.6 | 46600 | 4.55 | 49000 | 17.1 | 3.9 | 37900 | 4.0833
217351800 | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS048SR*N******1 | EAM5*4*M*** | [5 empty] | 53500 | 21.9 | 4.5 | 45600 | 4.4583 | 48000 | 16.7 | 3.8 | 37100 | 4
202330346 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | WH-060-3-H-DCAC-C0-10-200-A |  | 59400 | 16.2 | 5.3 | 70300 | 4.95 | [5 empty] | 62700 | 16.57 | 3.27 | 44900 | 5.225
202330430 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | WV-060-A-H-DCAC-C0-10-200-A | [6 empty] | 62600 | 19.8 | 4.6 | 61500 | 5.2167
202330432 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | WV-060-3-H-DCAC-C0-10-200-A | [6 empty] | 62600 | 19.8 | 4.6 | 61500 | 5.2167
202330436 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-003-1-0-BCAY-V0-10-000-A | [6 empty] | 42600 | 23.1 | 4.3 | 37100 | 3.55
202330438 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-003-2-0-BCAY-V0-10-000-A | [6 empty] | 42600 | 23.1 | 4.3 | 37100 | 3.55
202330439 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-003-3-0-BCAY-V0-10-000-A | [6 empty] | 42600 | 23.1 | 4.3 | 37100 | 3.55
202330440 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-003-4-0-BCAY-V0-10-000-A | [6 empty] | 42600 | 23.1 | 4.3 | 37100 | 3.55
202330444 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-1-0-BCAY-V0-10-000-A | [6 empty] | 54000 | 23.5 | 4.6 | 45400 | 4.5
202330445 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-1-0-DCAY-S0-10-000-A | [6 empty] | 53000 | 21.8 | 4.6 | 44700 | 4.4167
202330446 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-2-0-BCAY-V0-10-000-A | [6 empty] | 54000 | 23.5 | 4.6 | 45400 | 4.5
202330447 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-3-0-BCAY-V0-10-000-A | [6 empty] | 54000 | 23.5 | 4.6 | 45400 | 4.5
202330448 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-4-0-BCAY-V0-10-000-A | [6 empty] | 54000 | 23.5 | 4.6 | 45400 | 4.5
202330449 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-2-0-DCAY-S0-10-000-A | [6 empty] | 53000 | 21.8 | 4.6 | 44700 | 4.4167
202330450 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-3-0-DCAY-S0-10-000-A | [6 empty] | 53000 | 21.8 | 4.6 | 44700 | 4.4167
202330451 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-4-0-DCAY-S0-10-000-A | [6 empty] | 53000 | 21.8 | 4.6 | 44700 | 4.4167
202330453 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-005-1-0-DCAY-S0-10-000-A | [6 empty] | 61500 | 22.3 | 4.6 | 53000 | 5.125
205698263 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT036*3 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698264 | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT036*3 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698265 | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT036*3 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698266 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT036 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698267 | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT036 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698268 | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT036 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698275 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT048*2 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698276 | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT048*2 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698277 | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT048*2 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698278 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT048*3 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698279 | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT048*3 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698280 | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT048*3 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205699453 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT048 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205699462 | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT048 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205699463 | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT048 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205752888 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TCH/V006A*W/K | [6 empty] | 7000 | 24 | 4.2 | 6300 | 0.58333
205754885 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V015A*W/K B | [6 empty] | 16500 | 25 | 4.5 | 14100 | 1.375 | 14800 | 18 | 3.6 | 11000 | 1.2333
205754886 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V015A*W/K C | [6 empty] | 16500 | 25 | 4.5 | 14100 | 1.375 | 14800 | 18 | 3.6 | 11000 | 1.2333
205754887 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V018A B | [6 empty] | 21500 | 22 | 4.2 | 17800 | 1.7917
205754888 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V018A C | [6 empty] | 21500 | 22 | 4.2 | 17800 | 1.7917
205754889 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V018A*W/K B | [6 empty] | 21500 | 23.6 | 4.5 | 17800 | 1.7917 | 19500 | 17.1 | 3.7 | 14100 | 1.625
205754890 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V018A*W/K C | [6 empty] | 21500 | 23.6 | 4.5 | 17800 | 1.7917 | 19500 | 17.1 | 3.7 | 14100 | 1.625
205754895 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V030A*W/K B | [6 empty] | 32000 | 21.6 | 4.3 | 30500 | 2.6667
205754896 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V030A*W/K C | [6 empty] | 32000 | 21.6 | 4.3 | 30500 | 2.6667
5220675 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH030B*E |  | 30000 | 17.3 | 5.8 | 33600 | 2.5 | [5 empty] | 31300 | 20.1 | 4.1 | 21600 | 2.6083
5220676 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH030B*F |  | 30000 | 17.3 | 5.8 | 33600 | 2.5 | [5 empty] | 31300 | 20.1 | 4.1 | 21600 | 2.6083
5220677 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH030B*J |  | 30000 | 17.3 | 5.8 | 33600 | 2.5 | [5 empty] | 31300 | 20.1 | 4.1 | 21600 | 2.6083
5220678 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH030B*K |  | 30000 | 17.3 | 5.8 | 33600 | 2.5 | [5 empty] | 31300 | 20.1 | 4.1 | 21600 | 2.6083
5220681 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH036B*E |  | 37300 | 19.2 | 6 | 40800 | 3.1083 | [5 empty] | 38500 | 22 | 4.3 | 26200 | 3.2083
215268781 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D2**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268782 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D4**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268783 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D2**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268784 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D4**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268785 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D4**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268786 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D2**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268787 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D4**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268788 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D4**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268789 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*D4**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
215268790 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*D2**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
215268791 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*D4**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
215268792 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*D4**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
215270403 | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024*******1**1 | FT*****36*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
215270404 | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FT*****36*** | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
215270405 | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FT*****48*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
215270406 | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1**1 | FT*****48*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
215270407 | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060*******1**1 | FT*****60*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
215270409 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024*******1**1 | FT*****36*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
215270410 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FT*****36*** | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
215270411 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FT*****48*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
215270412 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1**1 | FT*****48*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
215270413 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060*******1**1 | FT*****60*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
215270415 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024*******1**1 | FT*****36*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
215270416 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FT*****36*** | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
202330530 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-1-H-BCBC-V0-10-000-A | [6 empty] | 57500 | 26.1 | 4.4 | 46700 | 4.7917 | 51900 | 18.8 | 3.8 | 35200 | 4.325
202330531 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-1-H-DCAC-S0-10-000-A | [6 empty] | 54200 | 23.5 | 4.2 | 45800 | 4.5167 | 49200 | 17.9 | 3.6 | 34800 | 4.1
202330532 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-1-H-DCBC-S0-10-000-A | [6 empty] | 56200 | 23.9 | 4.4 | 46200 | 4.6833 | 50900 | 18.2 | 3.6 | 35100 | 4.2417
202330533 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-2-H-BCAC-V0-10-000-A | [6 empty] | 55200 | 24.7 | 4.3 | 46300 | 4.6 | 50000 | 18.3 | 3.6 | 35000 | 4.1667
202330534 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-2-H-BCBC-V0-10-000-A | [6 empty] | 57500 | 26.1 | 4.4 | 46700 | 4.7917 | 51900 | 18.8 | 3.8 | 35200 | 4.325
202330535 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-2-H-DCAC-S0-10-000-A | [6 empty] | 54200 | 23.5 | 4.2 | 45800 | 4.5167 | 49200 | 17.9 | 3.6 | 34800 | 4.1
202330536 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-2-H-DCBC-S0-10-000-A | [6 empty] | 56200 | 23.9 | 4.4 | 46200 | 4.6833 | 50900 | 18.2 | 3.6 | 35100 | 4.2417
202330537 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-3-H-BCAC-V0-10-000-A | [6 empty] | 55200 | 24.7 | 4.3 | 46300 | 4.6 | 50000 | 18.3 | 3.6 | 35000 | 4.1667
202330538 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-3-H-BCBC-V0-10-000-A | [6 empty] | 57500 | 26.1 | 4.4 | 46700 | 4.7917 | 51900 | 18.8 | 3.8 | 35200 | 4.325
202330539 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-3-H-DCAC-S0-10-000-A | [6 empty] | 54200 | 23.5 | 4.2 | 45800 | 4.5167 | 49200 | 17.9 | 3.6 | 34800 | 4.1
202330540 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-3-H-DCBC-S0-10-000-A | [6 empty] | 56200 | 23.9 | 4.4 | 46200 | 4.6833 | 50900 | 18.2 | 3.6 | 35100 | 4.2417
202330541 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-4-H-BCAC-V0-10-000-A | [6 empty] | 55200 | 24.7 | 4.3 | 46300 | 4.6 | 50000 | 18.3 | 3.6 | 35000 | 4.1667
202330542 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-4-H-BCBC-V0-10-000-A | [6 empty] | 57500 | 26.1 | 4.4 | 46700 | 4.7917 | 51900 | 18.8 | 3.8 | 35200 | 4.325
202330543 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-4-H-DCAC-S0-10-000-A | [6 empty] | 54200 | 23.5 | 4.2 | 45800 | 4.5167 | 49200 | 17.9 | 3.6 | 34800 | 4.1
202330544 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-4-H-DCBC-S0-10-000-A | [6 empty] | 56200 | 23.9 | 4.4 | 46200 | 4.6833 | 50900 | 18.2 | 3.6 | 35100 | 4.2417
202330547 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-005-1-H-DCAC-S0-10-000-A | [6 empty] | 62100 | 23.7 | 4.1 | 50000 | 5.175
202330551 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-005-2-H-DCAC-S0-10-000-A | [6 empty] | 62100 | 23.7 | 4.1 | 50000 | 5.175
202330555 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-005-3-H-DCAC-S0-10-000-A | [6 empty] | 62100 | 23.7 | 4.1 | 50000 | 5.175
202330559 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-005-4-H-DCAC-S0-10-000-A | [6 empty] | 62100 | 23.7 | 4.1 | 50000 | 5.175
215851777 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH048K3*C/S*C |  | 48200 | 16.99 | 4.98 | 56900 | 4.0167
215851778 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH048L3*C/S*C |  | 48200 | 16.82 | 4.93 | 56900 | 4.0167
215851783 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060K3*C/S*C |  | 60000 | 16.46 | 4.8 | 68600 | 5
215851784 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060L3*C/S*C |  | 60000 | 16.3 | 4.75 | 68600 | 5
215851795 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024J1*C/S*C |  | 24300 | 17.24 | 5.7 | 28000 | 2.025
215851796 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024K3*C/S*C |  | 24300 | 17.06 | 5.64 | 28000 | 2.025
215851801 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030J1*C/S*C |  | 31200 | 16.63 | 5.41 | 34700 | 2.6
215851803 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030K3*C/S*C |  | 31200 | 16.46 | 5.35 | 34700 | 2.6
215851809 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036J1*C/S*C |  | 38100 | 18.08 | 5.08 | 41100 | 3.175
215851810 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036K3*C/S*C |  | 38100 | 17.89 | 5.03 | 41100 | 3.175
215851815 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042K3*C/S*C |  | 43500 | 16.78 | 4.91 | 50000 | 3.625
215851818 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048K3*C/S*C |  | 50800 | 17.27 | 5.41 | 58500 | 4.2333
215851820 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048L3*C/S*C |  | 50800 | 17.09 | 5.35 | 58500 | 4.2333
215851825 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060K3*C/S*C |  | 60500 | 16.95 | 5.39 | 74700 | 5.0417
215851826 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060L3*C/S*C |  | 60500 | 16.78 | 5.34 | 74700 | 5.0417
215852846 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH024E1*C/S*C |  | 24500 | 17.53 | 5.29 | 26100 | 2.0417
215852847 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH024F3*C/S*C |  | 24500 | 17.18 | 5.19 | 26100 | 2.0417
215852850 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH030E1*C/S*C |  | 31400 | 17.12 | 5.36 | 34900 | 2.6167
215852851 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH030F3*C/S*C |  | 31400 | 16.78 | 5.26 | 34900 | 2.6167
215852854 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH036E1*C/S*C |  | 38000 | 18.43 | 5.36 | 42900 | 3.1667
215852855 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH036F3*C/S*C |  | 38000 | 18.06 | 5.25 | 42900 | 3.1667
9114315 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT060*A****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114316 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT060*A****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114317 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT060*A****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9910449 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS018*****1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910450 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS018*****1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910451 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS018*****1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910452 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910453 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910454 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
215415734 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)024A*B | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
215415735 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)024A*C | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
215415736 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)024A*VB | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
215415737 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)024A*VC | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
215415740 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)030A*VB | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
215415741 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)030A*VC | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
215415744 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)036A*VB | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
215415745 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BC(L/R/B/P/T/K/F)036A*VC | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
214772068 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK042B | [6 empty] | 47100 | 24.5 | 4.14 | 46200 | 3.925
214772069 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK0424 | [6 empty] | 47100 | 24.5 | 4.14 | 46200 | 3.925
214772070 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK048B | [6 empty] | 54500 | 24 | 4.31 | 50800 | 4.5417 | 50900 | 18.4 | 3.6 | 38900 | 4.2417
214772071 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK0484 | [6 empty] | 54500 | 24 | 4.31 | 50800 | 4.5417 | 50900 | 18.4 | 3.6 | 38900 | 4.2417
214772072 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK060B | [6 empty] | 64300 | 23.9 | 4.23 | 63700 | 5.3583 | 60100 | 18.3 | 3.65 | 50200 | 5.0083
214772073 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK0604 | [6 empty] | 64300 | 23.9 | 4.23 | 63700 | 5.3583 | 60100 | 18.3 | 3.65 | 50200 | 5.0083
214772074 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK0097 |  | 8700 | 18.1 | 6.4 | 10700 | 0.725 | 9600 | 29.7 | 5.16 | 8500 | 0.8 | 9000 | 21.2 | 3.91 | 6100 | 0.75
214772075 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK0127 |  | 11400 | 17.1 | 5.9 | 14300 | 0.95 | 12500 | 26.1 | 4.98 | 11500 | 1.0417 | 11900 | 19.8 | 3.78 | 8500 | 0.99167
214772076 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK0157 | [6 empty] | 17100 | 24.6 | 4.6 | 15600 | 1.425 | 16200 | 18.7 | 3.73 | 11800 | 1.35
214772077 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK0187 |  | 18900 | 17.5 | 5.43 | 23000 | 1.575 | 21100 | 29.6 | 4.77 | 18600 | 1.7583 | 19700 | 20.8 | 3.93 | 14400 | 1.6417
214772078 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK024B |  | 25300 | 18.1 | 5.55 | 32000 | 2.1083 | 27400 | 28.4 | 4.81 | 25900 | 2.2833 | 26200 | 21.2 | 3.8 | 19400 | 2.1833
216054500 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS006* | [6 empty] | 6900 | 22.9 | 4.3 | 6300 | 0.575
216057511 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVT060* | [6 empty] | 64200 | 22 | 4.5 | 57500 | 5.35 | 60900 | 17.6 | 3.8 | 46300 | 5.075
216057513 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS015* | [6 empty] | 15600 | 24.9 | 4.8 | 14300 | 1.3 | 14200 | 17.6 | 3.9 | 11200 | 1.1833
216057514 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS017* | [6 empty] | 18000 | 21.9 | 4.1 | 15800 | 1.5
216057515 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS018* | [6 empty] | 21400 | 26 | 4.7 | 17500 | 1.7833 | 20100 | 18.7 | 3.7 | 14100 | 1.675
216065302 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWS036* | [6 empty] | 35600 | 22.9 | 4.1 | 38300 | 2.9667 | 34900 | 17.7 | 3.3 | 31000 | 2.9083
216065303 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWS048* | [6 empty] | 52500 | 22.9 | 4.2 | 58700 | 4.375 | 50500 | 17.3 | 3.2 | 45200 | 4.2083
216065305 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT036* | [6 empty] | 42200 | 20.4 | 4.1 | 48000 | 3.5167 | 40200 | 15.4 | 3.3 | 38100 | 3.35
216065306 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT048* | [6 empty] | 52700 | 21.2 | 4.2 | 61100 | 4.3917 | 49500 | 16.3 | 3.5 | 49000 | 4.125
216065307 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT060* | [6 empty] | 62700 | 20.4 | 3.9 | 67000 | 5.225 | 60600 | 16.2 | 3.1 | 52900 | 5.05
216128491 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5TV036BD1**2 |  | 36000 | 17.9 | 5.6 | 42300 | 3 | 41400 | 26.9 | 5.1 | 35700 | 3.45 | 38000 | 20.1 | 4.3 | 29300 | 3.1667
216128493 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5TV048BD1**2 | [6 empty] | 52500 | 24.5 | 4.7 | 47400 | 4.375 | 49100 | 18.5 | 4.1 | 38400 | 4.0917
216411469 | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | SJ/PN024A | SAN024A | [5 empty] | 24700 | 25.2 | 4.8 | 22500 | 2.0583 | 23900 | 19 | 4 | 17900 | 1.9917
216411470 | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | SJ/PN036A | SAN036A | 36400 | 17.3 | 5.3 | 39400 | 3.0333 | 41800 | 25 | 4.7 | 33700 | 3.4833 | 38300 | 18.4 | 4 | 26900 | 3.1917
216411471 | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | SJ/PN048A | SAN048A | [5 empty] | 51900 | 22.2 | 4.4 | 46000 | 4.325 | 49000 | 18.1 | 3.7 | 35500 | 4.0833
216419856 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
216419857 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
216419860 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
216419863 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
216419865 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
216419867 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
216419868 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
216419879 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
216419880 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
216419882 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)018A | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
216419883 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)018A*V | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
216419898 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
216419899 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
216419902 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
216419904 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
216419907 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
216419908 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215743525 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0127 | [6 empty] | 13300 | 23.2 | 4.3 | 11600 | 1.1083
215746915 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK036A3 |  | 40281 | 19.2 | 6.06 | 47492 | 3.3567 | 43925 | 29.6 | 5.26 | 39058 | 3.6604 | 41280 | 22.1 | 4.28 | 29804 | 3.44
215746916 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK048A3 |  | 53537 | 17.6 | 5.79 | 62760 | 4.4614 | 57887 | 27.2 | 5.05 | 51760 | 4.8239 | 55159 | 20.4 | 4.14 | 39719 | 4.5966
215746923 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK036A4 |  | 40281 | 19.2 | 6.06 | 47492 | 3.3567 | 43925 | 29.6 | 5.26 | 39058 | 3.6604 | 41280 | 22.1 | 4.28 | 29804 | 3.44
215746924 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK036AW |  | 40281 | 19.2 | 6.06 | 47492 | 3.3567 | 43925 | 29.6 | 5.26 | 39058 | 3.6604 | 41280 | 22.1 | 4.28 | 29804 | 3.44
215746925 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK048A4 |  | 53537 | 17.6 | 5.79 | 62760 | 4.4614 | 57887 | 27.2 | 5.05 | 51760 | 4.8239 | 55159 | 20.4 | 4.14 | 39719 | 4.5966
215746926 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK048AW |  | 53537 | 17.6 | 5.79 | 62760 | 4.4614 | 57887 | 27.2 | 5.05 | 51760 | 4.8239 | 55159 | 20.4 | 4.14 | 39719 | 4.5966
215748031 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | R-55-HACW-X-1T-*-*DE** | [6 empty] | 48000 | 22.2 | 4.5 | 47000 | 4 | 43900 | 16 | 3.8 | 35600 | 3.6583
215748227 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SMT(S,M)24A*Q |  | 25000 | 17.6 | 5.1 | 28000 | 2.0833 | [5 empty] | 25900 | 20.4 | 3.7 | 18000 | 2.1583
217642919 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S3**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642920 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S3**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642921 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S4**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642922 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S4**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642938 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)006*R0**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
217642941 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)015*R0**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
217642943 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S0**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
217642945 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S0**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
217642946 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)042*S0**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217903459 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5R048*D4**5* | [6 empty] | 51000 | 23.9 | 4.9 | 47300 | 4.25 | 48500 | 18.1 | 3.8 | 38500 | 4.0417
4219424 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | R45HACW-P-1T-*-SDE** | [6 empty] | 38500 | 21.3 | 4.3 | 35700 | 3.2083 | 35100 | 16.3 | 3.6 | 27200 | 2.925
4219425 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | R55HACW-P-1T-*-SDE** | [6 empty] | 50200 | 22.5 | 4.5 | 47200 | 4.1833 | 45400 | 17 | 3.8 | 35600 | 3.7833
205754919 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JSH/V006A B | [6 empty] | 7400 | 25.5 | 4.4 | 6300 | 0.61667
205754920 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JSH/V006A C | [6 empty] | 7400 | 25.5 | 4.4 | 6300 | 0.61667
205754921 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JSH/V009A B | [6 empty] | 11100 | 25.2 | 4.3 | 9400 | 0.925
205754922 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JSH/V009A C | [6 empty] | 11100 | 25.2 | 4.3 | 9400 | 0.925
205767467 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | QEV/H/D1860 |  | 48000 | 17.3 | 5.5 | 60000 | 4 | 48000 | 35.5 | 4.3 | 60000 | 4 | 48000 | 21.6 | 3.3 | 60000 | 4
205767468 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H024B | [6 empty] | 26500 | 21.7 | 4.1 | 23000 | 2.2083 | 24600 | 16 | 3.6 | 17800 | 2.05
205767469 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H030 | [6 empty] | 32300 | 20.7 | 4.2 | 30000 | 2.6917 | 29900 | 15.7 | 3.6 | 23800 | 2.4917
205767470 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H036B | [6 empty] | 38200 | 22.3 | 4.3 | 35100 | 3.1833 | 35200 | 16.7 | 3.6 | 27300 | 2.9333
205767471 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H042 | [6 empty] | 46300 | 21.3 | 4.1 | 42300 | 3.8583 | 43100 | 16.1 | 3.4 | 33300 | 3.5917
205767472 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H048 | [6 empty] | 51800 | 20.9 | 4.4 | 45000 | 4.3167 | 48100 | 15.5 | 3.7 | 35600 | 4.0083
205767473 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TEV/H/D026B |  | 25000 | 17.4 | 6 | 31400 | 2.0833 | 28500 | 26.4 | 5.3 | 25800 | 2.375 | 26000 | 19.9 | 4.1 | 20200 | 2.1667
205767474 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TEV/H/D038B |  | 37700 | 17.9 | 5.8 | 45700 | 3.1417 | 42100 | 26.1 | 5.2 | 37900 | 3.5083 | 39000 | 20.3 | 4.4 | 29700 | 3.25
205767475 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TEV/H/D049B |  | 48600 | 16.8 | 5.1 | 56700 | 4.05 | 55000 | 25.3 | 4.6 | 46800 | 4.5833 | 49600 | 19.3 | 4 | 36400 | 4.1333
205767476 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TEV/H/D064B |  | 61500 | 16.2 | 5.4 | 77400 | 5.125
206608720 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J048**1* | SRAA048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
206608721 | 5 SERIES INDOOR SPLITS | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ060J1* | SAH060* | [5 empty] | 61700 | 23.6 | 4.3 | 54500 | 5.1417 | 56300 | 17.7 | 3.7 | 44000 | 4.6917
206608722 | 5 SERIES INDOOR SPLITS | WBAHP-C | Water-to-Air and Brine-to-Air | NSZ060J1* | SRAA060* | [5 empty] | 61700 | 23.6 | 4.3 | 54500 | 5.1417 | 56300 | 17.7 | 3.7 | 44000 | 4.6917
206608723 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J060**1* | SAH060* | [5 empty] | 61700 | 23.6 | 4.3 | 54500 | 5.1417 | 56300 | 17.7 | 3.7 | 44000 | 4.6917
206608724 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J060**1* | SRAA060* | [5 empty] | 61700 | 23.6 | 4.3 | 54500 | 5.1417 | 56300 | 17.7 | 3.7 | 44000 | 4.6917
206611110 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEH/V024C | [6 empty] | 26500 | 21.7 | 4.1 | 23000 | 2.2083 | 24600 | 16 | 3.6 | 17800 | 2.05
206611111 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEH/V024C | [6 empty] | 26500 | 21.7 | 4.1 | 23000 | 2.2083 | 24600 | 16 | 3.6 | 17800 | 2.05
206611112 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEH/V030C | [6 empty] | 32300 | 20.7 | 4.2 | 30000 | 2.6917 | 29900 | 15.7 | 3.6 | 23800 | 2.4917
206611113 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEH/V030C | [6 empty] | 32300 | 20.7 | 4.2 | 30000 | 2.6917 | 29900 | 15.7 | 3.6 | 23800 | 2.4917
206611114 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEH/V036C | [6 empty] | 38200 | 22.3 | 4.3 | 35100 | 3.1833 | 35200 | 16.7 | 3.6 | 27300 | 2.9333
206611115 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEH/V036C | [6 empty] | 38200 | 22.3 | 4.3 | 35100 | 3.1833 | 35200 | 16.7 | 3.6 | 27300 | 2.9333
206611116 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEH/V042C | [6 empty] | 46300 | 21.3 | 4.1 | 42300 | 3.8583 | 43100 | 16.1 | 3.4 | 33300 | 3.5917
206611117 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEH/V042C | [6 empty] | 46300 | 21.3 | 4.1 | 42300 | 3.8583 | 43100 | 16.1 | 3.4 | 33300 | 3.5917
206611118 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEH/V048C | [6 empty] | 51800 | 20.9 | 4.4 | 45000 | 4.3167 | 48100 | 15.5 | 3.7 | 35600 | 4.0083
206611119 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEH/V048C | [6 empty] | 51800 | 20.9 | 4.4 | 45000 | 4.3167 | 48100 | 15.5 | 3.7 | 35600 | 4.0083
206703384 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921140/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703385 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921141/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703386 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921230/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703387 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921231/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703388 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921240/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703389 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921241/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703390 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921330/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703391 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921331/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703392 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921340/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703393 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921341/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703394 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931130/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703395 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931131/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703396 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931140/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703397 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931141/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703398 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931230/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703399 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931231/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703400 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931240/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703401 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931241/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703402 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931330/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703403 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931331/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703404 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931340/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703405 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931341/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206710951 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921130/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206710952 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921131/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206722530 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TRH/V006A*W/K | [6 empty] | 7000 | 24 | 4.2 | 6300 | 0.58333
202729325 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729332 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729333 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729334 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729335 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729336 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729337 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202732300 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP042-1VT*******B | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732301 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732302 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732303 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732304 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732305 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732306 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732307 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732308 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732913 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSN-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 16.95 | 3.8 | 27400 | 3.1583
202732914 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP018-1HZ*******C | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732915 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSN-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 16.95 | 3.8 | 27400 | 3.1583
202732916 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP018-1HZ*******C | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732917 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732918 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732919 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732920 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732921 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732922 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732923 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732924 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732931 | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NEW040*1* | [6 empty] | 33000 | 20.1 | 4 | 40000 | 2.75 | 30600 | 16.1 | 3.3 | 34000 | 2.55
202732932 | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NEW050*1* | [6 empty] | 47000 | 20.1 | 3.9 | 54900 | 3.9167 | 44500 | 16.1 | 3.3 | 45000 | 3.7083
202732934 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036H3 | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
214063785 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
214063786 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
214067547 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**3*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
214067548 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**3*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214067549 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**3*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214067550 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**4*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
214067551 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**4*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214067552 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**4*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214067553 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**3*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214067554 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**3*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214067555 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**4*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214067556 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**4*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214067557 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
214067558 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214067559 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214067560 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
214067561 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214067562 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214067563 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**3*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
214067564 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**3*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214067565 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**3*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214067566 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**4*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
214067567 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**4*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214067568 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**4*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214067569 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**3*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214067570 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**3*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214067571 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214067572 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214067573 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**3*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
214067574 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**3*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214067575 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**3*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214067576 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**4*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
214067577 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**4*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214067578 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**4*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
205503115 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM024-1CS*******A | BVA-24WN1-M20 | [5 empty] | 28600 | 22.1 | 4.8 | 24200 | 2.3833 | 26500 | 16.6 | 4 | 19000 | 2.2083
205503116 | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | SM024-1CS*******A | BMAC2430BNTD | [5 empty] | 27400 | 23.2 | 4.8 | 24000 | 2.2833 | 25500 | 18.1 | 3.95 | 18900 | 2.125
205503117 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | BVA-36WN1-M20 | [5 empty] | 38400 | 21.3 | 4.5 | 36500 | 3.2 | 36400 | 16.8 | 3.95 | 29200 | 3.0333
205503118 | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | BMAC3036BNTD | [5 empty] | 39600 | 20.5 | 4.6 | 36000 | 3.3 | 37100 | 16.4 | 4.05 | 29800 | 3.0917
205503119 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | LM024-1CS*******A | BVA-24WN1-M20 | [5 empty] | 28600 | 22.1 | 4.8 | 24200 | 2.3833 | 26500 | 16.6 | 4 | 19000 | 2.2083
205503120 | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | LM024-1CS*******A | BMAC2430BNTD | [5 empty] | 27400 | 23.2 | 4.8 | 24000 | 2.2833 | 25500 | 18.1 | 3.95 | 18900 | 2.125
205503121 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | LM036-1CSC-*****B | BVA-36WN1-M20 | [5 empty] | 38400 | 21.3 | 4.5 | 36500 | 3.2 | 36400 | 16.8 | 3.95 | 29200 | 3.0333
205503122 | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | LM036-1CSC-*****B | BMAC3036BNTD | [5 empty] | 39600 | 20.5 | 4.6 | 36000 | 3.3 | 37100 | 16.4 | 4.05 | 29800 | 3.0917
205503123 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM024-1CS*******A | BVA-24WN1-M20 | [5 empty] | 28600 | 22.1 | 4.8 | 24200 | 2.3833 | 26500 | 16.6 | 4 | 19000 | 2.2083
205503124 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | SM024-1CS*******A | BMAC2430BNTD | [5 empty] | 27400 | 23.2 | 4.8 | 24000 | 2.2833 | 25500 | 18.1 | 3.95 | 18900 | 2.125
205503125 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | BVA-36WN1-M20 | [5 empty] | 38400 | 21.3 | 4.5 | 36500 | 3.2 | 36400 | 16.8 | 3.95 | 29200 | 3.0333
205503126 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | BMAC3036BNTD | [5 empty] | 39600 | 20.5 | 4.6 | 36000 | 3.3 | 37100 | 16.4 | 4.05 | 29800 | 3.0917
205503127 | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | LM024-1CS*******A | BVA-24WN1-M20 | [5 empty] | 28600 | 22.1 | 4.8 | 24200 | 2.3833 | 26500 | 16.6 | 4 | 19000 | 2.2083
205503128 | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | LM024-1CS*******A | BMAC2430BNTD | [5 empty] | 27400 | 23.2 | 4.8 | 24000 | 2.2833 | 25500 | 18.1 | 3.95 | 18900 | 2.125
205503129 | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | LM036-1CSC-*****B | BVA-36WN1-M20 | [5 empty] | 38400 | 21.3 | 4.5 | 36500 | 3.2 | 36400 | 16.8 | 3.95 | 29200 | 3.0333
205503130 | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | LM036-1CSC-*****B | BMAC3036BNTD | [5 empty] | 39600 | 20.5 | 4.6 | 36000 | 3.3 | 37100 | 16.4 | 4.05 | 29800 | 3.0917
205652453 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM048-1CS*-*****A | BVA-48WN1-M20 | [5 empty] | 54000 | 23.1 | 4.8 | 47000 | 4.5 | 51700 | 18.1 | 4 | 38000 | 4.3083
205652455 | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | SM048-1CS*-*****A | BMAC4248CNTF | [5 empty] | 52000 | 21.6 | 4.5 | 45500 | 4.3333 | 50300 | 17.5 | 3.9 | 37200 | 4.1917
205652456 | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | SM060-1CS*-*****A | BMAC4860CNTF | [5 empty] | 63600 | 20.5 | 4.4 | 58600 | 5.3 | 61800 | 16.9 | 3.8 | 47700 | 5.15
205652457 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | LM048-1CS*-*****A | BVA-48WN1-M20 | [5 empty] | 54000 | 23.1 | 4.8 | 47000 | 4.5 | 51700 | 18.1 | 4 | 38000 | 4.3083
205652459 | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | LM048-1CS*-*****A | BMAC4248CNTF | [5 empty] | 52000 | 21.6 | 4.5 | 45500 | 4.3333 | 50300 | 17.5 | 3.9 | 37200 | 4.1917
205652460 | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | LM060-1CS*-*****A | BMAC4860CNTF | [5 empty] | 63600 | 20.5 | 4.4 | 58600 | 5.3 | 61800 | 16.9 | 3.8 | 47700 | 5.15
205652461 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM048-1CS*-*****A | BVA-48WN1-M20 | [5 empty] | 54000 | 23.1 | 4.8 | 47000 | 4.5 | 51700 | 18.1 | 4 | 38000 | 4.3083
205652463 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | SM048-1CS*-*****A | BMAC4248CNTF | [5 empty] | 52000 | 21.6 | 4.5 | 45500 | 4.3333 | 50300 | 17.5 | 3.9 | 37200 | 4.1917
205652464 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | SM060-1CS*-*****A | BMAC4860CNTF | [5 empty] | 63600 | 20.5 | 4.4 | 58600 | 5.3 | 61800 | 16.9 | 3.8 | 47700 | 5.15
205652465 | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | LM048-1CS*-*****A | BVA-48WN1-M20 | [5 empty] | 54000 | 23.1 | 4.8 | 47000 | 4.5 | 51700 | 18.1 | 4 | 38000 | 4.3083
205652467 | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | LM048-1CS*-*****A | BMAC4248CNTF | [5 empty] | 52000 | 21.6 | 4.5 | 45500 | 4.3333 | 50300 | 17.5 | 3.9 | 37200 | 4.1917
205652468 | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | LM060-1CS*-*****A | BMAC4860CNTF | [5 empty] | 63600 | 20.5 | 4.4 | 58600 | 5.3 | 61800 | 16.9 | 3.8 | 47700 | 5.15
205698260 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT036*2 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698261 | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT036*2 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698262 | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT036*2 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
215224613 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*015***4*(A-H)** | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224614 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*015***4*(J-R)** | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224615 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*018***3*(A-H)** | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224616 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*018***3*(J-R)** | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224617 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*018***4*(A-H)** | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224618 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*018***4*(J-R)** | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224619 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***3*(A-H)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224620 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***3*(J-R)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224621 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***4*(A-H)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224622 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***4*(J-R)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224623 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***5*(A-H)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224624 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***5*(J-R)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224625 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***6*(A-H)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224626 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***6*(J-R)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224627 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***3*(A-H)** | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224628 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***3*(J-R)** | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224629 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***4*(A-H)** | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224630 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***4*(J-R)** | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224631 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***5*(A-H)** | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224632 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***5*(J-R)** | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224633 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***6*(A-H)** | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224634 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***6*(J-R)** | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224635 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***3*(A-H)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224636 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***3*(J-R)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224637 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***4*(A-H)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224638 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***4*(J-R)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224639 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***5*(A-H)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224640 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***5*(J-R)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224641 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***6*(A-H)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224642 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***6*(J-R)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224643 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042***3*(A-H)** | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224644 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042***3*(J-R)** | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224645 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042***5*(A-H)** | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224646 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042***5*(J-R)** | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224647 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042***6*(A-H)** | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
202732935 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036H4 | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
202732936 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036HW | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
202732937 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048H3 | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
202732938 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048H4 | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
202732939 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048HW | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
215742630 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 31630/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742631 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 31640/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742632 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 21630/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742633 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 21640/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215743134 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK006 | [6 empty] | 9300 | 21.7 | 4.5 | 8100 | 0.775
215743135 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK009 | [6 empty] | 9500 | 23 | 4.5 | 8400 | 0.79167
215743136 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK012 | [6 empty] | 13300 | 23.2 | 4.3 | 11600 | 1.1083
215743520 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0062 | [6 empty] | 9300 | 21.7 | 4.5 | 8100 | 0.775
215743521 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0067 | [6 empty] | 9300 | 21.7 | 4.5 | 8100 | 0.775
215743522 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0092 | [6 empty] | 9500 | 23 | 4.5 | 8400 | 0.79167
215743523 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0097 | [6 empty] | 9500 | 23 | 4.5 | 8400 | 0.79167
215743524 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0122 | [6 empty] | 13300 | 23.2 | 4.3 | 11600 | 1.1083
7519574 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*A | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519575 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*A | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519576 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519577 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519578 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519579 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
207200608 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS038*1*J | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207200609 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS038*1*J | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207200610 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HE040*1* | [6 empty] | 33000 | 20.1 | 4 | 40000 | 2.75 | 30600 | 16.1 | 3.3 | 34000 | 2.55
207200611 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HE050*1* | [6 empty] | 47000 | 20.1 | 3.9 | 54900 | 3.9167 | 44500 | 16.1 | 3.3 | 45000 | 3.7083
207200613 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | QT038**1*(1,2)* | [6 empty] | 38200 | 23.8 | 4.5 | 33200 | 3.1833 | 36000 | 18.7 | 3.9 | 27400 | 3
207200614 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | VI036**1*(1,2)** |  | 32300 | 17.7 | 5.3 | 51000 | 2.6917 | 38000 | 31.2 | 4.5 | 41700 | 3.1667 | 35800 | 21.6 | 3.5 | 32900 | 2.9833
207200615 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | VI048**1*1* |  | 40700 | 16.9 | 4.9 | 67000 | 3.3917 | 49000 | 30 | 4 | 55200 | 4.0833 | 45000 | 20 | 3.4 | 43500 | 3.75
207200616 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | VI060**1*1* |  | 50000 | 15.9 | 4.9 | 79000 | 4.1667 | 60000 | 27.1 | 4.3 | 66000 | 5 | 56000 | 19.1 | 3.4 | 51700 | 4.6667
214776161 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK009 | [6 empty] | 9500 | 23.6 | 4.13 | 8600 | 0.79167
214776167 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0091-5 | [6 empty] | 9700 | 27 | 4.44 | 8400 | 0.80833
214776168 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0121-5 | [6 empty] | 13500 | 26.2 | 4.21 | 10500 | 1.125
214776169 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0151-5 | [6 empty] | 16500 | 21.8 | 4.79 | 16400 | 1.375 | 15800 | 17.1 | 3.93 | 12500 | 1.3167
214776170 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0181-5 | [6 empty] | 19400 | 21.6 | 4.47 | 19000 | 1.6167
214776171 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0241-5 | [6 empty] | 26300 | 24 | 4.56 | 24700 | 2.1917 | 25200 | 18.5 | 3.82 | 20100 | 2.1
214776172 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0361-5 | [6 empty] | 41700 | 22.6 | 4.26 | 37200 | 3.475
214776173 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0092 | [6 empty] | 9500 | 23.6 | 4.13 | 8600 | 0.79167
214776174 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0097 | [6 empty] | 9500 | 23.6 | 4.13 | 8600 | 0.79167
214776185 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0092-5 | [6 empty] | 9700 | 27 | 4.44 | 8400 | 0.80833
214776186 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0097-5 | [6 empty] | 9700 | 27 | 4.44 | 8400 | 0.80833
214776187 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0122-5 | [6 empty] | 13500 | 26.2 | 4.21 | 10500 | 1.125
214776188 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0127-5 | [6 empty] | 13500 | 26.2 | 4.21 | 10500 | 1.125
214776189 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0152-5 | [6 empty] | 16500 | 21.8 | 4.79 | 16400 | 1.375 | 15800 | 17.1 | 3.93 | 12500 | 1.3167
214776190 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0157-5 | [6 empty] | 16500 | 21.8 | 4.79 | 16400 | 1.375 | 15800 | 17.1 | 3.93 | 12500 | 1.3167
214776191 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0182-5 | [6 empty] | 19400 | 21.6 | 4.47 | 19000 | 1.6167
214776192 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0187-5 | [6 empty] | 19400 | 21.6 | 4.47 | 19000 | 1.6167
214776193 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0242-5 | [6 empty] | 26300 | 24 | 4.56 | 24700 | 2.1917 | 25200 | 18.5 | 3.82 | 20100 | 2.1
214776194 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0247-5 | [6 empty] | 26300 | 24 | 4.56 | 24700 | 2.1917 | 25200 | 18.5 | 3.82 | 20100 | 2.1
214776195 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0362-5 | [6 empty] | 41700 | 22.6 | 4.26 | 37200 | 3.475
214776196 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0367-5 | [6 empty] | 41700 | 22.6 | 4.26 | 37200 | 3.475
214796343 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)024BD1**2 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
214796344 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)030BD1**2 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
214796345 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)036BD1**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
214796346 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)042BD1**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
214796347 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)048BD1**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
214796667 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)018BD1**2 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
214810491 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018BD1**2 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
214810492 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024BD1**2 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
214810493 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030BD1**2 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
214810494 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036BD1**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
214810495 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042BD1**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
214810496 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048BD1**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
214823444 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)018BD1**2 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
214823445 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024BD1**2 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
202873345 | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YAWE050**1* | [6 empty] | 47000 | 20.1 | 3.9 | 54900 | 3.9167 | 44500 | 16.1 | 3.3 | 45000 | 3.7083
202921908 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-1VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921909 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-3VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921910 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-4VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921911 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP036-1VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921912 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921913 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-3HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921914 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-4HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921915 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921952 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921953 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-3HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921954 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-4HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921956 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921957 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-1VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921958 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-3VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921959 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-4VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921960 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP036-1VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922686 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***3/CA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922689 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***5/EA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922692 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***6/FA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922695 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922697 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922700 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922703 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922706 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922708 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922711 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922714 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922716 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV036***3/CA |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922719 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV036***5/EA |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922722 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV036***6/FA |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922725 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922728 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922731 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922734 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922737 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922740 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922742 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922745 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
203113888 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J036**1 | SAH036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
212587993 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX09*-7 | [6 empty] | 11500 | 23.9 | 4.1 | 8800 | 0.95833
212587994 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | HRCX09*-7 | [6 empty] | 11500 | 23.9 | 4.1 | 8800 | 0.95833
201907619 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*0*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907620 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*0*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907621 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*0*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907622 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907623 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907624 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907625 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907626 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907627 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907628 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
201907629 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
201907630 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
201907631 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
201907632 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
201907633 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207349401 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349402 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349403 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**4*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349404 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**4*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349405 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**3*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349406 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207530615 | BOSCH | WBAHP-O | Water-to-Air and Brine-to-Air | CA009-1*C-*****D | [6 empty] | 10000 | 22.1 | 4.25 | 8600 | 0.83333
207542447 | FHP | WBAHP-O | Water-to-Air and Brine-to-Air | CA009-1*C-*****D | [6 empty] | 10000 | 22.1 | 4.25 | 8600 | 0.83333
207549518 | CARRIER | WBAHP-O | Water-to-Air and Brine-to-Air | 50PEC09***E3/CF | [6 empty] | 10000 | 22.1 | 4.25 | 8600 | 0.83333
213711981 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048E1*B*T |  | 48300 | 17.5 | 5 | 57000 | 4.025
213711982 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048E1*B*C |  | 48300 | 17.5 | 5 | 57000 | 4.025
213711984 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH060E1*B*T |  | 60872 | 17.4 | 5.72 | 78027 | 5.0727
215837698 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030F3*C/S*T |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
217754443 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F1*B*T |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
217754446 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F1*B*C |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
217754449 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F1*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
217754453 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F1*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
217754457 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F1*B*T |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
217754461 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F1*B*C |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
217754553 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030F1*C/S*C |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
217754554 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030K1*C/S*C |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
216625455 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)009*R2**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
216625456 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)012*R2**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
216625457 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)015*R2**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216625458 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)015*R0**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216625459 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)015*R2**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216625460 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*R2**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216625461 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*R0**4 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216625462 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*R2**4 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216625463 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S2**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625464 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S3**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625465 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S4**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625466 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S0**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625467 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S2**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625468 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S3**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625469 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S4**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625470 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*S2**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625645 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*D0**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625646 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*D2**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625647 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*D2**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625648 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*D3**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625649 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*D3**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625650 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*D4**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625651 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*D4**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625652 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*S0**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625653 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*S0**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625654 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*S2**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625655 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*S2**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625656 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*S3**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625657 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*S3**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625658 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*S4**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625659 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030*S4**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625660 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D0**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625661 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D0**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625662 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D0**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625663 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D2**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625664 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D2**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625665 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D2**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625666 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D3**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625667 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D3**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625668 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D3**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625669 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D4**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625670 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D4**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625671 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D4**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625672 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S0**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625673 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S0**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625674 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S0**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625675 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S2**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625676 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S2**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625677 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S2**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625678 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S3**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625679 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S3**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625680 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S3**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625681 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S4**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625682 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S4**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625683 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S4**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625684 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D0**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625685 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D0**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625686 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D0**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625687 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D2**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625688 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D3**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625689 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D3**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625690 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D3**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625691 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D4**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625692 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D4**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625693 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D4**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625694 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S0**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625695 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S0**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
204100658 | 5 SERIES INDOOR SPLITS | WBAHP-CB | Water-to-Air and Brine-to-Air | NDZ064J1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
204100659 | 5 SERIES INDOOR SPLITS | WBAHP-C | Water-to-Air and Brine-to-Air | NDZ064J1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
204100660 | 5 SERIES OUTDOOR SPLITS | WBAHP-CB | Water-to-Air and Brine-to-Air | NDS064J1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
204100661 | 5 SERIES OUTDOOR SPLITS | WBAHP-C | Water-to-Air and Brine-to-Air | NDS064J1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
204101161 | 5 SERIES | WBAHP | Water-to-Air and Brine-to-Air | NDV/NDH064J1*(1,4) |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
204117015 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 101/102J064**1*(1,4) |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
204117016 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
204117017 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
204140569 | GEO-THERMAL SPLIT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ024*******1**1 | CAP**24**AL* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
204140570 | CARRIER | WBAHP-C | Water-to-Air and Brine-to-Air | GZ024*******1**1 | CAP**24**AL* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
204140571 | BRYANT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ024*******1**1 | CAP**24**AL* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
204140572 | HEIL | WBAHP-C | Water-to-Air and Brine-to-Air | HS024*******1**1 | EAM4X24L**A* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
204140573 | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS024*******1**1 | EAM4X24L**A* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
204140574 | KEEPRITE | WBAHP-C | Water-to-Air and Brine-to-Air | HS024*******1**1 | EAM4X24L**A* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
204140575 | TEMPSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | HS024*******1**1 | EAM4X24L**A* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
204140576 | COMFORTMAKER | WBAHP-C | Water-to-Air and Brine-to-Air | HS024*******1**1 | EAM4X24L**A* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
204140577 | DAY & NIGHT | WBAHP-C | Water-to-Air and Brine-to-Air | HS024*******1**1 | EAM4X24L**A* | [5 empty] | 28000 | 22.5 | 4.3 | 23900 | 2.3333 | 26100 | 15.9 | 3.45 | 19000 | 2.175
207177429 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG006A | [6 empty] | 8100 | 21.3 | 4.1 | 7500 | 0.675
216979845 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979846 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979847 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979848 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
215399790 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024J1*C/S*T |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215399791 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024K3*C/S*T |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215399794 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024J1*C/S*C |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215399795 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024K3*C/S*C |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
5423010 | TTHERM GEO | WBWHP | Water-to-Water and Brine-to-Water | THA-036-* | [6 empty] | 40100 | 20.7 | 3.7 | 43900 | 3.3417 | 36600 | 16.1 | 3.1 | 32300 | 3.05
5423011 | TTHERM GEO | WBWHP | Water-to-Water and Brine-to-Water | THA-048-* | [6 empty] | 55100 | 20.1 | 3.6 | 60100 | 4.5917 | 54200 | 16.1 | 3.1 | 45200 | 4.5167
207337515 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J042**1 | SAH042* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207337516 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J042**1 | SRAA048* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207337517 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H048**1 | SAH048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
207337518 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H048**1 | SRAA048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
207338124 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | QT064**1*1* | [6 empty] | 63900 | 21 | 4.5 | 58600 | 5.325 | 58300 | 16.2 | 3.8 | 46600 | 4.8583
207338125 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | YT024*A | [6 empty] | 25100 | 20.6 | 4.4 | 23500 | 2.0917 | 23100 | 15.6 | 3.8 | 18900 | 1.925
207338127 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 141/142C036**1*(1,2) |  | 32300 | 17.7 | 5.3 | 51000 | 2.6917 | 38000 | 31.2 | 4.5 | 41700 | 3.1667 | 35800 | 21.6 | 3.5 | 32900 | 2.9833
207338128 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 141/142C048**1*1 |  | 40700 | 16.9 | 4.9 | 67000 | 3.3917 | 49000 | 30 | 4 | 55200 | 4.0833 | 45000 | 20 | 3.4 | 43500 | 3.75
207338129 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 141/142C060**1*1 |  | 50000 | 15.9 | 4.9 | 79000 | 4.1667 | 60000 | 27.1 | 4.3 | 66000 | 5 | 56000 | 19.1 | 3.4 | 51700 | 4.6667
207338249 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETE0241-5 | [6 empty] | 25100 | 22.1 | 4.2 | 22400 | 2.0917
207338250 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETE0242-5 | [6 empty] | 25100 | 22.1 | 4.2 | 22400 | 2.0917
207338251 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETE0247-5 | [6 empty] | 25100 | 22.1 | 4.2 | 22400 | 2.0917
207348654 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*0*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348655 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*0*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348656 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*0*5 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348657 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*3*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348658 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*3*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348659 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*3*5 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348660 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*4*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348661 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*4*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348662 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*4*5 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207348663 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*0*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348664 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*0*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348665 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*0*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348666 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348667 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348668 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348669 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348670 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348671 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
215832281 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6009D* | [6 empty] | 10000 | 23 | 4.2 | 8000 | 0.83333 | 9500 | 18.9 | 3.6 | 6500 | 0.79167
215832282 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6012D* | [6 empty] | 13000 | 23 | 4.6 | 11000 | 1.0833 | 12000 | 17.9 | 3.8 | 8500 | 1
215832283 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6018D* | [6 empty] | 20400 | 25 | 4.3 | 16000 | 1.7 | 19000 | 18 | 3.6 | 12000 | 1.5833
215832284 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6024D* | [6 empty] | 28000 | 25 | 4.3 | 21400 | 2.3333 | 26000 | 18.4 | 3.6 | 17500 | 2.1667
215832285 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6030D* | [6 empty] | 32400 | 24 | 4.2 | 26000 | 2.7 | 30000 | 18.4 | 3.6 | 21000 | 2.5
215832286 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6036D* | [6 empty] | 39000 | 23.2 | 4.1 | 35000 | 3.25 | 36400 | 18 | 3.6 | 28000 | 3.0333
215832287 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6042D* | [6 empty] | 45500 | 23.3 | 4.3 | 38000 | 3.7917 | 43500 | 18.5 | 3.8 | 31000 | 3.625
215832288 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6048D* | [6 empty] | 52500 | 23.6 | 4.2 | 45500 | 4.375 | 49500 | 18 | 3.6 | 36000 | 4.125
215832289 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6060D* | [6 empty] | 64000 | 23.5 | 4.3 | 51000 | 5.3333 | 60000 | 18.1 | 3.6 | 41000 | 5
215832291 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6009D* | [6 empty] | 10000 | 23 | 4.2 | 8000 | 0.83333 | 9500 | 18.9 | 3.6 | 6500 | 0.79167
215832292 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6012D* | [6 empty] | 13000 | 23 | 4.6 | 11000 | 1.0833 | 12000 | 17.9 | 3.8 | 8500 | 1
215832293 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6018D* | [6 empty] | 20400 | 25 | 4.3 | 16000 | 1.7 | 19000 | 18 | 3.6 | 12000 | 1.5833
215832294 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6024D* | [6 empty] | 28000 | 25 | 4.3 | 21400 | 2.3333 | 26000 | 18.4 | 3.6 | 17500 | 2.1667
215832295 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6030D* | [6 empty] | 32400 | 24 | 4.2 | 26000 | 2.7 | 30000 | 18.4 | 3.6 | 21000 | 2.5
215832296 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6036D* | [6 empty] | 39000 | 23.2 | 4.1 | 35000 | 3.25 | 36400 | 18 | 3.6 | 28000 | 3.0333
215832297 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6042D* | [6 empty] | 45500 | 23.3 | 4.3 | 38000 | 3.7917 | 43500 | 18.5 | 3.8 | 31000 | 3.625
215832298 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6048D* | [6 empty] | 52500 | 23.6 | 4.2 | 45500 | 4.375 | 49500 | 18 | 3.6 | 36000 | 4.125
215832299 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6060D* | [6 empty] | 64000 | 23.5 | 4.3 | 51000 | 5.3333 | 60000 | 18.1 | 3.6 | 41000 | 5
217752718 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060K1*B*C |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
217752724 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH024K1*B*C |  | 24500 | 17 | 5.14 | 26100 | 2.0417
217752726 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH030K1*B*C |  | 31400 | 16.61 | 5.2 | 34900 | 2.6167
217752728 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH036K1*B*C |  | 38000 | 17.88 | 5.2 | 42900 | 3.1667
217752730 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH042K1*B*C |  | 44000 | 17.07 | 4.97 | 50300 | 3.6667
217752732 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH048K1*B*C |  | 48200 | 16.99 | 4.98 | 56900 | 4.0167
217752733 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH048L1*B*C |  | 48200 | 16.82 | 4.93 | 56900 | 4.0167
217752736 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060K1*B*C |  | 60000 | 16.46 | 4.8 | 68600 | 5
217752737 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060L1*B*C |  | 60000 | 16.3 | 4.75 | 68600 | 5
217752744 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024K1*B*C |  | 24300 | 17.06 | 5.64 | 28000 | 2.025
215270417 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FT*****48*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
215270418 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1**1 | FT*****48*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
215270419 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060*******1**1 | FT*****60*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
215270421 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024*******1**1 | FE****003*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
215270422 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE****003*** | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
215270423 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE****005*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
215270424 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1**1 | FE****005*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
215270425 | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060*******1**1 | FE****006*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
215270427 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024*******1**1 | FE****003*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
215270428 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE****003*** | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
215270429 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE****005*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
215270430 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1**1 | FE****005*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
215270431 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060*******1**1 | FE****006*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
215278610 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W3A(V/H)024BD1**1 | [6 empty] | 25700 | 21.3 | 4.6 | 23000 | 2.1417 | 23200 | 15.7 | 4 | 19000 | 1.9333
215278611 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W3A(V/H)036BD1**1 | [6 empty] | 37500 | 20.5 | 4.3 | 35400 | 3.125 | 35600 | 15.8 | 3.7 | 26800 | 2.9667
215278612 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W3A(V/H)048BD1**1 | [6 empty] | 51200 | 19.6 | 4.2 | 46000 | 4.2667 | 49000 | 16 | 3.7 | 37300 | 4.0833
215278613 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W3A(V/H)060BD1**1 | [6 empty] | 63000 | 18.8 | 4 | 55800 | 5.25 | 59500 | 15.2 | 3.4 | 45800 | 4.9583
215285739 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 5.7 | 29000 | 2.1083 | 28600 | 26.1 | 5 | 23700 | 2.3833 | 26300 | 19.9 | 4.1 | 17800 | 2.1917
215285740 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 5.3 | 43100 | 3.125 | 42000 | 23.9 | 4.8 | 36000 | 3.5 | 39200 | 18.6 | 4.2 | 28400 | 3.2667
215285741 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 5.4 | 60200 | 4 | 55000 | 26 | 4.6 | 49100 | 4.5833 | 51700 | 19.4 | 4 | 38200 | 4.3083
215285742 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)060A |  | 61800 | 16.9 | 5.4 | 67300 | 5.15 | [5 empty] | 62600 | 18.7 | 3.9 | 44300 | 5.2167
216801913 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT035-2***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801914 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT035-4***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801916 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT061-4***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801918 | BOSCH-GEO | WBWHP | Water-to-Water and Brine-to-Water | TW025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801919 | BOSCH-GEO | WBWHP | Water-to-Water and Brine-to-Water | TW035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801920 | BOSCH-GEO | WBWHP | Water-to-Water and Brine-to-Water | TW049-1***-*****C | [6 empty] | 44000 | 21.5 | 4.25 | 50000 | 3.6667 | 42500 | 16.9 | 3.46 | 39500 | 3.5417
216801921 | BOSCH-GEO | WBWHP | Water-to-Water and Brine-to-Water | TW061-1***-*****C | [6 empty] | 55000 | 20.7 | 3.96 | 59500 | 4.5833 | 51500 | 15.9 | 3.16 | 47500 | 4.2917
216801922 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801923 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT025-3***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801924 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801925 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT035-3***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801928 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT061-1***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801929 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT061-3***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801932 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***3/CB |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801933 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***4/DB |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801934 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***5/EB |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801935 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***6/FB |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801936 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW035***3/CB | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801937 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW035***4/DB | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801938 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW035***5/EB | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801939 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW035***6/FB | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801943 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW061***3/CB | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801944 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW061***5/EB | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801945 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW061***6/FB | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801983 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**3*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801984 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**3*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801985 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**3*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801986 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**3*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801987 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**4*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801988 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**4*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801989 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**4*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
215852858 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH042E1*C/S*C |  | 44000 | 17.59 | 5.12 | 50300 | 3.6667
215852859 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH042F3*C/S*C |  | 44000 | 17.24 | 5.02 | 50300 | 3.6667
215852862 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060E1*C/S*C |  | 60000 | 16.8 | 4.9 | 68600 | 5
215852863 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060F3*C/S*C |  | 60000 | 16.46 | 4.8 | 68600 | 5
10304639 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | YAZT026**1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10304640 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | YAZT026**1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10304641 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ026*1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10304642 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H026**1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10304646 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H026**1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10304657 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTZ026*1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10305457 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104H026**1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10305458 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104H026**1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10316642 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | YAST026**1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10316643 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS026*1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10316644 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | YAST026**1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10316645 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS026*1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
10316654 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | YAST049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
10316655 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104H049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
10316656 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS049*1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
10316657 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | YAST049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
10316658 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS049*1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
10316660 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104H049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
10316661 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | YAST064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
214595581 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-2-0-GCBC-V0-10-000-A | [6 empty] | 48100 | 21.3 | 4.1 | 48300 | 4.0083
214595583 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-3-0-GCBC-V0-10-000-A | [6 empty] | 48100 | 21.3 | 4.1 | 48300 | 4.0083
214595585 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-4-0-GCBC-V0-10-000-A | [6 empty] | 48100 | 21.3 | 4.1 | 48300 | 4.0083
214595607 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-003-2-H-GCBC-V0-10-000-A | [6 empty] | 46200 | 25 | 4.2 | 36500 | 3.85
214595611 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-003-3-H-GCBC-V0-10-000-A | [6 empty] | 46200 | 25 | 4.2 | 36500 | 3.85
214595615 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-003-4-H-GCBC-V0-10-000-A | [6 empty] | 46200 | 25 | 4.2 | 36500 | 3.85
214595618 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-1-H-FCAC-S0-10-000-A | [6 empty] | 54200 | 23 | 4.1 | 44000 | 4.5167
214595619 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-1-H-FCBC-S0-10-000-A | [6 empty] | 56200 | 23.4 | 4.3 | 44400 | 4.6833
214595620 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-2-H-GCAC-V0-10-000-A | [6 empty] | 55200 | 24.2 | 4.2 | 44400 | 4.6
214595621 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-2-H-GCBC-V0-10-000-A | [6 empty] | 57500 | 25.6 | 4.3 | 44800 | 4.7917 | 51900 | 18.4 | 3.7 | 33800 | 4.325
214595622 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-2-H-FCAC-S0-10-000-A | [6 empty] | 54200 | 23 | 4.1 | 44000 | 4.5167
214595623 | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-2-H-FCBC-S0-10-000-A | [6 empty] | 56200 | 23.4 | 4.3 | 44400 | 4.6833
215852868 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024E1*C/S*C |  | 24300 | 17.59 | 5.81 | 28000 | 2.025
215852869 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024F3*C/S*C |  | 24300 | 17.24 | 5.7 | 28000 | 2.025
215852870 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030E1*C/S*C |  | 31200 | 16.97 | 5.52 | 34700 | 2.6
215852871 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030F3*C/S*C |  | 31200 | 16.63 | 5.41 | 34700 | 2.6
215852874 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036E1*C/S*C |  | 38100 | 18.45 | 5.18 | 41100 | 3.175
215852875 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036F3*C/S*C |  | 38100 | 18.08 | 5.08 | 41100 | 3.175
215852878 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042E1*C/S*C |  | 43500 | 17.3 | 5.06 | 50000 | 3.625
215852879 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042F3*C/S*C |  | 43500 | 16.95 | 4.96 | 50000 | 3.625
215852882 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048E1*C/S*C |  | 50800 | 17.62 | 5.52 | 58500 | 4.2333
215852883 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048F3*C/S*C |  | 50800 | 17.27 | 5.41 | 58500 | 4.2333
215852884 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060E1*C/S*C |  | 60500 | 17.3 | 5.5 | 74700 | 5.0417
215852885 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060F3*C/S*C |  | 60500 | 16.95 | 5.39 | 74700 | 5.0417
216739869 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV024E1*C/S*C |  | 22700 | 15.3 | 5 | 27800 | 1.8917
216739881 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036E1*C/S*C |  | 35600 | 16.5 | 4.9 | 39100 | 2.9667
216739882 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036F3*C/S*C |  | 35600 | 16.2 | 4.8 | 39100 | 2.9667
216739883 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036J1*C/S*C |  | 35600 | 16.2 | 4.8 | 39100 | 2.9667
216739884 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036K3*C/S*C |  | 35600 | 16 | 4.8 | 39100 | 2.9667
216739895 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048E1*C/S*C |  | 49200 | 16.9 | 5 | 58000 | 4.1
216739896 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048F3*C/S*C |  | 49200 | 16.5 | 4.9 | 58000 | 4.1
216739897 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048K3*C/S*C |  | 49200 | 16.5 | 4.9 | 58000 | 4.1
216739910 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024E1*C/S*C |  | 24400 | 16.9 | 5.1 | 29500 | 2.0333
216739911 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024F3*C/S*C |  | 24400 | 16.6 | 5 | 29500 | 2.0333
216739912 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024J1*C/S*C |  | 24400 | 16.6 | 5 | 29500 | 2.0333
216739913 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024K3*C/S*C |  | 24400 | 16.4 | 5 | 29500 | 2.0333
5646388 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT036D3 | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646389 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT036D3 | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646391 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT048D | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646392 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT048D | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646393 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT048D | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646394 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT048D2 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646395 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT048D2 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646396 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT048D2 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646397 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT048D3 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646398 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT048D3 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646399 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT048D3 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646765 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT048D | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646766 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT048D | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646767 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT048D | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646768 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT048D2 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646769 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT048D2 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646770 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT048D2 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646771 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT048D3 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646772 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT048D3 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646773 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT048D3 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5699505 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0421 |  | 44100 | 18.25 | 5.95 | 54700 | 3.675 | 50100 | 32.46 | 5.08 | 43600 | 4.175 | 46200 | 22.03 | 3.98 | 31900 | 3.85
5699525 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0422 |  | 44100 | 18.25 | 5.95 | 54700 | 3.675 | 50100 | 32.46 | 5.08 | 43600 | 4.175 | 46200 | 22.03 | 3.98 | 31900 | 3.85
5699526 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0424 |  | 44100 | 18.25 | 5.95 | 54700 | 3.675 | 50100 | 32.46 | 5.08 | 43600 | 4.175 | 46200 | 22.03 | 3.98 | 31900 | 3.85
5699527 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0601 |  | 61800 | 15.6 | 5.5 | 81200 | 5.15 | [5 empty] | 64600 | 18.3 | 4 | 50000 | 5.3833
5699534 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0602 |  | 61800 | 15.6 | 5.5 | 81200 | 5.15 | [5 empty] | 64600 | 18.3 | 4 | 50000 | 5.3833
5699535 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0604 |  | 61800 | 15.6 | 5.5 | 81200 | 5.15 | [5 empty] | 64600 | 18.3 | 4 | 50000 | 5.3833
5699628 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0241 |  | 25100 | 18.3 | 6.44 | 30300 | 2.0917 | 28400 | 31.76 | 5.33 | 24300 | 2.3667 | 26200 | 21.82 | 4.35 | 18500 | 2.1833
5699631 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0242 |  | 25100 | 18.3 | 6.44 | 30300 | 2.0917 | 28400 | 31.76 | 5.33 | 24300 | 2.3667 | 26200 | 21.82 | 4.35 | 18500 | 2.1833
5699633 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0244 |  | 25100 | 18.3 | 6.44 | 30300 | 2.0917 | 28400 | 31.76 | 5.33 | 24300 | 2.3667 | 26200 | 21.82 | 4.35 | 18500 | 2.1833
5699634 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0331 |  | 33800 | 15.79 | 5.85 | 40200 | 2.8167 | 37900 | 25.01 | 4.98 | 32300 | 3.1583 | 35300 | 18.51 | 4.1 | 24700 | 2.9417
5699635 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0332 |  | 33800 | 15.79 | 5.85 | 40200 | 2.8167 | 37900 | 25.01 | 4.98 | 32300 | 3.1583 | 35300 | 18.51 | 4.1 | 24700 | 2.9417
5699637 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0334 |  | 33800 | 15.79 | 5.85 | 40200 | 2.8167 | 37900 | 25.01 | 4.98 | 32300 | 3.1583 | 35300 | 18.51 | 4.1 | 24700 | 2.9417
5699639 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0421 |  | 42600 | 18.6 | 6.7 | 51800 | 3.55 | 47300 | 30.9 | 5.6 | 42000 | 3.9417 | 44600 | 22 | 4.5 | 31500 | 3.7167
5699644 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0422 |  | 42600 | 18.6 | 6.7 | 51800 | 3.55 | 47300 | 30.9 | 5.6 | 42000 | 3.9417 | 44600 | 22 | 4.5 | 31500 | 3.7167
5699650 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0424 |  | 42600 | 18.6 | 6.7 | 51800 | 3.55 | 47300 | 30.9 | 5.6 | 42000 | 3.9417 | 44600 | 22 | 4.5 | 31500 | 3.7167
5699652 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0501 |  | 50200 | 16.5 | 5.8 | 64400 | 4.1833 | 56200 | 26 | 5.1 | 52500 | 4.6833 | 52400 | 19.3 | 4.2 | 40100 | 4.3667
5699653 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0502 |  | 50200 | 16.5 | 5.8 | 64400 | 4.1833 | 56200 | 26 | 5.1 | 52500 | 4.6833 | 52400 | 19.3 | 4.2 | 40100 | 4.3667
5699654 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0504 |  | 50200 | 16.5 | 5.8 | 64400 | 4.1833 | 56200 | 26 | 5.1 | 52500 | 4.6833 | 52400 | 19.3 | 4.2 | 40100 | 4.3667
5699655 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0601 |  | 60700 | 14.8 | 5.3 | 81600 | 5.0583 | [5 empty] | 63200 | 17 | 3.8 | 50400 | 5.2667
6501973 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**3*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
6501974 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
6501975 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
6501986 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
6501987 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
6501988 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
6501989 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**3*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
6501990 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**4*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
6501991 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**4*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
6581406 | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YAWS018**1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
6581407 | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YAWS025**1 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
207335338 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 111K038**1*(1,2)* | [6 empty] | 38200 | 23.8 | 4.5 | 33200 | 3.1833 | 36000 | 18.7 | 3.9 | 27400 | 3
207335397 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GT026**1*(1,4)*J |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
207335398 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GT038**1*(1,2,4)*K |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207335399 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GT049**1*(1,2,4)*K |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207335400 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GT064**1*(1,4)*K |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207335402 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS012**1*0*J | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
207335403 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS018**1*(1,4)*J | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
207335404 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS018**1*0*J | [6 empty] | 20600 | 24.7 | 4.3 | 18700 | 1.7167
207335406 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS022**1*(1,4)*J | [6 empty] | 21900 | 27.5 | 5 | 19500 | 1.825 | 19200 | 18.7 | 4 | 15000 | 1.6
207335407 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS030**1*(0,3)*J |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
207335408 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS030**1*(1,4)*J |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
207335409 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS036**1*(0,3)*K |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207335410 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS036**1*(1,2,4)*K | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
207335411 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS042**1*(0,3)*K | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
207335412 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS048**1*(0,3)*K | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
207335413 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS048**1*(1,2,4)*K | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207335514 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS042**1*(1,2,4)*K |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
207335570 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFS012**1*0****J | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
207335571 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFS018**1*(1,4)****J | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
207335572 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFS022**1*(1,4)****J | [6 empty] | 21900 | 27.5 | 5 | 19500 | 1.825 | 19200 | 18.7 | 4 | 15000 | 1.6
207335573 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFS030**1*(1,4)****J |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
207335574 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFS036**1*(1,2,4)*K | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
207335575 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFS042**1*(1,2,4)*K |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
207335576 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFS048**1*(1,2,4)*K | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207335579 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFT026**1*(1,4)****J |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
207335580 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFT038**1*(1,4)*K |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207335581 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFT049**1*(1,4)*K |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207335582 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YAFT064**1*(1,4)*K |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207335584 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YZFT026**1*(1,4)****H |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
207335585 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YZFT038**1*(1,4)*J |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207335586 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YZFT049**1*(1,4)*J |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207335587 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YZFT064**1*(1,4)*J |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
209156961 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6024A | [6 empty] | 25400 | 24 | 4.1 | 22000 | 2.1167
209156963 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6036A | [6 empty] | 41500 | 24 | 4.1 | 35500 | 3.4583
209156964 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6042A | [6 empty] | 46500 | 24 | 4.2 | 39000 | 3.875
209156974 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6006*6* | [6 empty] | 8600 | 26 | 4.5 | 7200 | 0.71667
209156975 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6009*6* | [6 empty] | 11200 | 26 | 4.5 | 8200 | 0.93333
209156976 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6012*6* | [6 empty] | 13800 | 26 | 4.5 | 10400 | 1.15
209156977 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6015*6* | [6 empty] | 18100 | 23.1 | 4.3 | 15500 | 1.5083
209156981 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSHXE06A6* | [6 empty] | 7800 | 23.5 | 4.3 | 6400 | 0.65
209156987 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSHXE06A7* | [6 empty] | 7800 | 23.5 | 4.3 | 6400 | 0.65
209156993 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6006*7* | [6 empty] | 8600 | 26 | 4.5 | 7200 | 0.71667
209156994 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6009*7* | [6 empty] | 11200 | 26 | 4.5 | 8200 | 0.93333
209156995 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6012*7* | [6 empty] | 13800 | 26 | 4.5 | 10400 | 1.15
216979849 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979850 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979851 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979852 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979853 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979854 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979855 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979856 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979857 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979858 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979859 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979860 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979861 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979862 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979863 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979864 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979865 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979866 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979867 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979868 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979869 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979870 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979871 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979872 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979873 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979874 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979875 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979876 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979877 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979878 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979879 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979880 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979881 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979882 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979883 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979884 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979885 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979886 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979887 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979888 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979889 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979890 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979891 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979892 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979893 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979894 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979895 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979896 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
7487661 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT048 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487662 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT048 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487663 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT048 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487664 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT048*2 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487665 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT048*2 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487666 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT048*2 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487667 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT048*3 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487668 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT048*3 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487669 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT048*3 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7499543 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM024-1CF/HZ/VT*-*****A |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7499546 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM024-2CF/HZ/VT*-*****A |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7499547 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM024-3CF/HZ/VT*-*****A |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7499548 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM024-4CF/HZ/VT*-*****A |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7499550 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM036-1VT/CF/HZ*-*****A |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7499552 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM036-2VT/CF/HZ*-*****A |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7499553 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM036-3VT/CF/HZ*-*****A |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7499554 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM036-4VT/CF/HZ*-*****A |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7499556 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM048-1VT/CF/HZ*-*****A | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7499559 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM048-3VT/CF/HZ*-*****A | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7499560 | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM048-4VT/CF/HZ*-*****A | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
5599272 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | SM036-1CF/HZ/VT |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
217037819 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SZ060BD1 | S5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037821 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SS024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037822 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037823 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SS048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037824 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SS060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037826 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SZ024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037827 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037828 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SZ048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037829 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SZ060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217048157 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S024SN10* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048158 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S024SN12* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048159 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S024SN14* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048160 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S048SN10* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048161 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S048SN13* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048162 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S048SN14* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048163 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S048SN15* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048164 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S060SN10* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048165 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S060SN13* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048166 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S060SN14* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048167 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S060SN15* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048174 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S024SN10* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048175 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S024SN12* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048176 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S024SN14* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048794 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ024BS1* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048795 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ048BS1* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048796 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ060BS1* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048798 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S024SN10* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048799 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S024SN12* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048800 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S024SN14* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048801 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S048SN10* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048802 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S048SN13* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048803 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S048SN14* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048804 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S048SN15* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048805 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S060SN10* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048806 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S060SN13* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048807 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S060SN14* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048808 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S060SN15* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217351752 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | GW024WA********1 |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351753 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | GW036WA********1 | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351754 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | GW048WA********1 | [6 empty] | 44000 | 21.5 | 4.25 | 50000 | 3.6667 | 42500 | 16.9 | 3.46 | 39500 | 3.5417
217351755 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | GW060WA********1 | [6 empty] | 55000 | 20.7 | 3.96 | 59500 | 4.5833 | 51500 | 15.9 | 3.16 | 47500 | 4.2917
217351757 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | [5 empty] | 28200 | 24.2 | 4.9 | 23400 | 2.35 | 26000 | 18.5 | 4.1 | 18800 | 2.1667
217351758 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | [5 empty] | 27600 | 23.7 | 4.8 | 23000 | 2.3 | 25400 | 18.1 | 4 | 18400 | 2.1167
217351759 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | [5 empty] | 40000 | 21.7 | 4.6 | 36600 | 3.3333 | 36800 | 16.9 | 3.7 | 28200 | 3.0667
217351760 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | [5 empty] | 39000 | 21.3 | 4.5 | 35800 | 3.25 | 36000 | 16.6 | 3.7 | 27600 | 3
217351761 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | [5 empty] | 41000 | 22.8 | 4.8 | 34800 | 3.4167 | 39000 | 18.5 | 3.7 | 27400 | 3.25
217351762 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | [5 empty] | 40500 | 22.3 | 4.7 | 34200 | 3.375 | 38000 | 18.1 | 3.7 | 26800 | 3.1667
217351763 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | [5 empty] | 52000 | 21.5 | 4.6 | 46500 | 4.3333 | 48500 | 17.1 | 4 | 37800 | 4.0417
217351764 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048SA*N******1 | F(T,G,E)5(A,B)***48*** | [5 empty] | 51000 | 21 | 4.5 | 45500 | 4.25 | 47500 | 16.7 | 3.9 | 37000 | 3.9583
217351765 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | [5 empty] | 63500 | 21.7 | 4.4 | 60000 | 5.2917 | 60500 | 17.6 | 3.7 | 47000 | 5.0417
217351766 | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | [5 empty] | 62500 | 21.3 | 4.3 | 59000 | 5.2083 | 59500 | 17.3 | 3.7 | 46000 | 4.9583
217351768 | BRYANT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ024SA*C******1 | CAAMP2***AMA | [5 empty] | 27200 | 24.8 | 4.5 | 23900 | 2.2667 | 25900 | 17.5 | 3.8 | 18900 | 2.1583
217351769 | BRYANT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ024SA*N******1 | CAAMP2***AMA | [5 empty] | 26700 | 24.3 | 4.4 | 23400 | 2.225 | 25400 | 17.1 | 3.7 | 18500 | 2.1167
217351770 | BRYANT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ036SA*C******1 | CAAMP3***AMA | [5 empty] | 40300 | 22.8 | 4.4 | 34500 | 3.3583 | 37400 | 17.7 | 3.6 | 27600 | 3.1167
217351771 | BRYANT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ036SA*N******1 | CAAMP3***AMA | [5 empty] | 39500 | 22.3 | 4.3 | 33800 | 3.2917 | 36600 | 17.4 | 3.6 | 27100 | 3.05
217351772 | BRYANT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ048SA*C******1 | CAAMP4***AMA | [5 empty] | 54600 | 22.3 | 4.6 | 46600 | 4.55 | 49000 | 17.1 | 3.9 | 37900 | 4.0833
217351773 | BRYANT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ048SA*N******1 | CAAMP4***AMA | [5 empty] | 53500 | 21.9 | 4.5 | 45600 | 4.4583 | 48000 | 16.7 | 3.8 | 37100 | 4
203344888 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH009**0*6 | [6 empty] | 10300 | 22 | 4.1 | 9600 | 0.85833
203344891 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH009**9*6 | [6 empty] | 10300 | 22 | 4.1 | 9600 | 0.85833
203363126 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**0*1* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363127 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**0*4* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
7167540 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V024***4/DA |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7167541 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V024***6/FA |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7167542 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V036***3/CA |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7167543 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V036***5/EA |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7167544 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V036***4/DA |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7167545 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V036***6/FA |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7167546 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V048***3/CA | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7167547 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V048***5/EA | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7167548 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V048***6/FA | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7170602 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS018 | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
7170603 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS018 | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
7170604 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS018 | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
202514053 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT060 | [6 empty] | 62300 | 20.7 | 3.9 | 66900 | 5.1917 | 57900 | 15.8 | 3.1 | 52400 | 4.825
202514054 | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT060 | [6 empty] | 62300 | 20.7 | 3.9 | 66900 | 5.1917 | 57900 | 15.8 | 3.1 | 52400 | 4.825
202514055 | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT060 | [6 empty] | 62300 | 20.7 | 3.9 | 66900 | 5.1917 | 57900 | 15.8 | 3.1 | 52400 | 4.825
206438717 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP007-1HZ/VT*-*****B | [6 empty] | 8400 | 25.1 | 4.7 | 6900 | 0.7
206438718 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP007-2HZ/VT*-*****B | [6 empty] | 8400 | 25.1 | 4.7 | 6900 | 0.7
206438719 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP009-1HZ/VT*-*****B | [6 empty] | 10500 | 24.35 | 4.5 | 9000 | 0.875
216569714 | GeoCool | WBAHP | Water-to-Air and Brine-to-Air | GCHPV/H/D036BT**A*** | [6 empty] | 41500 | 27.2 | 4.9 | 36600 | 3.4583 | 39000 | 17.86 | 4.2 | 28500 | 3.25
216569715 | GeoCool | WBAHP | Water-to-Air and Brine-to-Air | GCHPV/H/D048BT**A*** | [6 empty] | 54800 | 26 | 4.9 | 48200 | 4.5667 | 51500 | 16.65 | 4.2 | 37000 | 4.2917
216621309 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)009*R0**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
216621310 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)012*R0**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
216621311 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)015*R0**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216621312 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*R0**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216621313 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S0**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216621314 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*S0**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216621315 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S0**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216621316 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S0**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216621317 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S0**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216621323 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*D0**1 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
216621324 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*D0**4 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
216621325 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D0**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621326 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D2**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621327 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D3**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621328 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D4**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621329 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D0**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621330 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D2**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621331 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D3**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621332 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D4**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621333 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D0**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621334 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D3**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621335 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D0**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621336 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D3**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621337 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D0**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621338 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D3**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621339 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D0**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621340 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D3**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621341 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D0**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621342 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D3**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621343 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D0**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621344 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D3**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621345 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D0**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621346 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D3**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621347 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D0**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621348 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D3**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621349 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D0**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621350 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D3**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621351 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D0**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621352 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D3**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621353 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D0**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621354 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D3**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
217967018 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK024A |  | 24500 | 18.9 | 6.7 | 32000 | 2.0417 | 26900 | 32.5 | 5.6 | 25700 | 2.2417 | 25400 | 22.4 | 4.4 | 19200 | 2.1167
217967019 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK024A |  | 25100 | 20.4 | 6.6 | 30500 | 2.0917 | 28300 | 38.8 | 5.6 | 24900 | 2.3583 | 26300 | 24.7 | 4.6 | 18800 | 2.1917
217967020 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK033A |  | 32200 | 15.6 | 5.9 | 43600 | 2.6833 | 35500 | 25.2 | 5.1 | 35600 | 2.9583 | 33300 | 18.1 | 4.1 | 27700 | 2.775
217967021 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK033A |  | 33300 | 17 | 6.1 | 39900 | 2.775 | 37500 | 28.8 | 5.3 | 32900 | 3.125 | 35300 | 20.3 | 4.3 | 25500 | 2.9417
217967022 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK042A |  | 40300 | 17.9 | 6.4 | 50400 | 3.3583 | 45000 | 30.2 | 5.5 | 41200 | 3.75 | 42200 | 21.3 | 4.4 | 32500 | 3.5167
217967023 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK042A |  | 42900 | 18.8 | 6.3 | 54100 | 3.575 | 46600 | 32.1 | 5.4 | 43400 | 3.8833 | 44900 | 22.7 | 4.4 | 34400 | 3.7417
217967024 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK050A |  | 49400 | 16 | 6 | 68200 | 4.1167 | 55900 | 25.5 | 5.2 | 54500 | 4.6583 | 52100 | 18.5 | 4.2 | 41300 | 4.3417
217967025 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK050A |  | 50300 | 17.4 | 5.8 | 63000 | 4.1917 | 52200 | 25.9 | 5.1 | 51500 | 4.35 | 50400 | 19.3 | 4.3 | 40400 | 4.2
217967026 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK060A |  | 58500 | 14.9 | 5.5 | 84000 | 4.875 | 63800 | 21.6 | 4.8 | 67400 | 5.3167 | 61900 | 17 | 3.9 | 51400 | 5.1583
217967027 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK060A |  | 59000 | 15.7 | 5.6 | 78800 | 4.9167 | 62300 | 22.7 | 5 | 63700 | 5.1917 | 61200 | 17.9 | 4.1 | 49500 | 5.1
217967028 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK024B |  | 24500 | 18.9 | 6.7 | 32000 | 2.0417 | 26900 | 32.5 | 5.6 | 25700 | 2.2417 | 25400 | 22.4 | 4.4 | 19200 | 2.1167
217967029 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK024B |  | 25100 | 20.4 | 6.6 | 30500 | 2.0917 | 28300 | 38.8 | 5.6 | 24900 | 2.3583 | 26300 | 24.7 | 4.6 | 18800 | 2.1917
217967030 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK033B |  | 32200 | 15.6 | 5.9 | 43600 | 2.6833 | 35500 | 25.2 | 5.1 | 35600 | 2.9583 | 33300 | 18.1 | 4.1 | 27700 | 2.775
217967031 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK033B |  | 33300 | 17 | 6.1 | 39900 | 2.775 | 37500 | 28.8 | 5.3 | 32900 | 3.125 | 35300 | 20.3 | 4.3 | 25500 | 2.9417
217967032 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK042B |  | 40300 | 17.9 | 6.4 | 50400 | 3.3583 | 45000 | 30.2 | 5.5 | 41200 | 3.75 | 42200 | 21.3 | 4.4 | 32500 | 3.5167
217967033 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK042B |  | 42900 | 18.8 | 6.3 | 54100 | 3.575 | 46600 | 32.1 | 5.4 | 43400 | 3.8833 | 44900 | 22.7 | 4.4 | 34400 | 3.7417
217967034 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK050B |  | 49400 | 16 | 6 | 68200 | 4.1167 | 55900 | 25.5 | 5.2 | 54500 | 4.6583 | 52100 | 18.5 | 4.2 | 41300 | 4.3417
217967035 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK050B |  | 50300 | 17.4 | 5.8 | 63000 | 4.1917 | 52200 | 25.9 | 5.1 | 51500 | 4.35 | 50400 | 19.3 | 4.3 | 40400 | 4.2
217967036 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK060B |  | 58500 | 14.9 | 5.5 | 84000 | 4.875 | 63800 | 21.6 | 4.8 | 67400 | 5.3167 | 61900 | 17 | 3.9 | 51400 | 5.1583
217967037 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK060B |  | 59000 | 15.7 | 5.6 | 78800 | 4.9167 | 62300 | 22.7 | 5 | 63700 | 5.1917 | 61200 | 17.9 | 4.1 | 49500 | 5.1
7519580 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519581 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519582 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519583 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519584 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519727 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519748 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519756 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519769 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*A***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519770 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*A***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519771 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*A***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519772 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*2***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519773 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*2***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519774 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*2***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519775 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*3***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519776 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*3***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519777 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*3***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7520238 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*****1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520239 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*****1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520240 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*****1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520241 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*2***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520242 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*2***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520243 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*2***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520244 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*3***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520245 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*3***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520246 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*A***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520247 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*A***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520248 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*A***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520249 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*3***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520250 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*****1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520251 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*****1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520252 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*****1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520253 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*2***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520254 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*2***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520255 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*2***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520256 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*3***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520257 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*3***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520258 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*3***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520259 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*A***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520260 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*A***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520261 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*A***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7523956 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS018*****1 |  | 20700 | 18.8 | 6.2 | 23700 | 1.725 | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
7523957 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS018*****1 |  | 20700 | 18.8 | 6.2 | 23700 | 1.725 | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
7523958 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS018*****1 |  | 20700 | 18.8 | 6.2 | 23700 | 1.725 | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
7523959 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS018*A***1 |  | 20700 | 18.8 | 6.2 | 23700 | 1.725 | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
7523960 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS018*A***1 |  | 20700 | 18.8 | 6.2 | 23700 | 1.725 | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
7523961 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS018*A***1 |  | 20700 | 18.8 | 6.2 | 23700 | 1.725 | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
7607519 | TTHERM GEO | WBWHP | Water-to-Water and Brine-to-Water | THA-024-* | [6 empty] | 27000 | 21.1 | 3.6 | 24800 | 2.25 | 23000 | 16.2 | 3.1 | 21500 | 1.9167
217602221 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**3*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
217602222 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**3*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
217602224 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**3*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217602225 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**3*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217602227 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**3*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
217602228 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042C**3*(A-H)** | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
217602230 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042C**3*(J-R)** | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
217602231 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048C**3*(A-H)** | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
217602233 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048C**3*(J-R)** | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
217602236 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*060C**3*(J-R)** | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
217642876 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)006*R0**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
217642879 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)015*R0**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
217642881 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)024*S0**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
217642883 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)036*S0**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
217642884 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S0**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642888 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)006*R2**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75