## Read Me
Mass Save Heat Pump Qualified Products List (HPQPL) | [7 empty] | Data updated | 2026-07-15
IMPORTANT NOTICE
1. AHRI has replaced the "Heating Capacity (H1Full) - Single or High Stage (47F), btuh" field with the "Heating Capacity (47F), btuh (Appendix M1)" field. This data update has resulted in systems that once qualified to no longer qualify. These systems will be eligible for a rebate if installed on or before March 31, 2026, but will no longer be eligible for a rebate beginning April 1, 2026. These systems are marked with "No - DS" in column B. 2. As of January 1, 2026, new residential and light commercial heat pump Systems with a global warming potential (GWP) greater than 700, including Systems that use R-410A refrigerant, have been removed from the Heat Pump Qualified Product List (HPQPL). Please note, new residential and light commercial heat pump variable refrigerant flow Systems that are 65,000 BTU/h or greater can be installed prior to January 1, 2027. Additionally, self-contained heat pump Products with GWPs >700 that are fully assembled and charged at the factory can be installed prior to January 1, 2028. - System: A grouping of HVAC components, otherwise known as split systems (ex: IDUs paired with ODUs). - Product: A self-contained unit, otherwise known as a packaged heat pump (ex: evaporator coil, condenser, and compressor all located in one cabinet).
Installation Type | Equipment Type | Equipment Capacity1 |  | Efficiency Ratings
|  | Tons | Btu/Hr | EER2 | IEER3 | COP4 @ 47°F | COP4 @ 17°F
Residential and Commercial | Air Source Heat Pumps (ASHP) | < 5.4 | < 65,000 | See ASHPs < 5.4 Tons table below
Commercial |  | ≥ 5.4 and < 11.33 | ≥ 65,000 and < 135,000 | 11.1 | 15.4 | 3.5 | 2.25
|  | ≥ 11.33 and < 20 | ≥ 135,000 and < 240,000 | 10.7 | 14.6 | 3.4 | 2.05
|  | ≥ 20 and ≤ 150 | ≥ 240,000 and ≤ 1,800,000 | 9.6 | 13 | 3.3 | 2.05
Residential | Air to Water Heat Pumps (AWHP) | See AWHP criteria listed below
Residential | Ground Source Heat Pumps (GSHP) | ENERGY STAR Certified (see tab)
Commercial | Ground Source Heat Pumps - Closed Loop (GSHP-C), GLHP | ≤ 150 | ≤ 1,800,000 | 17.1 | --- | 3.6 | ---
| Ground Source Heat Pumps - Open Loop (GSHP-O), GWHP | ≤ 150 | ≤ 1,800,000 | 21.1 | --- | 4.1 | ---
1 Btu / Hr based on AHRI rated cooling capacity @ 95°F; Tons are calculated as Btu / Hr divided by 12,000 Btu / Hr 2 Energy Efficiency Ratio 3 Integrated Energy Efficiency Ratio 4 Coefficient of Performance
Equipment Type | Equipment Capacity1 |  | Efficiency Ratings
| Tons | Btu/Hr | EER² (1230-2021) Listed "Active" | EER² (1230-2014) | IEER3 | COP4 @ 47°F | COP4 @ 17°F
Air Source Variable Refriegerant Flow Heat Pumps (VRF) | ≥ 5.4 and < 11.33 | ≥ 65,000 and < 135,000 | 10.3 | 11.1 | 18.9 | 3.4 | 2.25
| ≥ 11.33 and < 20 | ≥ 135,000 and < 240,000 | 9.9 | 10.7 | 18 | 3.25 | 2.07
| ≥ 20 and ≤ 150 | ≥ 240,000 and ≤ 1,800,000 | 9.1 | 9.6 | 16.4 | 3.25 | 2.07
1 Btu / Hr based on AHRI rated cooling capacity @ 95°F; Tons are calculated as Btu / Hr divided by 12,000 Btu / Hr 2 Energy Efficiency Ratio 3 Integrated Energy Efficiency Ratio 4 Coefficient of Performance
Air Source Heat Pumps (ASHPs) < 5.4 Tons
Equipment |  |  | Efficiency Ratings 1
|  |  | HSPF2 2 | SEER2 3 | HCR4 @5°F | COP5 @5°F
Ductless | Mini-Split | Single-Zone | 8.5 | 15.2 | 70% | 1.75
Ductless | Mini-Split | Multi-Zone
Ducted | Mini-Split | Single-Zone | 8.1 | 15.2 | 70% | 1.75
Ducted | Mini-Split | Multi-Zone
Ducted | Central | --
Single Packaged Roof Top Units (Commercial Only) |  |  | 7.2 | 15.2 | 10.6 EER2⁶
Ducted | High Velocity | -- | 7 | 12.5 | 70% | 1.5
1 Aligns with ENERGY STAR 6.1 Cold-Climate Specification, except Ducted High Velocity Heat Pumps 2 Heating Season Performance Factor 3 Seasonal Energy Efficiency Ratio 4 Heating Capacity Ratio, calculated as heating capacity at the specified temperature divided by heating capacity @ 47°F 5 Coefficient of Performance 6 Energy Efficiency Ratio
The Data Fields below are sourced directly from the AHRI Directory of Cerified Product Performance
AHRI Directory
Air Source Heat Pumps < 5.4 Tons |  |  | Air Source Heat Pumps > 5.4 Tons |  | VRF Heat Pumps |  |  | Ground Source Heat Pumps
AHRI Certified Reference Number |  |  | AHRI Certified Reference Number |  | AHRI Certified Reference Number |  |  | AHRI Certified Reference Number
Brand Name |  |  | Brand Name |  | Brand Name |  |  | Brand Name
AHRI Type |  |  | AHRI Type |  | AHRI Type |  |  | AHRI Type
Indoor Type |  |  | Outdoor Unit Model Number |  | Indoor Type |  |  | Program Type
Outdoor Unit Model Number |  |  | Indoor Unit Model Number |  | System Model Number |  |  | Outdoor Unit Model Number
Indoor Unit Model Number(s) |  |  | Cooling Capacity (95F) |  | Module Model Number 1 |  |  | Indoor Unit Model Number(s)
Furnace Model Number |  |  | EER (95F) |  | Module Model Number 2 |  |  | Full Load GLHP Cooling Capacity (Btuh)
Cooling Capacity (AFull) - Single or High Stage (95F), btuh |  |  | IEER |  | Module Model Number 3 |  |  | Full Load GLHP Cooling EER (Btuh/watt)
SEER2 |  |  | COP at 47°F |  | Cooling Capacity (95F) |  |  | Full Load GLHP Heating COP
EER2 (AFull) - Single or High Stage (95F) |  |  | Heating Capacity at 47°F |  | EER (95F) |  |  | Full Load GLHP Heating Capacity (Btuh)
HSPF2 (Region IV) |  |  | Heating Capacity at 17°F |  | IEER
Heating Capacity (H1Full) - Single or High Stage (47F), btuh |  |  | COP at 17°F |  | High COP (47F)
Heating Capacity at 5°F as calculated by M1 |  |  |  |  | High Heating Capacity (47F)
Heating COP at 5°F as calculated by M1 |  |  |  |  | Low Heating Capacity (17F)
Heating Capacity at 17°F as calculated by M1 |  |  |  |  | Low COP (17F)
Equipment Category | AHRI Types
Ducted | ·HRCU-A-CB = Split System: Heat Pump with Remote Outdoor Unit-Air-Source ·HRCU-A-C =Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source (Ducted) ·HSP-A = Single-Package Heat Pump Air-Source ·HMSV-A-CB = Multi-Split Heat Pump (Ducted, Mixed) ·HMSR-A-CB = Multi-Split Heat Recovery Heat Pump (Ducted, Mixed)
Ductless | ·HRCU-A-CB-O =Mini-Split Heat Pump, with Remote Outdoor Unit Air-Source, Free Delivery ·HMSV-A-CB-O = Multi-Split Heat Pump, Free Delivery (Non-ducted) ·HMSR-A-CB-O = Multi-Split Heat Recovery Heat Pump, Free Delivery (Non-ducted)
Ducted High Velocity | ·SDHV-HRCU-A-CB = Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled
Air to Water Heat Pumps (Residential Only)
Criteria is as follows:
•Minimum COP of 1.7 while delivering 110°F supply water at an outside temperature of 5°F.
•Fully displacing existing hydronic heating
•Maximum 6 tons nominal capacity
Integrated Controls
Integrated controls automatically switch between a heat pump and fossil fuel heating system at a pre-set outdoor temperature.
Eligibility
For residential heat pump rebates: |  | click here
For commercial heat pump rebates |  | click here

## High Velocity ASHPs
AHRI Certified Reference Number | Date No Longer Eligible | Tonnage | Equipment Type | Outdoor Unit Brand Name | AHRI Type | Outdoor Unit Model Number | Indoor Unit Brand Name | Indoor Unit Type | Indoor Unit Model Number(s) | Furnace Model Number | Cooling Capacity (AFull) - Single or High Stage (95F), btuh | SEER2 | HSPF2 (Region IV) | Heating Capacity (47F), btuh | Heating Capacity at 5°F as calculated by M1 | Heating Capacity Ratio @ 5°F | Heating COP at 5°F as calculated by M1 | EER (95F) | IEER | COP at 47°F | COP at 17°F | Refrigerant Type | Rebate Type
217048334 |  | 2.2 | Central HP < 5.4 tons | BOSCH | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | BOVA-36RTB-M20S | UNICO SYSTEM |  | M3036C*1-B***+M3036B**-EC**+TXV-3T-454 |  | 26400 | 14.1 | 7.4 | 27200 | 19400 | 71.32% | 1.55 |  |  |  |  | R-454B | Residential & Commercial
217048386 |  | 3.4583 | Central HP < 5.4 tons | BOSCH | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | BOVA-60RTB-M20S | UNICO SYSTEM |  | M3642C*1-B***+M3642B**-EC**+TXV-3T-454 |  | 41500 | 14.2 | 7.6 | 42200 | 31000 | 73.46% | 1.65 |  |  |  |  | R-454B | Residential & Commercial
217656828 |  | 2.7167 | Central HP < 5.4 tons | HISENSE | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | AUWR-3624P | UNICO SYSTEM |  | M3642C*1-BA***+M3642B**-EC**+TXV-4T-454 |  | 32600 | 12.75 | 7.2 | 28600 | 26000 | 90.91% | 1.84 |  |  |  |  | R-454B | Residential & Commercial
218114674 |  | 2.7167 | Central HP < 5.4 tons | HISENSE | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | AOH-36U3T24P | UNICO SYSTEM |  | M3642C*1-BA***+M3642B**-EC**+TXV-4T-454 |  | 32600 | 12.75 | 7.2 | 28600 | 26000 | 90.91% | 1.84 |  |  |  |  | R-454B | Residential & Commercial
218338087 |  | 3.8333 | Central HP < 5.4 tons | HISENSE | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | AOH-48U3T24P | UNICO SYSTEM |  | M3642C*1-E**1+M3642B**-EC*+T4 |  | 46000 | 13.6 | 7.2 | 47500 | 33600 | 70.74% | 1.84 |  |  |  |  | R-454B | Residential & Commercial
218338088 |  | 3.8333 | Central HP < 5.4 tons | FRIEDRICH | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | WFPU17Y483D | UNICO SYSTEM |  | M3642C*1-E**1+M3642B**-EC*+T4 |  | 46000 | 13.6 | 7.2 | 47500 | 33600 | 70.74% | 1.84 |  |  |  |  | R-454B | Residential & Commercial

## Residential Air to Water HPs
Last update: 7/17/2026
Manufacturer | System Type | Model Name | Model # | Nominal Capacity in Tons | COP @ A5W110* | Refrigerant** | Notes
Airquest | Mono-bloc | D3CM | D3CMWAN0510781AK | 4.3 | 1.9 | R32
Airquest | Mono-bloc | D3CM | D3CMWAN0340431AK | 3 | 2.2 | R32
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-3.5T. | 3.5 | 2.46 | Please independently confirm
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-5T. | 5 | 2.34 | Please independently confirm
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-6T. | 6 | 2.34 | Please independently confirm
Arcoaire | Mono-bloc | D3CM | D3CMWAN0510781AK | 4.3 | 1.9 | R32
Arcoaire | Mono-bloc | D3CM | D3CMWAN0340431AK | 3 | 2.2 | R32
Arctic Heat Pumps | Mono-bloc |  | 035ZA/BE-R32 | 2.5 | 2.2 | R32
Arctic Heat Pumps | Mono-bloc |  | 050ZA/BE-R32 | 4 | 2.45 | R32
Arctic Heat Pumps | Mono-bloc |  | 060ZA/BE-R32 | 5 | 2.39 | R32
Arctic Heat Pumps | Mono-bloc |  | 030ZA/BEH2 | 4 | 2.03 | Please independently confirm
Arctic Heat Pumps | Mono-bloc |  | MAHRW030A (BEH2)-R32 | 4 | 1.84 | R32
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 020A | 2.5 | 2.26 | Please independently confirm
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 040A | 4 | 2.18 | Please independently confirm
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 060A | 5 | 2.26 | Please independently confirm
Bryant | Mono-bloc | 33NM3 | 33NM3AW034043 | 3 | 2.2 | R32
Bryant | Mono-bloc | 33NM3 | 33NM3AW051078 | 4.3 | 1.9 | R32
Carrier | Mono-bloc | 33NM3 | 33NM3AW051078 | 4.3 | 1.9 | R32
Carrier | Mono-bloc | 33NM3 | 33NM3AW034043 | 3 | 2.2 | R32
Chiltrix Inc. | Mono-bloc Air to Water Heat Pump | CX65 | CX65 | 5.5 | 2.47 | R32
Chiltrix Inc. | Mono-bloc Air to Water Heat Pump | CX65X | CX65X | 5.5 | 2.47 | R32
Chiltrix Inc. | Mono-bloc Air to Water Heat Pump | CX65 | CX75 | 6.4 | 2.47 | R32
Chiltrix Inc. | Mono-bloc Air to Water Heat Pump | CX65X | CX75X | 6.4 | 2.47 | R32
Chiltrix Inc. | R32 Air To Water Heat Pump | CX50 | CX50 | 4.8 | 2.18 | R32
Chiltrix Inc. | Mono-bloc Air to Water Heat Pump | CX45 | CX45 | 3.9 | 2.27 | R32
Chiltrix Inc. | Mono-bloc Air to Water Heat Pump | CX45X | CX45X | 3.9 | 2.27 | R32
Chiltrix Inc. | Mono-bloc Air to Water Heat Pump | CX40 | CX40 | 3.5 | 2.27 | R32
Chiltrix Inc. | Mono-bloc Air to Water Heat Pump | CX40X | CX40X | 3.5 | 2.27 | R32
Chiltrix Inc. | Mono-bloc | CX35 | CX35 | 3.5 | 2.187 | R32
Chiltrix Inc. | Mono-bloc | CX34 | CX34 | 3 | 2 | R32
Comfortmaker | Mono-bloc | D3CM | D3CMWAN0510781AK | 4.3 | 1.9 | R32
Comfortmaker | Mono-bloc | D3CM | D3CMWAN0340431AK | 3 | 2.2 | R32
Daikin | Mono-bloc | Altherma 3 H HT | UPRA036DAVJ | 2.9 | 2.2 | R32
Daikin | Mono-bloc | Altherma 3 H HT | UPRA043DAVJ | 2.9 | 2.17 | R32
Day & Night | Mono-bloc | D3CM | D3CMWAN0340431AK | 3 | 2.2 | R32
Day & Night | Mono-bloc | D3CM | D3CMWAN0510781AK | 4.3 | 1.9 | R32
ECOER | Mono-bloc | Smart Green One | ESMA-060ADP | 5.2 | 2.04 | R32
ECOER | Mono-bloc | Smart Green One | ESBM-060GPP | 5.5 | 2.27 | R32
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 1-7 PRO (81001/P) | 1 | 2.5 | R290 (propane)
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 1-9 PRO (81004/P) | 1.3 | 2.31 | R290 (propane)
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 3-12 PRO (81002/P) | 1.75 | 2.23 | R290 (propane)
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 3-18 PRO (81005/P2) | 2.75 | 2.42 | R290 (propane)
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR EVI 4-20 (81003) | 3.79 | 2.92 | R290 (propane)
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-1H | 2 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-2H | 3 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-11 | 2 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-12 | 2 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-13 | 3 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-14 | 4 | 2.3 | CO2
Heil | Mono-bloc | D3CM | D3CMWAN0510781AK | 4.3 | 1.9 | R32
Heil | Mono-bloc | D3CM | D3CMWAN0340431AK | 3 | 2.2 | R32
Keeprite | Mono-bloc | D3CM | D3CMWAN0340431AK | 3 | 2.2 | R32
Keeprite | Mono-bloc | D3CM | D3CMWAN0510781AK | 4.3 | 1.9 | R32
LG | Mono-bloc | LATS AWHP | KPHTC411M | 3.41 | 2.5 | R32
LG | Mono-bloc | LATS AWHP | KPHTC481M | 4 | 2.15 | R32
LG | Mono-bloc | LATS AWHP | KPHTC551M | 4.58 | 2.38 | R32
Lochinvar | Mono-bloc | Lochinvar | RAH040 | 3.42 | 1.9 | R32
Midea | Split | M Thermal Arctic Split | MHA-V12WD2MN8-B2 | 3.5 | 2.11 | R32
Midea | Split | M Thermal Arctic Split | MHA-V14WD2MN8-B2 | 4 | 2.08 | R32
Midea | Split | M Thermal Arctic Split | MHA-V16WD2MN8-B2 | 4.5 | 2.06 | R32
Midea | Split | M Thermal Arctic Split | MHA-V16WD2MN8 / HB–A160CMGN8 | 4 | 2.1 | R32
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA24NMZ-U1 | 2 | 1.98 | R32 | Paired with the Ecodan Hydro Box Indoor Unit, ERSF-NM6E
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA36NMZ-U1 | 3 | 1.93 | R32 | Paired with the Ecodan Hydro Box Indoor Unit, ERSF-NM6E
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA48NMZ-U1 | 4 | 1.99 | R32 | Paired with the Ecodan Hydro Box Indoor Unit, ERSF-NM6E
NTI Boilers Inc. | Mono-bloc | Verta | NHP32-036 | 2.7 | 1.94 | R32
NTI Boilers Inc. | Mono-bloc | Verta | NHP32-060 | 4.7 | 2 | R32
Samsung | Mono-bloc | EHS Mono HT Quiet | AE055FCYDCG/AA | 4.55 | 2.16 | R32
Samsung | Mono-bloc | EHS Mono HT Quiet | AE041FCYDCG/AA | 3.41 | 2.15 | R32
SpacePak | Monobloc | Solstice R32 Series | CC32-18 | 1.7 | 1.54 | R32
SpacePak | Monobloc | Solstice R32 Series | CC32-40 | 2.8 | 2.83 | R32
SpacePak | Monobloc | Solstice R32 Series | CC32-60 | 4.3 | 2.39 | R32
Tempstar | Mono-bloc | D3CM | D3CMWAN0340431AK | 3 | 2.2 | R32
Tempstar | Mono-bloc | D3CM | D3CMWAN0510781AK | 4.3 | 1.9 | R32
U.S. Boiler Company, LLC | Mono-bloc | Ambient Heat Pump System (HPS) | HPS-5T60-DF | 5 | 1.9 | R32
U.S. Boiler Company, LLC | Mono-bloc | Ambient Heat Pump System (HPS) | HPS-5T60 | 5 | 1.9 | R32
Viessmann | Split | Vitocal 100-AW | AM2V 034043 | 3 | 2.2 | R32
Viessmann | Split | Vitocal 100-AW | AM2V 051078 | 4.3 | 1.9 | R32
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 41 | 2.62 | 2.11 | R32
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 48 | 2.76 | 2.08 | R32
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 55 | 2.79 | 2.06 | R32
* Equivalent value. Equipment automatically reduces outlet water temperature to 110°F when ambient conditions drop to 5°F. ** Please independently confirm that system does not use R410 refrigerant, per the EPA A2L Transition order.

## Commercial Air Source VRF
AHRI Certified Reference Number | Date No Longer Eligible | Outdoor Unit Brand Name | AHRI Type | Module Model Number 1 | Module Model Number 2 | Module Model Number 3 | Module Model Number 4 | Outdoor Unit Model Number | Indoor Type | Full Load Cooling Capacity (Btuh) | EER | IEER | Heating Capacity 47°F (Btuh) | COP 47°F | Heating Capacity 17°F (Btuh) | COP 17°F | Refrigerant Type | Tonnage
209445576 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Non-Ducted Indoor Units | 69000 | 12.3 | 24.2 | 76000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
209445577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Ducted Indoor Units | 69000 | 12 | 21.5 | 76000 | 4.1 | 56000 | 2.65 | R-410A | 5.75
209937596 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 22.85 | 76000 | 4.2 | 56000 | 2.67 | R-410A | 5.75
209937595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.3 | 103000 | 3.9 | 76000 | 2.53 | R-410A | 7.6667
209445578 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Non-Ducted Indoor Units | 92000 | 12 | 23.4 | 103000 | 4 | 76000 | 2.6 | R-410A | 7.6667
209445579 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Ducted Indoor Units | 92000 | 11.8 | 21.2 | 103000 | 3.8 | 76000 | 2.47 | R-410A | 7.6667
209445580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Non-Ducted Indoor Units | 114000 | 11.8 | 24.5 | 129000 | 3.9 | 92000 | 2.5 | R-410A | 9.5
209445573 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Ducted Indoor Units | 114000 | 11.4 | 21 | 129000 | 3.65 | 92000 | 2.37 | R-410A | 9.5
209937594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.75 | 129000 | 3.77 | 92000 | 2.43 | R-410A | 9.5
209938003 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 22.85 | 76000 | 4.2 | 56000 | 2.67 | R-410A | 5.75
209447005 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Non-Ducted Indoor Units | 69000 | 12.3 | 24.2 | 76000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
209447006 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Ducted Indoor Units | 69000 | 12 | 21.5 | 76000 | 4.1 | 56000 | 2.65 | R-410A | 5.75
209447007 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Non-Ducted Indoor Units | 92000 | 12 | 23.4 | 103000 | 4 | 76000 | 2.6 | R-410A | 7.6667
209447008 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Ducted Indoor Units | 92000 | 11.8 | 21.2 | 103000 | 3.8 | 76000 | 2.47 | R-410A | 7.6667
209938002 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.3 | 103000 | 3.9 | 76000 | 2.53 | R-410A | 7.6667
209445574 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Non-Ducted Indoor Units | 114000 | 11.8 | 24.5 | 129000 | 3.9 | 92000 | 2.5 | R-410A | 9.5
209445575 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Ducted Indoor Units | 114000 | 11.4 | 21 | 129000 | 3.65 | 92000 | 2.37 | R-410A | 9.5
209938001 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.75 | 129000 | 3.77 | 92000 | 2.43 | R-410A | 9.5
218044847 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TL |  |  |  | MXZ-SM72TL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 23.75 | 76000 | 4.29 | 56000 | 2.76 | R-454B | 5.75
218044838 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TL |  |  |  | MXZ-SM72TL | Non-Ducted Indoor Units | 69000 | 12.7 | 25 | 76000 | 4.38 | 56000 | 2.76 | R-454B | 5.75
218044839 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TL |  |  |  | MXZ-SM72TL | Ducted Indoor Units | 69000 | 12.5 | 22.5 | 76000 | 4.2 | 56000 | 2.76 | R-454B | 5.75
218044840 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TL |  |  |  | MXZ-SM96TL | Non-Ducted Indoor Units | 92000 | 12.2 | 24.2 | 103000 | 4.05 | 76000 | 2.64 | R-454B | 7.6667
218044841 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TL |  |  |  | MXZ-SM96TL | Ducted Indoor Units | 92000 | 12.2 | 22.1 | 103000 | 3.83 | 76000 | 2.59 | R-454B | 7.6667
218044848 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TL |  |  |  | MXZ-SM96TL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.2 | 23.15 | 103000 | 3.94 | 76000 | 2.61 | R-454B | 7.6667
218044849 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TL |  |  |  | MXZ-SM120TL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12 | 23.6 | 123000 | 3.87 | 92000 | 2.49 | R-454B | 9.5
218044842 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TL |  |  |  | MXZ-SM120TL | Non-Ducted Indoor Units | 114000 | 12.2 | 25.3 | 123000 | 3.94 | 92000 | 2.53 | R-454B | 9.5
218044843 |  | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TL |  |  |  | MXZ-SM120TL | Ducted Indoor Units | 114000 | 11.8 | 21.9 | 123000 | 3.81 | 92000 | 2.46 | R-454B | 9.5
218079204 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L72TBMU |  |  |  | PUMY-L72TBMU | Non-Ducted Indoor Units | 69000 | 12.7 | 25 | 76000 | 4.38 | 56000 | 2.76 | R-454B | 5.75
218079205 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L72TBMU |  |  |  | PUMY-L72TBMU | Ducted Indoor Units | 69000 | 12.5 | 22.5 | 76000 | 4.2 | 56000 | 2.76 | R-454B | 5.75
218079206 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L72TBMU |  |  |  | PUMY-L72TBMU | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 23.75 | 76000 | 4.29 | 56000 | 2.76 | R-454B | 5.75
218079207 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L96TBMU |  |  |  | PUMY-L96TBMU | Non-Ducted Indoor Units | 92000 | 12.2 | 24.2 | 103000 | 4.05 | 76000 | 2.64 | R-454B | 7.6667
218079208 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L96TBMU |  |  |  | PUMY-L96TBMU | Ducted Indoor Units | 92000 | 12.2 | 22.1 | 103000 | 3.83 | 76000 | 2.59 | R-454B | 7.6667
218079209 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L96TBMU |  |  |  | PUMY-L96TBMU | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.2 | 23.15 | 103000 | 3.94 | 76000 | 2.61 | R-454B | 7.6667
218079210 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L120TBMU |  |  |  | PUMY-L120TBMU | Non-Ducted Indoor Units | 114000 | 12.2 | 25.3 | 123000 | 3.94 | 92000 | 2.53 | R-454B | 9.5
218079211 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L120TBMU |  |  |  | PUMY-L120TBMU | Ducted Indoor Units | 114000 | 11.8 | 21.9 | 123000 | 3.81 | 92000 | 2.46 | R-454B | 9.5
218079212 |  | Mitsubishi Electric | HMSV-A-CB | PUMY-L120TBMU |  |  |  | PUMY-L120TBMU | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12 | 23.6 | 123000 | 3.87 | 92000 | 2.49 | R-454B | 9.5
218214200 |  | FUJITSU | HMSR-A-CB | AOSU072VSAN7 |  |  |  | AOSU072VSAN7 | Non-Ducted Indoor Units | 69000 | 12.25 | 28.1 | 77000 | 3.82 | 56000 | 2.38 | R-32 | 5.75
218214211 |  | FUJITSU | HMSR-A-CB | AOSU072VSAN7 |  |  |  | AOSU072VSAN7 | Ducted Indoor Units | 69000 | 12.4 | 22.4 | 77000 | 3.82 | 56000 | 2.38 | R-32 | 5.75
218214247 |  | FUJITSU | HMSR-A-CB | AOSU096VSAN7 |  |  |  | AOSU096VSAN7 | Non-Ducted Indoor Units | 92000 | 11.95 | 23.9 | 103000 | 3.49 | 70000 | 2.27 | R-32 | 7.6667
218214249 |  | FUJITSU | HMSR-A-CB | AOSU096VSAN7 |  |  |  | AOSU096VSAN7 | Ducted Indoor Units | 92000 | 11.8 | 21.4 | 103000 | 3.49 | 70000 | 2.27 | R-32 | 7.6667
218214212 |  | FUJITSU | HMSR-A-CB | AOSU120VSAN7 |  |  |  | AOSU120VSAN7 | Ducted Indoor Units | 115000 | 11.8 | 20.6 | 129000 | 3.46 | 87000 | 2.48 | R-32 | 9.5833
218214201 |  | FUJITSU | HMSR-A-CB | AOSU120VSAN7 |  |  |  | AOSU120VSAN7 | Non-Ducted Indoor Units | 115000 | 11.75 | 23.4 | 129000 | 3.46 | 87000 | 2.48 | R-32 | 9.5833
218214216 |  | FUJITSU | HMSR-A-CB | AORU120VSAN7 |  |  |  | AORU120VSAN7 | Ducted Indoor Units | 115000 | 11.8 | 20.6 | 129000 | 3.46 | 87000 | 2.48 | R-32 | 9.5833
218214205 |  | FUJITSU | HMSR-A-CB | AORU120VSAN7 |  |  |  | AORU120VSAN7 | Non-Ducted Indoor Units | 115000 | 11.75 | 23.4 | 129000 | 3.46 | 87000 | 2.48 | R-32 | 9.5833
218214220 |  | FUJITSU | HMSR-A-CB | AORU072VSAN7 |  |  |  | AORU072VSAN7 | Non-Ducted Indoor Units | 69000 | 12.25 | 28.1 | 77000 | 3.82 | 56000 | 2.38 | R-32 | 5.75
218214221 |  | FUJITSU | HMSR-A-CB | AORU072VSAN7 |  |  |  | AORU072VSAN7 | Ducted Indoor Units | 69000 | 12.4 | 22.4 | 77000 | 3.82 | 56000 | 2.38 | R-32 | 5.75
218214248 |  | FUJITSU | HMSR-A-CB | AORU096VSAN7 |  |  |  | AORU096VSAN7 | Non-Ducted Indoor Units | 92000 | 11.95 | 23.9 | 103000 | 3.49 | 70000 | 2.27 | R-32 | 7.6667
218214250 |  | FUJITSU | HMSR-A-CB | AORU096VSAN7 |  |  |  | AORU096VSAN7 | Ducted Indoor Units | 92000 | 11.8 | 21.4 | 103000 | 3.49 | 70000 | 2.27 | R-32 | 7.6667
218327214 |  | HISENSE | HMSR-A-CB | AVWT-72FFDS5H |  |  |  | AVWT-72FFDS5H | Ducted Indoor Units | 69000 | 12.55 | 20.19 | 75000 | 3.63 | 51000 | 2.49 | R-32 | 5.75
218327215 |  | HISENSE | HMSR-A-CB | AVWT-72FFDS5H |  |  |  | AVWT-72FFDS5H | Non-Ducted Indoor Units | 69000 | 12.95 | 23.88 | 75000 | 4.06 | 51000 | 2.81 | R-32 | 5.75
218327216 |  | HISENSE | HMSR-A-CB | AVWT-72FFDS5H |  |  |  | AVWT-72FFDS5H | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.75 | 22.03 | 75000 | 3.84 | 51000 | 2.65 | R-32 | 5.75
218327217 |  | HISENSE | HMSR-A-CB | AVWT-96FFDS5H |  |  |  | AVWT-96FFDS5H | Ducted Indoor Units | 92000 | 12.45 | 22.85 | 100000 | 3.6 | 67000 | 2.61 | R-32 | 7.6667
218327218 |  | HISENSE | HMSR-A-CB | AVWT-96FFDS5H |  |  |  | AVWT-96FFDS5H | Non-Ducted Indoor Units | 92000 | 13.4 | 24.6 | 100000 | 3.9 | 67000 | 2.79 | R-32 | 7.6667
218327219 |  | HISENSE | HMSR-A-CB | AVWT-96FFDS5H |  |  |  | AVWT-96FFDS5H | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.92 | 23.72 | 100000 | 3.75 | 67000 | 2.7 | R-32 | 7.6667
218327220 |  | HISENSE | HMSR-A-CB | AVWT-120FFDS5H |  |  |  | AVWT-120FFDS5H | Ducted Indoor Units | 114000 | 12.35 | 22.13 | 126000 | 3.93 | 84000 | 2.71 | R-32 | 9.5
218327221 |  | HISENSE | HMSR-A-CB | AVWT-120FFDS5H |  |  |  | AVWT-120FFDS5H | Non-Ducted Indoor Units | 114000 | 12.7 | 25.45 | 126000 | 4.34 | 84000 | 2.95 | R-32 | 9.5
218327222 |  | HISENSE | HMSR-A-CB | AVWT-120FFDS5H |  |  |  | AVWT-120FFDS5H | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.52 | 23.79 | 126000 | 4.13 | 84000 | 2.83 | R-32 | 9.5
218425714 |  | GE Appliances | HMSR-A-CB | MWHQ072NC4CA* |  |  |  | MWHQ072NC4CA* | Ducted Indoor Units | 69000 | 12 | 20.5 | 77000 | 3.5 | 53000 | 2.4 | R-32 | 5.75
218425684 |  | GE Appliances | HMSR-A-CB | MWHQ072NC4CA* |  |  |  | MWHQ072NC4CA* | Non-Ducted Indoor Units | 69000 | 12.6 | 23.6 | 77000 | 3.6 | 53000 | 2.5 | R-32 | 5.75
218425685 |  | GE Appliances | HMSR-A-CB | MWHQ096NC2CA* |  |  |  | MWHQ096NC2CA* | Ducted Indoor Units | 91000 | 12.2 | 21.8 | 103000 | 3.5 | 72000 | 2.4 | R-32 | 7.5833
218425686 |  | GE Appliances | HMSR-A-CB | MWHQ096NC2CA* |  |  |  | MWHQ096NC2CA* | Non-Ducted Indoor Units | 91000 | 11.9 | 23.1 | 103000 | 3.6 | 72000 | 2.4 | R-32 | 7.5833
218425687 |  | GE Appliances | HMSR-A-CB | MWHQ096NC4CA* |  |  |  | MWHQ096NC4CA* | Ducted Indoor Units | 91000 | 12.2 | 21.8 | 103000 | 3.5 | 72000 | 2.4 | R-32 | 7.5833
218425688 |  | GE Appliances | HMSR-A-CB | MWHQ096NC4CA* |  |  |  | MWHQ096NC4CA* | Non-Ducted Indoor Units | 91000 | 11.9 | 23.1 | 103000 | 3.6 | 72000 | 2.4 | R-32 | 7.5833
218425689 |  | GE Appliances | HMSR-A-CB | MWHQ120NC2CA* |  |  |  | MWHQ120NC2CA* | Ducted Indoor Units | 115000 | 11.2 | 20.6 | 129000 | 3.4 | 82000 | 2.3 | R-32 | 9.5833
218425690 |  | GE Appliances | HMSR-A-CB | MWHQ120NC2CA* |  |  |  | MWHQ120NC2CA* | Non-Ducted Indoor Units | 115000 | 11.6 | 21.8 | 129000 | 3.6 | 84000 | 2.3 | R-32 | 9.5833
218425691 |  | GE Appliances | HMSR-A-CB | MWHQ120NC4CA* |  |  |  | MWHQ120NC4CA* | Ducted Indoor Units | 115000 | 11.2 | 20.6 | 129000 | 3.4 | 84000 | 2.3 | R-32 | 9.5833
218425692 |  | GE Appliances | HMSR-A-CB | MWHQ120NC4CA* |  |  |  | MWHQ120NC4CA* | Non-Ducted Indoor Units | 115000 | 11.6 | 21.8 | 129000 | 3.6 | 84000 | 2.3 | R-32 | 9.5833
218425713 |  | GE Appliances | HMSR-A-CB | MWHQ072NC2CA* |  |  |  | MWHQ072NC2CA* | Ducted Indoor Units | 69000 | 12 | 20.5 | 77000 | 3.5 | 53000 | 2.4 | R-32 | 5.75
218425683 |  | GE Appliances | HMSR-A-CB | MWHQ072NC2CA* |  |  |  | MWHQ072NC2CA* | Non-Ducted Indoor Units | 69000 | 12.6 | 23.6 | 77000 | 3.6 | 53000 | 2.5 | R-32 | 5.75
218425723 |  | HITACHI | HMSV-A-CB | HVAHR120C33CW |  |  |  | HVAHR120C33CW* | Non-Ducted Indoor Units | 115000 | 12.2 | 19.6 | 129000 | 4.13 | 92000 | 2.39 | R-32 | 9.5833
218425727 |  | HITACHI | HMSR-A-CB | HVAHR120C33CW |  |  |  | HVAHR120C33CW | Non-Ducted Indoor Units | 115000 | 12.2 | 19.6 | 129000 | 4.13 | 92000 | 2.39 | R-32 | 9.5833
218425725 |  | HITACHI | HMSV-A-CB | HVAHR120C43CW |  |  |  | HVAHR120C43CW* | Non-Ducted Indoor Units | 115000 | 12.2 | 19.6 | 129000 | 4.13 | 92000 | 2.39 | R-32 | 9.5833
218425729 |  | HITACHI | HMSR-A-CB | HVAHR120C43CW |  |  |  | HVAHR120C43CW | Non-Ducted Indoor Units | 115000 | 12.2 | 19.6 | 129000 | 4.13 | 92000 | 2.39 | R-32 | 9.5833
218471039 |  | LG | HMSV-A-CB | ZRUN072BSS0 |  |  |  | ZRUN072BSS0 | Non-Ducted Indoor Units | 69000 | 12.7 | 25 | 77000 | 4.38 | 54000 | 2.56 | R-32 | 5.75
218471040 |  | LG | HMSV-A-CB | ZRUN072BSS0 |  |  |  | ZRUN072BSS0 | Ducted Indoor Units | 69000 | 10.9 | 20.5 | 77000 | 3.66 | 54000 | 2.44 | R-32 | 5.75
218471043 |  | LG | HMSV-A-CB | ZRUN072BSS0 |  |  |  | ZRUN072BSS0 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.8 | 22.75 | 77000 | 4.02 | 54000 | 2.5 | R-32 | 5.75
218471044 |  | LG | HMSV-A-CB | ZRUN096BSS0 |  |  |  | ZRUN096BSS0 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.55 | 24.05 | 103000 | 3.59 | 62000 | 2.43 | R-32 | 7.6667
218471041 |  | LG | HMSV-A-CB | ZRUN096BSS0 |  |  |  | ZRUN096BSS0 | Non-Ducted Indoor Units | 92000 | 11.6 | 24.5 | 103000 | 3.73 | 62000 | 2.47 | R-32 | 7.6667
218471042 |  | LG | HMSV-A-CB | ZRUN096BSS0 |  |  |  | ZRUN096BSS0 | Ducted Indoor Units | 92000 | 11.5 | 23.6 | 103000 | 3.45 | 62000 | 2.39 | R-32 | 7.6667
213886432 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886392 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886360 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602243 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
216602117 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602170 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602177 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602124 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602253 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886364 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
213886396 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886436 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886390 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
213886430 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886358 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602237 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
216602113 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602167 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602173 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602120 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602248 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886362 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886394 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886434 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886398 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886366 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602258 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
216602127 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602180 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602166 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602111 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602235 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886357 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886389 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
213886429 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886433 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886393 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886361 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602246 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
216602119 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602172 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602179 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602126 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602256 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886365 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
213886397 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886437 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886391 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
213886431 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886359 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602240 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
216602115 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602169 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602175 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602122 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602251 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886363 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886395 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886435 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886439 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886399 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886367 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602260 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
216602129 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602182 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602164 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602108 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602232 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886356 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886388 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
213886428 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213897041 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Ducted Indoor Units | 69000 | 12.2 | 19.8 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213897059 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.5 | 69000 | 3.62 | 51000 | 2.4 | R-410A | 5.75
213897015 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.2 | 69000 | 3.64 | 51000 | 2.4 | R-410A | 5.75
213897016 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Non-Ducted Indoor Units | 92000 | 12.2 | 23.6 | 92000 | 3.5 | 66000 | 2.4 | R-410A | 7.6667
213897060 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 21.5 | 92000 | 3.45 | 66000 | 2.4 | R-410A | 7.6667
213897042 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Ducted Indoor Units | 92000 | 12 | 19.4 | 92000 | 3.4 | 66000 | 2.4 | R-410A | 7.6667
213897043 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* |  |  |  | RXYQ120AATJ* | Ducted Indoor Units | 114000 | 11.1 | 19.3 | 110000 | 3.4 | 72000 | 2.25 | R-410A | 9.5
213897068 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.5 | 69000 | 3.62 | 51000 | 2.4 | R-410A | 5.75
213897050 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Ducted Indoor Units | 69000 | 12.2 | 19.8 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213897028 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.2 | 69000 | 3.64 | 51000 | 2.4 | R-410A | 5.75
213897029 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Non-Ducted Indoor Units | 92000 | 12.2 | 23.6 | 92000 | 3.5 | 66000 | 2.4 | R-410A | 7.6667
213897051 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Ducted Indoor Units | 92000 | 12 | 19.4 | 92000 | 3.4 | 66000 | 2.4 | R-410A | 7.6667
213897069 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 21.5 | 92000 | 3.45 | 66000 | 2.4 | R-410A | 7.6667
213897052 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* |  |  |  | RXYQ120AAYD* | Ducted Indoor Units | 114000 | 11.1 | 19.3 | 110000 | 3.4 | 72000 | 2.25 | R-410A | 9.5
213885856 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
213885853 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
215685126 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
215685127 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) |  |  |  | GMV-VQ96WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.8 | 20.55 | 103000 | 3.95 | 76000 | 2.25 | R-410A | 7.6667
213885857 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) |  |  |  | GMV-VQ96WM/C-F(U) | Ducted Indoor Units | 92000 | 11.6 | 20.2 | 103000 | 3.9 | 78000 | 2.25 | R-410A | 7.6667
213885858 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) |  |  |  | GMV-VQ120WM/C-F(U) | Ducted Indoor Units | 114000 | 11 | 19.7 | 129000 | 3.8 | 81000 | 2.25 | R-410A | 9.5
215685128 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) |  |  |  | GMV-VQ120WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.5 | 20.05 | 129000 | 3.87 | 81000 | 2.25 | R-410A | 9.5
214728275 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP072C432Y2 |  |  |  | VEP072C432Y2 | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
215685129 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP072C432Y2 |  |  |  | VEP072C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.72 | 20.8 | 77000 | 3.81 | 64000 | 2.25 | R-410A | 5.75
215685121 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/C-F(U) |  |  |  | GMV-Q72WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.72 | 20.8 | 77000 | 3.81 | 64000 | 2.25 | R-410A | 5.75
213880759 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/C-F(U) |  |  |  | GMV-Q72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
213928536 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/C-F(U) |  |  |  | GMV-Q96WM/C-F(U) | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
215685122 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/C-F(U) |  |  |  | GMV-Q96WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
215685130 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP096C432Y2 |  |  |  | VEP096C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
214728280 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP096C432Y2 |  |  |  | VEP096C432Y2 | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
213896679 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896710 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896728 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896729 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* |  |  |  | REYQ96XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896680 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* |  |  |  | REYQ96XBTJ* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896690 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* |  |  |  | REYQ120XBTJ* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896773 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* |  |  |  | REYQ120XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896696 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896716 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896734 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896735 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* |  |  |  | REYQ96XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896697 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* |  |  |  | REYQ96XBYD* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896837 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* |  |  |  | REYQ120XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896817 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* |  |  |  | REYQ120XBYD* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896722 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896740 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896703 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896704 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* |  |  |  | REYQ96XBYC* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896741 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* |  |  |  | REYQ96XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896841 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* |  |  |  | REYQ120XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896821 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* |  |  |  | REYQ120XBYC* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896746 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XBYC* |  |  |  | RXYQ72XBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 18.9 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896805 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* |  |  |  | RXYQ96XBYC* | Non-Ducted Indoor Units | 92000 | 10.5 | 19.8 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* |  |  |  | RXYQ120XBYC* | Non-Ducted Indoor Units | 114000 | 10.3 | 19.3 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBTJ* |  |  |  | RXLQ72TBTJ* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896883 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBYD* |  |  |  | RXLQ72TBYD* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896887 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBYC* |  |  |  | RXLQ72TBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896876 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBTJ* |  |  |  | RELQ72TBTJ* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896909 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBYD* |  |  |  | RELQ72TBYD* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896915 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBYC* |  |  |  | RELQ72TBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
214289936 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME2CA* |  |  |  | MVHQ072ME2CA* | Ducted Indoor Units | 69000 | 12 | 20.5 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289937 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME2CA* |  |  |  | MVHQ072ME2CA* | Non-Ducted Indoor Units | 69000 | 12.6 | 23.6 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289957 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME2CA* |  |  |  | MVHQ096ME2CA* | Ducted Indoor Units | 91000 | 12.2 | 21.8 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289958 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME2CA* |  |  |  | MVHQ096ME2CA* | Non-Ducted Indoor Units | 91000 | 11.9 | 23.1 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289972 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* |  |  |  | MVHQ120ME2CA* | Ducted Indoor Units | 115000 | 11.2 | 21.6 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289973 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* |  |  |  | MVHQ120ME2CA* | Non-Ducted Indoor Units | 115000 | 11.6 | 23 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289938 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME4CA* |  |  |  | MVHQ072ME4CA* | Ducted Indoor Units | 69000 | 12 | 20.5 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289939 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME4CA* |  |  |  | MVHQ072ME4CA* | Non-Ducted Indoor Units | 69000 | 12.6 | 23.6 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289959 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME4CA* |  |  |  | MVHQ096ME4CA* | Ducted Indoor Units | 91000 | 12.2 | 21.8 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289960 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME4CA* |  |  |  | MVHQ096ME4CA* | Non-Ducted Indoor Units | 91000 | 11.9 | 23.1 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289974 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* |  |  |  | MVHQ120ME4CA* | Ducted Indoor Units | 115000 | 11.2 | 21.6 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289975 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* |  |  |  | MVHQ120ME4CA* | Non-Ducted Indoor Units | 115000 | 11.6 | 23 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214296004 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B33CW |  |  |  | HVAHR120B33CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189682 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B33CW |  |  |  | HVAHR120B33CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
214296014 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B43CW |  |  |  | HVAHR120B43CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B43CW |  |  |  | HVAHR120B43CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
215828403 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B53CW |  |  |  | HVAHR120B53CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189702 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B53CW |  |  |  | HVAHR120B53CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
214825944 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C |  |  |  | TVRF-VQ72WM/C | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
214825941 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C |  |  |  | TVRF-VQ72WM/C | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
218330477 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C |  |  |  | TVRF-VQ72WM/C | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
214825945 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C |  |  |  | TVRF-VQ96WM/C | Ducted Indoor Units | 92000 | 11.6 | 20.2 | 103000 | 3.9 | 78000 | 2.25 | R-410A | 7.6667
214825946 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ120WM/C |  |  |  | TVRF-VQ120WM/C | Ducted Indoor Units | 114000 | 11 | 19.7 | 129000 | 3.8 | 81000 | 2.25 | R-410A | 9.5
214825938 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD72K/220V |  |  |  | TVRF-SHD72K/220V | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
214825949 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD96K/220V |  |  |  | TVRF-SHD96K/220V | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
214826363 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
214826372 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
214826403 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602708 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602723 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602775 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602778 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602724 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602710 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826404 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
214826373 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
214826364 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826365 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
214826374 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
214826405 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602711 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602725 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602780 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
214826383 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072DXVGQR |  |  |  | AM072DXVGQR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
214826392 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072DXVGQR |  |  |  | AM072DXVGQR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602741 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4J |  |  |  | VRC072S4M-4J | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602756 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4J |  |  |  | VRC072S4M-4J | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602758 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J |  |  |  | VRC096S4M-4J | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602742 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J |  |  |  | VRC096S4M-4J | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826393 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR |  |  |  | AM096DXVGQR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
214826384 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR |  |  |  | AM096DXVGQR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826385 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR |  |  |  | AM120DXVGQR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
214826394 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR |  |  |  | AM120DXVGQR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602744 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J |  |  |  | VRC120S4M-4J | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602759 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J |  |  |  | VRC120S4M-4J | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
217729292 |  | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.05 | 51000 | 2.75 | R-32 | 5.75
217729293 |  | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Ducted Indoor Units | 69000 | 11.9 | 19.7 | 77000 | 3.85 | 51000 | 2.65 | R-32 | 5.75
217729759 |  | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 21.9 | 77000 | 3.95 | 51000 | 2.7 | R-32 | 5.75
217729760 |  | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 23.3 | 103000 | 4.17 | 67000 | 2.85 | R-32 | 7.6667
217729294 |  | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Non-Ducted Indoor Units | 92000 | 13.3 | 27.6 | 103000 | 4.45 | 67000 | 2.95 | R-32 | 7.6667
217729295 |  | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Ducted Indoor Units | 92000 | 11 | 19 | 103000 | 3.9 | 67000 | 2.75 | R-32 | 7.6667
217729296 |  | LG | HMSR-A-CB | ZRUM121BTE6 |  |  |  | ZRUM121BTE6 | Non-Ducted Indoor Units | 114000 | 12.1 | 25.9 | 129000 | 4.13 | 84000 | 2.9 | R-32 | 9.5
217729761 |  | LG | HMSR-A-CB | ZRUM121BTE6 |  |  |  | ZRUM121BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.15 | 22.45 | 129000 | 3.88 | 84000 | 2.77 | R-32 | 9.5
217729780 |  | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 21.9 | 77000 | 3.95 | 51000 | 2.7 | R-32 | 5.75
217729298 |  | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.05 | 51000 | 2.75 | R-32 | 5.75
217729299 |  | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Ducted Indoor Units | 69000 | 11.9 | 19.7 | 77000 | 3.85 | 51000 | 2.65 | R-32 | 5.75
217729300 |  | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Non-Ducted Indoor Units | 92000 | 13.3 | 27.6 | 103000 | 4.45 | 67000 | 2.95 | R-32 | 7.6667
217729301 |  | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Ducted Indoor Units | 92000 | 11 | 19 | 103000 | 3.9 | 67000 | 2.75 | R-32 | 7.6667
217729781 |  | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 23.3 | 103000 | 4.17 | 67000 | 2.85 | R-32 | 7.6667
217729782 |  | LG | HMSR-A-CB | ZRUM121DTE6 |  |  |  | ZRUM121DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.15 | 22.45 | 129000 | 3.88 | 84000 | 2.77 | R-32 | 9.5
217729302 |  | LG | HMSR-A-CB | ZRUM121DTE6 |  |  |  | ZRUM121DTE6 | Non-Ducted Indoor Units | 114000 | 12.1 | 25.9 | 129000 | 4.13 | 84000 | 2.9 | R-32 | 9.5
217734265 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217734323 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734380 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217734382 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734325 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734266 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Non-Ducted Indoor Units | 92000 | 10.9 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734267 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Non-Ducted Indoor Units | 115000 | 11.5 | 23.3 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217734327 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Ducted Indoor Units | 115000 | 11.6 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734384 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.55 | 22.5 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217734361 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734418 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734307 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734309 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Non-Ducted Indoor Units | 92000 | 11.8 | 24.3 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217734420 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 23 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217734363 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734365 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Ducted Indoor Units | 115000 | 12.1 | 21.8 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734422 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.25 | 22.9 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734311 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217734288 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217734324 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734381 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217734383 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734326 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734289 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Non-Ducted Indoor Units | 92000 | 10.9 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734290 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Non-Ducted Indoor Units | 115000 | 11.5 | 23.3 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217734328 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Ducted Indoor Units | 115000 | 11.6 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734385 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.55 | 22.5 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217734362 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734419 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734308 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734310 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Non-Ducted Indoor Units | 92000 | 11.8 | 24.3 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217734421 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 23 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217734364 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734366 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Ducted Indoor Units | 115000 | 12.1 | 21.8 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734423 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.25 | 22.9 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734312 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217734975 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734976 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217735082 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217735086 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.9 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734983 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734984 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Non-Ducted Indoor Units | 92000 | 10.7 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734991 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Ducted Indoor Units | 115000 | 11.5 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734992 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Non-Ducted Indoor Units | 115000 | 11.4 | 23 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217735090 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.45 | 22.35 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217735084 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734979 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734980 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734987 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734988 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Non-Ducted Indoor Units | 92000 | 11.7 | 24.2 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217735088 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.95 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217735092 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.15 | 22.85 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734995 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Ducted Indoor Units | 115000 | 11.9 | 21.7 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734996 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217734977 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734978 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217735083 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217735087 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.9 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734985 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734986 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Non-Ducted Indoor Units | 92000 | 10.7 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734993 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Ducted Indoor Units | 115000 | 11.5 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734994 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Non-Ducted Indoor Units | 115000 | 11.4 | 23 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217735091 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.45 | 22.35 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217735085 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734981 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734982 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734989 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734990 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Non-Ducted Indoor Units | 92000 | 11.7 | 24.2 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217735089 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.95 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217735093 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.15 | 22.85 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734997 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Ducted Indoor Units | 115000 | 11.9 | 21.7 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734998 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217883041 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217883043 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217883045 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217901715 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM72TXU-A |  |  |  | PURY-EM72TXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901719 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM72TXU-A |  |  |  | PURY-EM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
218088111 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM72TXU-A |  |  |  | PURY-EM72TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 24.2 | 76000 | 4.35 | 61000 | 2.79 | R-32 | 5.75
218088119 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM96TXU-A |  |  |  | PURY-EM96TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.05 | 24.95 | 103000 | 4.2 | 79000 | 2.57 | R-32 | 7.6667
217901723 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM96TXU-A |  |  |  | PURY-EM96TXU-A | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217901727 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM96TXU-A |  |  |  | PURY-EM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217901731 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A |  |  |  | PURY-EM120TXU-A | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217901735 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A |  |  |  | PURY-EM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
218088127 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A |  |  |  | PURY-EM120TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13 | 23.6 | 129000 | 3.9 | 93000 | 2.48 | R-32 | 9.5833
217901721 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A |  |  |  | PURY-HM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901717 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A |  |  |  | PURY-HM72TXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
218088113 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A |  |  |  | PURY-HM72TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 24.2 | 76000 | 4.35 | 61000 | 2.79 | R-32 | 5.75
218088121 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A |  |  |  | PURY-HM96TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.75 | 23.2 | 103000 | 4.19 | 79000 | 2.69 | R-32 | 7.6667
217901725 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A |  |  |  | PURY-HM96TXU-A | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217901729 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A |  |  |  | PURY-HM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217901737 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A |  |  |  | PURY-HM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217901733 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A |  |  |  | PURY-HM120TXU-A | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
218088129 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A |  |  |  | PURY-HM120TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.55 | 23.2 | 129000 | 3.97 | 93000 | 2.63 | R-32 | 9.5833
218088112 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM72YXU-A |  |  |  | PURY-EM72YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 24.2 | 76000 | 4.35 | 61000 | 2.79 | R-32 | 5.75
217901720 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM72YXU-A |  |  |  | PURY-EM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901716 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM72YXU-A |  |  |  | PURY-EM72YXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901724 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM96YXU-A |  |  |  | PURY-EM96YXU-A | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217901728 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM96YXU-A |  |  |  | PURY-EM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
218088120 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM96YXU-A |  |  |  | PURY-EM96YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.05 | 24.95 | 103000 | 4.2 | 79000 | 2.57 | R-32 | 7.6667
218088128 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A |  |  |  | PURY-EM120YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13 | 23.6 | 129000 | 3.9 | 93000 | 2.48 | R-32 | 9.5833
217901732 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A |  |  |  | PURY-EM120YXU-A | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217901736 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A |  |  |  | PURY-EM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
218088114 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A |  |  |  | PURY-HM72YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 24.2 | 76000 | 4.35 | 61000 | 2.79 | R-32 | 5.75
217901722 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A |  |  |  | PURY-HM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901718 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A |  |  |  | PURY-HM72YXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901726 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A |  |  |  | PURY-HM96YXU-A | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217901730 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A |  |  |  | PURY-HM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
218088122 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A |  |  |  | PURY-HM96YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.75 | 23.2 | 103000 | 4.19 | 79000 | 2.69 | R-32 | 7.6667
218088130 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A |  |  |  | PURY-HM120YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.55 | 23.2 | 129000 | 3.97 | 93000 | 2.63 | R-32 | 9.5833
217901738 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A |  |  |  | PURY-HM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217901734 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A |  |  |  | PURY-HM120YXU-A | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217902261 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AMM0AN |  |  |  | TURYE0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902259 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AMM0AN |  |  |  | TURYE0723AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
218088183 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AMM0AN |  |  |  | TURYE0723AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 24.2 | 76000 | 4.35 | 61000 | 2.79 | R-32 | 5.75
218088191 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AMM0AN |  |  |  | TURYE0963AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.05 | 24.95 | 103000 | 4.2 | 79000 | 2.57 | R-32 | 7.6667
217902269 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AMM0AN |  |  |  | TURYE0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217902267 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AMM0AN |  |  |  | TURYE0963AMM0AN | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217902277 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN |  |  |  | TURYE1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217902275 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN |  |  |  | TURYE1203AMM0AN | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
218088199 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN |  |  |  | TURYE1203AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13 | 23.6 | 129000 | 3.9 | 93000 | 2.48 | R-32 | 9.5833
217902260 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN |  |  |  | TURYH0723AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902262 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN |  |  |  | TURYH0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
218088185 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN |  |  |  | TURYH0723AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 24.2 | 76000 | 4.35 | 61000 | 2.79 | R-32 | 5.75
218088193 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN |  |  |  | TURYH0963AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.75 | 23.2 | 103000 | 4.19 | 79000 | 2.69 | R-32 | 7.6667
217902268 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN |  |  |  | TURYH0963AMM0AN | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217902270 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN |  |  |  | TURYH0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217902276 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN |  |  |  | TURYH1203AMM0AN | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217902278 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN |  |  |  | TURYH1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
218088201 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN |  |  |  | TURYH1203AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.55 | 23.2 | 129000 | 3.97 | 93000 | 2.63 | R-32 | 9.5833
218088184 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AMM0AN |  |  |  | TURYE0724AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 24.2 | 76000 | 4.35 | 61000 | 2.79 | R-32 | 5.75
217902263 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AMM0AN |  |  |  | TURYE0724AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902265 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AMM0AN |  |  |  | TURYE0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902271 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AMM0AN |  |  |  | TURYE0964AMM0AN | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217902273 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AMM0AN |  |  |  | TURYE0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
218088192 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AMM0AN |  |  |  | TURYE0964AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.05 | 24.95 | 103000 | 4.2 | 79000 | 2.57 | R-32 | 7.6667
218088200 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN |  |  |  | TURYE1204AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13 | 23.6 | 129000 | 3.9 | 93000 | 2.48 | R-32 | 9.5833
217902279 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN |  |  |  | TURYE1204AMM0AN | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217902281 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN |  |  |  | TURYE1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
218088186 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN |  |  |  | TURYH0724AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 24.2 | 76000 | 4.35 | 61000 | 2.79 | R-32 | 5.75
217902266 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN |  |  |  | TURYH0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902264 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN |  |  |  | TURYH0724AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902274 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN |  |  |  | TURYH0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217902272 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN |  |  |  | TURYH0964AMM0AN | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
218088194 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN |  |  |  | TURYH0964AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.75 | 23.2 | 103000 | 4.19 | 79000 | 2.69 | R-32 | 7.6667
218088202 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN |  |  |  | TURYH1204AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.55 | 23.2 | 129000 | 3.97 | 93000 | 2.63 | R-32 | 9.5833
217902282 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN |  |  |  | TURYH1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217902280 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN |  |  |  | TURYH1204AMM0AN | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217901675 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72TXU-A |  |  |  | PUHY-EM72TXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901676 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72TXU-A |  |  |  | PUHY-EM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
218088107 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72TXU-A |  |  |  | PUHY-EM72TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 15 | 25.55 | 76000 | 4.5 | 61000 | 2.9 | R-32 | 5.75
218088115 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96TXU-A |  |  |  | PUHY-EM96TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.35 | 25.9 | 103000 | 4.32 | 79000 | 2.68 | R-32 | 7.6667
217901683 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96TXU-A |  |  |  | PUHY-EM96TXU-A | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217901684 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96TXU-A |  |  |  | PUHY-EM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217901691 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A |  |  |  | PUHY-EM120TXU-A | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217901692 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A |  |  |  | PUHY-EM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
218088123 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A |  |  |  | PUHY-EM120TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.3 | 25.15 | 129000 | 4.04 | 93000 | 2.55 | R-32 | 9.5833
217901679 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A |  |  |  | PUHY-HM72TXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901680 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A |  |  |  | PUHY-HM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
218088109 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A |  |  |  | PUHY-HM72TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 15 | 25.55 | 76000 | 4.5 | 61000 | 2.9 | R-32 | 5.75
218088117 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A |  |  |  | PUHY-HM96TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.1 | 23.9 | 103000 | 4.28 | 79000 | 2.75 | R-32 | 7.6667
217901687 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A |  |  |  | PUHY-HM96TXU-A | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217901688 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A |  |  |  | PUHY-HM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217901695 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A |  |  |  | PUHY-HM120TXU-A | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217901696 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A |  |  |  | PUHY-HM120TXU-A | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
218088125 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A |  |  |  | PUHY-HM120TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.85 | 23.85 | 129000 | 4.1 | 93000 | 2.69 | R-32 | 9.5833
218088108 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72YXU-A |  |  |  | PUHY-EM72YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 15 | 25.55 | 76000 | 4.5 | 61000 | 2.9 | R-32 | 5.75
217901677 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72YXU-A |  |  |  | PUHY-EM72YXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901678 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72YXU-A |  |  |  | PUHY-EM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901685 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96YXU-A |  |  |  | PUHY-EM96YXU-A | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217901686 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96YXU-A |  |  |  | PUHY-EM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
218088116 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96YXU-A |  |  |  | PUHY-EM96YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.35 | 25.9 | 103000 | 4.32 | 79000 | 2.68 | R-32 | 7.6667
218088124 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A |  |  |  | PUHY-EM120YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.3 | 25.15 | 129000 | 4.04 | 93000 | 2.55 | R-32 | 9.5833
217901693 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A |  |  |  | PUHY-EM120YXU-A | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217901694 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A |  |  |  | PUHY-EM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
218088110 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A |  |  |  | PUHY-HM72YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 15 | 25.55 | 76000 | 4.5 | 61000 | 2.9 | R-32 | 5.75
217901681 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A |  |  |  | PUHY-HM72YXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901682 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A |  |  |  | PUHY-HM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901689 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A |  |  |  | PUHY-HM96YXU-A | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217901690 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A |  |  |  | PUHY-HM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
218088118 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A |  |  |  | PUHY-HM96YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.1 | 23.9 | 103000 | 4.28 | 79000 | 2.75 | R-32 | 7.6667
218088126 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A |  |  |  | PUHY-HM120YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.85 | 23.85 | 129000 | 4.1 | 93000 | 2.69 | R-32 | 9.5833
217901697 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A |  |  |  | PUHY-HM120YXU-A | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217901698 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A |  |  |  | PUHY-HM120YXU-A | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217902187 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AMM0AN |  |  |  | TUHYE0723AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902189 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AMM0AN |  |  |  | TUHYE0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
218088179 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AMM0AN |  |  |  | TUHYE0723AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 15 | 25.55 | 76000 | 4.5 | 61000 | 2.9 | R-32 | 5.75
218088187 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AMM0AN |  |  |  | TUHYE0963AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.35 | 25.9 | 103000 | 4.32 | 79000 | 2.68 | R-32 | 7.6667
217902197 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AMM0AN |  |  |  | TUHYE0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217902195 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AMM0AN |  |  |  | TUHYE0963AMM0AN | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217902205 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN |  |  |  | TUHYE1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217902203 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN |  |  |  | TUHYE1203AMM0AN | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
218088195 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN |  |  |  | TUHYE1203AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.3 | 25.15 | 129000 | 4.04 | 93000 | 2.55 | R-32 | 9.5833
217902190 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN |  |  |  | TUHYH0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902188 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN |  |  |  | TUHYH0723AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
218088181 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN |  |  |  | TUHYH0723AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 15 | 25.55 | 76000 | 4.5 | 61000 | 2.9 | R-32 | 5.75
218088189 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN |  |  |  | TUHYH0963AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.1 | 23.9 | 103000 | 4.28 | 79000 | 2.75 | R-32 | 7.6667
217902196 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN |  |  |  | TUHYH0963AMM0AN | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217902198 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN |  |  |  | TUHYH0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217902204 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN |  |  |  | TUHYH1203AMM0AN | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217902206 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN |  |  |  | TUHYH1203AMM0AN | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
218088197 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN |  |  |  | TUHYH1203AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.85 | 23.85 | 129000 | 4.1 | 93000 | 2.69 | R-32 | 9.5833
218088180 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AMM0AN |  |  |  | TUHYE0724AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 15 | 25.55 | 76000 | 4.5 | 61000 | 2.9 | R-32 | 5.75
217902191 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AMM0AN |  |  |  | TUHYE0724AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902193 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AMM0AN |  |  |  | TUHYE0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902199 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AMM0AN |  |  |  | TUHYE0964AMM0AN | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217902201 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AMM0AN |  |  |  | TUHYE0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
218088188 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AMM0AN |  |  |  | TUHYE0964AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.35 | 25.9 | 103000 | 4.32 | 79000 | 2.68 | R-32 | 7.6667
218088196 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN |  |  |  | TUHYE1204AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.3 | 25.15 | 129000 | 4.04 | 93000 | 2.55 | R-32 | 9.5833
217902207 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN |  |  |  | TUHYE1204AMM0AN | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217902209 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN |  |  |  | TUHYE1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
218088182 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN |  |  |  | TUHYH0724AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 15 | 25.55 | 76000 | 4.5 | 61000 | 2.9 | R-32 | 5.75
217902194 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN |  |  |  | TUHYH0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902192 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN |  |  |  | TUHYH0724AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902202 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN |  |  |  | TUHYH0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217902200 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN |  |  |  | TUHYH0964AMM0AN | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
218088190 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN |  |  |  | TUHYH0964AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.1 | 23.9 | 103000 | 4.28 | 79000 | 2.75 | R-32 | 7.6667
218088198 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN |  |  |  | TUHYH1204AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 13.85 | 23.85 | 129000 | 4.1 | 93000 | 2.69 | R-32 | 9.5833
217902210 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN |  |  |  | TUHYH1204AMM0AN | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217902208 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN |  |  |  | TUHYH1204AMM0AN | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
218003044 |  | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218003112 |  | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004887 |  | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043859 |  | LENNOX | HMSV-A-CB | VPD072S6M-5Y |  |  |  | VPD072S6M-5Y | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043927 |  | LENNOX | HMSV-A-CB | VPD072S6M-5Y |  |  |  | VPD072S6M-5Y | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218043995 |  | LENNOX | HMSV-A-CB | VPD072S6M-5Y |  |  |  | VPD072S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043999 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y |  |  |  | VPD096S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218043931 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y |  |  |  | VPD096S6M-5Y | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218043863 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y |  |  |  | VPD096S6M-5Y | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218004891 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003116 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003048 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003052 |  | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004385 |  | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218004895 |  | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043867 |  | LENNOX | HMSV-A-CB | VPD120S6M-5Y |  |  |  | VPD120S6M-5Y | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218044003 |  | LENNOX | HMSV-A-CB | VPD120S6M-5Y |  |  |  | VPD120S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043991 |  | LENNOX | HMSV-A-CB | VPD120S6M-5Y |  |  |  | VPD120S6M-5Y | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003045 |  | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218003113 |  | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004888 |  | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043860 |  | LENNOX | HMSR-A-CB | VRD072S6M-5Y |  |  |  | VRD072S6M-5Y | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043928 |  | LENNOX | HMSR-A-CB | VRD072S6M-5Y |  |  |  | VRD072S6M-5Y | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218043996 |  | LENNOX | HMSR-A-CB | VRD072S6M-5Y |  |  |  | VRD072S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218044000 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y |  |  |  | VRD096S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218043932 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y |  |  |  | VRD096S6M-5Y | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218043864 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y |  |  |  | VRD096S6M-5Y | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218004892 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003117 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003049 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003053 |  | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004386 |  | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218004896 |  | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043868 |  | LENNOX | HMSR-A-CB | VRD120S6M-5Y |  |  |  | VRD120S6M-5Y | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218044004 |  | LENNOX | HMSR-A-CB | VRD120S6M-5Y |  |  |  | VRD120S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043992 |  | LENNOX | HMSR-A-CB | VRD120S6M-5Y |  |  |  | VRD120S6M-5Y | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003046 |  | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218003114 |  | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004889 |  | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043861 |  | LENNOX | HMSV-A-CB | VPD072S6M-5G |  |  |  | VPD072S6M-5G | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043929 |  | LENNOX | HMSV-A-CB | VPD072S6M-5G |  |  |  | VPD072S6M-5G | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218043997 |  | LENNOX | HMSV-A-CB | VPD072S6M-5G |  |  |  | VPD072S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218044001 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G |  |  |  | VPD096S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218043933 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G |  |  |  | VPD096S6M-5G | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218043865 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G |  |  |  | VPD096S6M-5G | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218004893 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003118 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003050 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003054 |  | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004387 |  | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218004897 |  | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043869 |  | LENNOX | HMSV-A-CB | VPD120S6M-5G |  |  |  | VPD120S6M-5G | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218044005 |  | LENNOX | HMSV-A-CB | VPD120S6M-5G |  |  |  | VPD120S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043993 |  | LENNOX | HMSV-A-CB | VPD120S6M-5G |  |  |  | VPD120S6M-5G | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003047 |  | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218003115 |  | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004890 |  | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043862 |  | LENNOX | HMSR-A-CB | VRD072S6M-5G |  |  |  | VRD072S6M-5G | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043930 |  | LENNOX | HMSR-A-CB | VRD072S6M-5G |  |  |  | VRD072S6M-5G | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218043998 |  | LENNOX | HMSR-A-CB | VRD072S6M-5G |  |  |  | VRD072S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218044002 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G |  |  |  | VRD096S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218043934 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G |  |  |  | VRD096S6M-5G | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218043866 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G |  |  |  | VRD096S6M-5G | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218004894 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003119 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003051 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003055 |  | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004388 |  | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218004898 |  | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043870 |  | LENNOX | HMSR-A-CB | VRD120S6M-5G |  |  |  | VRD120S6M-5G | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218044006 |  | LENNOX | HMSR-A-CB | VRD120S6M-5G |  |  |  | VRD120S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043994 |  | LENNOX | HMSR-A-CB | VRD120S6M-5G |  |  |  | VRD120S6M-5G | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218005699 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005667 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005739 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044063 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y |  |  |  | VPD072L6M-5Y | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218044095 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y |  |  |  | VPD072L6M-5Y | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218044135 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y |  |  |  | VPD072L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044139 |  | LENNOX | HMSV-A-CB | VPD096L6M-5Y |  |  |  | VPD096L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044099 |  | LENNOX | HMSV-A-CB | VPD096L6M-5Y |  |  |  | VPD096L6M-5Y | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044067 |  | LENNOX | HMSV-A-CB | VPD096L6M-5Y |  |  |  | VPD096L6M-5Y | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005743 |  | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005703 |  | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005671 |  | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005675 |  | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005707 |  | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005747 |  | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044071 |  | LENNOX | HMSV-A-CB | VPD120L6M-5Y |  |  |  | VPD120L6M-5Y | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218044103 |  | LENNOX | HMSV-A-CB | VPD120L6M-5Y |  |  |  | VPD120L6M-5Y | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044143 |  | LENNOX | HMSV-A-CB | VPD120L6M-5Y |  |  |  | VPD120L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044136 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y |  |  |  | VRD072L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044096 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y |  |  |  | VRD072L6M-5Y | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218044064 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y |  |  |  | VRD072L6M-5Y | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005740 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005700 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005668 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005672 |  | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005744 |  | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005704 |  | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044068 |  | LENNOX | HMSR-A-CB | VRD096L6M-5Y |  |  |  | VRD096L6M-5Y | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218044100 |  | LENNOX | HMSR-A-CB | VRD096L6M-5Y |  |  |  | VRD096L6M-5Y | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044140 |  | LENNOX | HMSR-A-CB | VRD096L6M-5Y |  |  |  | VRD096L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044144 |  | LENNOX | HMSR-A-CB | VRD120L6M-5Y |  |  |  | VRD120L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044104 |  | LENNOX | HMSR-A-CB | VRD120L6M-5Y |  |  |  | VRD120L6M-5Y | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044072 |  | LENNOX | HMSR-A-CB | VRD120L6M-5Y |  |  |  | VRD120L6M-5Y | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005708 |  | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005748 |  | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005676 |  | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005701 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005669 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005741 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044097 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G |  |  |  | VPD072L6M-5G | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218044065 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G |  |  |  | VPD072L6M-5G | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218044137 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G |  |  |  | VPD072L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044141 |  | LENNOX | HMSV-A-CB | VPD096L6M-5G |  |  |  | VPD096L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044069 |  | LENNOX | HMSV-A-CB | VPD096L6M-5G |  |  |  | VPD096L6M-5G | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218044101 |  | LENNOX | HMSV-A-CB | VPD096L6M-5G |  |  |  | VPD096L6M-5G | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005745 |  | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005705 |  | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005673 |  | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005677 |  | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005709 |  | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005749 |  | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044073 |  | LENNOX | HMSV-A-CB | VPD120L6M-5G |  |  |  | VPD120L6M-5G | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218044105 |  | LENNOX | HMSV-A-CB | VPD120L6M-5G |  |  |  | VPD120L6M-5G | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044145 |  | LENNOX | HMSV-A-CB | VPD120L6M-5G |  |  |  | VPD120L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044138 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G |  |  |  | VRD072L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044098 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G |  |  |  | VRD072L6M-5G | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218044066 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G |  |  |  | VRD072L6M-5G | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005742 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005702 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005670 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005674 |  | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005746 |  | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005706 |  | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044070 |  | LENNOX | HMSR-A-CB | VRD096L6M-5G |  |  |  | VRD096L6M-5G | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218044102 |  | LENNOX | HMSR-A-CB | VRD096L6M-5G |  |  |  | VRD096L6M-5G | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044142 |  | LENNOX | HMSR-A-CB | VRD096L6M-5G |  |  |  | VRD096L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044146 |  | LENNOX | HMSR-A-CB | VRD120L6M-5G |  |  |  | VRD120L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044106 |  | LENNOX | HMSR-A-CB | VRD120L6M-5G |  |  |  | VRD120L6M-5G | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044074 |  | LENNOX | HMSR-A-CB | VRD120L6M-5G |  |  |  | VRD120L6M-5G | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005710 |  | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005750 |  | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005678 |  | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218007897 |  | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C |  |  |  | MV8-2R72V2XN10C | Ducted Indoor Units | 69000 | 12.6 | 23.9 | 77000 | 3.87 | 64000 | 2.25 | R-454B | 5.75
218007898 |  | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C |  |  |  | MV8-2R72V2XN10C | Non-Ducted Indoor Units | 69000 | 12.8 | 24.5 | 77000 | 4.25 | 64000 | 2.25 | R-454B | 5.75
218007909 |  | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C |  |  |  | MV8-2R72V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.7 | 24.2 | 77000 | 4.06 | 64000 | 2.25 | R-454B | 5.75
218007910 |  | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C |  |  |  | MV8-2R96V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 24.6 | 104000 | 4.05 | 87000 | 2.25 | R-454B | 7.6667
218007899 |  | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C |  |  |  | MV8-2R96V2XN10C | Ducted Indoor Units | 92000 | 12 | 22.8 | 104000 | 3.9 | 87000 | 2.25 | R-454B | 7.6667
218007900 |  | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C |  |  |  | MV8-2R96V2XN10C | Non-Ducted Indoor Units | 92000 | 12.7 | 26.4 | 104000 | 4.2 | 87000 | 2.25 | R-454B | 7.6667
218007901 |  | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C |  |  |  | MV8-2R120V2XN10C | Ducted Indoor Units | 115000 | 11.6 | 22 | 130000 | 3.72 | 91000 | 2.25 | R-454B | 9.5833
218007902 |  | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C |  |  |  | MV8-2R120V2XN10C | Non-Ducted Indoor Units | 115000 | 12.1 | 24.5 | 130000 | 4.06 | 91000 | 2.25 | R-454B | 9.5833
218007911 |  | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C |  |  |  | MV8-2R120V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.25 | 130000 | 3.89 | 91000 | 2.25 | R-454B | 9.5833
218007912 |  | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C |  |  |  | MV8-2R72V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.7 | 24.2 | 77000 | 4.06 | 64000 | 2.25 | R-454B | 5.75
218007903 |  | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C |  |  |  | MV8-2R72V2ZN10C | Ducted Indoor Units | 69000 | 12.6 | 23.9 | 77000 | 3.87 | 64000 | 2.25 | R-454B | 5.75
218007904 |  | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C |  |  |  | MV8-2R72V2ZN10C | Non-Ducted Indoor Units | 69000 | 12.8 | 24.5 | 77000 | 4.25 | 64000 | 2.25 | R-454B | 5.75
218007905 |  | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C |  |  |  | MV8-2R96V2ZN10C | Ducted Indoor Units | 92000 | 12 | 22.8 | 104000 | 3.9 | 87000 | 2.25 | R-454B | 7.6667
218007906 |  | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C |  |  |  | MV8-2R96V2ZN10C | Non-Ducted Indoor Units | 92000 | 12.7 | 26.4 | 104000 | 4.2 | 87000 | 2.25 | R-454B | 7.6667
218007913 |  | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C |  |  |  | MV8-2R96V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 24.6 | 104000 | 4.05 | 87000 | 2.25 | R-454B | 7.6667
218007914 |  | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C |  |  |  | MV8-2R120V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.25 | 130000 | 3.89 | 91000 | 2.25 | R-454B | 9.5833
218007907 |  | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C |  |  |  | MV8-2R120V2ZN10C | Ducted Indoor Units | 115000 | 11.6 | 22 | 130000 | 3.72 | 91000 | 2.25 | R-454B | 9.5833
218007908 |  | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C |  |  |  | MV8-2R120V2ZN10C | Non-Ducted Indoor Units | 115000 | 12.1 | 24.5 | 130000 | 4.06 | 91000 | 2.25 | R-454B | 9.5833
218008878 |  | MIDEA | HMSV-A-CB | MV8-X72V2XN10C |  |  |  | MV8-X72V2XN10C | Ducted Indoor Units | 69000 | 12.2 | 22 | 77000 | 3.87 | 64000 | 2.35 | R-454B | 5.75
218008879 |  | MIDEA | HMSV-A-CB | MV8-X72V2XN10C |  |  |  | MV8-X72V2XN10C | Non-Ducted Indoor Units | 69000 | 12.7 | 23 | 77000 | 4.3 | 64000 | 2.51 | R-454B | 5.75
218008880 |  | MIDEA | HMSV-A-CB | MV8-X96V2XN10C |  |  |  | MV8-X96V2XN10C | Ducted Indoor Units | 92000 | 11.8 | 22 | 103000 | 3.8 | 87000 | 2.33 | R-454B | 7.6667
218008881 |  | MIDEA | HMSV-A-CB | MV8-X96V2XN10C |  |  |  | MV8-X96V2XN10C | Non-Ducted Indoor Units | 92000 | 12.5 | 24.5 | 103000 | 4.05 | 87000 | 2.45 | R-454B | 7.6667
218008882 |  | MIDEA | HMSV-A-CB | MV8-X120V2XN10C |  |  |  | MV8-X120V2XN10C | Ducted Indoor Units | 115000 | 11.5 | 21.5 | 129000 | 3.71 | 93000 | 2.31 | R-454B | 9.5833
218008883 |  | MIDEA | HMSV-A-CB | MV8-X120V2XN10C |  |  |  | MV8-X120V2XN10C | Non-Ducted Indoor Units | 115000 | 12 | 23 | 129000 | 4 | 93000 | 2.36 | R-454B | 9.5833
218008884 |  | MIDEA | HMSV-A-CB | MV8-X72V2ZN10C |  |  |  | MV8-X72V2ZN10C | Ducted Indoor Units | 69000 | 12.2 | 22 | 77000 | 3.87 | 64000 | 2.35 | R-454B | 5.75
218008885 |  | MIDEA | HMSV-A-CB | MV8-X72V2ZN10C |  |  |  | MV8-X72V2ZN10C | Non-Ducted Indoor Units | 69000 | 12.7 | 23 | 77000 | 4.3 | 64000 | 2.51 | R-454B | 5.75
218008886 |  | MIDEA | HMSV-A-CB | MV8-X96V2ZN10C |  |  |  | MV8-X96V2ZN10C | Ducted Indoor Units | 92000 | 11.8 | 22 | 103000 | 3.8 | 87000 | 2.33 | R-454B | 7.6667
218008887 |  | MIDEA | HMSV-A-CB | MV8-X96V2ZN10C |  |  |  | MV8-X96V2ZN10C | Non-Ducted Indoor Units | 92000 | 12.5 | 24.5 | 103000 | 4.05 | 87000 | 2.45 | R-454B | 7.6667
218008888 |  | MIDEA | HMSV-A-CB | MV8-X120V2ZN10C |  |  |  | MV8-X120V2ZN10C | Ducted Indoor Units | 115000 | 11.5 | 21.5 | 129000 | 3.71 | 93000 | 2.31 | R-454B | 9.5833
218008889 |  | MIDEA | HMSV-A-CB | MV8-X120V2ZN10C |  |  |  | MV8-X120V2ZN10C | Non-Ducted Indoor Units | 115000 | 12 | 23 | 129000 | 4 | 93000 | 2.36 | R-454B | 9.5833
218036901 |  | DAIKIN | HMSV-A-CB | RXYA72AATJ* |  |  |  | RXYA72AATJ* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.5 | 69000 | 3.64 | 51000 | 2.4 | R-32 | 5.75
218036937 |  | DAIKIN | HMSV-A-CB | RXYA72AATJ* |  |  |  | RXYA72AATJ* | Ducted Indoor Units | 69000 | 12.4 | 21 | 69000 | 3.6 | 51000 | 2.4 | R-32 | 5.75
218036973 |  | DAIKIN | HMSV-A-CB | RXYA72AATJ* |  |  |  | RXYA72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.45 | 22.25 | 69000 | 3.62 | 51000 | 2.4 | R-32 | 5.75
218036974 |  | DAIKIN | HMSV-A-CB | RXYA96AATJ* |  |  |  | RXYA96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 22.65 | 92000 | 3.45 | 72000 | 2.27 | R-32 | 7.6667
218036938 |  | DAIKIN | HMSV-A-CB | RXYA96AATJ* |  |  |  | RXYA96AATJ* | Ducted Indoor Units | 92000 | 12 | 20.8 | 92000 | 3.4 | 72000 | 2.25 | R-32 | 7.6667
218036902 |  | DAIKIN | HMSV-A-CB | RXYA96AATJ* |  |  |  | RXYA96AATJ* | Non-Ducted Indoor Units | 92000 | 12.2 | 24.5 | 92000 | 3.5 | 72000 | 2.3 | R-32 | 7.6667
218036903 |  | DAIKIN | HMSV-A-CB | RXYA120AATJ* |  |  |  | RXYA120AATJ* | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036939 |  | DAIKIN | HMSV-A-CB | RXYA120AATJ* |  |  |  | RXYA120AATJ* | Ducted Indoor Units | 114000 | 11.1 | 20 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036975 |  | DAIKIN | HMSV-A-CB | RXYA120AATJ* |  |  |  | RXYA120AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.1 | 21.4 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036919 |  | DAIKIN | HMSV-A-CB | RXYA72AAYD* |  |  |  | RXYA72AAYD* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.5 | 69000 | 3.64 | 51000 | 2.4 | R-32 | 5.75
218036955 |  | DAIKIN | HMSV-A-CB | RXYA72AAYD* |  |  |  | RXYA72AAYD* | Ducted Indoor Units | 69000 | 12.4 | 21 | 69000 | 3.6 | 51000 | 2.4 | R-32 | 5.75
218036991 |  | DAIKIN | HMSV-A-CB | RXYA72AAYD* |  |  |  | RXYA72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.45 | 22.25 | 69000 | 3.62 | 51000 | 2.4 | R-32 | 5.75
218036992 |  | DAIKIN | HMSV-A-CB | RXYA96AAYD* |  |  |  | RXYA96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 22.65 | 92000 | 3.45 | 72000 | 2.27 | R-32 | 7.6667
218036956 |  | DAIKIN | HMSV-A-CB | RXYA96AAYD* |  |  |  | RXYA96AAYD* | Ducted Indoor Units | 92000 | 12 | 20.8 | 92000 | 3.4 | 72000 | 2.25 | R-32 | 7.6667
218036920 |  | DAIKIN | HMSV-A-CB | RXYA96AAYD* |  |  |  | RXYA96AAYD* | Non-Ducted Indoor Units | 92000 | 12.2 | 24.5 | 92000 | 3.5 | 72000 | 2.3 | R-32 | 7.6667
218036921 |  | DAIKIN | HMSV-A-CB | RXYA120AAYD* |  |  |  | RXYA120AAYD* | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036957 |  | DAIKIN | HMSV-A-CB | RXYA120AAYD* |  |  |  | RXYA120AAYD* | Ducted Indoor Units | 114000 | 11.1 | 20 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036993 |  | DAIKIN | HMSV-A-CB | RXYA120AAYD* |  |  |  | RXYA120AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.1 | 21.4 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218037009 |  | DAIKIN | HMSR-A-CB | REYA72AATJ* |  |  |  | REYA72AATJ* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.6 | 69000 | 3.8 | 51000 | 2.4 | R-32 | 5.75
218037045 |  | DAIKIN | HMSR-A-CB | REYA72AATJ* |  |  |  | REYA72AATJ* | Ducted Indoor Units | 69000 | 12.4 | 21.2 | 69000 | 3.6 | 51000 | 2.4 | R-32 | 5.75
218037081 |  | DAIKIN | HMSR-A-CB | REYA72AATJ* |  |  |  | REYA72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.45 | 22.4 | 69000 | 3.7 | 51000 | 2.4 | R-32 | 5.75
218037082 |  | DAIKIN | HMSR-A-CB | REYA96AATJ* |  |  |  | REYA96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 22.7 | 92000 | 3.7 | 72000 | 2.27 | R-32 | 7.6667
218037046 |  | DAIKIN | HMSR-A-CB | REYA96AATJ* |  |  |  | REYA96AATJ* | Ducted Indoor Units | 92000 | 12 | 21.2 | 92000 | 3.6 | 72000 | 2.25 | R-32 | 7.6667
218037010 |  | DAIKIN | HMSR-A-CB | REYA96AATJ* |  |  |  | REYA96AATJ* | Non-Ducted Indoor Units | 92000 | 12.2 | 24.2 | 92000 | 3.8 | 72000 | 2.3 | R-32 | 7.6667
218037011 |  | DAIKIN | HMSR-A-CB | REYA120AATJ* |  |  |  | REYA120AATJ* | Non-Ducted Indoor Units | 114000 | 11.1 | 23 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037047 |  | DAIKIN | HMSR-A-CB | REYA120AATJ* |  |  |  | REYA120AATJ* | Ducted Indoor Units | 114000 | 11.1 | 20.2 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037083 |  | DAIKIN | HMSR-A-CB | REYA120AATJ* |  |  |  | REYA120AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.1 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037027 |  | DAIKIN | HMSR-A-CB | REYA72AAYD* |  |  |  | REYA72AAYD* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.6 | 69000 | 3.8 | 51000 | 2.4 | R-32 | 5.75
218037063 |  | DAIKIN | HMSR-A-CB | REYA72AAYD* |  |  |  | REYA72AAYD* | Ducted Indoor Units | 69000 | 12.4 | 21.2 | 69000 | 3.6 | 51000 | 2.4 | R-32 | 5.75
218037099 |  | DAIKIN | HMSR-A-CB | REYA72AAYD* |  |  |  | REYA72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.45 | 22.4 | 69000 | 3.7 | 51000 | 2.4 | R-32 | 5.75
218037100 |  | DAIKIN | HMSR-A-CB | REYA96AAYD* |  |  |  | REYA96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 22.7 | 92000 | 3.7 | 72000 | 2.27 | R-32 | 7.6667
218037064 |  | DAIKIN | HMSR-A-CB | REYA96AAYD* |  |  |  | REYA96AAYD* | Ducted Indoor Units | 92000 | 12 | 21.2 | 92000 | 3.6 | 72000 | 2.25 | R-32 | 7.6667
218037028 |  | DAIKIN | HMSR-A-CB | REYA96AAYD* |  |  |  | REYA96AAYD* | Non-Ducted Indoor Units | 92000 | 12.2 | 24.2 | 92000 | 3.8 | 72000 | 2.3 | R-32 | 7.6667
218037029 |  | DAIKIN | HMSR-A-CB | REYA120AAYD* |  |  |  | REYA120AAYD* | Non-Ducted Indoor Units | 114000 | 11.1 | 23 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037065 |  | DAIKIN | HMSR-A-CB | REYA120AAYD* |  |  |  | REYA120AAYD* | Ducted Indoor Units | 114000 | 11.1 | 20.2 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037101 |  | DAIKIN | HMSR-A-CB | REYA120AAYD* |  |  |  | REYA120AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.1 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
214094394 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094538 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094242 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094395 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094490 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094346 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094194 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094347 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094290 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094442 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094586 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094443 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091756 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091612 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091468 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091613 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091708 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091564 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091420 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091565 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091516 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091804 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091660 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091661 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
213916335 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.4 | 21.8 | 77000 | 3.83 | 54000 | 2.45 | R-410A | 5.75
213916331 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 10.5 | 21.8 | 77000 | 3.62 | 54000 | 2.4 | R-410A | 5.75
213916332 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 10.3 | 21.8 | 77000 | 4.04 | 54000 | 2.5 | R-410A | 5.75
213895937 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 20 | 69000 | 3.7 | 51000 | 2.35 | R-410A | 5.75
213895919 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Ducted Indoor Units | 69000 | 11.8 | 19 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213895897 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Non-Ducted Indoor Units | 69000 | 12.2 | 21 | 69000 | 3.8 | 51000 | 2.3 | R-410A | 5.75
213895898 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Non-Ducted Indoor Units | 92000 | 11.4 | 22.1 | 92000 | 3.8 | 72000 | 2.3 | R-410A | 7.6667
213895716 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Ducted Indoor Units | 92000 | 11.9 | 19.3 | 92000 | 3.6 | 72000 | 2.25 | R-410A | 7.6667
213895938 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.65 | 20.7 | 92000 | 3.7 | 72000 | 2.27 | R-410A | 7.6667
213896224 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* |  |  |  | REYQ120AATJ* | Non-Ducted Indoor Units | 114000 | 10.6 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213896246 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* |  |  |  | REYQ120AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.75 | 20.1 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213895908 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Non-Ducted Indoor Units | 69000 | 12.2 | 21 | 69000 | 3.8 | 51000 | 2.3 | R-410A | 5.75
213895947 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 20 | 69000 | 3.7 | 51000 | 2.35 | R-410A | 5.75
213895928 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Ducted Indoor Units | 69000 | 11.8 | 19 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213895948 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.65 | 20.7 | 92000 | 3.7 | 72000 | 2.27 | R-410A | 7.6667
213895909 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Non-Ducted Indoor Units | 92000 | 11.4 | 22.1 | 92000 | 3.8 | 72000 | 2.3 | R-410A | 7.6667
213895718 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Ducted Indoor Units | 92000 | 11.9 | 19.3 | 92000 | 3.6 | 72000 | 2.25 | R-410A | 7.6667
213896254 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* |  |  |  | REYQ120AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.75 | 20.1 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213896228 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* |  |  |  | REYQ120AAYD* | Non-Ducted Indoor Units | 114000 | 10.6 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213893881 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
213893925 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893987 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602343 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602443 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602547 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602450 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
216602354 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602337 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893929 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893885 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893877 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893889 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893933 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893991 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602362 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602457 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602553 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893927 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893989 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
213893883 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602550 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602447 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602349 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602340 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602454 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
216602357 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893887 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893879 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893931 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893935 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893993 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893891 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602557 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602366 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602461 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893926 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893988 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
213893882 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602549 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602446 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602346 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602795 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
214826411 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
214826412 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602797 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602338 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602452 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
216602356 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893886 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893878 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893930 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893934 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893992 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893890 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602555 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602364 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602459 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602799 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
214826413 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893928 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893990 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
213893884 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602552 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602449 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602351 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602342 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602455 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
216602360 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893888 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893880 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893932 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893936 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893994 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893892 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602558 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602369 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602462 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213916286 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916854 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916284 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916287 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916288 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
213916309 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916862 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916291 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916289 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916292 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
216699455 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) |  |  |  | GMV-120WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
218043593 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G2 |  |  |  | VEP120C432G2 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
218405543 | 1/1/2027 | ADINA | HMSV-A-CB | ADN-120WM/B-U(U) |  |  |  | ADN-120WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
214091436 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091580 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091724 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091581 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091596 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091452 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091740 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091597 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091676 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091532 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214078203 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091533 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091548 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091404 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091549 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091484 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091628 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091772 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091629 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091644 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091500 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091788 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091645 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094178 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094330 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094474 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094331 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094258 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094410 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094554 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094411 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094426 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094570 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094274 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094427 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094210 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094362 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094506 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094363 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094378 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094522 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094226 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094379 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094458 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094314 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094162 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094315 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
213893629 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213916540 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213894863 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213894865 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213916555 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213893631 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893634 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893635 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916541 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916556 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893638 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893639 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916542 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213894867 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894875 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213894877 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213894869 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213916557 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213893524 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893525 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916490 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916509 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893528 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893529 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893532 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893533 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916491 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916510 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893536 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893537 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916492 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213894871 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894879 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213894881 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213894873 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213916511 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213916528 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893828 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893825 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893826 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893829 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213916534 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916530 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893540 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893541 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893544 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893545 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213916536 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916699 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893770 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893771 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893772 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893859 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213916701 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916703 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893773 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893774 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213893775 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893776 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916705 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916707 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213894966 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894967 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213894968 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894969 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213916709 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213916773 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916777 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916781 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893777 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893778 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893787 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893788 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893854 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893855 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893856 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893860 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213916775 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893789 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893790 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916779 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893779 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893780 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213916783 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916794 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213894883 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213893857 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893858 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213894957 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213916796 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916798 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893821 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893822 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213893823 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893824 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916800 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916802 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213894990 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894991 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213894992 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894993 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213916804 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213916529 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893562 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893563 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893566 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893567 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916535 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
214050138 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
213895982 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896102 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896106 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 |  |  |  | PURY-EP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
214050142 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 |  |  |  | PURY-EP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
214050078 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 |  |  |  | PURY-EP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896658 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 |  |  |  | PURY-EP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
214050136 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
213896100 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895980 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896104 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 |  |  |  | PURY-EP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
214050140 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 |  |  |  | PURY-EP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
214050076 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 |  |  |  | PURY-EP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896656 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 |  |  |  | PURY-EP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
214050162 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
213896130 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895998 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896002 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896134 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050166 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
214050146 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120YNU-A1 |  |  |  | PURY-HP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896662 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120YNU-A1 |  |  |  | PURY-HP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
213896127 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895996 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
214050160 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
214050164 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
213896000 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896132 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050144 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120TNU-A1 |  |  |  | PURY-HP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896660 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120TNU-A1 |  |  |  | PURY-HP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
214050210 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
213896150 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896014 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896154 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 |  |  |  | PURY-P96YNU-A1 | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
214050214 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 |  |  |  | PURY-P96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896666 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 |  |  |  | PURY-P120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
213896148 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896012 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
214050208 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
214050212 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 |  |  |  | PURY-P96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896152 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 |  |  |  | PURY-P96TNU-A1 | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896664 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 |  |  |  | PURY-P120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
214050284 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
213896158 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896022 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896162 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN |  |  |  | TURYE0964AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
214050288 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN |  |  |  | TURYE0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
214050292 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN |  |  |  | TURYE1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896670 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN |  |  |  | TURYE1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
214050282 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
213896156 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896020 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896160 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN |  |  |  | TURYE0963AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
214050286 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN |  |  |  | TURYE0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
214050290 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN |  |  |  | TURYE1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896668 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN |  |  |  | TURYE1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
214050352 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
213896190 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896046 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896050 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896194 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050356 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
214050360 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AN41AN |  |  |  | TURYH1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896674 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AN41AN |  |  |  | TURYH1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
213896188 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896044 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
214050350 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
214050354 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
213896048 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896192 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050358 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AN41AN |  |  |  | TURYH1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896672 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AN41AN |  |  |  | TURYH1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
214050376 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
213896062 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896206 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896210 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN |  |  |  | TURYP0964AN41AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
214050380 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN |  |  |  | TURYP0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896678 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN |  |  |  | TURYP1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
213896204 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896060 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
214050374 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
214050378 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN |  |  |  | TURYP0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896208 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN |  |  |  | TURYP0963AN41AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896676 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN |  |  |  | TURYP1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
213896312 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-B |  |  |  | PURY-P72ZKMU-B | Non-Ducted Indoor Units | 69000 | 11.4 | 19.8 | 76000 | 3.46 | 56000 | 2.26 | R-410A | 5.75
214050548 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-B |  |  |  | PURY-P72ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.35 | 19.1 | 76000 | 3.54 | 56000 | 2.26 | R-410A | 5.75
214050555 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B |  |  |  | PURY-P96ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.95 | 19.95 | 103000 | 3.46 | 71000 | 2.26 | R-410A | 7.6667
213896357 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B |  |  |  | PURY-P96ZKMU-B | Ducted Indoor Units | 92000 | 10.9 | 21.1 | 103000 | 3.46 | 71000 | 2.26 | R-410A | 7.6667
213896282 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Ducted Indoor Units | 69000 | 12.3 | 20.2 | 76000 | 3.74 | 56000 | 2.59 | R-410A | 5.75
213896293 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Non-Ducted Indoor Units | 69000 | 12.4 | 22.2 | 76000 | 3.85 | 56000 | 2.25 | R-410A | 5.75
213916477 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.2 | 76000 | 3.79 | 56000 | 2.42 | R-410A | 5.75
213916478 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12 | 21.15 | 103000 | 3.73 | 76000 | 2.56 | R-410A | 7.6667
213896294 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Non-Ducted Indoor Units | 92000 | 12.1 | 20.1 | 103000 | 3.74 | 76000 | 2.42 | R-410A | 7.6667
213896337 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Ducted Indoor Units | 92000 | 11.9 | 22.2 | 103000 | 3.73 | 76000 | 2.71 | R-410A | 7.6667
213896316 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B |  |  |  | PUHY-P120ZKMU-B | Ducted Indoor Units | 115000 | 11.4 | 19.5 | 129000 | 3.62 | 92000 | 2.51 | R-410A | 9.5833
213916323 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916691 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916324 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916316 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916325 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
217284733 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
217284734 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
217284739 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
217284736 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-W |  |  |  | GMV-VQ96WM/C-W | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
217284737 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-W |  |  |  | GMV-VQ96WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
217563533 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
217563467 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
217563468 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
217650552 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C-W |  |  |  | TVRF-VQ96WM/C-W | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
217650553 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C-W |  |  |  | TVRF-VQ96WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
213686135 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
213686136 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
213686137 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
213686138 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
213686139 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
213686140 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
213686141 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
213686142 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
213686143 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
210135420 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
210135423 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
210135408 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
208758264 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
208758265 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
208758266 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
208758267 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
208758268 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
208758269 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
210135409 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
210135410 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
210135424 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
210135425 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
210135411 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
210135412 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
208758270 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
208758271 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
218083193 |  | HITACHI | HMSV-A-CB | HVAHR168C33S |  |  |  | HVAHR168C33S* | Non-Ducted Indoor Units | 160000 | 11.4 | 19.1 | 180000 | 3.97 | 124000 | 2.44 | R-32 | 13.3333
218083213 |  | HITACHI | HMSR-A-CB | HVAHR168C33S |  |  |  | HVAHR168C33S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.1 | 180000 | 3.97 | 124000 | 2.44 | R-32 | 13.3333
218083293 |  | HITACHI | HMSV-A-CB | HVAHR168C33S |  |  |  | HVAHR168C33S* | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 18.25 | 180000 | 3.74 | 124000 | 2.28 | R-32 | 13.3333
218083311 |  | HITACHI | HMSR-A-CB | HVAHR168C33S |  |  |  | HVAHR168C33S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 18.25 | 180000 | 3.74 | 124000 | 2.28 | R-32 | 13.3333
218083216 |  | HITACHI | HMSR-A-CB | HVAHR240C33S |  |  |  | HVAHR240C33S | Non-Ducted Indoor Units | 230000 | 10.4 | 18.9 | 238000 | 3.47 | 150000 | 2.22 | R-32 | 19.1667
218083196 |  | HITACHI | HMSV-A-CB | HVAHR240C33S |  |  |  | HVAHR240C33S* | Non-Ducted Indoor Units | 230000 | 10.4 | 18.9 | 238000 | 3.47 | 150000 | 2.22 | R-32 | 19.1667
218083223 |  | HITACHI | HMSR-A-CB | HVAHR168C43S |  |  |  | HVAHR168C43S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.1 | 180000 | 3.97 | 124000 | 2.44 | R-32 | 13.3333
218083203 |  | HITACHI | HMSV-A-CB | HVAHR168C43S |  |  |  | HVAHR168C43S* | Non-Ducted Indoor Units | 160000 | 11.4 | 19.1 | 180000 | 3.97 | 124000 | 2.44 | R-32 | 13.3333
218083302 |  | HITACHI | HMSV-A-CB | HVAHR168C43S |  |  |  | HVAHR168C43S* | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 18.25 | 180000 | 3.74 | 124000 | 2.28 | R-32 | 13.3333
218083320 |  | HITACHI | HMSR-A-CB | HVAHR168C43S |  |  |  | HVAHR168C43S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 18.25 | 180000 | 3.74 | 124000 | 2.28 | R-32 | 13.3333
218083206 |  | HITACHI | HMSV-A-CB | HVAHR240C43S |  |  |  | HVAHR240C43S* | Non-Ducted Indoor Units | 230000 | 10.4 | 18.9 | 238000 | 3.47 | 150000 | 2.22 | R-32 | 19.1667
218083226 |  | HITACHI | HMSR-A-CB | HVAHR240C43S |  |  |  | HVAHR240C43S | Non-Ducted Indoor Units | 230000 | 10.4 | 18.9 | 238000 | 3.47 | 150000 | 2.22 | R-32 | 19.1667
218362493 |  | FUJITSU | HMSR-A-CB | AOSU120VSAN7 | AOSU096VSAN7 |  |  | AOSU216VSAG7 | Non-Ducted Indoor Units | 206000 | 11.5 | 23 | 232000 | 3.38 | 158000 | 2.34 | R-32 | 17.1667
218363895 |  | FUJITSU | HMSR-A-CB | AOSU120VSAN7 | AOSU120VSAN7 |  |  | AOSU240VSAG7 | Non-Ducted Indoor Units | 230000 | 11.6 | 24.6 | 258000 | 3.42 | 172000 | 2.21 | R-32 | 19.1667
218452865 |  | FUJITSU | HMSR-A-CB | AOSU120VSAN7 | AOSU096VSAN7 |  |  | AOSU216VSAG7 | Ducted Indoor Units | 206000 | 11.3 | 20.4 | 232000 | 3.6 | 158000 | 2.39 | R-32 | 17.1667
218452866 |  | FUJITSU | HMSR-A-CB | AOSU120VSAN7 | AOSU120VSAN7 |  |  | AOSU240VSAG7 | Ducted Indoor Units | 230000 | 11.5 | 20.2 | 258000 | 3.64 | 172000 | 2.47 | R-32 | 19.1667
218214202 |  | FUJITSU | HMSR-A-CB | AOSU144VSAN7 |  |  |  | AOSU144VSAN7 | Non-Ducted Indoor Units | 206000 | 12.2 | 23.3 | 154000 | 3.72 | 106000 | 2.41 | R-32 | 17.1667
218214213 |  | FUJITSU | HMSR-A-CB | AOSU144VSAN7 |  |  |  | AOSU144VSAN7 | Ducted Indoor Units | 206000 | 11.8 | 21.6 | 154000 | 3.72 | 106000 | 2.41 | R-32 | 17.1667
218214214 |  | FUJITSU | HMSR-A-CB | AOSU168VSAN7 |  |  |  | AOSU168VSAN7 | Ducted Indoor Units | 230000 | 11.4 | 20.6 | 180000 | 3.55 | 124000 | 2.34 | R-32 | 19.1667
218214203 |  | FUJITSU | HMSR-A-CB | AOSU168VSAN7 |  |  |  | AOSU168VSAN7 | Non-Ducted Indoor Units | 230000 | 11.85 | 23 | 180000 | 3.55 | 124000 | 2.34 | R-32 | 19.1667
218214204 |  | FUJITSU | HMSR-A-CB | AOSU192VSAN7 |  |  |  | AOSU192VSAN7 | Non-Ducted Indoor Units | 138000 | 10.9 | 22.4 | 206000 | 3.4 | 142000 | 2.17 | R-32 | 11.5
218214215 |  | FUJITSU | HMSR-A-CB | AOSU192VSAN7 |  |  |  | AOSU192VSAN7 | Ducted Indoor Units | 138000 | 10.9 | 20.1 | 206000 | 3.4 | 142000 | 2.17 | R-32 | 11.5
218362494 |  | FUJITSU | HMSR-A-CB | AORU120VSAN7 | AORU096VSAN7 |  |  | AORU216VSAG7 | Non-Ducted Indoor Units | 206000 | 11.5 | 23 | 232000 | 3.38 | 158000 | 2.34 | R-32 | 17.1667
218363901 |  | FUJITSU | HMSR-A-CB | AORU120VSAN7 | AORU120VSAN7 |  |  | AORU240VSAG7 | Non-Ducted Indoor Units | 230000 | 11.6 | 24.6 | 258000 | 3.42 | 172000 | 2.21 | R-32 | 19.1667
218452872 |  | FUJITSU | HMSR-A-CB | AORU120VSAN7 | AORU096VSAN7 |  |  | AORU216VSAG7 | Ducted Indoor Units | 206000 | 11.3 | 20.4 | 232000 | 3.6 | 158000 | 2.39 | R-32 | 17.1667
218452873 |  | FUJITSU | HMSR-A-CB | AORU120VSAN7 | AORU120VSAN7 |  |  | AORU240VSAG7 | Ducted Indoor Units | 230000 | 11.5 | 20.2 | 258000 | 3.64 | 172000 | 2.47 | R-32 | 19.1667
218214206 |  | FUJITSU | HMSR-A-CB | AORU144VSAN7 |  |  |  | AORU144VSAN7 | Non-Ducted Indoor Units | 206000 | 12.2 | 23.3 | 154000 | 3.72 | 106000 | 2.41 | R-32 | 17.1667
218214217 |  | FUJITSU | HMSR-A-CB | AORU144VSAN7 |  |  |  | AORU144VSAN7 | Ducted Indoor Units | 206000 | 11.8 | 21.6 | 154000 | 3.72 | 106000 | 2.41 | R-32 | 17.1667
218214218 |  | FUJITSU | HMSR-A-CB | AORU168VSAN7 |  |  |  | AORU168VSAN7 | Ducted Indoor Units | 230000 | 11.4 | 20.6 | 180000 | 3.55 | 124000 | 2.34 | R-32 | 19.1667
218214207 |  | FUJITSU | HMSR-A-CB | AORU168VSAN7 |  |  |  | AORU168VSAN7 | Non-Ducted Indoor Units | 230000 | 11.85 | 23 | 180000 | 3.55 | 124000 | 2.34 | R-32 | 19.1667
218214208 |  | FUJITSU | HMSR-A-CB | AORU192VSAN7 |  |  |  | AORU192VSAN7 | Non-Ducted Indoor Units | 138000 | 10.9 | 22.4 | 206000 | 3.4 | 142000 | 2.17 | R-32 | 11.5
218214219 |  | FUJITSU | HMSR-A-CB | AORU192VSAN7 |  |  |  | AORU192VSAN7 | Ducted Indoor Units | 138000 | 10.9 | 20.1 | 206000 | 3.4 | 142000 | 2.17 | R-32 | 11.5
218327223 |  | HISENSE | HMSR-A-CB | AVWT-144FFDS5H |  |  |  | AVWT-144FFDS5H | Ducted Indoor Units | 138000 | 11.85 | 21.59 | 150000 | 3.82 | 98000 | 2.81 | R-32 | 11.5
218327224 |  | HISENSE | HMSR-A-CB | AVWT-144FFDS5H |  |  |  | AVWT-144FFDS5H | Non-Ducted Indoor Units | 138000 | 12.05 | 23.72 | 150000 | 4.15 | 98000 | 2.96 | R-32 | 11.5
218327225 |  | HISENSE | HMSR-A-CB | AVWT-144FFDS5H |  |  |  | AVWT-144FFDS5H | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.95 | 22.65 | 150000 | 3.98 | 98000 | 2.88 | R-32 | 11.5
218327226 |  | HISENSE | HMSR-A-CB | AVWT-168FFDS5H |  |  |  | AVWT-168FFDS5H | Ducted Indoor Units | 160000 | 11.3 | 20.64 | 180000 | 3.81 | 117000 | 2.85 | R-32 | 13.3333
218327227 |  | HISENSE | HMSR-A-CB | AVWT-168FFDS5H |  |  |  | AVWT-168FFDS5H | Non-Ducted Indoor Units | 160000 | 11.65 | 22.86 | 180000 | 4.02 | 117000 | 2.91 | R-32 | 13.3333
218327228 |  | HISENSE | HMSR-A-CB | AVWT-168FFDS5H |  |  |  | AVWT-168FFDS5H | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.47 | 21.75 | 180000 | 3.91 | 117000 | 2.88 | R-32 | 13.3333
218327229 |  | HISENSE | HMSR-A-CB | AVWT-192FFDS5H |  |  |  | AVWT-192FFDS5H | Ducted Indoor Units | 184000 | 10.9 | 20.3 | 200000 | 3.74 | 134000 | 2.82 | R-32 | 15.3333
218327230 |  | HISENSE | HMSR-A-CB | AVWT-192FFDS5H |  |  |  | AVWT-192FFDS5H | Non-Ducted Indoor Units | 184000 | 10.9 | 21.08 | 200000 | 3.99 | 134000 | 2.89 | R-32 | 15.3333
218327231 |  | HISENSE | HMSR-A-CB | AVWT-192FFDS5H |  |  |  | AVWT-192FFDS5H | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.9 | 20.69 | 200000 | 3.86 | 134000 | 2.85 | R-32 | 15.3333
218327232 |  | HISENSE | HMSR-A-CB | AVWT-216FFDS5H |  |  |  | AVWT-216FFDS5H | Ducted Indoor Units | 206000 | 10.9 | 20.79 | 220000 | 3.5 | 150000 | 2.72 | R-32 | 17.1667
218327233 |  | HISENSE | HMSR-A-CB | AVWT-216FFDS5H |  |  |  | AVWT-216FFDS5H | Non-Ducted Indoor Units | 206000 | 11.1 | 22.57 | 220000 | 3.8 | 150000 | 2.85 | R-32 | 17.1667
218327234 |  | HISENSE | HMSR-A-CB | AVWT-216FFDS5H |  |  |  | AVWT-216FFDS5H | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 21.68 | 220000 | 3.65 | 150000 | 2.78 | R-32 | 17.1667
218327235 |  | HISENSE | HMSR-A-CB | AVWT-240FFDS5H |  |  |  | AVWT-240FFDS5H | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 250000 | 3.43 | 168000 | 2.57 | R-32 | 19
218327236 |  | HISENSE | HMSR-A-CB | AVWT-240FFDS5H |  |  |  | AVWT-240FFDS5H | Non-Ducted Indoor Units | 228000 | 10.95 | 22.28 | 250000 | 3.67 | 168000 | 2.78 | R-32 | 19
218327237 |  | HISENSE | HMSR-A-CB | AVWT-240FFDS5H |  |  |  | AVWT-240FFDS5H | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.92 | 21.24 | 250000 | 3.55 | 168000 | 2.67 | R-32 | 19
218425693 |  | GE Appliances | HMSR-A-CB | MWHQ144NC2CA* |  |  |  | MWHQ144NC2CA* | Ducted Indoor Units | 138000 | 10.8 | 20.3 | 154000 | 3.5 | 108000 | 2.4 | R-32 | 11.5
218425694 |  | GE Appliances | HMSR-A-CB | MWHQ144NC2CA* |  |  |  | MWHQ144NC2CA* | Non-Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.6 | 108000 | 2.5 | R-32 | 11.5
218425695 |  | GE Appliances | HMSR-A-CB | MWHQ144NC4CA* |  |  |  | MWHQ144NC4CA* | Ducted Indoor Units | 138000 | 10.8 | 20.3 | 154000 | 3.5 | 108000 | 2.4 | R-32 | 11.5
218425696 |  | GE Appliances | HMSR-A-CB | MWHQ144NC4CA* |  |  |  | MWHQ144NC4CA* | Non-Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.6 | 108000 | 2.5 | R-32 | 11.5
218425697 |  | GE Appliances | HMSR-A-CB | MWHQ168NC2CA* |  |  |  | MWHQ168NC2CA* | Ducted Indoor Units | 160000 | 11.5 | 21.5 | 180000 | 3.5 | 122000 | 2.5 | R-32 | 13.3333
218425698 |  | GE Appliances | HMSR-A-CB | MWHQ168NC2CA* |  |  |  | MWHQ168NC2CA* | Non-Ducted Indoor Units | 160000 | 11.4 | 22.1 | 180000 | 3.6 | 122000 | 2.5 | R-32 | 13.3333
218425699 |  | GE Appliances | HMSR-A-CB | MWHQ168NC4CA* |  |  |  | MWHQ168NC4CA* | Ducted Indoor Units | 160000 | 11.5 | 21.5 | 180000 | 3.5 | 122000 | 2.5 | R-32 | 13.3333
218425700 |  | GE Appliances | HMSR-A-CB | MWHQ168NC4CA* |  |  |  | MWHQ168NC4CA* | Non-Ducted Indoor Units | 160000 | 11.4 | 22.1 | 180000 | 3.6 | 122000 | 2.5 | R-32 | 13.3333
218425701 |  | GE Appliances | HMSR-A-CB | MWHQ192NC2CA* |  |  |  | MWHQ192NC2CA* | Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.4 | 138000 | 2.4 | R-32 | 15.3333
218425702 |  | GE Appliances | HMSR-A-CB | MWHQ192NC2CA* |  |  |  | MWHQ192NC2CA* | Non-Ducted Indoor Units | 184000 | 11.2 | 21.1 | 206000 | 3.5 | 138000 | 2.4 | R-32 | 15.3333
218425703 |  | GE Appliances | HMSR-A-CB | MWHQ192NC4CA* |  |  |  | MWHQ192NC4CA* | Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.4 | 138000 | 2.4 | R-32 | 15.3333
218425704 |  | GE Appliances | HMSR-A-CB | MWHQ192NC4CA* |  |  |  | MWHQ192NC4CA* | Non-Ducted Indoor Units | 184000 | 11.2 | 21.1 | 206000 | 3.5 | 138000 | 2.4 | R-32 | 15.3333
218425705 |  | GE Appliances | HMSR-A-CB | MWHQ216NC2CA* |  |  |  | MWHQ216NC2CA* | Ducted Indoor Units | 206000 | 11.3 | 20.8 | 232000 | 3.3 | 156000 | 2.4 | R-32 | 17.1667
218425706 |  | GE Appliances | HMSR-A-CB | MWHQ216NC2CA* |  |  |  | MWHQ216NC2CA* | Non-Ducted Indoor Units | 206000 | 10.6 | 21 | 232000 | 3.5 | 156000 | 2.4 | R-32 | 17.1667
218425707 |  | GE Appliances | HMSR-A-CB | MWHQ216NC4CA* |  |  |  | MWHQ216NC4CA* | Ducted Indoor Units | 206000 | 11.3 | 20.8 | 232000 | 3.3 | 156000 | 2.4 | R-32 | 17.1667
218425708 |  | GE Appliances | HMSR-A-CB | MWHQ216NC4CA* |  |  |  | MWHQ216NC4CA* | Non-Ducted Indoor Units | 206000 | 10.6 | 21 | 232000 | 3.5 | 156000 | 2.4 | R-32 | 17.1667
218425709 |  | GE Appliances | HMSR-A-CB | MWHQ240NC2CA* |  |  |  | MWHQ240NC2CA* | Ducted Indoor Units | 222000 | 10.3 | 19 | 240000 | 3.3 | 168000 | 2.3 | R-32 | 18.5
218425711 |  | GE Appliances | HMSR-A-CB | MWHQ240NC4CA* |  |  |  | MWHQ240NC4CA* | Ducted Indoor Units | 222000 | 10.3 | 19 | 240000 | 3.3 | 168000 | 2.3 | R-32 | 18.5
218425736 |  | HITACHI | HMSR-A-CB | HVAHR144C33CW |  |  |  | HVAHR144C33CW | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.9 | 18 | 154000 | 3.56 | 110000 | 2.29 | R-32 | 11.5
218425732 |  | HITACHI | HMSV-A-CB | HVAHR144C33CW |  |  |  | HVAHR144C33CW* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.9 | 18 | 154000 | 3.56 | 110000 | 2.29 | R-32 | 11.5
218425728 |  | HITACHI | HMSR-A-CB | HVAHR144C33CW |  |  |  | HVAHR144C33CW | Non-Ducted Indoor Units | 138000 | 11.8 | 19.1 | 154000 | 3.78 | 110000 | 2.35 | R-32 | 11.5
218425724 |  | HITACHI | HMSV-A-CB | HVAHR144C33CW |  |  |  | HVAHR144C33CW* | Non-Ducted Indoor Units | 138000 | 11.8 | 19.1 | 154000 | 3.78 | 110000 | 2.35 | R-32 | 11.5
218425738 |  | HITACHI | HMSR-A-CB | HVAHR144C43CW |  |  |  | HVAHR144C43CW | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.9 | 18 | 154000 | 3.56 | 110000 | 2.29 | R-32 | 11.5
218425734 |  | HITACHI | HMSV-A-CB | HVAHR144C43CW |  |  |  | HVAHR144C43CW* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.9 | 18 | 154000 | 3.56 | 110000 | 2.29 | R-32 | 11.5
218425730 |  | HITACHI | HMSR-A-CB | HVAHR144C43CW |  |  |  | HVAHR144C43CW | Non-Ducted Indoor Units | 138000 | 11.8 | 19.1 | 154000 | 3.78 | 110000 | 2.35 | R-32 | 11.5
218425726 |  | HITACHI | HMSV-A-CB | HVAHR144C43CW |  |  |  | HVAHR144C43CW* | Non-Ducted Indoor Units | 138000 | 11.8 | 19.1 | 154000 | 3.78 | 110000 | 2.35 | R-32 | 11.5
218469259 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM192TXU-A |  |  |  | PUHY-GM192TXU-A | Non-Ducted Indoor Units | 184000 | 13.6 | 25.9 | 204000 | 4.04 | 144000 | 2.42 | R-32 | 15.3333
218469256 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM192TXU-A |  |  |  | PUHY-GM192TXU-A | Ducted Indoor Units | 184000 | 13.1 | 22.9 | 204000 | 3.91 | 144000 | 2.4 | R-32 | 15.3333
218469257 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM216TXU-A |  |  |  | PUHY-GM216TXU-A | Ducted Indoor Units | 206000 | 12.8 | 22.6 | 232000 | 3.79 | 162000 | 2.25 | R-32 | 17.1667
218469260 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM216TXU-A |  |  |  | PUHY-GM216TXU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.7 | 232000 | 3.9 | 162000 | 2.26 | R-32 | 17.1667
218469261 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM240TXU-A |  |  |  | PUHY-GM240TXU-A | Non-Ducted Indoor Units | 230000 | 12.6 | 23.1 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469258 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM240TXU-A |  |  |  | PUHY-GM240TXU-A | Ducted Indoor Units | 230000 | 12.2 | 22 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469262 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM192YXU-A |  |  |  | PUHY-GM192YXU-A | Ducted Indoor Units | 184000 | 13.1 | 22.9 | 204000 | 3.91 | 144000 | 2.4 | R-32 | 15.3333
218469265 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM192YXU-A |  |  |  | PUHY-GM192YXU-A | Non-Ducted Indoor Units | 184000 | 13.6 | 25.9 | 204000 | 4.04 | 144000 | 2.42 | R-32 | 15.3333
218469266 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM216YXU-A |  |  |  | PUHY-GM216YXU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.7 | 232000 | 3.9 | 162000 | 2.26 | R-32 | 17.1667
218469263 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM216YXU-A |  |  |  | PUHY-GM216YXU-A | Ducted Indoor Units | 206000 | 12.8 | 22.6 | 232000 | 3.79 | 162000 | 2.25 | R-32 | 17.1667
218469264 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM240YXU-A |  |  |  | PUHY-GM240YXU-A | Ducted Indoor Units | 230000 | 12.2 | 22 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469267 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-GM240YXU-A |  |  |  | PUHY-GM240YXU-A | Non-Ducted Indoor Units | 230000 | 12.6 | 23.1 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469283 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG1923AMM0AN |  |  |  | TUHYG1923AMM0AN | Non-Ducted Indoor Units | 184000 | 13.6 | 25.9 | 204000 | 4.04 | 144000 | 2.42 | R-32 | 15.3333
218469280 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG1923AMM0AN |  |  |  | TUHYG1923AMM0AN | Ducted Indoor Units | 184000 | 13.1 | 22.9 | 204000 | 3.91 | 144000 | 2.4 | R-32 | 15.3333
218469281 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG2163AMM0AN |  |  |  | TUHYG2163AMM0AN | Ducted Indoor Units | 206000 | 12.8 | 22.6 | 232000 | 3.79 | 162000 | 2.25 | R-32 | 17.1667
218469284 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG2163AMM0AN |  |  |  | TUHYG2163AMM0AN | Non-Ducted Indoor Units | 206000 | 13.3 | 24.7 | 232000 | 3.9 | 162000 | 2.26 | R-32 | 17.1667
218469285 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG2403AMM0AN |  |  |  | TUHYG2403AMM0AN | Non-Ducted Indoor Units | 230000 | 12.6 | 23.1 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469282 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG2403AMM0AN |  |  |  | TUHYG2403AMM0AN | Ducted Indoor Units | 230000 | 12.2 | 22 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469286 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG1924AMM0AN |  |  |  | TUHYG1924AMM0AN | Ducted Indoor Units | 184000 | 13.1 | 22.9 | 204000 | 3.91 | 144000 | 2.4 | R-32 | 15.3333
218469289 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG1924AMM0AN |  |  |  | TUHYG1924AMM0AN | Non-Ducted Indoor Units | 184000 | 13.6 | 25.9 | 204000 | 4.04 | 144000 | 2.42 | R-32 | 15.3333
218469290 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG2164AMM0AN |  |  |  | TUHYG2164AMM0AN | Non-Ducted Indoor Units | 206000 | 13.3 | 24.7 | 232000 | 3.9 | 162000 | 2.26 | R-32 | 17.1667
218469287 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG2164AMM0AN |  |  |  | TUHYG2164AMM0AN | Ducted Indoor Units | 206000 | 12.8 | 22.6 | 232000 | 3.79 | 162000 | 2.25 | R-32 | 17.1667
218469288 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG2404AMM0AN |  |  |  | TUHYG2404AMM0AN | Ducted Indoor Units | 230000 | 12.2 | 22 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469291 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYG2404AMM0AN |  |  |  | TUHYG2404AMM0AN | Non-Ducted Indoor Units | 230000 | 12.6 | 23.1 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469247 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM192TXU-A |  |  |  | PURY-GM192TXU-A | Non-Ducted Indoor Units | 184000 | 13.2 | 24.4 | 204000 | 3.98 | 144000 | 2.37 | R-32 | 15.3333
218469244 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM192TXU-A |  |  |  | PURY-GM192TXU-A | Ducted Indoor Units | 184000 | 12.7 | 22.3 | 204000 | 3.73 | 144000 | 2.32 | R-32 | 15.3333
218469245 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM216TXU-A |  |  |  | PURY-GM216TXU-A | Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.59 | 162000 | 2.21 | R-32 | 17.1667
218469248 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM216TXU-A |  |  |  | PURY-GM216TXU-A | Non-Ducted Indoor Units | 206000 | 12.8 | 23.6 | 232000 | 3.82 | 162000 | 2.22 | R-32 | 17.1667
218469249 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM240TXU-A |  |  |  | PURY-GM240TXU-A | Non-Ducted Indoor Units | 230000 | 12 | 22.1 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469246 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM240TXU-A |  |  |  | PURY-GM240TXU-A | Ducted Indoor Units | 230000 | 11.9 | 21.5 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469250 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM192YXU-A |  |  |  | PURY-GM192YXU-A | Ducted Indoor Units | 184000 | 12.7 | 22.3 | 204000 | 3.73 | 144000 | 2.32 | R-32 | 15.3333
218469253 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM192YXU-A |  |  |  | PURY-GM192YXU-A | Non-Ducted Indoor Units | 184000 | 13.2 | 24.4 | 204000 | 3.98 | 144000 | 2.37 | R-32 | 15.3333
218469254 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM216YXU-A |  |  |  | PURY-GM216YXU-A | Non-Ducted Indoor Units | 206000 | 12.8 | 23.6 | 232000 | 3.82 | 162000 | 2.22 | R-32 | 17.1667
218469251 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM216YXU-A |  |  |  | PURY-GM216YXU-A | Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.59 | 162000 | 2.21 | R-32 | 17.1667
218469252 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM240YXU-A |  |  |  | PURY-GM240YXU-A | Ducted Indoor Units | 230000 | 11.9 | 21.5 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469255 |  | Mitsubishi Electric | HMSR-A-CB | PURY-GM240YXU-A |  |  |  | PURY-GM240YXU-A | Non-Ducted Indoor Units | 230000 | 12 | 22.1 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469268 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG1923AMM0AN |  |  |  | TURYG1923AMM0AN | Ducted Indoor Units | 184000 | 12.7 | 22.3 | 204000 | 3.73 | 144000 | 2.32 | R-32 | 15.3333
218469271 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG1923AMM0AN |  |  |  | TURYG1923AMM0AN | Non-Ducted Indoor Units | 184000 | 13.2 | 24.4 | 204000 | 3.98 | 144000 | 2.37 | R-32 | 15.3333
218469272 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG2163AMM0AN |  |  |  | TURYG2163AMM0AN | Non-Ducted Indoor Units | 206000 | 12.8 | 23.6 | 232000 | 3.82 | 162000 | 2.22 | R-32 | 17.1667
218469269 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG2163AMM0AN |  |  |  | TURYG2163AMM0AN | Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.59 | 162000 | 2.21 | R-32 | 17.1667
218469270 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG2403AMM0AN |  |  |  | TURYG2403AMM0AN | Ducted Indoor Units | 230000 | 11.9 | 21.5 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469273 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG2403AMM0AN |  |  |  | TURYG2403AMM0AN | Non-Ducted Indoor Units | 230000 | 12 | 22.1 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469274 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG1924AMM0AN |  |  |  | TURYG1924AMM0AN | Ducted Indoor Units | 184000 | 12.7 | 22.3 | 204000 | 3.73 | 144000 | 2.32 | R-32 | 15.3333
218469277 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG1924AMM0AN |  |  |  | TURYG1924AMM0AN | Non-Ducted Indoor Units | 184000 | 13.2 | 24.4 | 204000 | 3.98 | 144000 | 2.37 | R-32 | 15.3333
218469278 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG2164AMM0AN |  |  |  | TURYG2164AMM0AN | Non-Ducted Indoor Units | 206000 | 12.8 | 23.6 | 232000 | 3.82 | 162000 | 2.22 | R-32 | 17.1667
218469275 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG2164AMM0AN |  |  |  | TURYG2164AMM0AN | Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.59 | 162000 | 2.21 | R-32 | 17.1667
218469276 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG2404AMM0AN |  |  |  | TURYG2404AMM0AN | Ducted Indoor Units | 230000 | 11.9 | 21.5 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
218469279 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYG2404AMM0AN |  |  |  | TURYG2404AMM0AN | Non-Ducted Indoor Units | 230000 | 12 | 22.1 | 258000 | 3.33 | 172000 | 2.21 | R-32 | 19.1667
216602281 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602197 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602143 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886442 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886446 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213886402 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886406 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886370 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886374 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602267 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602207 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602214 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602276 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602311 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602318 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602325 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602333 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
216602187 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602193 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602139 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602133 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602146 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602285 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602200 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602185 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602132 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602138 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602265 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602274 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602191 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602205 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602212 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602309 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602316 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602323 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602331 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886369 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886373 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213886401 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886405 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886413 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886441 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886445 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213893862 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893866 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893870 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893874 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886449 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213886409 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886377 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602283 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602198 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602144 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886447 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213886443 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886407 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886403 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886371 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886375 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602269 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602208 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602216 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602279 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602312 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602335 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
216602328 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602319 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602195 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602188 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602141 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602135 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602148 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602287 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602202 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602183 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602190 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602136 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602130 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602262 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602272 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602203 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602210 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602314 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602308 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602321 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602330 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886368 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886372 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213886400 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886404 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886440 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886444 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213897018 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Non-Ducted Indoor Units | 138000 | 11 | 21.8 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213897062 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 20.3 | 138000 | 3.32 | 90000 | 2.1 | R-410A | 11.5
213897044 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Ducted Indoor Units | 138000 | 10.9 | 18.8 | 138000 | 3.35 | 90000 | 2.1 | R-410A | 11.5
213897085 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Non-Ducted Indoor Units | 156000 | 10.3 | 21.7 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897095 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Ducted Indoor Units | 156000 | 10.2 | 18.4 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897111 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.25 | 20.05 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897019 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Non-Ducted Indoor Units | 184000 | 11.3 | 21.8 | 184000 | 3.48 | 130000 | 2.22 | R-410A | 15.3333
213897063 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.25 | 20.2 | 184000 | 3.44 | 130000 | 2.22 | R-410A | 15.3333
213897045 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Ducted Indoor Units | 184000 | 11.2 | 18.6 | 184000 | 3.4 | 130000 | 2.22 | R-410A | 15.3333
213897086 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Non-Ducted Indoor Units | 206000 | 10.3 | 20.8 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897112 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.6 | 19.6 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213895075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Ducted Indoor Units | 206000 | 10.9 | 18.4 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897020 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Non-Ducted Indoor Units | 228000 | 10.6 | 20 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897113 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.25 | 19 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897096 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Ducted Indoor Units | 228000 | 9.9 | 18 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897031 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Non-Ducted Indoor Units | 138000 | 11 | 21.8 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213897053 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Ducted Indoor Units | 138000 | 10.9 | 18.8 | 138000 | 3.35 | 90000 | 2.1 | R-410A | 11.5
213897071 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 20.3 | 138000 | 3.32 | 90000 | 2.1 | R-410A | 11.5
213897090 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Non-Ducted Indoor Units | 156000 | 10.3 | 21.7 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897120 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.25 | 20.05 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897103 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Ducted Indoor Units | 156000 | 10.2 | 18.4 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Ducted Indoor Units | 184000 | 11.2 | 18.6 | 184000 | 3.4 | 130000 | 2.22 | R-410A | 15.3333
213897032 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Non-Ducted Indoor Units | 184000 | 11.3 | 21.8 | 184000 | 3.48 | 130000 | 2.22 | R-410A | 15.3333
213897072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.25 | 20.2 | 184000 | 3.44 | 130000 | 2.22 | R-410A | 15.3333
213897091 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Non-Ducted Indoor Units | 206000 | 10.3 | 20.8 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897121 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.6 | 19.6 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213895076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Ducted Indoor Units | 206000 | 10.9 | 18.4 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897033 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Non-Ducted Indoor Units | 228000 | 10.6 | 20 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897104 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Ducted Indoor Units | 228000 | 9.9 | 18 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897122 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.25 | 19 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
214091401 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) | GMV-VQ72WM/C-F(U) |  |  | GMV-VQ144WM/C-F(U) | Ducted Indoor Units | 138000 | 11.7 | 22.4 | 154000 | 3.95 | 131000 | 2.07 | R-410A | 11.5
214091398 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) | GMV-VQ72WM/C-F(U) |  |  | GMV-VQ144WM/C-F(U) | Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 4 | 131000 | 2.07 | R-410A | 11.5
214091399 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) | GMV-VQ96WM/C-F(U) |  |  | GMV-VQ192WM/C-F(U) | Non-Ducted Indoor Units | 184000 | 10.3 | 20.4 | 206000 | 3.93 | 150000 | 2.07 | R-410A | 15.3333
214091402 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) | GMV-VQ96WM/C-F(U) |  |  | GMV-VQ192WM/C-F(U) | Ducted Indoor Units | 184000 | 11.1 | 20.3 | 206000 | 3.66 | 150000 | 2.07 | R-410A | 15.3333
214091403 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) | GMV-VQ120WM/C-F(U) |  |  | GMV-VQ240WM/C-F(U) | Ducted Indoor Units | 228000 | 10.5 | 19.5 | 256000 | 3.41 | 170000 | 2.07 | R-410A | 19
213928537 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q144WM/C-F(U) |  |  |  | GMV-Q144WM/C-F(U) | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
215685132 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP144C432Y2 |  |  |  | VEP144C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 19.65 | 154000 | 3.44 | 100000 | 2.07 | R-410A | 11.5
214728281 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP144C432Y2 |  |  |  | VEP144C432Y2 | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
215685124 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q144WM/C-F(U) |  |  |  | GMV-Q144WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 19.65 | 154000 | 3.44 | 100000 | 2.07 | R-410A | 11.5
213896730 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896731 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ120XBTJ* |  |  | REYQ216XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896682 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896683 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ120XBTJ* |  |  | REYQ216XBTJ* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896712 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896684 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* |  |  | REYQ240XBTJ* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896774 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* |  |  | REYQ240XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896797 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBTJ* |  |  |  | REYQ144XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896736 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896737 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ120XBYD* |  |  | REYQ216XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896699 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896700 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ120XBYD* |  |  | REYQ216XBYD* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896718 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896750 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* |  |  | REYQ240XBYD* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896778 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* |  |  | REYQ240XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896800 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBYD* |  |  |  | REYQ144XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896742 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896743 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ120XBYC* |  |  | REYQ216XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896706 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896707 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ120XBYC* |  |  | REYQ216XBYC* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896724 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896782 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* |  |  | REYQ240XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896754 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* |  |  | REYQ240XBYC* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896803 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBYC* |  |  |  | REYQ144XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896747 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* | RXYQ96XBYC* |  |  | RXYQ192XBYC* | Non-Ducted Indoor Units | 184000 | 10.7 | 18.4 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896809 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* | RXYQ120XBYC* |  |  | RXYQ216XBYC* | Non-Ducted Indoor Units | 206000 | 10.2 | 18.4 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896810 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* |  |  | RXYQ240XBYC* | Non-Ducted Indoor Units | 228000 | 9.9 | 18.6 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
214389359 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME2CA* |  |  |  | MVHQ144ME2CA* | Ducted Indoor Units | 138000 | 10.8 | 20.3 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214389360 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME2CA* |  |  |  | MVHQ144ME2CA* | Non-Ducted Indoor Units | 138000 | 10.8 | 20 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214229577 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME2CA* |  |  |  | MVHQ168ME2CA* | Ducted Indoor Units | 160000 | 11.5 | 21.5 | 180000 | 3.4 | 122000 | 2.4 | R-410A | 13.3333
214229578 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME2CA* |  |  |  | MVHQ168ME2CA* | Non-Ducted Indoor Units | 160000 | 11.4 | 23.2 | 180000 | 3.6 | 122000 | 2.5 | R-410A | 13.3333
214264484 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* |  |  |  | MVHQ192ME2CA* | Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.3 | 138000 | 2.4 | R-410A | 15.3333
214264485 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* |  |  |  | MVHQ192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.2 | 22.2 | 206000 | 3.5 | 138000 | 2.4 | R-410A | 15.3333
214097889 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME2CA* |  |  |  | MVHQ216ME2CA* | Ducted Indoor Units | 206000 | 11.3 | 20.8 | 232000 | 3.3 | 156000 | 2.4 | R-410A | 17.1667
214097890 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME2CA* |  |  |  | MVHQ216ME2CA* | Non-Ducted Indoor Units | 206000 | 10.9 | 22 | 232000 | 3.5 | 156000 | 2.4 | R-410A | 17.1667
214264488 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME2CA* |  |  |  | MVHQ240ME2CA* | Ducted Indoor Units | 222000 | 10.7 | 20.3 | 240000 | 3.3 | 168000 | 2.3 | R-410A | 18.5
214264490 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME2CA* |  |  |  | MVHQ240ME2CA* | Non-Ducted Indoor Units | 222000 | 10.1 | 20.3 | 240000 | 3.4 | 168000 | 2.4 | R-410A | 18.5
214229579 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME4CA* |  |  |  | MVHQ168ME4CA* | Ducted Indoor Units | 160000 | 11.5 | 21.5 | 180000 | 3.4 | 122000 | 2.4 | R-410A | 13.3333
214229580 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME4CA* |  |  |  | MVHQ168ME4CA* | Non-Ducted Indoor Units | 160000 | 11.4 | 23.2 | 180000 | 3.6 | 122000 | 2.5 | R-410A | 13.3333
214264486 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* |  |  |  | MVHQ192ME4CA* | Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.3 | 138000 | 2.4 | R-410A | 15.3333
214264487 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* |  |  |  | MVHQ192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.2 | 22.2 | 206000 | 3.5 | 138000 | 2.4 | R-410A | 15.3333
214264489 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME4CA* |  |  |  | MVHQ240ME4CA* | Ducted Indoor Units | 222000 | 10.7 | 20.3 | 240000 | 3.3 | 168000 | 2.3 | R-410A | 18.5
214264491 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME4CA* |  |  |  | MVHQ240ME4CA* | Non-Ducted Indoor Units | 222000 | 10.1 | 20.3 | 240000 | 3.4 | 168000 | 2.4 | R-410A | 18.5
217189685 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B33CW | HVAHR096B33CW |  |  | HVAHR192B33CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
214296007 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B33CW | HVAHR096B33CW |  |  | HVAHR192B33CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
217189695 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B43CW | HVAHR096B43CW |  |  | HVAHR192B43CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
214296017 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B43CW | HVAHR096B43CW |  |  | HVAHR192B43CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
217189704 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B53CW | HVAHR072B53CW |  |  | HVAHR168B53CW* | Non-Ducted Indoor Units | 160000 | 11.2 | 18.7 | 180000 | 4.2 | 124000 | 2.6 | R-410A | 13.3333
217189705 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B53CW | HVAHR096B53CW |  |  | HVAHR192B53CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
215828405 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B53CW | HVAHR072B53CW |  |  | HVAHR168B53CW | Non-Ducted Indoor Units | 160000 | 11.2 | 18.7 | 180000 | 4.2 | 124000 | 2.6 | R-410A | 13.3333
215828406 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B53CW | HVAHR096B53CW |  |  | HVAHR192B53CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
215828408 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B53CW | HVAHR120B53CW |  |  | HVAHR240B53CW | Non-Ducted Indoor Units | 230000 | 12 | 18.6 | 258000 | 4.1 | 178000 | 2.55 | R-410A | 19.1667
217189707 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B53CW | HVAHR120B53CW |  |  | HVAHR240B53CW* | Non-Ducted Indoor Units | 230000 | 12 | 18.6 | 258000 | 4.1 | 178000 | 2.55 | R-410A | 19.1667
215828414 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 18 | 154000 | 3.6 | 110000 | 2.4 | R-410A | 11.5
217189703 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW* | Non-Ducted Indoor Units | 138000 | 11.7 | 18.7 | 154000 | 3.8 | 110000 | 2.6 | R-410A | 11.5
217190041 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 18 | 154000 | 3.6 | 110000 | 2.4 | R-410A | 11.5
215828404 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW | Non-Ducted Indoor Units | 138000 | 11.7 | 18.7 | 154000 | 3.8 | 110000 | 2.6 | R-410A | 11.5
214825950 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD144K/220V |  |  |  | TVRF-SHD144K/220V | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
216602783 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602727 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602713 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826406 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
214826375 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
214826366 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826367 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
214826376 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
214826407 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602714 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602728 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602786 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602788 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J |  |  |  | VPC192S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602716 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J |  |  |  | VPC192S4M-4J | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH |  |  |  | AM192DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
214826368 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH |  |  |  | AM192DXVGQH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826369 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216DXVGQH |  |  |  | AM216DXVGQH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
214826409 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216DXVGQH |  |  |  | AM216DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602717 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4J |  |  |  | VPC216S4M-4J | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602791 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4J |  |  |  | VPC216S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602719 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4J |  |  |  | VPC240S4M-4J | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826370 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240DXVGQH |  |  |  | AM240DXVGQH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602761 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4J |  |  |  | VRC144S4M-4J | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602746 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4J |  |  |  | VRC144S4M-4J | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826395 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144DXVGQR |  |  |  | AM144DXVGQR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
214826386 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144DXVGQR |  |  |  | AM144DXVGQR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826387 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168DXVGQR |  |  |  | AM168DXVGQR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
214826396 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168DXVGQR |  |  |  | AM168DXVGQR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602748 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4J |  |  |  | VRC168S4M-4J | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602763 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4J |  |  |  | VRC168S4M-4J | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602749 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J |  |  |  | VRC192S4M-4J | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826388 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR |  |  |  | AM192DXVGQR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826389 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216DXVGQR |  |  |  | AM216DXVGQR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602751 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4J |  |  |  | VRC216S4M-4J | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602753 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4J |  |  |  | VRC240S4M-4J | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826390 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240DXVGQR |  |  |  | AM240DXVGQR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
217729762 |  | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 152000 | 3.9 | 98000 | 2.75 | R-32 | 11.5
217729304 |  | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.5 | 152000 | 4 | 98000 | 2.8 | R-32 | 11.5
217729305 |  | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Ducted Indoor Units | 138000 | 11.6 | 20.5 | 152000 | 3.8 | 98000 | 2.7 | R-32 | 11.5
217729306 |  | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Non-Ducted Indoor Units | 160000 | 11 | 22.6 | 180000 | 3.7 | 117000 | 2.57 | R-32 | 13.3333
217729307 |  | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Ducted Indoor Units | 160000 | 11.1 | 19.8 | 180000 | 3.47 | 117000 | 2.62 | R-32 | 13.3333
217729763 |  | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.05 | 21.2 | 180000 | 3.58 | 117000 | 2.59 | R-32 | 13.3333
217729764 |  | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.25 | 206000 | 3.54 | 134000 | 2.65 | R-32 | 15.3333
217729308 |  | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.1 | 206000 | 3.78 | 134000 | 2.7 | R-32 | 15.3333
217729309 |  | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Ducted Indoor Units | 184000 | 10.9 | 20.4 | 206000 | 3.3 | 134000 | 2.61 | R-32 | 15.3333
217729310 |  | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Non-Ducted Indoor Units | 206000 | 10.5 | 22.3 | 230000 | 3.73 | 150000 | 2.7 | R-32 | 17.1667
217729311 |  | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Ducted Indoor Units | 206000 | 11.5 | 22.1 | 230000 | 3.45 | 150000 | 2.67 | R-32 | 17.1667
217729765 |  | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.2 | 230000 | 3.59 | 150000 | 2.68 | R-32 | 17.1667
217729766 |  | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 10.6 | 21.75 | 256000 | 3.39 | 168000 | 2.55 | R-32 | 18.5
217729312 |  | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Non-Ducted Indoor Units | 222000 | 10.3 | 21.8 | 256000 | 3.53 | 168000 | 2.6 | R-32 | 18.5
217729313 |  | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Ducted Indoor Units | 222000 | 10.9 | 21.7 | 256000 | 3.25 | 168000 | 2.51 | R-32 | 18.5
217729783 |  | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 152000 | 3.9 | 98000 | 2.75 | R-32 | 11.5
217729319 |  | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.5 | 152000 | 4 | 98000 | 2.8 | R-32 | 11.5
217729320 |  | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Ducted Indoor Units | 138000 | 11.6 | 20.5 | 152000 | 3.8 | 98000 | 2.7 | R-32 | 11.5
217729321 |  | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Non-Ducted Indoor Units | 160000 | 11 | 22.6 | 180000 | 3.7 | 117000 | 2.57 | R-32 | 13.3333
217729322 |  | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Ducted Indoor Units | 160000 | 11.1 | 19.8 | 180000 | 3.47 | 117000 | 2.62 | R-32 | 13.3333
217729784 |  | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.05 | 21.2 | 180000 | 3.58 | 117000 | 2.59 | R-32 | 13.3333
217729785 |  | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.25 | 206000 | 3.54 | 134000 | 2.65 | R-32 | 15.3333
217729323 |  | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.1 | 206000 | 3.78 | 134000 | 2.7 | R-32 | 15.3333
217729324 |  | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Ducted Indoor Units | 184000 | 10.9 | 20.4 | 206000 | 3.3 | 134000 | 2.61 | R-32 | 15.3333
217729325 |  | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Non-Ducted Indoor Units | 206000 | 10.5 | 22.3 | 230000 | 3.73 | 150000 | 2.7 | R-32 | 17.1667
217729326 |  | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Ducted Indoor Units | 206000 | 11.5 | 22.1 | 230000 | 3.45 | 150000 | 2.67 | R-32 | 17.1667
217729786 |  | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.2 | 230000 | 3.59 | 150000 | 2.68 | R-32 | 17.1667
217729787 |  | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 10.6 | 21.75 | 256000 | 3.39 | 168000 | 2.55 | R-32 | 18.5
217729327 |  | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Non-Ducted Indoor Units | 222000 | 10.3 | 21.8 | 256000 | 3.53 | 168000 | 2.6 | R-32 | 18.5
217729328 |  | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Ducted Indoor Units | 222000 | 10.9 | 21.7 | 256000 | 3.25 | 168000 | 2.51 | R-32 | 18.5
217734390 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.3 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217734333 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.6 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217734270 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.2 | 24 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217734392 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.25 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217734386 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217734335 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217734329 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217734337 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Ducted Indoor Units | 230000 | 10.6 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217734394 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 22 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217734268 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217734271 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.1 | 23.3 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217734272 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.9 | 22.9 | 258000 | 3.99 | 174000 | 2.44 | R-454B | 19.1667
217734269 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217734331 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Ducted Indoor Units | 160000 | 10.6 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217734388 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217734367 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217734424 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217734313 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217734315 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Non-Ducted Indoor Units | 184000 | 13 | 23.3 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217734426 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 22.35 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217734369 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Ducted Indoor Units | 184000 | 12.2 | 21.4 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217734371 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Ducted Indoor Units | 230000 | 11.7 | 21.4 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217734428 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.85 | 22.35 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217734317 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Non-Ducted Indoor Units | 230000 | 12 | 23.3 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217734391 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.3 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217734334 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.6 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217734293 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.2 | 24 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217734393 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.25 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217734387 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217734336 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217734330 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217734338 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Ducted Indoor Units | 230000 | 10.6 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217734395 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 22 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217734291 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217734294 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.1 | 23.3 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217734295 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.9 | 22.9 | 258000 | 3.99 | 174000 | 2.44 | R-454B | 19.1667
217734292 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217734332 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Ducted Indoor Units | 160000 | 10.6 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217734389 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217734368 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217734425 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217734314 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217734316 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Non-Ducted Indoor Units | 184000 | 13 | 23.3 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217734427 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 22.35 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217734370 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Ducted Indoor Units | 184000 | 12.2 | 21.4 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217734372 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Ducted Indoor Units | 230000 | 11.7 | 21.4 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217734429 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.85 | 22.35 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217734318 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Non-Ducted Indoor Units | 230000 | 12 | 23.3 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217735100 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.15 | 22.15 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217735011 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Ducted Indoor Units | 184000 | 10.4 | 20.5 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217735012 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Non-Ducted Indoor Units | 184000 | 9.9 | 23.8 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217735094 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.35 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217735104 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.4 | 22 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217735106 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2401HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.85 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217735018 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217735019 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Non-Ducted Indoor Units | 206000 | 9.9 | 22.8 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217735022 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2401HT6P-UL | Ducted Indoor Units | 230000 | 10.5 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217734999 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217735000 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Non-Ducted Indoor Units | 138000 | 11.2 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217735003 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Ducted Indoor Units | 160000 | 10.4 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217735004 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217735096 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217735098 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 22.85 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217735007 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217735008 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.6 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217735014 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Ducted Indoor Units | 184000 | 10.9 | 21.2 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217735015 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Non-Ducted Indoor Units | 184000 | 11.1 | 23 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217735102 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217735108 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 22.1 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217735026 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Ducted Indoor Units | 230000 | 10.9 | 21.2 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217735027 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Non-Ducted Indoor Units | 230000 | 11.1 | 23 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217735101 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Non-Ducted Indoor Units | 184000 | 9.9 | 23.8 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217735013 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Ducted Indoor Units | 184000 | 10.4 | 20.5 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217735136 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.15 | 22.15 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217735095 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.35 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217735107 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2401HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.85 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217735105 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.4 | 22 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217735024 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2401HT9P-UL | Ducted Indoor Units | 230000 | 10.5 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217735020 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217735021 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Non-Ducted Indoor Units | 206000 | 9.9 | 22.8 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217735001 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217735002 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Non-Ducted Indoor Units | 138000 | 11.2 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217735005 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Ducted Indoor Units | 160000 | 10.4 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217735006 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217735097 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217735099 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 22.85 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217735009 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217735010 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.6 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217735016 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Ducted Indoor Units | 184000 | 10.9 | 21.2 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217735017 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Non-Ducted Indoor Units | 184000 | 11.1 | 23 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217735103 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217735109 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 22.1 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217735028 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Ducted Indoor Units | 230000 | 10.9 | 21.2 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217735029 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Non-Ducted Indoor Units | 230000 | 11.1 | 23 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217883042 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 112000 | 2.7 | R-454B | 11.5
217883044 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 112000 | 2.56 | R-454B | 11.5
217883046 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 112000 | 2.63 | R-454B | 11.5
218088135 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A |  |  |  | PURY-EM144TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 22.15 | 152000 | 3.84 | 118000 | 2.4 | R-32 | 11.5
217901739 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A |  |  |  | PURY-EM144TXU-A | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217901741 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A |  |  |  | PURY-EM144TXU-A | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217901743 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A |  |  |  | PURY-EM168TXU-A | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217901745 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A |  |  |  | PURY-EM168TXU-A | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
218088141 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A |  |  |  | PURY-EM168TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.65 | 21.8 | 178000 | 3.62 | 136000 | 2.3 | R-32 | 13.3333
218088147 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A |  |  |  | PURY-EM192TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 21.6 | 184000 | 3.62 | 144000 | 2.25 | R-32 | 15.3333
217901747 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A |  |  |  | PURY-EM192TXU-A | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217901751 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A |  |  |  | PURY-EM192TXU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902155 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A | PURY-HM72TXU-A |  |  | PURY-HM144TSXU-A | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902157 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A | PURY-HM72TXU-A |  |  | PURY-HM144TSXU-A | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
218088137 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A | PURY-HM72TXU-A |  |  | PURY-HM144TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.65 | 23.2 | 152000 | 4.11 | 118000 | 2.66 | R-32 | 11.5
218088149 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A | PURY-HM96TXU-A |  |  | PURY-HM192TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13.35 | 22.95 | 204000 | 4.01 | 144000 | 2.59 | R-32 | 15.3333
217901749 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A | PURY-HM96TXU-A |  |  | PURY-HM192TSXU-A | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217901753 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A | PURY-HM96TXU-A |  |  | PURY-HM192TSXU-A | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217902159 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A | PURY-HM120TXU-A |  |  | PURY-HM240TSXU-A | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902161 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A | PURY-HM120TXU-A |  |  | PURY-HM240TSXU-A | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
218088153 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A | PURY-HM120TXU-A |  |  | PURY-HM240TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 13.15 | 23 | 258000 | 3.74 | 172000 | 2.5 | R-32 | 19.1667
217901742 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A |  |  |  | PURY-EM144YXU-A | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217901740 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A |  |  |  | PURY-EM144YXU-A | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
218088136 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A |  |  |  | PURY-EM144YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 22.15 | 152000 | 3.84 | 118000 | 2.4 | R-32 | 11.5
218088142 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A |  |  |  | PURY-EM168YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.65 | 21.8 | 178000 | 3.62 | 136000 | 2.3 | R-32 | 13.3333
217901746 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A |  |  |  | PURY-EM168YXU-A | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217901744 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A |  |  |  | PURY-EM168YXU-A | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217901748 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A |  |  |  | PURY-EM192YXU-A | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217901752 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A |  |  |  | PURY-EM192YXU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
218088148 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A |  |  |  | PURY-EM192YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 21.6 | 184000 | 3.62 | 144000 | 2.25 | R-32 | 15.3333
218088138 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A | PURY-HM72YXU-A |  |  | PURY-HM144YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.65 | 23.2 | 152000 | 4.11 | 118000 | 2.66 | R-32 | 11.5
217902156 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A | PURY-HM72YXU-A |  |  | PURY-HM144YSXU-A | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902158 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A | PURY-HM72YXU-A |  |  | PURY-HM144YSXU-A | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217901750 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A | PURY-HM96YXU-A |  |  | PURY-HM192YSXU-A | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217901754 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A | PURY-HM96YXU-A |  |  | PURY-HM192YSXU-A | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
218088150 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A | PURY-HM96YXU-A |  |  | PURY-HM192YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13.35 | 22.95 | 204000 | 4.01 | 144000 | 2.59 | R-32 | 15.3333
218088154 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A | PURY-HM120YXU-A |  |  | PURY-HM240YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 13.15 | 23 | 258000 | 3.74 | 172000 | 2.5 | R-32 | 19.1667
217902160 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A | PURY-HM120YXU-A |  |  | PURY-HM240YSXU-A | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902162 |  | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A | PURY-HM120YXU-A |  |  | PURY-HM240YSXU-A | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
218088205 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN |  |  |  | TURYE1443AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 22.15 | 152000 | 3.84 | 118000 | 2.4 | R-32 | 11.5
217902285 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN |  |  |  | TURYE1443AMM0AN | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217902283 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN |  |  |  | TURYE1443AMM0AN | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217902291 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN |  |  |  | TURYE1683AMM0AN | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217902292 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN |  |  |  | TURYE1683AMM0AN | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
218088213 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN |  |  |  | TURYE1683AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.65 | 21.8 | 178000 | 3.62 | 136000 | 2.3 | R-32 | 13.3333
218088219 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN |  |  |  | TURYE1923AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 21.6 | 184000 | 3.62 | 144000 | 2.25 | R-32 | 15.3333
217902295 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN |  |  |  | TURYE1923AMM0AN | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217902297 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN |  |  |  | TURYE1923AMM0AN | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902284 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN | TURYH0723AMM0AN |  |  | TURYH1443BMM0AN | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902286 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN | TURYH0723AMM0AN |  |  | TURYH1443BMM0AN | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
218088209 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN | TURYH0723AMM0AN |  |  | TURYH1443BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.65 | 23.2 | 152000 | 4.11 | 118000 | 2.66 | R-32 | 11.5
218088221 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN | TURYH0963AMM0AN |  |  | TURYH1923BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13.35 | 22.95 | 204000 | 4.01 | 144000 | 2.59 | R-32 | 15.3333
217902298 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN | TURYH0963AMM0AN |  |  | TURYH1923BMM0AN | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217902296 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN | TURYH0963AMM0AN |  |  | TURYH1923BMM0AN | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217902303 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN | TURYH1203AMM0AN |  |  | TURYH2403BMM0AN | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902304 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN | TURYH1203AMM0AN |  |  | TURYH2403BMM0AN | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
218088225 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN | TURYH1203AMM0AN |  |  | TURYH2403BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 13.15 | 23 | 258000 | 3.74 | 172000 | 2.5 | R-32 | 19.1667
217902287 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN |  |  |  | TURYE1444AMM0AN | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217902289 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN |  |  |  | TURYE1444AMM0AN | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
218088206 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN |  |  |  | TURYE1444AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 22.15 | 152000 | 3.84 | 118000 | 2.4 | R-32 | 11.5
218088214 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN |  |  |  | TURYE1684AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.65 | 21.8 | 178000 | 3.62 | 136000 | 2.3 | R-32 | 13.3333
217902293 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN |  |  |  | TURYE1684AMM0AN | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217902294 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN |  |  |  | TURYE1684AMM0AN | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217902301 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN |  |  |  | TURYE1924AMM0AN | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902299 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN |  |  |  | TURYE1924AMM0AN | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
218088220 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN |  |  |  | TURYE1924AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 21.6 | 184000 | 3.62 | 144000 | 2.25 | R-32 | 15.3333
218088210 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN | TURYH0724AMM0AN |  |  | TURYH1444BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.65 | 23.2 | 152000 | 4.11 | 118000 | 2.66 | R-32 | 11.5
217902290 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN | TURYH0724AMM0AN |  |  | TURYH1444BMM0AN | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217902288 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN | TURYH0724AMM0AN |  |  | TURYH1444BMM0AN | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902300 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN | TURYH0964AMM0AN |  |  | TURYH1924BMM0AN | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217902302 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN | TURYH0964AMM0AN |  |  | TURYH1924BMM0AN | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
218088222 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN | TURYH0964AMM0AN |  |  | TURYH1924BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13.35 | 22.95 | 204000 | 4.01 | 144000 | 2.59 | R-32 | 15.3333
218088226 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN | TURYH1204AMM0AN |  |  | TURYH2404BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 13.15 | 23 | 258000 | 3.74 | 172000 | 2.5 | R-32 | 19.1667
217902305 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN | TURYH1204AMM0AN |  |  | TURYH2404BMM0AN | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902306 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN | TURYH1204AMM0AN |  |  | TURYH2404BMM0AN | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
218088131 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A |  |  |  | PUHY-EM144TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13 | 22.9 | 152000 | 3.93 | 118000 | 2.48 | R-32 | 11.5
217901699 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A |  |  |  | PUHY-EM144TXU-A | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217901700 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A |  |  |  | PUHY-EM144TXU-A | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217901703 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A |  |  |  | PUHY-EM168TXU-A | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217901704 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A |  |  |  | PUHY-EM168TXU-A | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
218088139 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A |  |  |  | PUHY-EM168TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.1 | 22.4 | 178000 | 3.72 | 136000 | 2.37 | R-32 | 13.3333
218088143 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A |  |  |  | PUHY-EM192TXU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 21.75 | 184000 | 3.74 | 144000 | 2.33 | R-32 | 15.3333
217901707 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A |  |  |  | PUHY-EM192TXU-A | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217901708 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A |  |  |  | PUHY-EM192TXU-A | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902123 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A | PUHY-HM72TXU-A |  |  | PUHY-HM144TSXU-A | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902124 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A | PUHY-HM72TXU-A |  |  | PUHY-HM144TSXU-A | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
218088133 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A | PUHY-HM72TXU-A |  |  | PUHY-HM144TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.9 | 24.55 | 152000 | 4.23 | 118000 | 2.76 | R-32 | 11.5
218088145 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A | PUHY-HM96TXU-A |  |  | PUHY-HM192TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13.7 | 23.6 | 204000 | 4.1 | 144000 | 2.65 | R-32 | 15.3333
217901711 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A | PUHY-HM96TXU-A |  |  | PUHY-HM192TSXU-A | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217901712 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A | PUHY-HM96TXU-A |  |  | PUHY-HM192TSXU-A | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902127 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A | PUHY-HM120TXU-A |  |  | PUHY-HM240TSXU-A | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902128 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A | PUHY-HM120TXU-A |  |  | PUHY-HM240TSXU-A | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
218088151 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A | PUHY-HM120TXU-A |  |  | PUHY-HM240TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 13.45 | 23.6 | 258000 | 3.86 | 172000 | 2.56 | R-32 | 19.1667
217901701 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A |  |  |  | PUHY-EM144YXU-A | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217901702 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A |  |  |  | PUHY-EM144YXU-A | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
218088132 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A |  |  |  | PUHY-EM144YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13 | 22.9 | 152000 | 3.93 | 118000 | 2.48 | R-32 | 11.5
218088140 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A |  |  |  | PUHY-EM168YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.1 | 22.4 | 178000 | 3.72 | 136000 | 2.37 | R-32 | 13.3333
217901705 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A |  |  |  | PUHY-EM168YXU-A | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217901706 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A |  |  |  | PUHY-EM168YXU-A | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217901709 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A |  |  |  | PUHY-EM192YXU-A | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217901710 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A |  |  |  | PUHY-EM192YXU-A | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
218088144 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A |  |  |  | PUHY-EM192YXU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 21.75 | 184000 | 3.74 | 144000 | 2.33 | R-32 | 15.3333
218088134 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A | PUHY-HM72YXU-A |  |  | PUHY-HM144YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.9 | 24.55 | 152000 | 4.23 | 118000 | 2.76 | R-32 | 11.5
217902125 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A | PUHY-HM72YXU-A |  |  | PUHY-HM144YSXU-A | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902126 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A | PUHY-HM72YXU-A |  |  | PUHY-HM144YSXU-A | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217901713 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A | PUHY-HM96YXU-A |  |  | PUHY-HM192YSXU-A | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217901714 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A | PUHY-HM96YXU-A |  |  | PUHY-HM192YSXU-A | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
218088146 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A | PUHY-HM96YXU-A |  |  | PUHY-HM192YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13.7 | 23.6 | 204000 | 4.1 | 144000 | 2.65 | R-32 | 15.3333
218088152 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A | PUHY-HM120YXU-A |  |  | PUHY-HM240YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 13.45 | 23.6 | 258000 | 3.86 | 172000 | 2.56 | R-32 | 19.1667
217902129 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A | PUHY-HM120YXU-A |  |  | PUHY-HM240YSXU-A | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902130 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A | PUHY-HM120YXU-A |  |  | PUHY-HM240YSXU-A | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
218088203 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN |  |  |  | TUHYE1443AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13 | 22.9 | 152000 | 3.93 | 118000 | 2.48 | R-32 | 11.5
217902213 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN |  |  |  | TUHYE1443AMM0AN | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217902211 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN |  |  |  | TUHYE1443AMM0AN | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217902219 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN |  |  |  | TUHYE1683AMM0AN | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217902220 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN |  |  |  | TUHYE1683AMM0AN | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
218088211 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN |  |  |  | TUHYE1683AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.1 | 22.4 | 178000 | 3.72 | 136000 | 2.37 | R-32 | 13.3333
218088215 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN |  |  |  | TUHYE1923AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 21.75 | 184000 | 3.74 | 144000 | 2.33 | R-32 | 15.3333
217902225 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN |  |  |  | TUHYE1923AMM0AN | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902223 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN |  |  |  | TUHYE1923AMM0AN | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217902212 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN | TUHYH0723AMM0AN |  |  | TUHYH1443BMM0AN | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902214 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN | TUHYH0723AMM0AN |  |  | TUHYH1443BMM0AN | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
218088207 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN | TUHYH0723AMM0AN |  |  | TUHYH1443BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.9 | 24.55 | 152000 | 4.23 | 118000 | 2.76 | R-32 | 11.5
218088217 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN | TUHYH0963AMM0AN |  |  | TUHYH1923BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13.7 | 23.6 | 204000 | 4.1 | 144000 | 2.65 | R-32 | 15.3333
217902224 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN | TUHYH0963AMM0AN |  |  | TUHYH1923BMM0AN | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217902226 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN | TUHYH0963AMM0AN |  |  | TUHYH1923BMM0AN | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902231 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN | TUHYH1203AMM0AN |  |  | TUHYH2403BMM0AN | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902232 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN | TUHYH1203AMM0AN |  |  | TUHYH2403BMM0AN | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
218088223 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN | TUHYH1203AMM0AN |  |  | TUHYH2403BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 13.45 | 23.6 | 258000 | 3.86 | 172000 | 2.56 | R-32 | 19.1667
217902215 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN |  |  |  | TUHYE1444AMM0AN | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217902217 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN |  |  |  | TUHYE1444AMM0AN | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
218088204 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN |  |  |  | TUHYE1444AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13 | 22.9 | 152000 | 3.93 | 118000 | 2.48 | R-32 | 11.5
218088212 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN |  |  |  | TUHYE1684AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.1 | 22.4 | 178000 | 3.72 | 136000 | 2.37 | R-32 | 13.3333
217902221 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN |  |  |  | TUHYE1684AMM0AN | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217902222 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN |  |  |  | TUHYE1684AMM0AN | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217902227 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN |  |  |  | TUHYE1924AMM0AN | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217902229 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN |  |  |  | TUHYE1924AMM0AN | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
218088216 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN |  |  |  | TUHYE1924AMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 21.75 | 184000 | 3.74 | 144000 | 2.33 | R-32 | 15.3333
218088208 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN | TUHYH0724AMM0AN |  |  | TUHYH1444BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.9 | 24.55 | 152000 | 4.23 | 118000 | 2.76 | R-32 | 11.5
217902218 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN | TUHYH0724AMM0AN |  |  | TUHYH1444BMM0AN | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217902216 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN | TUHYH0724AMM0AN |  |  | TUHYH1444BMM0AN | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902230 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN | TUHYH0964AMM0AN |  |  | TUHYH1924BMM0AN | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902228 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN | TUHYH0964AMM0AN |  |  | TUHYH1924BMM0AN | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
218088218 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN | TUHYH0964AMM0AN |  |  | TUHYH1924BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13.7 | 23.6 | 204000 | 4.1 | 144000 | 2.65 | R-32 | 15.3333
218088224 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN | TUHYH1204AMM0AN |  |  | TUHYH2404BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 13.45 | 23.6 | 258000 | 3.86 | 172000 | 2.56 | R-32 | 19.1667
217902233 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN | TUHYH1204AMM0AN |  |  | TUHYH2404BMM0AN | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902234 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN | TUHYH1204AMM0AN |  |  | TUHYH2404BMM0AN | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
218003068 |  | SAMSUNG | HMSV-A-CB | AM216HCVGFG |  |  |  | AM216HCVGFG | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004911 |  | SAMSUNG | HMSV-A-CB | AM216HCVGFG |  |  |  | AM216HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043883 |  | LENNOX | HMSV-A-CB | VPD216S6M-5Y |  |  |  | VPD216S6M-5Y | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218044019 |  | LENNOX | HMSV-A-CB | VPD216S6M-5Y |  |  |  | VPD216S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043887 |  | LENNOX | HMSV-A-CB | VPD240S6M-5Y |  |  |  | VPD240S6M-5Y | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003072 |  | SAMSUNG | HMSV-A-CB | AM240HCVGFG |  |  |  | AM240HCVGFG | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003069 |  | SAMSUNG | HMSR-A-CB | AM216HCVGFS |  |  |  | AM216HCVGFS | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004912 |  | SAMSUNG | HMSR-A-CB | AM216HCVGFS |  |  |  | AM216HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043884 |  | LENNOX | HMSR-A-CB | VRD216S6M-5Y |  |  |  | VRD216S6M-5Y | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218044020 |  | LENNOX | HMSR-A-CB | VRD216S6M-5Y |  |  |  | VRD216S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043888 |  | LENNOX | HMSR-A-CB | VRD240S6M-5Y |  |  |  | VRD240S6M-5Y | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003073 |  | SAMSUNG | HMSR-A-CB | AM240HCVGFS |  |  |  | AM240HCVGFS | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003070 |  | SAMSUNG | HMSV-A-CB | AM216HCVGJG |  |  |  | AM216HCVGJG | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004913 |  | SAMSUNG | HMSV-A-CB | AM216HCVGJG |  |  |  | AM216HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043885 |  | LENNOX | HMSV-A-CB | VPD216S6M-5G |  |  |  | VPD216S6M-5G | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218044021 |  | LENNOX | HMSV-A-CB | VPD216S6M-5G |  |  |  | VPD216S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043889 |  | LENNOX | HMSV-A-CB | VPD240S6M-5G |  |  |  | VPD240S6M-5G | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003074 |  | SAMSUNG | HMSV-A-CB | AM240HCVGJG |  |  |  | AM240HCVGJG | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003071 |  | SAMSUNG | HMSR-A-CB | AM216HCVGJS |  |  |  | AM216HCVGJS | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004914 |  | SAMSUNG | HMSR-A-CB | AM216HCVGJS |  |  |  | AM216HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043886 |  | LENNOX | HMSR-A-CB | VRD216S6M-5G |  |  |  | VRD216S6M-5G | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218044022 |  | LENNOX | HMSR-A-CB | VRD216S6M-5G |  |  |  | VRD216S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043890 |  | LENNOX | HMSR-A-CB | VRD240S6M-5G |  |  |  | VRD240S6M-5G | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003075 |  | SAMSUNG | HMSR-A-CB | AM240HCVGJS |  |  |  | AM240HCVGJS | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218044007 |  | LENNOX | HMSV-A-CB | VPD144S6M-5Y |  |  |  | VPD144S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218043935 |  | LENNOX | HMSV-A-CB | VPD144S6M-5Y |  |  |  | VPD144S6M-5Y | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218043871 |  | LENNOX | HMSV-A-CB | VPD144S6M-5Y |  |  |  | VPD144S6M-5Y | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218004899 |  | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003120 |  | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003056 |  | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003060 |  | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003124 |  | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004903 |  | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043875 |  | LENNOX | HMSV-A-CB | VPD168S6M-5Y |  |  |  | VPD168S6M-5Y | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218043939 |  | LENNOX | HMSV-A-CB | VPD168S6M-5Y |  |  |  | VPD168S6M-5Y | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218044011 |  | LENNOX | HMSV-A-CB | VPD168S6M-5Y |  |  |  | VPD168S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218044015 |  | LENNOX | HMSV-A-CB | VPD192S6M-5Y |  |  |  | VPD192S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218043879 |  | LENNOX | HMSV-A-CB | VPD192S6M-5Y |  |  |  | VPD192S6M-5Y | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004907 |  | SAMSUNG | HMSV-A-CB | AM192HCVGFG |  |  |  | AM192HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003064 |  | SAMSUNG | HMSV-A-CB | AM192HCVGFG |  |  |  | AM192HCVGFG | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218044008 |  | LENNOX | HMSR-A-CB | VRD144S6M-5Y |  |  |  | VRD144S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218043936 |  | LENNOX | HMSR-A-CB | VRD144S6M-5Y |  |  |  | VRD144S6M-5Y | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218043872 |  | LENNOX | HMSR-A-CB | VRD144S6M-5Y |  |  |  | VRD144S6M-5Y | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218004900 |  | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003121 |  | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003057 |  | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003061 |  | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003125 |  | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004904 |  | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043876 |  | LENNOX | HMSR-A-CB | VRD168S6M-5Y |  |  |  | VRD168S6M-5Y | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218043940 |  | LENNOX | HMSR-A-CB | VRD168S6M-5Y |  |  |  | VRD168S6M-5Y | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218044012 |  | LENNOX | HMSR-A-CB | VRD168S6M-5Y |  |  |  | VRD168S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218044016 |  | LENNOX | HMSR-A-CB | VRD192S6M-5Y |  |  |  | VRD192S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218043880 |  | LENNOX | HMSR-A-CB | VRD192S6M-5Y |  |  |  | VRD192S6M-5Y | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004908 |  | SAMSUNG | HMSR-A-CB | AM192HCVGFS |  |  |  | AM192HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003065 |  | SAMSUNG | HMSR-A-CB | AM192HCVGFS |  |  |  | AM192HCVGFS | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218044009 |  | LENNOX | HMSV-A-CB | VPD144S6M-5G |  |  |  | VPD144S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218043937 |  | LENNOX | HMSV-A-CB | VPD144S6M-5G |  |  |  | VPD144S6M-5G | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218043873 |  | LENNOX | HMSV-A-CB | VPD144S6M-5G |  |  |  | VPD144S6M-5G | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218004901 |  | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003122 |  | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003058 |  | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003062 |  | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003126 |  | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004905 |  | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043877 |  | LENNOX | HMSV-A-CB | VPD168S6M-5G |  |  |  | VPD168S6M-5G | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218043941 |  | LENNOX | HMSV-A-CB | VPD168S6M-5G |  |  |  | VPD168S6M-5G | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218044013 |  | LENNOX | HMSV-A-CB | VPD168S6M-5G |  |  |  | VPD168S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218044017 |  | LENNOX | HMSV-A-CB | VPD192S6M-5G |  |  |  | VPD192S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218043881 |  | LENNOX | HMSV-A-CB | VPD192S6M-5G |  |  |  | VPD192S6M-5G | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004909 |  | SAMSUNG | HMSV-A-CB | AM192HCVGJG |  |  |  | AM192HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003066 |  | SAMSUNG | HMSV-A-CB | AM192HCVGJG |  |  |  | AM192HCVGJG | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218044010 |  | LENNOX | HMSR-A-CB | VRD144S6M-5G |  |  |  | VRD144S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218043938 |  | LENNOX | HMSR-A-CB | VRD144S6M-5G |  |  |  | VRD144S6M-5G | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218043874 |  | LENNOX | HMSR-A-CB | VRD144S6M-5G |  |  |  | VRD144S6M-5G | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218004902 |  | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003123 |  | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003059 |  | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003063 |  | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003127 |  | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004906 |  | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043878 |  | LENNOX | HMSR-A-CB | VRD168S6M-5G |  |  |  | VRD168S6M-5G | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218043942 |  | LENNOX | HMSR-A-CB | VRD168S6M-5G |  |  |  | VRD168S6M-5G | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218044014 |  | LENNOX | HMSR-A-CB | VRD168S6M-5G |  |  |  | VRD168S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218044018 |  | LENNOX | HMSR-A-CB | VRD192S6M-5G |  |  |  | VRD192S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218043882 |  | LENNOX | HMSR-A-CB | VRD192S6M-5G |  |  |  | VRD192S6M-5G | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004910 |  | SAMSUNG | HMSR-A-CB | AM192HCVGJS |  |  |  | AM192HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003067 |  | SAMSUNG | HMSR-A-CB | AM192HCVGJS |  |  |  | AM192HCVGJS | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218005679 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005683 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005711 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005715 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005751 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005755 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044075 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y |  |  | VPD144L6M-5Y | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218044079 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y |  |  | VPD168L6M-5Y | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218044107 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y |  |  | VPD144L6M-5Y | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218044111 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y |  |  | VPD168L6M-5Y | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044119 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD072L6M-5Y |  | VPD216L6M-5Y | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218044123 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD096L6M-5Y |  | VPD240L6M-5Y | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218044147 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y |  |  | VPD144L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044151 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y |  |  | VPD168L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044167 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD072L6M-5Y |  | VPD216L6M-5Y | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218044171 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD096L6M-5Y |  | VPD240L6M-5Y | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218044179 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD096L6M-5Y |  | VPD240L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218044175 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD072L6M-5Y |  | VPD216L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218044155 |  | LENNOX | HMSV-A-CB | VPD096L6M-5Y | VPD096L6M-5Y |  |  | VPD192L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218044115 |  | LENNOX | HMSV-A-CB | VPD096L6M-5Y | VPD096L6M-5Y |  |  | VPD192L6M-5Y | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218044083 |  | LENNOX | HMSV-A-CB | VPD096L6M-5Y | VPD096L6M-5Y |  |  | VPD192L6M-5Y | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218044148 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y |  |  | VRD144L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044152 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y |  |  | VRD168L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044108 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y |  |  | VRD144L6M-5Y | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218044112 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y |  |  | VRD168L6M-5Y | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044124 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD096L6M-5Y |  | VRD240L6M-5Y | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218044120 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD072L6M-5Y |  | VRD216L6M-5Y | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218044176 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD072L6M-5Y |  | VRD216L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218044180 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD096L6M-5Y |  | VRD240L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218044172 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD096L6M-5Y |  | VRD240L6M-5Y | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218044168 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD072L6M-5Y |  | VRD216L6M-5Y | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218044076 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y |  |  | VRD144L6M-5Y | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218044080 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y |  |  | VRD168L6M-5Y | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005752 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005756 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218005716 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005712 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005680 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005684 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218044084 |  | LENNOX | HMSR-A-CB | VRD096L6M-5Y | VRD096L6M-5Y |  |  | VRD192L6M-5Y | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218044116 |  | LENNOX | HMSR-A-CB | VRD096L6M-5Y | VRD096L6M-5Y |  |  | VRD192L6M-5Y | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218044156 |  | LENNOX | HMSR-A-CB | VRD096L6M-5Y | VRD096L6M-5Y |  |  | VRD192L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218005681 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005685 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005753 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005757 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218005713 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005717 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044077 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G |  |  | VPD144L6M-5G | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218044081 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G |  |  | VPD168L6M-5G | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218044109 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G |  |  | VPD144L6M-5G | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218044113 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G |  |  | VPD168L6M-5G | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044121 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD072L6M-5G |  | VPD216L6M-5G | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218044125 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD096L6M-5G |  | VPD240L6M-5G | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218044149 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G |  |  | VPD144L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044153 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G |  |  | VPD168L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044169 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD072L6M-5G |  | VPD216L6M-5G | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218044173 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD096L6M-5G |  | VPD240L6M-5G | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218044181 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD096L6M-5G |  | VPD240L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218044177 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD072L6M-5G |  | VPD216L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218044157 |  | LENNOX | HMSV-A-CB | VPD096L6M-5G | VPD096L6M-5G |  |  | VPD192L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218044117 |  | LENNOX | HMSV-A-CB | VPD096L6M-5G | VPD096L6M-5G |  |  | VPD192L6M-5G | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218044085 |  | LENNOX | HMSV-A-CB | VPD096L6M-5G | VPD096L6M-5G |  |  | VPD192L6M-5G | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218044150 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G |  |  | VRD144L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044154 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G |  |  | VRD168L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044110 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G |  |  | VRD144L6M-5G | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218044114 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G |  |  | VRD168L6M-5G | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044126 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD096L6M-5G |  | VRD240L6M-5G | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218044122 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD072L6M-5G |  | VRD216L6M-5G | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218044178 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD072L6M-5G |  | VRD216L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218044182 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD096L6M-5G |  | VRD240L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218044174 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD096L6M-5G |  | VRD240L6M-5G | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218044170 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD072L6M-5G |  | VRD216L6M-5G | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218044078 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G |  |  | VRD144L6M-5G | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218044082 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G |  |  | VRD168L6M-5G | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005754 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005758 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218005718 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005714 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005682 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005686 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218044086 |  | LENNOX | HMSR-A-CB | VRD096L6M-5G | VRD096L6M-5G |  |  | VRD192L6M-5G | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218044118 |  | LENNOX | HMSR-A-CB | VRD096L6M-5G | VRD096L6M-5G |  |  | VRD192L6M-5G | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218044158 |  | LENNOX | HMSR-A-CB | VRD096L6M-5G | VRD096L6M-5G |  |  | VRD192L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218066395 |  | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C | MV8-2R72V2XN10C |  |  | MV8-2R144V2XN10C | Ducted Indoor Units | 138000 | 11.9 | 21.8 | 152000 | 3.63 | 118000 | 2.35 | R-454B | 11.5
218066396 |  | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C | MV8-2R72V2XN10C |  |  | MV8-2R144V2XN10C | Non-Ducted Indoor Units | 138000 | 12.4 | 24.2 | 152000 | 3.96 | 118000 | 2.5 | R-454B | 11.5
218079673 |  | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C | MV8-2R72V2XN10C |  |  | MV8-2R144V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.15 | 23 | 152000 | 3.79 | 118000 | 2.42 | R-454B | 11.5
218079675 |  | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C | MV8-2R96V2XN10C |  |  | MV8-2R192V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.6 | 22.8 | 206000 | 3.65 | 144000 | 2.36 | R-454B | 15.3333
218066397 |  | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C | MV8-2R96V2XN10C |  |  | MV8-2R192V2XN10C | Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.57 | 144000 | 2.28 | R-454B | 15.3333
218066398 |  | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C | MV8-2R96V2XN10C |  |  | MV8-2R192V2XN10C | Non-Ducted Indoor Units | 184000 | 11.7 | 24 | 206000 | 3.73 | 144000 | 2.45 | R-454B | 15.3333
218066399 |  | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C | MV8-2R120V2XN10C |  |  | MV8-2R240V2XN10C | Ducted Indoor Units | 230000 | 10.9 | 21 | 258000 | 3.46 | 172000 | 2.27 | R-454B | 19.1667
218066405 |  | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C | MV8-2R120V2XN10C |  |  | MV8-2R240V2XN10C | Non-Ducted Indoor Units | 230000 | 11 | 23 | 258000 | 3.52 | 172000 | 2.37 | R-454B | 19.1667
218079677 |  | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C | MV8-2R120V2XN10C |  |  | MV8-2R240V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 22 | 258000 | 3.49 | 172000 | 2.32 | R-454B | 19.1667
218079674 |  | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C | MV8-2R72V2ZN10C |  |  | MV8-2R144V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.15 | 23 | 152000 | 3.79 | 118000 | 2.42 | R-454B | 11.5
218066400 |  | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C | MV8-2R72V2ZN10C |  |  | MV8-2R144V2ZN10C | Ducted Indoor Units | 138000 | 11.9 | 21.8 | 152000 | 3.63 | 118000 | 2.35 | R-454B | 11.5
218066401 |  | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C | MV8-2R72V2ZN10C |  |  | MV8-2R144V2ZN10C | Non-Ducted Indoor Units | 138000 | 12.4 | 24.2 | 152000 | 3.96 | 118000 | 2.5 | R-454B | 11.5
218066402 |  | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C | MV8-2R96V2ZN10C |  |  | MV8-2R192V2ZN10C | Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.57 | 144000 | 2.28 | R-454B | 15.3333
218066403 |  | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C | MV8-2R96V2ZN10C |  |  | MV8-2R192V2ZN10C | Non-Ducted Indoor Units | 184000 | 11.7 | 24 | 206000 | 3.73 | 144000 | 2.45 | R-454B | 15.3333
218079676 |  | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C | MV8-2R96V2ZN10C |  |  | MV8-2R192V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.6 | 22.8 | 206000 | 3.65 | 144000 | 2.36 | R-454B | 15.3333
218079678 |  | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C | MV8-2R120V2ZN10C |  |  | MV8-2R240V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 22 | 258000 | 3.49 | 172000 | 2.32 | R-454B | 19.1667
218066404 |  | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C | MV8-2R120V2ZN10C |  |  | MV8-2R240V2ZN10C | Ducted Indoor Units | 230000 | 10.9 | 21 | 258000 | 3.46 | 172000 | 2.27 | R-454B | 19.1667
218066406 |  | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C | MV8-2R120V2ZN10C |  |  | MV8-2R240V2ZN10C | Non-Ducted Indoor Units | 230000 | 11 | 23 | 258000 | 3.52 | 172000 | 2.37 | R-454B | 19.1667
218083104 |  | MIDEA | HMSV-A-CB | MV8-X72V2XN10C | MV8-X72V2XN10C |  |  | MV8-X144V2XN10C | Non-Ducted Indoor Units | 138000 | 12.1 | 22.5 | 152000 | 3.96 | 118000 | 2.38 | R-454B | 11.5
218083106 |  | MIDEA | HMSV-A-CB | MV8-X72V2XN10C | MV8-X72V2XN10C |  |  | MV8-X144V2XN10C | Ducted Indoor Units | 138000 | 11.6 | 21.5 | 152000 | 3.68 | 118000 | 2.35 | R-454B | 11.5
218083107 |  | MIDEA | HMSV-A-CB | MV8-X96V2XN10C | MV8-X96V2XN10C |  |  | MV8-X192V2XN10C | Ducted Indoor Units | 184000 | 11.2 | 21.5 | 206000 | 3.61 | 144000 | 2.28 | R-454B | 15.3333
218083108 |  | MIDEA | HMSV-A-CB | MV8-X96V2XN10C | MV8-X96V2XN10C |  |  | MV8-X192V2XN10C | Non-Ducted Indoor Units | 184000 | 11.7 | 23.5 | 206000 | 3.73 | 144000 | 2.33 | R-454B | 15.3333
218083109 |  | MIDEA | HMSV-A-CB | MV8-X120V2XN10C | MV8-X120V2XN10C |  |  | MV8-X240V2XN10C | Ducted Indoor Units | 230000 | 10.7 | 21 | 258000 | 3.52 | 172000 | 2.27 | R-454B | 19.1667
218083165 |  | MIDEA | HMSV-A-CB | MV8-X120V2XN10C | MV8-X120V2XN10C |  |  | MV8-X240V2XN10C | Non-Ducted Indoor Units | 230000 | 11 | 22.5 | 258000 | 3.52 | 172000 | 2.24 | R-454B | 19.1667
218083166 |  | MIDEA | HMSV-A-CB | MV8-X72V2ZN10C | MV8-X72V2ZN10C |  |  | MV8-X144V2ZN10C | Non-Ducted Indoor Units | 138000 | 12.1 | 22.5 | 152000 | 3.96 | 118000 | 2.38 | R-454B | 11.5
218083110 |  | MIDEA | HMSV-A-CB | MV8-X72V2ZN10C | MV8-X72V2ZN10C |  |  | MV8-X144V2ZN10C | Ducted Indoor Units | 138000 | 11.6 | 21.5 | 152000 | 3.68 | 118000 | 2.35 | R-454B | 11.5
218083111 |  | MIDEA | HMSV-A-CB | MV8-X96V2ZN10C | MV8-X96V2ZN10C |  |  | MV8-X192V2ZN10C | Ducted Indoor Units | 184000 | 11.2 | 21.5 | 206000 | 3.61 | 144000 | 2.28 | R-454B | 15.3333
218083167 |  | MIDEA | HMSV-A-CB | MV8-X96V2ZN10C | MV8-X96V2ZN10C |  |  | MV8-X192V2ZN10C | Non-Ducted Indoor Units | 184000 | 11.7 | 23.5 | 206000 | 3.73 | 144000 | 2.33 | R-454B | 15.3333
218083112 |  | MIDEA | HMSV-A-CB | MV8-X120V2ZN10C | MV8-X120V2ZN10C |  |  | MV8-X240V2ZN10C | Ducted Indoor Units | 230000 | 10.7 | 21 | 258000 | 3.52 | 172000 | 2.27 | R-454B | 19.1667
218083113 |  | MIDEA | HMSV-A-CB | MV8-X120V2ZN10C | MV8-X120V2ZN10C |  |  | MV8-X240V2ZN10C | Non-Ducted Indoor Units | 230000 | 11 | 22.5 | 258000 | 3.52 | 172000 | 2.24 | R-454B | 19.1667
218036976 |  | DAIKIN | HMSV-A-CB | RXYA144AATJ* |  |  |  | RXYA144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11 | 21 | 138000 | 3.32 | 90000 | 2.1 | R-32 | 11.5
218036940 |  | DAIKIN | HMSV-A-CB | RXYA144AATJ* |  |  |  | RXYA144AATJ* | Ducted Indoor Units | 138000 | 11 | 19.6 | 138000 | 3.35 | 90000 | 2.1 | R-32 | 11.5
218036904 |  | DAIKIN | HMSV-A-CB | RXYA144AATJ* |  |  |  | RXYA144AATJ* | Non-Ducted Indoor Units | 138000 | 11 | 22.4 | 138000 | 3.3 | 90000 | 2.1 | R-32 | 11.5
218036905 |  | DAIKIN | HMSV-A-CB | RXYA168AATJ* |  |  |  | RXYA168AATJ* | Non-Ducted Indoor Units | 156000 | 10.7 | 21.7 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036941 |  | DAIKIN | HMSV-A-CB | RXYA168AATJ* |  |  |  | RXYA168AATJ* | Ducted Indoor Units | 156000 | 10.7 | 18.8 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036977 |  | DAIKIN | HMSV-A-CB | RXYA168AATJ* |  |  |  | RXYA168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.7 | 20.25 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036978 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* |  |  |  | RXYA192AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 20.9 | 184000 | 3.44 | 130000 | 2.24 | R-32 | 15.3333
218036942 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* |  |  |  | RXYA192AATJ* | Ducted Indoor Units | 184000 | 11.3 | 19.4 | 184000 | 3.4 | 130000 | 2.24 | R-32 | 15.3333
218036906 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* |  |  |  | RXYA192AATJ* | Non-Ducted Indoor Units | 184000 | 11.4 | 22.4 | 184000 | 3.48 | 130000 | 2.24 | R-32 | 15.3333
218036907 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* |  |  |  | RXYA216AATJ* | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036943 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* |  |  |  | RXYA216AATJ* | Ducted Indoor Units | 206000 | 11 | 18.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036979 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* |  |  |  | RXYA216AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 20.2 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036980 |  | DAIKIN | HMSV-A-CB | RXYA240AATJ* |  |  |  | RXYA240AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 19.2 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036944 |  | DAIKIN | HMSV-A-CB | RXYA240AATJ* |  |  |  | RXYA240AATJ* | Ducted Indoor Units | 228000 | 10.7 | 18 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036908 |  | DAIKIN | HMSV-A-CB | RXYA240AATJ* |  |  |  | RXYA240AATJ* | Non-Ducted Indoor Units | 228000 | 10.7 | 20.4 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036994 |  | DAIKIN | HMSV-A-CB | RXYA144AAYD* |  |  |  | RXYA144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11 | 21 | 138000 | 3.32 | 90000 | 2.1 | R-32 | 11.5
218036958 |  | DAIKIN | HMSV-A-CB | RXYA144AAYD* |  |  |  | RXYA144AAYD* | Ducted Indoor Units | 138000 | 11 | 19.6 | 138000 | 3.35 | 90000 | 2.1 | R-32 | 11.5
218036922 |  | DAIKIN | HMSV-A-CB | RXYA144AAYD* |  |  |  | RXYA144AAYD* | Non-Ducted Indoor Units | 138000 | 11 | 22.4 | 138000 | 3.3 | 90000 | 2.1 | R-32 | 11.5
218036923 |  | DAIKIN | HMSV-A-CB | RXYA168AAYD* |  |  |  | RXYA168AAYD* | Non-Ducted Indoor Units | 156000 | 10.7 | 21.7 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036959 |  | DAIKIN | HMSV-A-CB | RXYA168AAYD* |  |  |  | RXYA168AAYD* | Ducted Indoor Units | 156000 | 10.7 | 18.8 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036995 |  | DAIKIN | HMSV-A-CB | RXYA168AAYD* |  |  |  | RXYA168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.7 | 20.25 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036996 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* |  |  |  | RXYA192AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 20.9 | 184000 | 3.44 | 130000 | 2.24 | R-32 | 15.3333
218036960 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* |  |  |  | RXYA192AAYD* | Ducted Indoor Units | 184000 | 11.3 | 19.4 | 184000 | 3.4 | 130000 | 2.24 | R-32 | 15.3333
218036924 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* |  |  |  | RXYA192AAYD* | Non-Ducted Indoor Units | 184000 | 11.4 | 22.4 | 184000 | 3.48 | 130000 | 2.24 | R-32 | 15.3333
218036925 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* |  |  |  | RXYA216AAYD* | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036961 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* |  |  |  | RXYA216AAYD* | Ducted Indoor Units | 206000 | 11 | 18.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036997 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* |  |  |  | RXYA216AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 20.2 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036998 |  | DAIKIN | HMSV-A-CB | RXYA240AAYD* |  |  |  | RXYA240AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 19.2 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036962 |  | DAIKIN | HMSV-A-CB | RXYA240AAYD* |  |  |  | RXYA240AAYD* | Ducted Indoor Units | 228000 | 10.7 | 18 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036926 |  | DAIKIN | HMSV-A-CB | RXYA240AAYD* |  |  |  | RXYA240AAYD* | Non-Ducted Indoor Units | 228000 | 10.7 | 20.4 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218037084 |  | DAIKIN | HMSR-A-CB | REYA144AATJ* |  |  |  | REYA144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.1 | 21.2 | 138000 | 3.32 | 90000 | 2.1 | R-32 | 11.5
218037048 |  | DAIKIN | HMSR-A-CB | REYA144AATJ* |  |  |  | REYA144AATJ* | Ducted Indoor Units | 138000 | 11 | 19.7 | 138000 | 3.35 | 90000 | 2.1 | R-32 | 11.5
218037012 |  | DAIKIN | HMSR-A-CB | REYA144AATJ* |  |  |  | REYA144AATJ* | Non-Ducted Indoor Units | 138000 | 11.2 | 22.7 | 138000 | 3.3 | 90000 | 2.1 | R-32 | 11.5
218037013 |  | DAIKIN | HMSR-A-CB | REYA168AATJ* |  |  |  | REYA168AATJ* | Non-Ducted Indoor Units | 156000 | 10.7 | 21.7 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037049 |  | DAIKIN | HMSR-A-CB | REYA168AATJ* |  |  |  | REYA168AATJ* | Ducted Indoor Units | 156000 | 10.7 | 19 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037085 |  | DAIKIN | HMSR-A-CB | REYA168AATJ* |  |  |  | REYA168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.7 | 20.35 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037086 |  | DAIKIN | HMSR-A-CB | REYA192AATJ* |  |  |  | REYA192AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21 | 184000 | 3.44 | 130000 | 2.25 | R-32 | 15.3333
218037050 |  | DAIKIN | HMSR-A-CB | REYA192AATJ* |  |  |  | REYA192AATJ* | Ducted Indoor Units | 184000 | 11.3 | 19.8 | 184000 | 3.4 | 130000 | 2.25 | R-32 | 15.3333
218037014 |  | DAIKIN | HMSR-A-CB | REYA192AATJ* |  |  |  | REYA192AATJ* | Non-Ducted Indoor Units | 184000 | 11.4 | 22.2 | 184000 | 3.48 | 130000 | 2.25 | R-32 | 15.3333
218037015 |  | DAIKIN | HMSR-A-CB | REYA216AATJ* |  |  |  | REYA216AATJ* | Non-Ducted Indoor Units | 206000 | 10.9 | 21.8 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037051 |  | DAIKIN | HMSR-A-CB | REYA216AATJ* |  |  |  | REYA216AATJ* | Ducted Indoor Units | 206000 | 11 | 18.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037087 |  | DAIKIN | HMSR-A-CB | REYA216AATJ* |  |  |  | REYA216AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 20.25 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037088 |  | DAIKIN | HMSR-A-CB | REYA240AATJ* |  |  |  | REYA240AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 19.2 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037052 |  | DAIKIN | HMSR-A-CB | REYA240AATJ* |  |  |  | REYA240AATJ* | Ducted Indoor Units | 228000 | 10.7 | 18 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037016 |  | DAIKIN | HMSR-A-CB | REYA240AATJ* |  |  |  | REYA240AATJ* | Non-Ducted Indoor Units | 228000 | 10.7 | 20.4 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037102 |  | DAIKIN | HMSR-A-CB | REYA144AAYD* |  |  |  | REYA144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.1 | 21.2 | 138000 | 3.32 | 90000 | 2.1 | R-32 | 11.5
218037066 |  | DAIKIN | HMSR-A-CB | REYA144AAYD* |  |  |  | REYA144AAYD* | Ducted Indoor Units | 138000 | 11 | 19.7 | 138000 | 3.35 | 90000 | 2.1 | R-32 | 11.5
218037030 |  | DAIKIN | HMSR-A-CB | REYA144AAYD* |  |  |  | REYA144AAYD* | Non-Ducted Indoor Units | 138000 | 11.2 | 22.7 | 138000 | 3.3 | 90000 | 2.1 | R-32 | 11.5
218037031 |  | DAIKIN | HMSR-A-CB | REYA168AAYD* |  |  |  | REYA168AAYD* | Non-Ducted Indoor Units | 156000 | 10.7 | 21.7 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037067 |  | DAIKIN | HMSR-A-CB | REYA168AAYD* |  |  |  | REYA168AAYD* | Ducted Indoor Units | 156000 | 10.7 | 19 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037103 |  | DAIKIN | HMSR-A-CB | REYA168AAYD* |  |  |  | REYA168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.7 | 20.35 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037104 |  | DAIKIN | HMSR-A-CB | REYA192AAYD* |  |  |  | REYA192AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21 | 184000 | 3.44 | 130000 | 2.25 | R-32 | 15.3333
218037068 |  | DAIKIN | HMSR-A-CB | REYA192AAYD* |  |  |  | REYA192AAYD* | Ducted Indoor Units | 184000 | 11.3 | 19.8 | 184000 | 3.4 | 130000 | 2.25 | R-32 | 15.3333
218037032 |  | DAIKIN | HMSR-A-CB | REYA192AAYD* |  |  |  | REYA192AAYD* | Non-Ducted Indoor Units | 184000 | 11.4 | 22.2 | 184000 | 3.48 | 130000 | 2.25 | R-32 | 15.3333
218037033 |  | DAIKIN | HMSR-A-CB | REYA216AAYD* |  |  |  | REYA216AAYD* | Non-Ducted Indoor Units | 206000 | 10.9 | 21.8 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037069 |  | DAIKIN | HMSR-A-CB | REYA216AAYD* |  |  |  | REYA216AAYD* | Ducted Indoor Units | 206000 | 11 | 18.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037105 |  | DAIKIN | HMSR-A-CB | REYA216AAYD* |  |  |  | REYA216AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 20.25 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037106 |  | DAIKIN | HMSR-A-CB | REYA240AAYD* |  |  |  | REYA240AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 19.2 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037070 |  | DAIKIN | HMSR-A-CB | REYA240AAYD* |  |  |  | REYA240AAYD* | Ducted Indoor Units | 228000 | 10.7 | 18 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037034 |  | DAIKIN | HMSR-A-CB | REYA240AAYD* |  |  |  | REYA240AAYD* | Non-Ducted Indoor Units | 228000 | 10.7 | 20.4 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
214432096 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B52S | TVAHR096B52S |  |  | TVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094397 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094246 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432130 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S | HVAHR096B52S |  |  | HVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094349 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094198 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311061 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S | YVAHR096B52S |  |  | YVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094445 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094294 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432078 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B52S | TVAHP096B52S |  |  | TVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091615 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091472 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432112 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S | HVAHP096B52S |  |  | HVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091567 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091424 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311044 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S | YVAHP096B52S |  |  | YVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091663 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091520 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
213895710 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* |  |  |  | REYQ144AATJ* | Non-Ducted Indoor Units | 138000 | 11.2 | 21.5 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213895939 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* |  |  |  | REYQ144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 19.8 | 138000 | 3.25 | 90000 | 2.1 | R-410A | 11.5
213896247 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* |  |  |  | REYQ168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.45 | 18.95 | 156000 | 3.25 | 104000 | 2.07 | R-410A | 13
213895949 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* |  |  |  | REYQ144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 19.8 | 138000 | 3.25 | 90000 | 2.1 | R-410A | 11.5
213895713 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* |  |  |  | REYQ144AAYD* | Non-Ducted Indoor Units | 138000 | 11.2 | 21.5 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213896255 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* |  |  |  | REYQ168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.45 | 18.95 | 156000 | 3.25 | 104000 | 2.07 | R-410A | 13
216602560 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602464 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602371 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893995 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893937 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893893 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893941 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213918736 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213916416 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602470 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602661 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602621 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602669 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y |  |  |  | VPC192S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602477 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y |  |  |  | VPC192S4M-4Y | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213918740 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH |  |  |  | AM192BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213893945 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH |  |  |  | AM192BXVGFH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893949 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM216BXVGFH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
213918744 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM216BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602483 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4Y |  |  |  | VPC216S4M-4Y | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602678 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4Y |  |  |  | VPC216S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602490 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4Y |  |  |  | VPC240S4M-4Y | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893953 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240BXVGFH |  |  |  | AM240BXVGFH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602467 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602375 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602563 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893895 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893997 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893939 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893943 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213916418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
213918738 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602473 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602665 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602624 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602675 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G |  |  |  | VPC192S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602480 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G |  |  |  | VPC192S4M-4G | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213918742 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH |  |  |  | AM192BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213893947 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH |  |  |  | AM192BXVGJH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893951 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM216BXVGJH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
213918746 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM216BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602486 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4G |  |  |  | VPC216S4M-4G | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602680 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4G |  |  |  | VPC216S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602493 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4G |  |  |  | VPC240S4M-4G | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893955 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240BXVGJH |  |  |  | AM240BXVGJH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826414 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602801 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602465 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602373 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602562 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893894 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893996 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893938 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893942 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213918737 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213916417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602472 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602804 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602623 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602663 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
214826415 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
214826416 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602672 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602806 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602478 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4Y | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213918741 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213893946 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192BXVGFR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893950 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216BXVGFR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
213918745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602485 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4Y | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602808 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602679 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
214826417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602492 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4Y |  |  |  | VRC240S4M-4Y | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893954 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240BXVGFR |  |  |  | AM240BXVGFR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602469 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602378 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602565 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893896 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893998 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893940 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893944 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213916419 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
213918739 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602475 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602667 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602626 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602676 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G |  |  |  | VRC192S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602481 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G |  |  |  | VRC192S4M-4G | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213918743 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR |  |  |  | AM192BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
213893948 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR |  |  |  | AM192BXVGJR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893952 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM216BXVGJR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
213918747 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM216BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602488 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4G |  |  |  | VRC216S4M-4G | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602681 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4G |  |  |  | VRC216S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602495 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4G |  |  |  | VRC240S4M-4G | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893956 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240BXVGJR |  |  |  | AM240BXVGJR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213916856 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916293 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916298 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916857 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916858 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
213916295 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
213916300 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
213916864 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916304 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916310 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916865 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916866 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
213916306 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
213916312 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
214432114 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B32S | TVAHP096B32S |  |  | TVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091583 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091440 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311042 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B42S | TVAHP096B42S |  |  | TVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091599 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091456 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311040 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S | HVAHP096B32S |  |  | HVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091535 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214078207 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432076 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S | HVAHP096B42S |  |  | HVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091551 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091408 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432080 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S | YVAHP096B32S |  |  | YVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091631 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091488 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432116 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S | YVAHP096B42S |  |  | YVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091647 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091504 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432094 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S | HVAHR096B42S |  |  | HVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094333 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094182 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432098 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S | YVAHR096B32S |  |  | YVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094413 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094262 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432134 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S | YVAHR096B42S |  |  | YVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094429 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094278 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432132 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B32S | TVAHR096B32S |  |  | TVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094365 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094214 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311059 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B42S | TVAHR096B42S |  |  | TVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094381 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094230 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311057 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S | HVAHR096B32S |  |  | HVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094317 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094166 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
213893573 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213916544 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916545 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213894787 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213894795 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213894789 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213894797 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213916559 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916560 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213893579 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213893575 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213916546 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213894815 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894823 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213894825 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213894817 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213916561 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213893569 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213916543 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213894767 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213894769 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213916558 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213893571 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213893471 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893464 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893465 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213916498 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213916496 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213894799 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Ducted Indoor Units | 206000 | 10.5 | 21.2 | 232000 | 3.65 | 196000 | 2.12 | R-410A | 17.1667
213894801 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Ducted Indoor Units | 206000 | 10.5 | 21.2 | 232000 | 3.65 | 196000 | 2.12 | R-410A | 17.1667
213916515 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916517 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893468 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893469 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893473 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916500 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213894818 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894827 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213894829 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213894820 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213916519 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213893459 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213916493 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213894771 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213894773 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213916512 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213893461 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213916494 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213894775 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894779 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213894777 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894781 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213916513 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213916495 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213894782 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894784 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213894785 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213894783 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213916514 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213916497 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 9.9 | 20.95 | 232000 | 3.51 | 162000 | 2.21 | R-410A | 17.1667
213894803 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Non-Ducted Indoor Units | 206000 | 9.9 | 21.7 | 232000 | 3.72 | 162000 | 2.31 | R-410A | 17.1667
213894791 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Ducted Indoor Units | 206000 | 9.9 | 20.2 | 232000 | 3.3 | 162000 | 2.12 | R-410A | 17.1667
213894793 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Ducted Indoor Units | 206000 | 9.9 | 20.2 | 232000 | 3.3 | 162000 | 2.12 | R-410A | 17.1667
213894805 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Non-Ducted Indoor Units | 206000 | 9.9 | 21.7 | 232000 | 3.72 | 162000 | 2.31 | R-410A | 17.1667
213916516 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 9.9 | 20.95 | 232000 | 3.51 | 162000 | 2.21 | R-410A | 17.1667
213916499 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213894806 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894811 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213894807 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894813 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213916518 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213916531 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893830 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893832 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893834 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893843 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213916537 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916533 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213894831 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213893555 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893557 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213894833 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213916539 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213916720 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213893740 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893741 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893742 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893743 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213916723 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916735 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213894984 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894985 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213894988 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894989 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213916739 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213916711 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213894890 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213893738 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213893739 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213894891 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213916713 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213916715 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213894970 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894971 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213894972 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894973 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213916717 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213916718 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213894974 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894975 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213894976 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894977 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213916721 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213916733 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213894982 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894983 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213894986 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894987 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213916737 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213916785 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893845 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893846 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893847 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213916938 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916939 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916788 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893781 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893782 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893783 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213916940 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213916936 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916791 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213894926 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213893785 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893786 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213916937 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213916941 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213916810 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916814 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213894898 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213894910 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213893793 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893795 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213893796 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213893794 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213894911 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213894899 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213916816 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213916812 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916818 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213894994 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894995 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213894996 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894997 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213916820 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213916806 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213894884 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213893791 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213893792 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213894885 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213916808 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213916532 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893548 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893549 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893552 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893553 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916538 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213896078 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213895966 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
214050094 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
214050102 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
213896082 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896386 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
213896466 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 |  |  |  | PURY-EP144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
214050082 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 |  |  |  | PURY-EP144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
214050086 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 |  |  |  | PURY-EP168YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
213896470 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 |  |  |  | PURY-EP168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
213896474 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896378 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
214050092 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213895964 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896076 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
214050090 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
214050098 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
213896080 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896382 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
213896464 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 |  |  |  | PURY-EP144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
214050080 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 |  |  |  | PURY-EP144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
214050084 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 |  |  |  | PURY-EP168TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
213896468 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 |  |  |  | PURY-EP168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
213896472 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896376 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
214050088 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
214050150 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
213896113 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895990 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213895994 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896123 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
214050154 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
213896109 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895988 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
214050148 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
214050152 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
213895992 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896118 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896006 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
213896138 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
214050182 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
214050186 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
213896502 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
213896410 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896494 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YNU-A1 |  |  |  | PURY-P144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
214050174 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YNU-A1 |  |  |  | PURY-P144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896498 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168YNU-A1 |  |  |  | PURY-P168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
214050180 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
213896004 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
213896136 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896408 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896500 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
214050184 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
214050172 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TNU-A1 |  |  |  | PURY-P144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896492 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TNU-A1 |  |  |  | PURY-P144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
213896496 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168TNU-A1 |  |  |  | PURY-P168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
213896030 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896166 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
214050308 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
214050316 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
213896170 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896434 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
213896510 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN |  |  |  | TURYE1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
214050296 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN |  |  |  | TURYE1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
214050300 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN |  |  |  | TURYE1684AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
213896514 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN |  |  |  | TURYE1684AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
213896518 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896426 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
214050306 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896028 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896164 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
214050304 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
214050312 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
213896168 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896430 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
213896508 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN |  |  |  | TURYE1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
214050294 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN |  |  |  | TURYE1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
214050298 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN |  |  |  | TURYE1683AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
213896512 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN |  |  |  | TURYE1683AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
213896516 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896424 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
214050302 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
214050364 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
213896198 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896054 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896058 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896202 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
214050368 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
213896196 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896052 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
214050362 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
214050366 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
213896056 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896200 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896214 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896070 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
214050396 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
214050400 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
213896546 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
213896458 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896538 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1444AN41AN |  |  |  | TURYP1444AN41AN | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
214050388 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1444AN41AN |  |  |  | TURYP1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896542 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1684AN41AN |  |  |  | TURYP1684AN41AN | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
213896212 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896068 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
214050394 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
214050398 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
213896456 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896544 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
213896536 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1443AN41AN |  |  |  | TURYP1443AN41AN | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
214050386 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1443AN41AN |  |  |  | TURYP1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896540 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1683AN41AN |  |  |  | TURYP1683AN41AN | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
214050513 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P72ZKMU-B |  |  | PURY-P168ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 18.3 | 178000 | 3.44 | 119000 | 2.12 | R-410A | 13.3333
214050519 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P96ZKMU-B |  |  | PURY-P192ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.4 | 18.65 | 204000 | 3.42 | 142000 | 2.13 | R-410A | 15.3333
213896343 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P72ZKMU-B |  |  | PURY-P168ZSKMU-B | Ducted Indoor Units | 160000 | 10.6 | 19.1 | 178000 | 3.6 | 119000 | 2.13 | R-410A | 13.3333
213896345 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P96ZKMU-B |  |  | PURY-P192ZSKMU-B | Ducted Indoor Units | 184000 | 10.3 | 19.6 | 204000 | 3.48 | 142000 | 2.1 | R-410A | 15.3333
213896322 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P192ZSKMU-B | Ducted Indoor Units | 184000 | 11 | 18.7 | 204000 | 3.48 | 150000 | 2.45 | R-410A | 15.3333
213896320 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Ducted Indoor Units | 160000 | 11.3 | 20.7 | 178000 | 3.54 | 132000 | 2.6 | R-410A | 13.3333
213896285 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Non-Ducted Indoor Units | 160000 | 11.4 | 19.2 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
213916481 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.35 | 19.95 | 178000 | 3.68 | 132000 | 2.39 | R-410A | 13.3333
213916482 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P192ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 18.25 | 204000 | 3.58 | 150000 | 2.31 | R-410A | 15.3333
213916483 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P216ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 18.8 | 232000 | 3.53 | 164000 | 2.28 | R-410A | 17.1667
213896324 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P216ZSKMU-B | Ducted Indoor Units | 206000 | 10.8 | 19.8 | 232000 | 3.51 | 164000 | 2.48 | R-410A | 17.1667
213896318 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144ZKMU-B |  |  |  | PUHY-P144ZKMU-B | Ducted Indoor Units | 138000 | 9.9 | 18.5 | 152000 | 3.46 | 109000 | 2.32 | R-410A | 11.5
213916693 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916326 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916318 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916694 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916695 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
213916328 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
213916320 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
213686145 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH |  |  |  | AVWT-144FLFSH | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
213686146 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH |  |  |  | AVWT-144FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
213686148 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FLFSH |  |  |  | AVWT-168FLFSH | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
213686149 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FLFSH |  |  |  | AVWT-168FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 22.45 | 170000 | 3.29 | 115000 | 2.16 | R-410A | 13.3333
213686151 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FLFSH |  |  |  | AVWT-192FLFSH | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
213686152 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FLFSH |  |  |  | AVWT-192FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
208758272 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
208758274 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB |  |  |  | CHV6-144URB | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
210135414 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 144FFFH |  |  |  | AVWT - 144FFFH | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
210135426 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 144FFFH |  |  |  | AVWT - 144FFFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
210135427 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 22.45 | 170000 | 3.32 | 115000 | 2.17 | R-410A | 13.3333
210135418 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Ducted Indoor Units | 160000 | 10.9 | 20.8 | 170000 | 3.26 | 115000 | 2.07 | R-410A | 13.3333
210135419 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
208758276 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Ducted Indoor Units | 160000 | 10.9 | 20.8 | 170000 | 3.26 | 115000 | 2.07 | R-410A | 13.3333
208758277 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
208758278 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
208758280 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-192URB |  |  |  | CHV6-192URB | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
210135416 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 192FFFH |  |  |  | AVWT - 192FFFH | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
210135428 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 192FFFH |  |  |  | AVWT - 192FFFH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
218083297 |  | HITACHI | HMSV-A-CB | HVAHR144C33S | HVAHR144C33S |  |  | HVAHR288C33S* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 17.45 | 284000 | 3.41 | 198000 | 2.31 | R-32 | 23
218083197 |  | HITACHI | HMSV-A-CB | HVAHR144C33S | HVAHR120C33S |  |  | HVAHR264C33S* | Non-Ducted Indoor Units | 252000 | 10.5 | 16.9 | 260000 | 3.88 | 174000 | 2.47 | R-32 | 21
218083198 |  | HITACHI | HMSV-A-CB | HVAHR144C33S | HVAHR144C33S |  |  | HVAHR288C33S* | Non-Ducted Indoor Units | 276000 | 10.7 | 19.2 | 284000 | 3.61 | 198000 | 2.49 | R-32 | 23
218083217 |  | HITACHI | HMSR-A-CB | HVAHR144C33S | HVAHR120C33S |  |  | HVAHR264C33S | Non-Ducted Indoor Units | 252000 | 10.5 | 16.9 | 260000 | 3.88 | 174000 | 2.47 | R-32 | 21
218083218 |  | HITACHI | HMSR-A-CB | HVAHR144C33S | HVAHR144C33S |  |  | HVAHR288C33S | Non-Ducted Indoor Units | 276000 | 10.7 | 19.2 | 284000 | 3.61 | 198000 | 2.49 | R-32 | 23
218083315 |  | HITACHI | HMSR-A-CB | HVAHR144C33S | HVAHR144C33S |  |  | HVAHR288C33S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 17.45 | 284000 | 3.41 | 198000 | 2.31 | R-32 | 23
218083306 |  | HITACHI | HMSV-A-CB | HVAHR144C43S | HVAHR144C43S |  |  | HVAHR288C43S* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 17.45 | 284000 | 3.41 | 198000 | 2.31 | R-32 | 23
218083324 |  | HITACHI | HMSR-A-CB | HVAHR144C43S | HVAHR144C43S |  |  | HVAHR288C43S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 17.45 | 284000 | 3.41 | 198000 | 2.31 | R-32 | 23
218083207 |  | HITACHI | HMSV-A-CB | HVAHR144C43S | HVAHR120C43S |  |  | HVAHR264C43S* | Non-Ducted Indoor Units | 252000 | 10.5 | 16.9 | 260000 | 3.88 | 174000 | 2.47 | R-32 | 21
218083208 |  | HITACHI | HMSV-A-CB | HVAHR144C43S | HVAHR144C43S |  |  | HVAHR288C43S* | Non-Ducted Indoor Units | 276000 | 10.7 | 19.2 | 284000 | 3.61 | 198000 | 2.49 | R-32 | 23
218083227 |  | HITACHI | HMSR-A-CB | HVAHR144C43S | HVAHR120C43S |  |  | HVAHR264C43S | Non-Ducted Indoor Units | 252000 | 10.5 | 16.9 | 260000 | 3.88 | 174000 | 2.47 | R-32 | 21
218083228 |  | HITACHI | HMSR-A-CB | HVAHR144C43S | HVAHR144C43S |  |  | HVAHR288C43S | Non-Ducted Indoor Units | 276000 | 10.7 | 19.2 | 284000 | 3.61 | 198000 | 2.49 | R-32 | 23
218363896 |  | FUJITSU | HMSR-A-CB | AOSU144VSAN7 | AOSU120VSAN7 |  |  | AOSU264VSAG7 | Non-Ducted Indoor Units | 252000 | 11.7 | 23.8 | 282000 | 3.36 | 194000 | 2.28 | R-32 | 21
218363897 |  | FUJITSU | HMSR-A-CB | AOSU144VSAN7 | AOSU144VSAN7 |  |  | AOSU288VSAG7 | Non-Ducted Indoor Units | 276000 | 9.8 | 22.9 | 308000 | 3.42 | 210000 | 2.27 | R-32 | 23
218363898 |  | FUJITSU | HMSR-A-CB | AOSU168VSAN7 | AOSU144VSAN7 |  |  | AOSU312VSAG7 | Non-Ducted Indoor Units | 298000 | 9.8 | 22.9 | 320000 | 3.42 | 214000 | 2.27 | R-32 | 24.8333
218363899 |  | FUJITSU | HMSR-A-CB | AOSU168VSAN7 | AOSU168VSAN7 |  |  | AOSU336VSAG7 | Non-Ducted Indoor Units | 320000 | 9.8 | 22.9 | 338000 | 3.42 | 224000 | 2.27 | R-32 | 26.6667
218363900 |  | FUJITSU | HMSR-A-CB | AOSU192VSAN7 | AOSU192VSAN7 |  |  | AOSU384VSAG7 | Non-Ducted Indoor Units | 366000 | 9.8 | 22.9 | 354000 | 3.42 | 240000 | 2.27 | R-32 | 30.5
218363907 |  | FUJITSU | HMSR-A-CB | AOSU192VSAN7 | AOSU168VSAN7 |  |  | AOSU360VSAG7 | Non-Ducted Indoor Units | 344000 | 9.8 | 22.9 | 346000 | 3.42 | 232000 | 2.27 | R-32 | 28.6667
218363902 |  | FUJITSU | HMSR-A-CB | AORU144VSAN7 | AORU120VSAN7 |  |  | AORU264VSAG7 | Non-Ducted Indoor Units | 252000 | 11.7 | 23.8 | 282000 | 3.36 | 194000 | 2.28 | R-32 | 21
218363903 |  | FUJITSU | HMSR-A-CB | AORU144VSAN7 | AORU144VSAN7 |  |  | AORU288VSAG7 | Non-Ducted Indoor Units | 276000 | 9.8 | 22.9 | 308000 | 3.42 | 210000 | 2.27 | R-32 | 23
218363904 |  | FUJITSU | HMSR-A-CB | AORU168VSAN7 | AORU144VSAN7 |  |  | AORU312VSAG7 | Non-Ducted Indoor Units | 298000 | 9.8 | 22.9 | 320000 | 3.42 | 214000 | 2.27 | R-32 | 24.8333
218363905 |  | FUJITSU | HMSR-A-CB | AORU168VSAN7 | AORU168VSAN7 |  |  | AORU336VSAG7 | Non-Ducted Indoor Units | 320000 | 9.8 | 22.9 | 338000 | 3.42 | 224000 | 2.27 | R-32 | 26.6667
218363906 |  | FUJITSU | HMSR-A-CB | AORU192VSAN7 | AORU192VSAN7 |  |  | AORU384VSAG7 | Non-Ducted Indoor Units | 366000 | 9.8 | 22.9 | 354000 | 3.42 | 240000 | 2.27 | R-32 | 30.5
218363908 |  | FUJITSU | HMSR-A-CB | AORU192VSAN7 | AORU168VSAN7 |  |  | AORU360VSAG7 | Non-Ducted Indoor Units | 344000 | 9.8 | 22.9 | 346000 | 3.42 | 232000 | 2.27 | R-32 | 28.6667
213886458 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH | AM120BXVTJH |  | AM288BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886454 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM120BXVTJH |  | AM264BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886386 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH | AM120BXVTJH |  | AM288BXVTJH | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886382 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM120BXVTJH |  | AM264BXVTJH | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602294 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC120L4M-4G |  | VPC264L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602303 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G | VPC120L4M-4G |  | VPC288L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
216602154 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC120L4M-4G |  | VPC264L4M-4G | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602161 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G | VPC120L4M-4G |  | VPC288L4M-4G | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602152 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC120L4M-4Y |  | VRC264L4M-4Y | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602159 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y | VRC120L4M-4Y |  | VRC288L4M-4Y | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602292 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC120L4M-4Y |  | VRC264L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602301 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y | VRC120L4M-4Y |  | VRC288L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886381 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM120BXVTFR |  | AM264BXVTFR | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
213886385 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR | AM120BXVTFR |  | AM288BXVTFR | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886453 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM120BXVTFR |  | AM264BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886457 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR | AM120BXVTFR |  | AM288BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886455 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM120BXVTJR |  | AM264BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886459 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR | AM120BXVTJR |  | AM288BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886387 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR | AM120BXVTJR |  | AM288BXVTJR | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886383 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM120BXVTJR |  | AM264BXVTJR | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602297 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC120L4M-4G |  | VRC264L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602305 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G | VRC120L4M-4G |  | VRC288L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
216602162 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G | VRC120L4M-4G |  | VRC288L4M-4G | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602155 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC120L4M-4G |  | VRC264L4M-4G | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602150 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC120L4M-4Y |  | VPC264L4M-4Y | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602157 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y | VPC120L4M-4Y |  | VPC288L4M-4Y | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602290 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC120L4M-4Y |  | VPC264L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602299 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y | VPC120L4M-4Y |  | VPC288L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886384 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH | AM120BXVTFH |  | AM288BXVTFH | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886380 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM120BXVTFH |  | AM264BXVTFH | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
213886452 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM120BXVTFH |  | AM264BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886456 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH | AM120BXVTFH |  | AM288BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213897064 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* | RXYQ144AATJ* |  |  | RXYQ264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 19.9 | 252000 | 3.3 | 168000 | 2.2 | R-410A | 21
213897021 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* | RXYQ144AATJ* |  |  | RXYQ264AATJ* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-410A | 21
213897022 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.7 | 274000 | 3.5 | 194000 | 2.2 | R-410A | 22.8333
213897023 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ168AATJ* |  |  | RXYQ312AATJ* | Non-Ducted Indoor Units | 296000 | 10.2 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-410A | 24.6667
213897047 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Ducted Indoor Units | 274000 | 10.4 | 18 | 274000 | 3.25 | 194000 | 2.1 | R-410A | 22.8333
213897065 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.35 | 274000 | 3.37 | 194000 | 2.15 | R-410A | 22.8333
213897066 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ168AATJ* |  |  | RXYQ312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.1 | 19 | 296000 | 3.35 | 212000 | 2.13 | R-410A | 24.6667
213897087 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ168AATJ* |  |  | RXYQ336AATJ* | Non-Ducted Indoor Units | 316000 | 9.3 | 18.4 | 310000 | 3.5 | 222000 | 2.1 | R-410A | 26.3333
213897114 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ168AATJ* |  |  | RXYQ336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.3 | 17.8 | 310000 | 3.35 | 222000 | 2.08 | R-410A | 26.3333
213897115 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.8 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-410A | 28.5
213897098 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Ducted Indoor Units | 342000 | 9.3 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-410A | 28.5
213897024 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-410A | 28.5
213897025 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Non-Ducted Indoor Units | 364000 | 10.4 | 20 | 364000 | 3.45 | 264000 | 2.1 | R-410A | 30.3333
213897026 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Non-Ducted Indoor Units | 388000 | 10 | 19.6 | 388000 | 3.45 | 276000 | 2.1 | R-410A | 32.3333
213897049 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Ducted Indoor Units | 364000 | 9.8 | 17.6 | 364000 | 3.25 | 264000 | 2.1 | R-410A | 30.3333
213897099 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Ducted Indoor Units | 388000 | 9.2 | 17 | 388000 | 3.25 | 276000 | 2.1 | R-410A | 32.3333
213897116 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.6 | 18.3 | 388000 | 3.35 | 276000 | 2.1 | R-410A | 32.3333
213897067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.1 | 18.8 | 364000 | 3.35 | 264000 | 2.1 | R-410A | 30.3333
213897088 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Non-Ducted Indoor Units | 424000 | 9.4 | 18.4 | 414000 | 3.3 | 280000 | 2.1 | R-410A | 35.3333
213897117 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 404000 | 9.35 | 17.75 | 404000 | 3.27 | 278000 | 2.08 | R-410A | 33.6667
213897118 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.25 | 17.4 | 414000 | 3.27 | 280000 | 2.1 | R-410A | 35.3333
213897100 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Ducted Indoor Units | 404000 | 9.1 | 16.5 | 404000 | 3.25 | 278000 | 2.1 | R-410A | 33.6667
213897101 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Ducted Indoor Units | 424000 | 9.1 | 16.4 | 414000 | 3.25 | 280000 | 2.1 | R-410A | 35.3333
213897027 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Non-Ducted Indoor Units | 404000 | 9.6 | 19 | 404000 | 3.3 | 278000 | 2.07 | R-410A | 33.6667
213897089 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* | RXYQ240AATJ* |  |  | RXYQ480AATJ* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.2 | 424000 | 3.25 | 282000 | 2.1 | R-410A | 36.3333
213897073 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* | RXYQ144AAYD* |  |  | RXYQ264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 19.9 | 252000 | 3.3 | 168000 | 2.2 | R-410A | 21
213897034 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* | RXYQ144AAYD* |  |  | RXYQ264AAYD* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-410A | 21
213897035 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.7 | 274000 | 3.5 | 194000 | 2.2 | R-410A | 22.8333
213897036 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ168AAYD* |  |  | RXYQ312AAYD* | Non-Ducted Indoor Units | 296000 | 10.2 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-410A | 24.6667
213897074 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.35 | 274000 | 3.37 | 194000 | 2.15 | R-410A | 22.8333
213897075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ168AAYD* |  |  | RXYQ312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.1 | 19 | 296000 | 3.35 | 212000 | 2.13 | R-410A | 24.6667
213897056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Ducted Indoor Units | 274000 | 10.4 | 18 | 274000 | 3.25 | 194000 | 2.1 | R-410A | 22.8333
213897092 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ168AAYD* |  |  | RXYQ336AAYD* | Non-Ducted Indoor Units | 316000 | 9.3 | 18.4 | 310000 | 3.5 | 222000 | 2.1 | R-410A | 26.3333
213897123 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ168AAYD* |  |  | RXYQ336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.3 | 17.8 | 310000 | 3.35 | 222000 | 2.08 | R-410A | 26.3333
213897124 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.8 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-410A | 28.5
213897106 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Ducted Indoor Units | 342000 | 9.3 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-410A | 28.5
213897037 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-410A | 28.5
213897038 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Non-Ducted Indoor Units | 364000 | 10.4 | 20 | 364000 | 3.45 | 264000 | 2.1 | R-410A | 30.3333
213897039 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Non-Ducted Indoor Units | 388000 | 10 | 19.6 | 388000 | 3.45 | 276000 | 2.1 | R-410A | 32.3333
213897107 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Ducted Indoor Units | 388000 | 9.2 | 17 | 388000 | 3.25 | 276000 | 2.1 | R-410A | 32.3333
213897125 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.6 | 18.3 | 388000 | 3.35 | 276000 | 2.1 | R-410A | 32.3333
213897076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.1 | 18.8 | 364000 | 3.35 | 264000 | 2.1 | R-410A | 30.3333
213897058 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Ducted Indoor Units | 364000 | 9.8 | 17.6 | 364000 | 3.25 | 264000 | 2.1 | R-410A | 30.3333
213897093 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Non-Ducted Indoor Units | 424000 | 9.4 | 18.4 | 414000 | 3.3 | 280000 | 2.1 | R-410A | 35.3333
213897126 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 404000 | 9.35 | 17.75 | 404000 | 3.27 | 278000 | 2.08 | R-410A | 33.6667
213897127 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.25 | 17.4 | 414000 | 3.27 | 280000 | 2.1 | R-410A | 35.3333
213897108 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Ducted Indoor Units | 404000 | 9.1 | 16.5 | 404000 | 3.25 | 278000 | 2.1 | R-410A | 33.6667
213897109 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Ducted Indoor Units | 424000 | 9.1 | 16.4 | 414000 | 3.25 | 280000 | 2.1 | R-410A | 35.3333
213897040 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Non-Ducted Indoor Units | 404000 | 9.6 | 19 | 404000 | 3.3 | 278000 | 2.07 | R-410A | 33.6667
213897094 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* | RXYQ240AAYD* |  |  | RXYQ480AAYD* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.2 | 424000 | 3.25 | 282000 | 2.1 | R-410A | 36.3333
213896688 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* | REYQ120XBTJ* |  | REYQ360XBTJ* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896685 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ144XBTJ* |  |  | REYQ264XBTJ* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896775 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ144XBTJ* |  |  | REYQ264XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896776 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* | REYQ120XBTJ* |  | REYQ360XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896751 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ144XBYD* |  |  | REYQ264XBYD* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896752 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* | REYQ120XBYD* |  | REYQ360XBYD* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896779 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ144XBYD* |  |  | REYQ264XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896780 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* | REYQ120XBYD* |  | REYQ360XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896783 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ144XBYC* |  |  | REYQ264XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896784 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* | REYQ120XBYC* |  | REYQ360XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896755 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ144XBYC* |  |  | REYQ264XBYC* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896756 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* | REYQ120XBYC* |  | REYQ360XBYC* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ144XBYC* |  |  | RXYQ264XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.45 | 17 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* | RXYQ120XBYC* |  | RXYQ360XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 338000 | 9.1 | 16.4 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.1667
213896813 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* | RXYQ120XBYC* |  | RXYQ360XBYC* | Non-Ducted Indoor Units | 338000 | 9.1 | 17.4 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.1667
213896748 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ144XBYC* |  |  | RXYQ264XBYC* | Non-Ducted Indoor Units | 252000 | 9.8 | 18.4 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
214608165 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* | MVHQ144ME2CA* |  |  | MVHQ264ME2CA* | Ducted Indoor Units | 252000 | 9.8 | 19.4 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214608166 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* | MVHQ144ME2CA* |  |  | MVHQ264ME2CA* | Non-Ducted Indoor Units | 252000 | 10.1 | 18.8 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214717494 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* | MVHQ192ME2CA* |  |  | MVHQ384ME2CA* | Ducted Indoor Units | 364000 | 9.4 | 18.5 | 384000 | 3.3 | 268000 | 2.3 | R-410A | 30.3333
214717496 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* | MVHQ192ME4CA* |  |  | MVHQ384ME4CA* | Ducted Indoor Units | 364000 | 9.4 | 18.5 | 384000 | 3.3 | 268000 | 2.3 | R-410A | 30.3333
217189688 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189689 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217189658 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
217190026 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190027 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
214295978 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296040 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
214296041 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
214296010 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
214296011 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217189668 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
217189698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189699 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217190036 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190037 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
214295986 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
214296051 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
214296020 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
214296021 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217189678 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
217190046 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190047 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
217189708 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189709 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
215828409 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
215828410 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
215828399 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
215828419 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
215828420 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
216602813 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602815 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602817 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602721 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602736 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602737 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602739 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602827 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602864 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602869 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602871 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
214826380 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
214826381 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
214826382 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
214836585 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
214836586 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
214836587 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
214836588 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
214826371 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
214833161 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
214833153 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
214833154 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
214833155 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
214833156 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM240DXVGQH |  |  | AM360DXVGQH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
214833159 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
214836589 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM240DXVGQH |  |  | AM360DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
214833165 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
214833166 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM144DXVGQH | AM192DXVGQH |  | AM456DXVGQH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
214836592 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602873 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC240S4M-4J |  |  | VPC360S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602824 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602837 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC144S4M-4J | VPC192S4M-4J |  | VPC456S4M-4J | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602819 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC240S4M-4J |  |  | VPC360S4M-4J | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602820 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602822 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602876 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602878 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
214836590 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
214836591 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
214833163 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
214833164 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
214833157 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
214833158 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602839 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC168S4M-4J |  |  | VRC264S4M-4J | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602841 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC192S4M-4J |  |  | VRC288S4M-4J | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602842 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC216S4M-4J |  |  | VRC312S4M-4J | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602771 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC168S4M-4J |  |  | VRC264S4M-4J | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602772 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC192S4M-4J |  |  | VRC288S4M-4J | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602774 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC216S4M-4J |  |  | VRC312S4M-4J | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602754 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC240S4M-4J |  |  | VRC336S4M-4J | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC240S4M-4J |  |  | VRC336S4M-4J | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4J |  |  | VRC264S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4J |  |  | VRC288S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602889 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4J |  |  | VRC312S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602891 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4J |  |  | VRC336S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216598853 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216598859 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216598860 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216598861 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216598862 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216598841 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216598842 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216598843 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216598844 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216598845 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216598846 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216598847 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216598848 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM240DXVGQR |  |  | AM360DXVGQR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216598863 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM240DXVGQR |  |  | AM360DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216598851 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216598857 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216598858 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM144DXVGQR | AM192DXVGQR |  | AM456DXVGQR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216598866 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602893 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4J |  |  | VRC360S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602849 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC144S4M-4J | VRC192S4M-4J |  | VRC456S4M-4J | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC240S4M-4J |  |  | VRC360S4M-4J | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602846 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC192S4M-4J |  |  | VRC384S4M-4J | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602847 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC216S4M-4J |  |  | VRC408S4M-4J | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602856 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC192S4M-4J |  |  | VRC384S4M-4J | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602858 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC216S4M-4J |  |  | VRC408S4M-4J | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4J |  |  | VRC384S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602898 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4J |  |  | VRC408S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216598855 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216598856 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216598864 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216598865 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216598849 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216598850 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
217729768 |  | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 282000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729769 |  | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11 | 21.5 | 308000 | 3.6 | 198000 | 2.54 | R-32 | 23
217729316 |  | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 282000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729334 |  | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 282000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729335 |  | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Non-Ducted Indoor Units | 276000 | 11.1 | 21.8 | 308000 | 3.66 | 198000 | 2.62 | R-32 | 23
217729336 |  | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Ducted Indoor Units | 276000 | 10.9 | 21.2 | 308000 | 3.54 | 198000 | 2.46 | R-32 | 23
217729337 |  | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Non-Ducted Indoor Units | 298000 | 10.8 | 21.2 | 332000 | 3.63 | 222000 | 2.55 | R-32 | 24.8333
217729338 |  | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Ducted Indoor Units | 298000 | 10.6 | 20.8 | 332000 | 3.47 | 222000 | 2.41 | R-32 | 24.8333
217729770 |  | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21 | 332000 | 3.55 | 222000 | 2.48 | R-32 | 24.8333
217729771 |  | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.5 | 358000 | 3.5 | 234000 | 2.42 | R-32 | 26.6667
217729351 |  | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Non-Ducted Indoor Units | 480000 | 9.3 | 18.4 | 506000 | 3.37 | 348000 | 2.33 | R-32 | 40
217729352 |  | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Ducted Indoor Units | 480000 | 9.3 | 17.8 | 506000 | 3.37 | 348000 | 2.15 | R-32 | 40
217729339 |  | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Non-Ducted Indoor Units | 320000 | 10.2 | 20.6 | 358000 | 3.61 | 234000 | 2.48 | R-32 | 26.6667
217729317 |  | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Ducted Indoor Units | 320000 | 10.3 | 20.4 | 358000 | 3.4 | 234000 | 2.36 | R-32 | 26.6667
217729778 |  | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 480000 | 9.3 | 18.1 | 506000 | 3.37 | 348000 | 2.24 | R-32 | 40
217729318 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Ducted Indoor Units | 344000 | 10.4 | 20.1 | 364000 | 3.39 | 248000 | 2.36 | R-32 | 28.6667
217729340 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Non-Ducted Indoor Units | 344000 | 10.5 | 21.2 | 364000 | 3.58 | 248000 | 2.37 | R-32 | 28.6667
217729341 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Non-Ducted Indoor Units | 366000 | 10.2 | 20.6 | 388000 | 3.5 | 266000 | 2.35 | R-32 | 30.5
217729342 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Ducted Indoor Units | 366000 | 10.1 | 19.5 | 388000 | 3.38 | 266000 | 2.34 | R-32 | 30.5
217729343 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Non-Ducted Indoor Units | 390000 | 9.9 | 20 | 412000 | 3.44 | 284000 | 2.32 | R-32 | 32.5
217729344 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Ducted Indoor Units | 390000 | 9.8 | 18.9 | 412000 | 3.38 | 284000 | 2.21 | R-32 | 32.5
217729345 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Non-Ducted Indoor Units | 410000 | 9.3 | 19.3 | 436000 | 3.44 | 298000 | 2.44 | R-32 | 34.1667
217729346 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Ducted Indoor Units | 410000 | 9.6 | 19.6 | 436000 | 3.38 | 298000 | 2.28 | R-32 | 34.1667
217729772 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 20.65 | 364000 | 3.48 | 248000 | 2.36 | R-32 | 28.6667
217729773 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.15 | 20.05 | 388000 | 3.44 | 266000 | 2.34 | R-32 | 30.5
217729774 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.85 | 19.45 | 412000 | 3.41 | 284000 | 2.26 | R-32 | 32.5
217729775 |  | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 19.45 | 436000 | 3.41 | 298000 | 2.36 | R-32 | 34.1667
217729776 |  | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.45 | 18.8 | 458000 | 3.38 | 318000 | 2.34 | R-32 | 36.1667
217729777 |  | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 454000 | 9.3 | 18.75 | 484000 | 3.37 | 332000 | 2.26 | R-32 | 37.8333
217729347 |  | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Non-Ducted Indoor Units | 434000 | 9.3 | 19 | 458000 | 3.39 | 318000 | 2.42 | R-32 | 36.1667
217729348 |  | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Ducted Indoor Units | 434000 | 9.6 | 18.6 | 458000 | 3.38 | 318000 | 2.26 | R-32 | 36.1667
217729349 |  | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Non-Ducted Indoor Units | 454000 | 9.3 | 18.8 | 484000 | 3.37 | 332000 | 2.38 | R-32 | 37.8333
217729350 |  | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Ducted Indoor Units | 454000 | 9.3 | 18.7 | 484000 | 3.37 | 332000 | 2.15 | R-32 | 37.8333
217729314 |  | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 256000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729315 |  | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 256000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729767 |  | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 256000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729789 |  | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 282000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729790 |  | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11 | 21.5 | 308000 | 3.6 | 198000 | 2.54 | R-32 | 23
217729353 |  | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 282000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729354 |  | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Non-Ducted Indoor Units | 276000 | 11.1 | 21.8 | 308000 | 3.66 | 198000 | 2.62 | R-32 | 23
217729355 |  | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Ducted Indoor Units | 276000 | 10.9 | 21.2 | 308000 | 3.54 | 198000 | 2.46 | R-32 | 23
217729331 |  | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 282000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729356 |  | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Non-Ducted Indoor Units | 298000 | 10.8 | 21.2 | 332000 | 3.63 | 222000 | 2.55 | R-32 | 24.8333
217729357 |  | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Ducted Indoor Units | 298000 | 10.6 | 20.8 | 332000 | 3.47 | 222000 | 2.41 | R-32 | 24.8333
217729791 |  | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21 | 332000 | 3.55 | 222000 | 2.48 | R-32 | 24.8333
217729792 |  | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.5 | 358000 | 3.5 | 234000 | 2.42 | R-32 | 26.6667
217729799 |  | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 480000 | 9.3 | 18.1 | 506000 | 3.37 | 348000 | 2.24 | R-32 | 40
217729370 |  | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Non-Ducted Indoor Units | 480000 | 9.3 | 18.4 | 506000 | 3.37 | 348000 | 2.33 | R-32 | 40
217729371 |  | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Ducted Indoor Units | 480000 | 9.3 | 17.8 | 506000 | 3.37 | 348000 | 2.15 | R-32 | 40
217729358 |  | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Non-Ducted Indoor Units | 320000 | 10.2 | 20.6 | 358000 | 3.61 | 234000 | 2.48 | R-32 | 26.6667
217729332 |  | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Ducted Indoor Units | 320000 | 10.3 | 20.4 | 358000 | 3.4 | 234000 | 2.36 | R-32 | 26.6667
217729333 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Ducted Indoor Units | 344000 | 10.4 | 20.1 | 364000 | 3.39 | 248000 | 2.36 | R-32 | 28.6667
217729359 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Non-Ducted Indoor Units | 344000 | 10.5 | 21.2 | 364000 | 3.58 | 248000 | 2.37 | R-32 | 28.6667
217729360 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Non-Ducted Indoor Units | 366000 | 10.2 | 20.6 | 388000 | 3.5 | 266000 | 2.35 | R-32 | 30.5
217729361 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Ducted Indoor Units | 366000 | 10.1 | 19.5 | 388000 | 3.38 | 266000 | 2.34 | R-32 | 30.5
217729362 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Non-Ducted Indoor Units | 390000 | 9.9 | 20 | 412000 | 3.44 | 284000 | 2.32 | R-32 | 32.5
217729363 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Ducted Indoor Units | 390000 | 9.8 | 18.9 | 412000 | 3.38 | 284000 | 2.21 | R-32 | 32.5
217729364 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Non-Ducted Indoor Units | 410000 | 9.3 | 19.3 | 436000 | 3.44 | 298000 | 2.44 | R-32 | 34.1667
217729365 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Ducted Indoor Units | 410000 | 9.6 | 19.6 | 436000 | 3.38 | 298000 | 2.28 | R-32 | 34.1667
217729793 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 20.65 | 364000 | 3.48 | 248000 | 2.36 | R-32 | 28.6667
217729794 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.15 | 20.05 | 388000 | 3.44 | 266000 | 2.34 | R-32 | 30.5
217729795 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.85 | 19.45 | 412000 | 3.41 | 284000 | 2.26 | R-32 | 32.5
217729796 |  | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 19.45 | 436000 | 3.41 | 298000 | 2.36 | R-32 | 34.1667
217729797 |  | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.45 | 18.8 | 458000 | 3.38 | 318000 | 2.34 | R-32 | 36.1667
217729798 |  | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 454000 | 9.3 | 18.75 | 484000 | 3.37 | 332000 | 2.26 | R-32 | 37.8333
217729366 |  | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Non-Ducted Indoor Units | 434000 | 9.3 | 19 | 458000 | 3.39 | 318000 | 2.42 | R-32 | 36.1667
217729367 |  | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Ducted Indoor Units | 434000 | 9.6 | 18.6 | 458000 | 3.38 | 318000 | 2.26 | R-32 | 36.1667
217729368 |  | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Non-Ducted Indoor Units | 454000 | 9.3 | 18.8 | 484000 | 3.37 | 332000 | 2.38 | R-32 | 37.8333
217729369 |  | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Ducted Indoor Units | 454000 | 9.3 | 18.7 | 484000 | 3.37 | 332000 | 2.15 | R-32 | 37.8333
217729329 |  | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 256000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729330 |  | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 256000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729788 |  | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 256000 | 3.38 | 182000 | 2.36 | R-32 | 21
217734341 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Ducted Indoor Units | 276000 | 10.5 | 21 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217734398 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.55 | 21.9 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217734274 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 22.8 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217734273 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2641FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.6 | 22.8 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217734275 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.5 | 22.2 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217734276 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL |  |  | MMY-UB3361FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.5 | 21.4 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217734277 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Non-Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217734278 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Non-Ducted Indoor Units | 366000 | 10.1 | 20.4 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217734279 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Non-Ducted Indoor Units | 390000 | 10 | 20.2 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217734280 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217734281 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4561FT6P-UL | Non-Ducted Indoor Units | 436000 | 9.9 | 19.8 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217734282 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4801FT6P-UL | Non-Ducted Indoor Units | 458000 | 9.4 | 19.8 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217734400 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 21.15 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217734396 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2641FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.95 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217734402 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL |  |  | MMY-UB3361FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 20.55 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217734404 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 19.35 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217734406 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.85 | 19.05 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217734408 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217734410 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.7 | 18.45 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217734412 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4561FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.7 | 17.8 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217734414 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4801FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.4 | 17.8 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217734343 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Ducted Indoor Units | 298000 | 10.4 | 20.1 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217734347 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Ducted Indoor Units | 344000 | 9.6 | 18.2 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217734349 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Ducted Indoor Units | 366000 | 9.6 | 17.7 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217734351 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Ducted Indoor Units | 390000 | 9.6 | 17.4 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217734353 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Ducted Indoor Units | 412000 | 9.5 | 16.9 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217734319 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Non-Ducted Indoor Units | 276000 | 11 | 21 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217734373 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217734430 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 20.4 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217734375 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Ducted Indoor Units | 344000 | 10.8 | 19 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217734321 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Non-Ducted Indoor Units | 344000 | 11 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217734432 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.9 | 19.95 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217734342 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Ducted Indoor Units | 276000 | 10.5 | 21 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217734399 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.55 | 21.9 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217734297 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 22.8 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217734298 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.5 | 22.2 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217734299 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL |  |  | MMY-UB3361FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.5 | 21.4 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217734300 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Non-Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217734301 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Non-Ducted Indoor Units | 366000 | 10.1 | 20.4 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217734302 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Non-Ducted Indoor Units | 390000 | 10 | 20.2 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217734303 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217734304 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4561FT9P-UL | Non-Ducted Indoor Units | 436000 | 9.9 | 19.8 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217734305 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4801FT9P-UL | Non-Ducted Indoor Units | 458000 | 9.4 | 19.8 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217734296 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2641FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.6 | 22.8 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217734401 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 21.15 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217734397 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2641FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.95 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217734409 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217734407 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.85 | 19.05 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217734405 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 19.35 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217734403 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL |  |  | MMY-UB3361FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 20.55 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217734415 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4801FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.4 | 17.8 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217734413 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4561FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.7 | 17.8 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217734411 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.7 | 18.45 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217734344 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Ducted Indoor Units | 298000 | 10.4 | 20.1 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217734352 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Ducted Indoor Units | 390000 | 9.6 | 17.4 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217734350 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Ducted Indoor Units | 366000 | 9.6 | 17.7 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217734348 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Ducted Indoor Units | 344000 | 9.6 | 18.2 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217734354 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Ducted Indoor Units | 412000 | 9.5 | 16.9 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217734320 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Non-Ducted Indoor Units | 276000 | 11 | 21 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217734374 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217734431 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 20.4 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217734376 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Ducted Indoor Units | 344000 | 10.8 | 19 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217734322 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Non-Ducted Indoor Units | 344000 | 11 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217734433 |  | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.9 | 19.95 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217735112 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 21.45 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217735034 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 20.6 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217735035 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Non-Ducted Indoor Units | 276000 | 9.7 | 22.3 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217735042 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Ducted Indoor Units | 298000 | 9.7 | 19.7 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217735043 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Non-Ducted Indoor Units | 298000 | 9.4 | 21.7 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217735047 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL |  |  | MMY-UB3361HT6P-UL | Non-Ducted Indoor Units | 320000 | 9.4 | 21.2 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217735050 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Ducted Indoor Units | 344000 | 9.1 | 17.8 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217735051 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Non-Ducted Indoor Units | 344000 | 9.1 | 20.1 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217735058 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Ducted Indoor Units | 366000 | 9.1 | 17.6 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217735059 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Non-Ducted Indoor Units | 366000 | 9.1 | 20.1 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217735062 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Ducted Indoor Units | 390000 | 9.1 | 17.2 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217735063 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Non-Ducted Indoor Units | 390000 | 9.1 | 19.7 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217735031 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2641HT6P-UL | Non-Ducted Indoor Units | 252000 | 9.7 | 22.3 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217735116 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.55 | 20.7 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217735118 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL |  |  | MMY-UB3361HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.5 | 20.25 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217735110 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2641HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.75 | 21.5 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217735120 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 18.95 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217735124 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.1 | 18.85 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217735126 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 18.45 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217735128 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 18.05 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217735130 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4561HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.1 | 17.4 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217735132 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4801HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.1 | 17.4 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217735066 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Ducted Indoor Units | 412000 | 9.1 | 16.6 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217735067 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Non-Ducted Indoor Units | 412000 | 9.1 | 19.5 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217735071 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4561HT6P-UL | Non-Ducted Indoor Units | 436000 | 9.1 | 19.3 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217735075 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4801HT6P-UL | Non-Ducted Indoor Units | 458000 | 9.1 | 19.3 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217735038 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Ducted Indoor Units | 276000 | 10.9 | 19.6 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217735039 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Non-Ducted Indoor Units | 276000 | 10.3 | 20.9 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217735114 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.6 | 20.25 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217735122 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 19.85 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217735054 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Ducted Indoor Units | 344000 | 10.3 | 18.8 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217735055 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Non-Ducted Indoor Units | 344000 | 10 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217735113 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 21.45 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217735036 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 20.6 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217735037 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Non-Ducted Indoor Units | 276000 | 9.7 | 22.3 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217735049 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL |  |  | MMY-UB3361HT9P-UL | Non-Ducted Indoor Units | 320000 | 9.4 | 21.2 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217735044 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Ducted Indoor Units | 298000 | 9.7 | 19.7 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217735045 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Non-Ducted Indoor Units | 298000 | 9.4 | 21.7 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217735052 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Ducted Indoor Units | 344000 | 9.1 | 17.8 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217735053 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Non-Ducted Indoor Units | 344000 | 9.1 | 20.1 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217735064 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Ducted Indoor Units | 390000 | 9.1 | 17.2 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217735065 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Non-Ducted Indoor Units | 390000 | 9.1 | 19.7 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217735060 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Ducted Indoor Units | 366000 | 9.1 | 17.6 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217735061 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Non-Ducted Indoor Units | 366000 | 9.1 | 20.1 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217735033 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2641HT9P-UL | Non-Ducted Indoor Units | 252000 | 9.7 | 22.3 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217735119 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL |  |  | MMY-UB3361HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.5 | 20.25 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217735117 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.55 | 20.7 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217735111 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2641HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.75 | 21.5 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217735121 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 18.95 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217735127 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 18.45 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217735125 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.1 | 18.85 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217735133 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4801HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.1 | 17.4 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217735131 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4561HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.1 | 17.4 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217735129 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 18.05 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217735077 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4801HT9P-UL | Non-Ducted Indoor Units | 458000 | 9.1 | 19.3 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217735073 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4561HT9P-UL | Non-Ducted Indoor Units | 436000 | 9.1 | 19.3 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217735068 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Ducted Indoor Units | 412000 | 9.1 | 16.6 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217735069 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Non-Ducted Indoor Units | 412000 | 9.1 | 19.5 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217735040 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Ducted Indoor Units | 276000 | 10.9 | 19.6 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217735041 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Non-Ducted Indoor Units | 276000 | 10.3 | 20.9 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217735115 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.6 | 20.25 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217735123 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 19.85 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217735056 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Ducted Indoor Units | 344000 | 10.3 | 18.8 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217735057 |  | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Non-Ducted Indoor Units | 344000 | 10 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217902163 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A | PURY-EM144TXU-A |  |  | PURY-EM264TSXU-A | Non-Ducted Indoor Units | 250000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 20.8333
217902165 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A | PURY-EM144TXU-A |  |  | PURY-EM264TSXU-A | Ducted Indoor Units | 250000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 20.8333
218088157 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A | PURY-EM144TXU-A |  |  | PURY-EM264TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 12.1 | 22.45 | 280000 | 3.61 | 172000 | 2.29 | R-32 | 20.8333
218088161 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM144TXU-A |  |  | PURY-EM288TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 304000 | 3.54 | 180000 | 2.27 | R-32 | 23
218088165 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM168TXU-A |  |  | PURY-EM312TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11.2 | 21.15 | 334000 | 3.45 | 196000 | 2.2 | R-32 | 24.8333
217902171 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM168TXU-A |  |  | PURY-EM312TSXU-A | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902172 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM168TXU-A |  |  | PURY-EM312TSXU-A | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902167 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM144TXU-A |  |  | PURY-EM288TSXU-A | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902168 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM144TXU-A |  |  | PURY-EM288TSXU-A | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902175 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM168TXU-A |  |  | PURY-EM336TSXU-A | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902176 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM168TXU-A |  |  | PURY-EM336TSXU-A | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902179 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM192TXU-A |  |  | PURY-EM360TSXU-A | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902180 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM192TXU-A |  |  | PURY-EM360TSXU-A | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
218088169 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM168TXU-A |  |  | PURY-EM336TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.7 | 20.75 | 360000 | 3.34 | 210000 | 2.19 | R-32 | 26.6667
218088173 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM192TXU-A |  |  | PURY-EM360TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 20.6 | 362000 | 3.33 | 220000 | 2.16 | R-32 | 28.6667
218088177 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A | PURY-EM192TXU-A |  |  | PURY-EM384TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 368000 | 9.8 | 19.9 | 368000 | 3.3 | 258000 | 2.13 | R-32 | 30.6667
217902183 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A | PURY-EM192TXU-A |  |  | PURY-EM384TSXU-A | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902184 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A | PURY-EM192TXU-A |  |  | PURY-EM384TSXU-A | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
218088158 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A | PURY-EM144YXU-A |  |  | PURY-EM264YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 12.1 | 22.45 | 280000 | 3.61 | 172000 | 2.29 | R-32 | 20.8333
217902164 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A | PURY-EM144YXU-A |  |  | PURY-EM264YSXU-A | Non-Ducted Indoor Units | 250000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 20.8333
217902166 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A | PURY-EM144YXU-A |  |  | PURY-EM264YSXU-A | Ducted Indoor Units | 250000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 20.8333
217902173 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM168YXU-A |  |  | PURY-EM312YSXU-A | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902174 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM168YXU-A |  |  | PURY-EM312YSXU-A | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902169 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM144YXU-A |  |  | PURY-EM288YSXU-A | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902170 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM144YXU-A |  |  | PURY-EM288YSXU-A | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
218088166 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM168YXU-A |  |  | PURY-EM312YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11.2 | 21.15 | 334000 | 3.45 | 196000 | 2.2 | R-32 | 24.8333
218088162 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM144YXU-A |  |  | PURY-EM288YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 304000 | 3.54 | 180000 | 2.27 | R-32 | 23
218088174 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM192YXU-A |  |  | PURY-EM360YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 20.6 | 362000 | 3.33 | 220000 | 2.16 | R-32 | 28.6667
218088170 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM168YXU-A |  |  | PURY-EM336YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.7 | 20.75 | 360000 | 3.34 | 210000 | 2.19 | R-32 | 26.6667
217902177 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM168YXU-A |  |  | PURY-EM336YSXU-A | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902178 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM168YXU-A |  |  | PURY-EM336YSXU-A | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902181 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM192YXU-A |  |  | PURY-EM360YSXU-A | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902182 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM192YXU-A |  |  | PURY-EM360YSXU-A | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902185 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A | PURY-EM192YXU-A |  |  | PURY-EM384YSXU-A | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902186 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A | PURY-EM192YXU-A |  |  | PURY-EM384YSXU-A | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
218088178 |  | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A | PURY-EM192YXU-A |  |  | PURY-EM384YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 368000 | 9.8 | 19.9 | 368000 | 3.3 | 258000 | 2.13 | R-32 | 30.6667
217902307 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN | TURYE1443AMM0AN |  |  | TURYE2643BMM0AN | Ducted Indoor Units | 252000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 21
217902308 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN | TURYE1443AMM0AN |  |  | TURYE2643BMM0AN | Non-Ducted Indoor Units | 252000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 21
218088229 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN | TURYE1443AMM0AN |  |  | TURYE2643BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12.1 | 22.45 | 280000 | 3.61 | 172000 | 2.29 | R-32 | 21
218088233 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1443AMM0AN |  |  | TURYE2883BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 304000 | 3.54 | 180000 | 2.27 | R-32 | 23
218088237 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1683AMM0AN |  |  | TURYE3123BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11.2 | 21.15 | 334000 | 3.45 | 196000 | 2.2 | R-32 | 24.8333
217902311 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1443AMM0AN |  |  | TURYE2883BMM0AN | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902312 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1443AMM0AN |  |  | TURYE2883BMM0AN | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902315 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1683AMM0AN |  |  | TURYE3123BMM0AN | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902316 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1683AMM0AN |  |  | TURYE3123BMM0AN | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902319 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1683AMM0AN |  |  | TURYE3363BMM0AN | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902320 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1683AMM0AN |  |  | TURYE3363BMM0AN | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902323 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1923AMM0AN |  |  | TURYE3603BMM0AN | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902324 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1923AMM0AN |  |  | TURYE3603BMM0AN | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
218088241 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1683AMM0AN |  |  | TURYE3363BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.7 | 20.75 | 360000 | 3.34 | 210000 | 2.19 | R-32 | 26.6667
218088245 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1923AMM0AN |  |  | TURYE3603BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 20.6 | 362000 | 3.33 | 220000 | 2.16 | R-32 | 28.6667
218088249 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN | TURYE1923AMM0AN |  |  | TURYE3843BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 368000 | 9.8 | 19.9 | 368000 | 3.3 | 258000 | 2.13 | R-32 | 30.6667
217902327 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN | TURYE1923AMM0AN |  |  | TURYE3843BMM0AN | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902328 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN | TURYE1923AMM0AN |  |  | TURYE3843BMM0AN | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
218088230 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN | TURYE1444AMM0AN |  |  | TURYE2644BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12.1 | 22.45 | 280000 | 3.61 | 172000 | 2.29 | R-32 | 21
217902309 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN | TURYE1444AMM0AN |  |  | TURYE2644BMM0AN | Ducted Indoor Units | 252000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 21
217902310 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN | TURYE1444AMM0AN |  |  | TURYE2644BMM0AN | Non-Ducted Indoor Units | 252000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 21
217902313 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1444AMM0AN |  |  | TURYE2884BMM0AN | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902314 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1444AMM0AN |  |  | TURYE2884BMM0AN | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902317 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1684AMM0AN |  |  | TURYE3124BMM0AN | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902318 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1684AMM0AN |  |  | TURYE3124BMM0AN | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
218088238 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1684AMM0AN |  |  | TURYE3124BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11.2 | 21.15 | 334000 | 3.45 | 196000 | 2.2 | R-32 | 24.8333
218088234 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1444AMM0AN |  |  | TURYE2884BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 304000 | 3.54 | 180000 | 2.27 | R-32 | 23
218088246 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1924AMM0AN |  |  | TURYE3604BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 20.6 | 362000 | 3.33 | 220000 | 2.16 | R-32 | 28.6667
218088242 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1684AMM0AN |  |  | TURYE3364BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.7 | 20.75 | 360000 | 3.34 | 210000 | 2.19 | R-32 | 26.6667
217902321 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1684AMM0AN |  |  | TURYE3364BMM0AN | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902322 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1684AMM0AN |  |  | TURYE3364BMM0AN | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902325 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1924AMM0AN |  |  | TURYE3604BMM0AN | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902326 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1924AMM0AN |  |  | TURYE3604BMM0AN | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902329 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN | TURYE1924AMM0AN |  |  | TURYE3844BMM0AN | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902330 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN | TURYE1924AMM0AN |  |  | TURYE3844BMM0AN | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
218088250 |  | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN | TURYE1924AMM0AN |  |  | TURYE3844BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 368000 | 9.8 | 19.9 | 368000 | 3.3 | 258000 | 2.13 | R-32 | 30.6667
217902131 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM264TSXU-A | Ducted Indoor Units | 250000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 20.8333
217902132 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM264TSXU-A | Non-Ducted Indoor Units | 250000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 20.8333
218088155 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM264TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 12.45 | 23.35 | 280000 | 3.71 | 172000 | 2.36 | R-32 | 20.8333
218088159 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM288TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.2 | 22.2 | 304000 | 3.61 | 180000 | 2.31 | R-32 | 23
218088163 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM312TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11.55 | 21.65 | 334000 | 3.53 | 196000 | 2.28 | R-32 | 24.8333
217902135 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM288TSXU-A | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902136 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM288TSXU-A | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902139 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM312TSXU-A | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902140 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM312TSXU-A | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902143 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM336TSXU-A | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902144 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM336TSXU-A | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902147 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM360TSXU-A | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902148 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM360TSXU-A | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
218088167 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM336TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11 | 21.35 | 360000 | 3.39 | 210000 | 2.19 | R-32 | 26.6667
218088171 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM360TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.7 | 20.85 | 362000 | 3.42 | 220000 | 2.17 | R-32 | 28.6667
218088175 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM384TSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 368000 | 10.35 | 20.45 | 368000 | 3.44 | 258000 | 2.19 | R-32 | 30.6667
217902151 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM384TSXU-A | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902152 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM384TSXU-A | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
218088156 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM264YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 12.45 | 23.35 | 280000 | 3.71 | 172000 | 2.36 | R-32 | 20.8333
217902133 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM264YSXU-A | Ducted Indoor Units | 250000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 20.8333
217902134 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM264YSXU-A | Non-Ducted Indoor Units | 250000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 20.8333
217902137 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM288YSXU-A | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902138 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM288YSXU-A | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902141 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM312YSXU-A | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902142 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM312YSXU-A | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
218088160 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM288YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.2 | 22.2 | 304000 | 3.61 | 180000 | 2.31 | R-32 | 23
218088164 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM312YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11.55 | 21.65 | 334000 | 3.53 | 196000 | 2.28 | R-32 | 24.8333
218088168 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM336YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11 | 21.35 | 360000 | 3.39 | 210000 | 2.19 | R-32 | 26.6667
218088172 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM360YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.7 | 20.85 | 362000 | 3.42 | 220000 | 2.17 | R-32 | 28.6667
217902145 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM336YSXU-A | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902146 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM336YSXU-A | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902149 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM360YSXU-A | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902150 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM360YSXU-A | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902153 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM384YSXU-A | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902154 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM384YSXU-A | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
218088176 |  | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM384YSXU-A | Mixed Ducted and Non-Ducted Indoor Units | 368000 | 10.35 | 20.45 | 368000 | 3.44 | 258000 | 2.19 | R-32 | 30.6667
217902235 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2643BMM0AN | Ducted Indoor Units | 252000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 21
217902236 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2643BMM0AN | Non-Ducted Indoor Units | 252000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 21
218088227 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2643BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12.45 | 23.35 | 280000 | 3.71 | 172000 | 2.36 | R-32 | 21
218088231 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2883BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.2 | 22.2 | 304000 | 3.61 | 180000 | 2.31 | R-32 | 23
218088235 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3123BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11.55 | 21.65 | 334000 | 3.53 | 196000 | 2.28 | R-32 | 24.8333
217902239 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2883BMM0AN | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902240 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2883BMM0AN | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902243 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3123BMM0AN | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902244 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3123BMM0AN | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902247 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3363BMM0AN | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902248 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3363BMM0AN | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902251 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3603BMM0AN | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902252 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3603BMM0AN | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
218088239 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3363BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11 | 21.35 | 360000 | 3.39 | 210000 | 2.19 | R-32 | 26.6667
218088243 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3603BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.7 | 20.85 | 362000 | 3.42 | 220000 | 2.17 | R-32 | 28.6667
218088247 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3843BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 368000 | 10.35 | 20.45 | 368000 | 3.44 | 258000 | 2.19 | R-32 | 30.6667
217902255 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3843BMM0AN | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902256 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3843BMM0AN | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
218088228 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2644BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12.45 | 23.35 | 280000 | 3.71 | 172000 | 2.36 | R-32 | 21
217902237 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2644BMM0AN | Ducted Indoor Units | 252000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 21
217902238 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2644BMM0AN | Non-Ducted Indoor Units | 252000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 21
217902241 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2884BMM0AN | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902242 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2884BMM0AN | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902245 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3124BMM0AN | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902246 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3124BMM0AN | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
218088232 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2884BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.2 | 22.2 | 304000 | 3.61 | 180000 | 2.31 | R-32 | 23
218088236 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3124BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11.55 | 21.65 | 334000 | 3.53 | 196000 | 2.28 | R-32 | 24.8333
218088240 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3364BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11 | 21.35 | 360000 | 3.39 | 210000 | 2.19 | R-32 | 26.6667
218088244 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3604BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.7 | 20.85 | 362000 | 3.42 | 220000 | 2.17 | R-32 | 28.6667
217902249 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3364BMM0AN | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902250 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3364BMM0AN | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902253 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3604BMM0AN | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902254 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3604BMM0AN | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902257 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3844BMM0AN | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902258 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3844BMM0AN | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
218088248 |  | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3844BMM0AN | Mixed Ducted and Non-Ducted Indoor Units | 368000 | 10.35 | 20.45 | 368000 | 3.44 | 258000 | 2.19 | R-32 | 30.6667
218044027 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD168S6M-5Y |  |  | VPD264S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218044031 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD192S6M-5Y |  |  | VPD288S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218044035 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD216S6M-5Y |  |  | VPD312S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218044039 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD240S6M-5Y |  |  | VPD336S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218043955 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD168S6M-5Y |  |  | VPD264S6M-5Y | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218043959 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD192S6M-5Y |  |  | VPD288S6M-5Y | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218043963 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD216S6M-5Y |  |  | VPD312S6M-5Y | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218043967 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD240S6M-5Y |  |  | VPD336S6M-5Y | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218043891 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD168S6M-5Y |  |  | VPD264S6M-5Y | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218043895 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD192S6M-5Y |  |  | VPD288S6M-5Y | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218043899 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD216S6M-5Y |  |  | VPD312S6M-5Y | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218043903 |  | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD240S6M-5Y |  |  | VPD336S6M-5Y | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218004919 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003144 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003148 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003152 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218004923 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004927 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004931 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218003140 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003080 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003084 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003088 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003076 |  | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003092 |  | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM240HCVGFG |  |  | AM360HCVGFG | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218004935 |  | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM240HCVGFG |  |  | AM360HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218003172 |  | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM144HCVGFG | AM192HCVGFG |  | AM456HCVGFG | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043907 |  | LENNOX | HMSV-A-CB | VPD120S6M-5Y | VPD240S6M-5Y |  |  | VPD360S6M-5Y | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218043919 |  | LENNOX | HMSV-A-CB | VPD120S6M-5Y | VPD120S6M-5Y | VPD192S6M-5Y |  | VPD432S6M-5Y | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218044043 |  | LENNOX | HMSV-A-CB | VPD120S6M-5Y | VPD240S6M-5Y |  |  | VPD360S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218043987 |  | LENNOX | HMSV-A-CB | VPD120S6M-5Y | VPD144S6M-5Y | VPD192S6M-5Y |  | VPD456S6M-5Y | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043975 |  | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD192S6M-5Y |  |  | VPD384S6M-5Y | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218043979 |  | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD216S6M-5Y |  |  | VPD408S6M-5Y | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218044047 |  | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD192S6M-5Y |  |  | VPD384S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218044051 |  | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD216S6M-5Y |  |  | VPD408S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218043911 |  | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD192S6M-5Y |  |  | VPD384S6M-5Y | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218043915 |  | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD216S6M-5Y |  |  | VPD408S6M-5Y | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003160 |  | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003164 |  | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218004939 |  | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004943 |  | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218003100 |  | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003096 |  | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218044036 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD216S6M-5Y |  |  | VRD312S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218044032 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD192S6M-5Y |  |  | VRD288S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218044028 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD168S6M-5Y |  |  | VRD264S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218044040 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD240S6M-5Y |  |  | VRD336S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218043956 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD168S6M-5Y |  |  | VRD264S6M-5Y | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218043968 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD240S6M-5Y |  |  | VRD336S6M-5Y | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218043964 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD216S6M-5Y |  |  | VRD312S6M-5Y | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218043960 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD192S6M-5Y |  |  | VRD288S6M-5Y | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218043892 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD168S6M-5Y |  |  | VRD264S6M-5Y | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218043904 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD240S6M-5Y |  |  | VRD336S6M-5Y | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218043900 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD216S6M-5Y |  |  | VRD312S6M-5Y | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218043896 |  | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD192S6M-5Y |  |  | VRD288S6M-5Y | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218004920 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003153 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003149 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003145 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218004932 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004928 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004924 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218003141 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003089 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003085 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003081 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003077 |  | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003093 |  | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM240HCVGFS |  |  | AM360HCVGFS | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218004936 |  | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM240HCVGFS |  |  | AM360HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218003173 |  | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM144HCVGFS | AM192HCVGFS |  | AM456HCVGFS | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043908 |  | LENNOX | HMSR-A-CB | VRD120S6M-5Y | VRD240S6M-5Y |  |  | VRD360S6M-5Y | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218043920 |  | LENNOX | HMSR-A-CB | VRD120S6M-5Y | VRD120S6M-5Y | VRD192S6M-5Y |  | VRD432S6M-5Y | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218044044 |  | LENNOX | HMSR-A-CB | VRD120S6M-5Y | VRD240S6M-5Y |  |  | VRD360S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218043988 |  | LENNOX | HMSR-A-CB | VRD120S6M-5Y | VRD144S6M-5Y | VRD192S6M-5Y |  | VRD456S6M-5Y | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043980 |  | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD216S6M-5Y |  |  | VRD408S6M-5Y | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218043976 |  | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD192S6M-5Y |  |  | VRD384S6M-5Y | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218044052 |  | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD216S6M-5Y |  |  | VRD408S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218044048 |  | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD192S6M-5Y |  |  | VRD384S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218043916 |  | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD216S6M-5Y |  |  | VRD408S6M-5Y | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218043912 |  | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD192S6M-5Y |  |  | VRD384S6M-5Y | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218003165 |  | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003161 |  | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218004940 |  | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004944 |  | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218003101 |  | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003097 |  | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218044029 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD168S6M-5G |  |  | VPD264S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218044033 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD192S6M-5G |  |  | VPD288S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218044037 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD216S6M-5G |  |  | VPD312S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218044041 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD240S6M-5G |  |  | VPD336S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218043957 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD168S6M-5G |  |  | VPD264S6M-5G | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218043969 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD240S6M-5G |  |  | VPD336S6M-5G | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218043961 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD192S6M-5G |  |  | VPD288S6M-5G | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218043965 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD216S6M-5G |  |  | VPD312S6M-5G | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218043893 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD168S6M-5G |  |  | VPD264S6M-5G | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218043905 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD240S6M-5G |  |  | VPD336S6M-5G | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218043897 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD192S6M-5G |  |  | VPD288S6M-5G | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218043901 |  | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD216S6M-5G |  |  | VPD312S6M-5G | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218004921 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003154 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003146 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003150 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218004925 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004929 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004933 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218003142 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003082 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003086 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003090 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003078 |  | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003094 |  | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM240HCVGJG |  |  | AM360HCVGJG | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218004937 |  | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM240HCVGJG |  |  | AM360HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218003174 |  | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM144HCVGJG | AM192HCVGJG |  | AM456HCVGJG | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043909 |  | LENNOX | HMSV-A-CB | VPD120S6M-5G | VPD240S6M-5G |  |  | VPD360S6M-5G | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218043921 |  | LENNOX | HMSV-A-CB | VPD120S6M-5G | VPD120S6M-5G | VPD192S6M-5G |  | VPD432S6M-5G | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218044045 |  | LENNOX | HMSV-A-CB | VPD120S6M-5G | VPD240S6M-5G |  |  | VPD360S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218043989 |  | LENNOX | HMSV-A-CB | VPD120S6M-5G | VPD144S6M-5G | VPD192S6M-5G |  | VPD456S6M-5G | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043977 |  | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD192S6M-5G |  |  | VPD384S6M-5G | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218043981 |  | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD216S6M-5G |  |  | VPD408S6M-5G | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218044049 |  | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD192S6M-5G |  |  | VPD384S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218044053 |  | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD216S6M-5G |  |  | VPD408S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218043913 |  | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD192S6M-5G |  |  | VPD384S6M-5G | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218043917 |  | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD216S6M-5G |  |  | VPD408S6M-5G | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003162 |  | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003166 |  | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218004941 |  | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004945 |  | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218003102 |  | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003098 |  | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218044038 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD216S6M-5G |  |  | VRD312S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218044034 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD192S6M-5G |  |  | VRD288S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218044030 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD168S6M-5G |  |  | VRD264S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218044042 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD240S6M-5G |  |  | VRD336S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218043958 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD168S6M-5G |  |  | VRD264S6M-5G | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218043970 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD240S6M-5G |  |  | VRD336S6M-5G | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218043966 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD216S6M-5G |  |  | VRD312S6M-5G | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218043962 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD192S6M-5G |  |  | VRD288S6M-5G | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218043894 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD168S6M-5G |  |  | VRD264S6M-5G | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218043906 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD240S6M-5G |  |  | VRD336S6M-5G | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218043902 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD216S6M-5G |  |  | VRD312S6M-5G | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218043898 |  | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD192S6M-5G |  |  | VRD288S6M-5G | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218004922 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003155 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003151 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003147 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218004934 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004930 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004926 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218003143 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003091 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003087 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003083 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003079 |  | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003095 |  | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM240HCVGJS |  |  | AM360HCVGJS | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218004938 |  | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM240HCVGJS |  |  | AM360HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218003175 |  | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM144HCVGJS | AM192HCVGJS |  | AM456HCVGJS | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043910 |  | LENNOX | HMSR-A-CB | VRD120S6M-5G | VRD240S6M-5G |  |  | VRD360S6M-5G | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218043922 |  | LENNOX | HMSR-A-CB | VRD120S6M-5G | VRD120S6M-5G | VRD192S6M-5G |  | VRD432S6M-5G | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218044046 |  | LENNOX | HMSR-A-CB | VRD120S6M-5G | VRD240S6M-5G |  |  | VRD360S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218043990 |  | LENNOX | HMSR-A-CB | VRD120S6M-5G | VRD144S6M-5G | VRD192S6M-5G |  | VRD456S6M-5G | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043982 |  | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD216S6M-5G |  |  | VRD408S6M-5G | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218043978 |  | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD192S6M-5G |  |  | VRD384S6M-5G | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218044054 |  | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD216S6M-5G |  |  | VRD408S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218044050 |  | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD192S6M-5G |  |  | VRD384S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218043918 |  | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD216S6M-5G |  |  | VRD408S6M-5G | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218043914 |  | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD192S6M-5G |  |  | VRD384S6M-5G | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218003167 |  | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003163 |  | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218004942 |  | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004946 |  | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218003103 |  | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003099 |  | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218005691 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005695 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005731 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005735 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005763 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005767 |  | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044087 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD120L6M-5Y |  | VPD264L6M-5Y | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218044091 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y | VPD120L6M-5Y |  | VPD288L6M-5Y | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218044127 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD120L6M-5Y |  | VPD264L6M-5Y | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218044131 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y | VPD120L6M-5Y |  | VPD288L6M-5Y | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044159 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD120L6M-5Y |  | VPD264L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044163 |  | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y | VPD120L6M-5Y |  | VPD288L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044164 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y | VRD120L6M-5Y |  | VRD288L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044160 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD120L6M-5Y |  | VRD264L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044132 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y | VRD120L6M-5Y |  | VRD288L6M-5Y | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044128 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD120L6M-5Y |  | VRD264L6M-5Y | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218044092 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y | VRD120L6M-5Y |  | VRD288L6M-5Y | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218044088 |  | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD120L6M-5Y |  | VRD264L6M-5Y | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005764 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005768 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005736 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005732 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005696 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005692 |  | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005693 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005697 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005765 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005769 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005733 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005737 |  | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044089 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD120L6M-5G |  | VPD264L6M-5G | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218044093 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G | VPD120L6M-5G |  | VPD288L6M-5G | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218044129 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD120L6M-5G |  | VPD264L6M-5G | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218044133 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G | VPD120L6M-5G |  | VPD288L6M-5G | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044161 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD120L6M-5G |  | VPD264L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044165 |  | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G | VPD120L6M-5G |  | VPD288L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044166 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G | VRD120L6M-5G |  | VRD288L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044162 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD120L6M-5G |  | VRD264L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044134 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G | VRD120L6M-5G |  | VRD288L6M-5G | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044130 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD120L6M-5G |  | VRD264L6M-5G | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218044094 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G | VRD120L6M-5G |  | VRD288L6M-5G | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218044090 |  | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD120L6M-5G |  | VRD264L6M-5G | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005766 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005770 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005738 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005734 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005698 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005694 |  | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218036909 |  | DAIKIN | HMSV-A-CB | RXYA120AATJ* | RXYA144AATJ* |  |  | RXYA264AATJ* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-32 | 21
218036981 |  | DAIKIN | HMSV-A-CB | RXYA120AATJ* | RXYA144AATJ* |  |  | RXYA264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.6 | 19.95 | 252000 | 3.3 | 168000 | 2.2 | R-32 | 21
218036982 |  | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA144AATJ* |  |  | RXYA288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.6 | 274000 | 3.37 | 194000 | 2.15 | R-32 | 22.8333
218036983 |  | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA168AATJ* |  |  | RXYA312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.2 | 19.15 | 296000 | 3.35 | 212000 | 2.15 | R-32 | 24.6667
218036946 |  | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA144AATJ* |  |  | RXYA288AATJ* | Ducted Indoor Units | 274000 | 10.4 | 18.2 | 274000 | 3.25 | 194000 | 2.1 | R-32 | 22.8333
218036910 |  | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA144AATJ* |  |  | RXYA288AATJ* | Non-Ducted Indoor Units | 274000 | 10.8 | 21 | 274000 | 3.5 | 194000 | 2.2 | R-32 | 22.8333
218036911 |  | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA168AATJ* |  |  | RXYA312AATJ* | Non-Ducted Indoor Units | 296000 | 10.3 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-32 | 24.6667
218036912 |  | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA168AATJ* |  |  | RXYA336AATJ* | Non-Ducted Indoor Units | 316000 | 9.4 | 19 | 310000 | 3.5 | 222000 | 2.1 | R-32 | 26.3333
218036913 |  | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA192AATJ* |  |  | RXYA360AATJ* | Non-Ducted Indoor Units | 342000 | 10.4 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-32 | 28.5
218036949 |  | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA192AATJ* |  |  | RXYA360AATJ* | Ducted Indoor Units | 342000 | 9.4 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-32 | 28.5
218036984 |  | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA168AATJ* |  |  | RXYA336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.4 | 18.15 | 310000 | 3.35 | 222000 | 2.1 | R-32 | 26.3333
218036985 |  | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA192AATJ* |  |  | RXYA360AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.9 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-32 | 28.5
218036986 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA192AATJ* |  |  | RXYA384AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.2 | 19.1 | 364000 | 3.35 | 264000 | 2.1 | R-32 | 30.3333
218036987 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA216AATJ* |  |  | RXYA408AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.7 | 18.55 | 388000 | 3.35 | 288000 | 2.1 | R-32 | 32.3333
218036950 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA192AATJ* |  |  | RXYA384AATJ* | Ducted Indoor Units | 364000 | 9.9 | 17.8 | 364000 | 3.25 | 264000 | 2.1 | R-32 | 30.3333
218036951 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA216AATJ* |  |  | RXYA408AATJ* | Ducted Indoor Units | 388000 | 9.3 | 17.2 | 388000 | 3.25 | 288000 | 2.1 | R-32 | 32.3333
218036914 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA192AATJ* |  |  | RXYA384AATJ* | Non-Ducted Indoor Units | 364000 | 10.5 | 20.4 | 364000 | 3.45 | 264000 | 2.1 | R-32 | 30.3333
218036915 |  | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA216AATJ* |  |  | RXYA408AATJ* | Non-Ducted Indoor Units | 388000 | 10.1 | 19.9 | 388000 | 3.45 | 288000 | 2.1 | R-32 | 32.3333
218036916 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA216AATJ* |  |  | RXYA432AATJ* | Non-Ducted Indoor Units | 410000 | 9.6 | 19 | 404000 | 3.3 | 312000 | 2.1 | R-32 | 34.1667
218036917 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA240AATJ* |  |  | RXYA456AATJ* | Non-Ducted Indoor Units | 424000 | 9.4 | 19 | 414000 | 3.3 | 314000 | 2.1 | R-32 | 35.3333
218036952 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA216AATJ* |  |  | RXYA432AATJ* | Ducted Indoor Units | 410000 | 9.2 | 16.8 | 404000 | 3.25 | 312000 | 2.1 | R-32 | 34.1667
218036953 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA240AATJ* |  |  | RXYA456AATJ* | Ducted Indoor Units | 424000 | 9.2 | 17 | 414000 | 3.25 | 314000 | 2.1 | R-32 | 35.3333
218036988 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA216AATJ* |  |  | RXYA432AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 17.9 | 404000 | 3.27 | 312000 | 2.1 | R-32 | 34.1667
218036989 |  | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA240AATJ* |  |  | RXYA456AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.3 | 18 | 414000 | 3.27 | 314000 | 2.1 | R-32 | 35.3333
218036918 |  | DAIKIN | HMSV-A-CB | RXYA240AATJ* | RXYA240AATJ* |  |  | RXYA480AATJ* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.4 | 418000 | 3.25 | 320000 | 2.1 | R-32 | 36.3333
218036927 |  | DAIKIN | HMSV-A-CB | RXYA120AAYD* | RXYA144AAYD* |  |  | RXYA264AAYD* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-32 | 21
218036999 |  | DAIKIN | HMSV-A-CB | RXYA120AAYD* | RXYA144AAYD* |  |  | RXYA264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.6 | 19.95 | 252000 | 3.3 | 168000 | 2.2 | R-32 | 21
218037000 |  | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA144AAYD* |  |  | RXYA288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.6 | 274000 | 3.37 | 194000 | 2.15 | R-32 | 22.8333
218037001 |  | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA168AAYD* |  |  | RXYA312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.2 | 19.15 | 296000 | 3.35 | 212000 | 2.15 | R-32 | 24.6667
218036964 |  | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA144AAYD* |  |  | RXYA288AAYD* | Ducted Indoor Units | 274000 | 10.4 | 18.2 | 274000 | 3.25 | 194000 | 2.1 | R-32 | 22.8333
218036928 |  | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA144AAYD* |  |  | RXYA288AAYD* | Non-Ducted Indoor Units | 274000 | 10.8 | 21 | 274000 | 3.5 | 194000 | 2.2 | R-32 | 22.8333
218036929 |  | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA168AAYD* |  |  | RXYA312AAYD* | Non-Ducted Indoor Units | 296000 | 10.3 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-32 | 24.6667
218036930 |  | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA168AAYD* |  |  | RXYA336AAYD* | Non-Ducted Indoor Units | 316000 | 9.4 | 19 | 310000 | 3.5 | 222000 | 2.1 | R-32 | 26.3333
218036931 |  | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA192AAYD* |  |  | RXYA360AAYD* | Non-Ducted Indoor Units | 342000 | 10.4 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-32 | 28.5
218036967 |  | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA192AAYD* |  |  | RXYA360AAYD* | Ducted Indoor Units | 342000 | 9.4 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-32 | 28.5
218037002 |  | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA168AAYD* |  |  | RXYA336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.4 | 18.15 | 310000 | 3.35 | 222000 | 2.1 | R-32 | 26.3333
218037003 |  | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA192AAYD* |  |  | RXYA360AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.9 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-32 | 28.5
218037004 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA192AAYD* |  |  | RXYA384AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.2 | 19.1 | 364000 | 3.35 | 264000 | 2.1 | R-32 | 30.3333
218037005 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA216AAYD* |  |  | RXYA408AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.7 | 18.55 | 388000 | 3.35 | 288000 | 2.1 | R-32 | 32.3333
218036968 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA192AAYD* |  |  | RXYA384AAYD* | Ducted Indoor Units | 364000 | 9.9 | 17.8 | 364000 | 3.25 | 264000 | 2.1 | R-32 | 30.3333
218036969 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA216AAYD* |  |  | RXYA408AAYD* | Ducted Indoor Units | 388000 | 9.3 | 17.2 | 388000 | 3.25 | 288000 | 2.1 | R-32 | 32.3333
218036932 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA192AAYD* |  |  | RXYA384AAYD* | Non-Ducted Indoor Units | 364000 | 10.5 | 20.4 | 364000 | 3.45 | 264000 | 2.1 | R-32 | 30.3333
218036933 |  | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA216AAYD* |  |  | RXYA408AAYD* | Non-Ducted Indoor Units | 388000 | 10.1 | 19.9 | 388000 | 3.45 | 288000 | 2.1 | R-32 | 32.3333
218036934 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA216AAYD* |  |  | RXYA432AAYD* | Non-Ducted Indoor Units | 410000 | 9.6 | 19 | 404000 | 3.3 | 312000 | 2.1 | R-32 | 34.1667
218036935 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA240AAYD* |  |  | RXYA456AAYD* | Non-Ducted Indoor Units | 424000 | 9.4 | 19 | 414000 | 3.3 | 314000 | 2.1 | R-32 | 35.3333
218036970 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA216AAYD* |  |  | RXYA432AAYD* | Ducted Indoor Units | 410000 | 9.2 | 16.8 | 404000 | 3.25 | 312000 | 2.1 | R-32 | 34.1667
218036971 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA240AAYD* |  |  | RXYA456AAYD* | Ducted Indoor Units | 424000 | 9.2 | 17 | 414000 | 3.25 | 314000 | 2.1 | R-32 | 35.3333
218037006 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA216AAYD* |  |  | RXYA432AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 17.9 | 404000 | 3.27 | 312000 | 2.1 | R-32 | 34.1667
218037007 |  | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA240AAYD* |  |  | RXYA456AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.3 | 18 | 414000 | 3.27 | 314000 | 2.1 | R-32 | 35.3333
218036936 |  | DAIKIN | HMSV-A-CB | RXYA240AAYD* | RXYA240AAYD* |  |  | RXYA480AAYD* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.4 | 418000 | 3.25 | 320000 | 2.1 | R-32 | 36.3333
218037017 |  | DAIKIN | HMSR-A-CB | REYA120AATJ* | REYA144AATJ* |  |  | REYA264AATJ* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 252000 | 3.7 | 168000 | 2.2 | R-32 | 21
218037053 |  | DAIKIN | HMSR-A-CB | REYA120AATJ* | REYA144AATJ* |  |  | REYA264AATJ* | Ducted Indoor Units | 252000 | 10.2 | 18.4 | 252000 | 3.25 | 168000 | 2.2 | R-32 | 21
218037089 |  | DAIKIN | HMSR-A-CB | REYA120AATJ* | REYA144AATJ* |  |  | REYA264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20 | 252000 | 3.47 | 168000 | 2.2 | R-32 | 21
218037090 |  | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA144AATJ* |  |  | REYA288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.7 | 274000 | 3.35 | 194000 | 2.15 | R-32 | 22.8333
218037091 |  | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA168AATJ* |  |  | REYA312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19.3 | 296000 | 3.3 | 212000 | 2.15 | R-32 | 24.6667
218037054 |  | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA144AATJ* |  |  | REYA288AATJ* | Ducted Indoor Units | 274000 | 10.4 | 18.4 | 274000 | 3.25 | 194000 | 2.1 | R-32 | 22.8333
218037018 |  | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA144AATJ* |  |  | REYA288AATJ* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 274000 | 3.45 | 194000 | 2.2 | R-32 | 22.8333
218037019 |  | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA168AATJ* |  |  | REYA312AATJ* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.6 | 296000 | 3.4 | 212000 | 2.2 | R-32 | 24.6667
218037020 |  | DAIKIN | HMSR-A-CB | REYA168AATJ* | REYA168AATJ* |  |  | REYA336AATJ* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.8 | 310000 | 3.4 | 222000 | 2.1 | R-32 | 26.3333
218037021 |  | DAIKIN | HMSR-A-CB | REYA168AATJ* | REYA192AATJ* |  |  | REYA360AATJ* | Non-Ducted Indoor Units | 342000 | 10.5 | 18.9 | 342000 | 3.4 | 244000 | 2.1 | R-32 | 28.5
218037092 |  | DAIKIN | HMSR-A-CB | REYA168AATJ* | REYA168AATJ* |  |  | REYA336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.75 | 310000 | 3.3 | 222000 | 2.1 | R-32 | 26.3333
218037093 |  | DAIKIN | HMSR-A-CB | REYA168AATJ* | REYA192AATJ* |  |  | REYA360AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.1 | 18.15 | 342000 | 3.3 | 244000 | 2.1 | R-32 | 28.5
218037094 |  | DAIKIN | HMSR-A-CB | REYA192AATJ* | REYA192AATJ* |  |  | REYA384AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.2 | 19.35 | 364000 | 3.27 | 264000 | 2.1 | R-32 | 30.3333
218037095 |  | DAIKIN | HMSR-A-CB | REYA192AATJ* | REYA216AATJ* |  |  | REYA408AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.85 | 18.55 | 388000 | 3.27 | 288000 | 2.1 | R-32 | 32.3333
218037022 |  | DAIKIN | HMSR-A-CB | REYA192AATJ* | REYA192AATJ* |  |  | REYA384AATJ* | Non-Ducted Indoor Units | 364000 | 10.5 | 20.7 | 364000 | 3.35 | 264000 | 2.1 | R-32 | 30.3333
218037023 |  | DAIKIN | HMSR-A-CB | REYA192AATJ* | REYA216AATJ* |  |  | REYA408AATJ* | Non-Ducted Indoor Units | 388000 | 10 | 19.9 | 388000 | 3.35 | 288000 | 2.1 | R-32 | 32.3333
218037024 |  | DAIKIN | HMSR-A-CB | REYA216AATJ* | REYA216AATJ* |  |  | REYA432AATJ* | Non-Ducted Indoor Units | 410000 | 9.8 | 18.8 | 404000 | 3.3 | 312000 | 2.1 | R-32 | 34.1667
218037025 |  | DAIKIN | HMSR-A-CB | REYA216AATJ* | REYA240AATJ* |  |  | REYA456AATJ* | Non-Ducted Indoor Units | 434000 | 9.4 | 18.3 | 414000 | 3.3 | 314000 | 2.1 | R-32 | 36.1667
218037096 |  | DAIKIN | HMSR-A-CB | REYA216AATJ* | REYA216AATJ* |  |  | REYA432AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.55 | 17.8 | 404000 | 3.25 | 312000 | 2.1 | R-32 | 34.1667
218037097 |  | DAIKIN | HMSR-A-CB | REYA216AATJ* | REYA240AATJ* |  |  | REYA456AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.2 | 17.25 | 414000 | 3.25 | 314000 | 2.1 | R-32 | 36.1667
218037035 |  | DAIKIN | HMSR-A-CB | REYA120AAYD* | REYA144AAYD* |  |  | REYA264AAYD* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 252000 | 3.7 | 168000 | 2.2 | R-32 | 21
218037071 |  | DAIKIN | HMSR-A-CB | REYA120AAYD* | REYA144AAYD* |  |  | REYA264AAYD* | Ducted Indoor Units | 252000 | 10.2 | 18.4 | 252000 | 3.25 | 168000 | 2.2 | R-32 | 21
218037107 |  | DAIKIN | HMSR-A-CB | REYA120AAYD* | REYA144AAYD* |  |  | REYA264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20 | 252000 | 3.47 | 168000 | 2.2 | R-32 | 21
218037108 |  | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA144AAYD* |  |  | REYA288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.7 | 274000 | 3.35 | 194000 | 2.15 | R-32 | 22.8333
218037109 |  | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA168AAYD* |  |  | REYA312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19.3 | 296000 | 3.3 | 212000 | 2.15 | R-32 | 24.6667
218037072 |  | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA144AAYD* |  |  | REYA288AAYD* | Ducted Indoor Units | 274000 | 10.4 | 18.4 | 274000 | 3.25 | 194000 | 2.1 | R-32 | 22.8333
218037036 |  | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA144AAYD* |  |  | REYA288AAYD* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 274000 | 3.45 | 194000 | 2.2 | R-32 | 22.8333
218037037 |  | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA168AAYD* |  |  | REYA312AAYD* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.6 | 296000 | 3.4 | 212000 | 2.2 | R-32 | 24.6667
218037038 |  | DAIKIN | HMSR-A-CB | REYA168AAYD* | REYA168AAYD* |  |  | REYA336AAYD* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.8 | 310000 | 3.4 | 222000 | 2.1 | R-32 | 26.3333
218037039 |  | DAIKIN | HMSR-A-CB | REYA168AAYD* | REYA192AAYD* |  |  | REYA360AAYD* | Non-Ducted Indoor Units | 342000 | 10.5 | 18.9 | 342000 | 3.4 | 244000 | 2.1 | R-32 | 28.5
218037110 |  | DAIKIN | HMSR-A-CB | REYA168AAYD* | REYA168AAYD* |  |  | REYA336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.75 | 310000 | 3.3 | 222000 | 2.1 | R-32 | 26.3333
218037111 |  | DAIKIN | HMSR-A-CB | REYA168AAYD* | REYA192AAYD* |  |  | REYA360AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.1 | 18.15 | 342000 | 3.3 | 244000 | 2.1 | R-32 | 28.5
218037112 |  | DAIKIN | HMSR-A-CB | REYA192AAYD* | REYA192AAYD* |  |  | REYA384AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.2 | 19.35 | 364000 | 3.27 | 264000 | 2.1 | R-32 | 30.3333
218037113 |  | DAIKIN | HMSR-A-CB | REYA192AAYD* | REYA216AAYD* |  |  | REYA408AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.85 | 18.55 | 388000 | 3.27 | 288000 | 2.1 | R-32 | 32.3333
218037040 |  | DAIKIN | HMSR-A-CB | REYA192AAYD* | REYA192AAYD* |  |  | REYA384AAYD* | Non-Ducted Indoor Units | 364000 | 10.5 | 20.7 | 364000 | 3.35 | 264000 | 2.1 | R-32 | 30.3333
218037041 |  | DAIKIN | HMSR-A-CB | REYA192AAYD* | REYA216AAYD* |  |  | REYA408AAYD* | Non-Ducted Indoor Units | 388000 | 10 | 19.9 | 388000 | 3.35 | 288000 | 2.1 | R-32 | 32.3333
218037042 |  | DAIKIN | HMSR-A-CB | REYA216AAYD* | REYA216AAYD* |  |  | REYA432AAYD* | Non-Ducted Indoor Units | 410000 | 9.8 | 18.8 | 404000 | 3.3 | 312000 | 2.1 | R-32 | 34.1667
218037043 |  | DAIKIN | HMSR-A-CB | REYA216AAYD* | REYA240AAYD* |  |  | REYA456AAYD* | Non-Ducted Indoor Units | 434000 | 9.4 | 18.3 | 414000 | 3.3 | 314000 | 2.1 | R-32 | 36.1667
218037114 |  | DAIKIN | HMSR-A-CB | REYA216AAYD* | REYA216AAYD* |  |  | REYA432AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.55 | 17.8 | 404000 | 3.25 | 312000 | 2.1 | R-32 | 34.1667
218037115 |  | DAIKIN | HMSR-A-CB | REYA216AAYD* | REYA240AAYD* |  |  | REYA456AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.2 | 17.25 | 414000 | 3.25 | 314000 | 2.1 | R-32 | 36.1667
213894856 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P432YSNU-A | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
214094553 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S | TVAHR144B52S |  | TVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094405 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094505 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S | HVAHR144B52S |  | HVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094357 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094601 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S | YVAHR144B52S |  | YVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094453 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091771 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S | TVAHP144B52S |  | TVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091623 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091723 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S | HVAHP144B52S |  | HVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091575 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091819 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S | YVAHP144B52S |  | YVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091671 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
213895940 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* | REYQ144AATJ* |  |  | REYQ264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.65 | 19.6 | 252000 | 3.45 | 168000 | 2.2 | R-410A | 21
213895899 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* | REYQ144AATJ* |  |  | REYQ264AATJ* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.2 | 252000 | 3.7 | 168000 | 2.2 | R-410A | 21
213895900 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ144AATJ* |  |  | REYQ288AATJ* | Non-Ducted Indoor Units | 274000 | 11.4 | 20.7 | 274000 | 3.4 | 194000 | 2.2 | R-410A | 22.8333
213895901 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ168AATJ* |  |  | REYQ312AATJ* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.4 | 296000 | 3.4 | 212000 | 2.2 | R-410A | 24.6667
213895941 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ144AATJ* |  |  | REYQ288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.25 | 274000 | 3.3 | 194000 | 2.15 | R-410A | 22.8333
213895942 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ168AATJ* |  |  | REYQ312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19 | 296000 | 3.3 | 212000 | 2.15 | R-410A | 24.6667
213895943 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* | REYQ168AATJ* |  |  | REYQ336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.5 | 310000 | 3.3 | 222000 | 2.1 | R-410A | 26.3333
213895902 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* | REYQ168AATJ* |  |  | REYQ336AATJ* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.7 | 310000 | 3.4 | 222000 | 2.1 | R-410A | 26.3333
213895910 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* | REYQ144AAYD* |  |  | REYQ264AAYD* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.2 | 252000 | 3.7 | 168000 | 2.2 | R-410A | 21
213895950 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* | REYQ144AAYD* |  |  | REYQ264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.65 | 19.6 | 252000 | 3.45 | 168000 | 2.2 | R-410A | 21
213895951 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ144AAYD* |  |  | REYQ288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.25 | 274000 | 3.3 | 194000 | 2.15 | R-410A | 22.8333
213895952 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ168AAYD* |  |  | REYQ312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19 | 296000 | 3.3 | 212000 | 2.15 | R-410A | 24.6667
213895911 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ144AAYD* |  |  | REYQ288AAYD* | Non-Ducted Indoor Units | 274000 | 11.4 | 20.7 | 274000 | 3.4 | 194000 | 2.2 | R-410A | 22.8333
213895912 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ168AAYD* |  |  | REYQ312AAYD* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.4 | 296000 | 3.4 | 212000 | 2.2 | R-410A | 24.6667
213895913 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* | REYQ168AAYD* |  |  | REYQ336AAYD* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.7 | 310000 | 3.4 | 222000 | 2.1 | R-410A | 26.3333
213895953 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* | REYQ168AAYD* |  |  | REYQ336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.5 | 310000 | 3.3 | 222000 | 2.1 | R-410A | 26.3333
216602567 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602573 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602579 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602585 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602497 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602503 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602510 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602517 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602380 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602389 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602398 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602407 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893961 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893965 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893969 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893999 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894003 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213894007 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894011 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213893897 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893901 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893905 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893909 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893957 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893913 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM240BXVGFH |  |  | AM360BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213893973 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM240BXVGFH |  |  | AM360BXVGFH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213916436 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM144BXVGFH | AM192BXVGFH |  | AM456BXVGFH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602417 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC240S4M-4Y |  |  | VPC360S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602524 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC240S4M-4Y |  |  | VPC360S4M-4Y | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602612 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602647 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602654 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC144S4M-4Y | VPC192S4M-4Y |  | VPC456S4M-4Y | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602688 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602605 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602598 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602426 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602435 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602537 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602531 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213894023 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
213893917 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893921 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213894019 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213893977 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893981 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602384 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602411 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602403 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602394 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602582 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602576 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602570 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602507 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602500 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602521 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602514 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602588 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213893971 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893967 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893963 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213894013 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213894001 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894009 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894005 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213893911 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893907 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893903 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893899 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893959 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893915 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM240BXVGJH |  |  | AM360BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213893975 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM240BXVGJH |  |  | AM360BXVGJH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213916438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM144BXVGJH | AM192BXVGJH |  | AM456BXVGJH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602613 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602651 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602657 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC144S4M-4G | VPC192S4M-4G |  | VPC456S4M-4G | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602694 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602528 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC240S4M-4G |  |  | VPC360S4M-4G | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602421 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC240S4M-4G |  |  | VPC360S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602608 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602602 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602438 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602430 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602540 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602534 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893919 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893923 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213894021 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213894025 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
213893983 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213893979 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602382 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602409 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602391 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602400 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602568 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602574 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602580 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602587 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602499 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602505 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602512 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602519 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893970 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893962 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893966 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213894012 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213894000 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894004 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213894008 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213893898 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893902 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893906 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893910 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893958 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893914 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM240BXVGFR |  |  | AM360BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213893974 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM240BXVGFR |  |  | AM360BXVGFR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213916437 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM144BXVGFR | AM192BXVGFR |  | AM456BXVGFR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
213916433 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
213918753 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
213893985 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602526 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4Y |  |  | VRC360S4M-4Y | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602544 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602419 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4Y |  |  | VRC360S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602649 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602656 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC144S4M-4Y | VRC192S4M-4Y |  | VRC456S4M-4Y | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602691 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602600 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602607 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602428 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602436 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602539 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602532 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213894024 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
213893918 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893922 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213894020 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213893978 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893982 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602386 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602414 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602405 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602396 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602584 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602578 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602571 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602508 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602502 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602523 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602515 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602590 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213893972 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893968 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893964 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213894014 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213894002 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894010 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894006 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213893912 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893908 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893904 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893900 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893960 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893916 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM240BXVGJR |  |  | AM360BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213893976 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM240BXVGJR |  |  | AM360BXVGJR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213916439 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM144BXVGJR | AM192BXVGJR |  | AM456BXVGJR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602652 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Non-Ducted Indoor Units | 412000 | 9.3 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602659 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC144S4M-4G | VRC192S4M-4G |  | VRC456S4M-4G | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602696 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.3 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602529 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC240S4M-4G |  |  | VRC360S4M-4G | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602546 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602423 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC240S4M-4G |  |  | VRC360S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602603 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602610 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602441 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602432 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602542 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602535 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893920 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893924 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213894022 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213894026 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
213893984 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213893980 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213916344 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916337 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916869 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916870 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916338 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916345 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916339 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
213916365 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916871 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916873 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916875 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
213916372 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916383 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916880 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916881 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916384 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916373 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916374 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
213916385 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916882 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916884 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916886 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
214091739 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S | TVAHP144B32S |  | TVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091591 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091755 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S | TVAHP144B42S |  | TVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091607 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091691 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S | HVAHP144B32S |  | HVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091543 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091707 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S | HVAHP144B42S |  | HVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091559 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091787 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S | YVAHP144B32S |  | YVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091639 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091803 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S | YVAHP144B42S |  | YVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091655 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094489 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S | HVAHR144B42S |  | HVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094341 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094569 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S | YVAHR144B32S |  | YVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094421 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094585 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S | YVAHR144B42S |  | YVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094521 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S | TVAHR144B32S |  | TVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094373 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094537 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S | TVAHR144B42S |  | TVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094389 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094473 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S | HVAHR144B32S |  | HVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094325 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094437 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
213893582 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893583 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893590 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893591 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893598 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893599 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213916547 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916548 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916549 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916562 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916563 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916564 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893602 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893603 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893586 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893587 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893606 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893607 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916550 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916565 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893610 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893611 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893621 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893613 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893617 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213916551 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916552 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916553 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213894835 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894839 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213894847 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213894849 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213894841 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213894837 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213916566 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916567 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916568 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213893619 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893615 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893623 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893625 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213916554 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213894855 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213894857 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213916569 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213893627 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893476 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893477 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893484 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893485 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893492 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893493 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213916501 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916502 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916503 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916520 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916521 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916522 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893488 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893489 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893496 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893497 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893480 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893481 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893500 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893501 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916504 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916523 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893504 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893505 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893515 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893508 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893509 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893519 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213916505 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916506 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916507 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213894843 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213894851 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213894853 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213894845 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213916524 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916525 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916526 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213893517 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893512 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893513 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893521 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893837 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916508 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894861 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213894860 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213916527 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893839 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916741 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916745 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916749 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893746 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893747 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893750 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893751 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893754 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893755 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893756 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893757 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893752 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893753 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893748 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893749 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213916747 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916743 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916751 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916753 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893758 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893759 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893760 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893761 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916755 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916757 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916761 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916765 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213894936 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213894944 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213893762 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893763 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893766 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893768 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893769 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893767 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893764 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893765 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213894945 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213894937 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213916763 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916759 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916767 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213916769 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894953 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213893849 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893850 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894954 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213916771 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916822 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916826 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916830 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893797 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893798 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893801 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893802 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893805 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893806 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893807 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893808 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893803 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893804 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893799 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893800 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213916832 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916828 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916824 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916834 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893809 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893810 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893811 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893812 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916836 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916838 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916842 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916846 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213894946 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213894930 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894938 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213893813 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893815 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893817 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893818 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893816 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893814 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213894939 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213894931 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894947 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213916848 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213916844 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916840 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916850 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213894948 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213893819 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893820 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213894882 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213916852 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213896090 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 | PURY-EP144YNU-A1 |  |  | PURY-EP288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213895970 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 | PURY-EP120YNU-A1 |  |  | PURY-EP264YSNU-A1 | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050126 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 | PURY-EP168YNU-A1 |  |  | PURY-EP336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896088 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 | PURY-EP144TNU-A1 |  |  | PURY-EP288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213895968 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 | PURY-EP120TNU-A1 |  |  | PURY-EP264TSNU-A1 | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050124 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 | PURY-EP168TNU-A1 |  |  | PURY-EP336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896178 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN | TURYE1444AN41AN |  |  | TURYE2884BN41AN | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213896034 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN | TURYE1204AN41AN |  |  | TURYE2644BN41AN | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050340 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN | TURYE1684AN41AN |  |  | TURYE3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896176 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN | TURYE1443AN41AN |  |  | TURYE2883BN41AN | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213896032 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN | TURYE1203AN41AN |  |  | TURYE2643BN41AN | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050338 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN | TURYE1683AN41AN |  |  | TURYE3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896326 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Ducted Indoor Units | 252000 | 11.3 | 18.2 | 280000 | 3.47 | 200000 | 2.52 | R-410A | 21
213896330 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Ducted Indoor Units | 298000 | 11 | 17.3 | 334000 | 3.46 | 236000 | 2.43 | R-410A | 24.8333
213896328 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Ducted Indoor Units | 276000 | 11.1 | 18.1 | 308000 | 3.49 | 216000 | 2.53 | R-410A | 23
213896288 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Non-Ducted Indoor Units | 252000 | 10.8 | 19 | 280000 | 3.62 | 200000 | 2.16 | R-410A | 21
213896289 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Non-Ducted Indoor Units | 276000 | 10.6 | 18.9 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 23
213896290 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Non-Ducted Indoor Units | 298000 | 10 | 17.5 | 334000 | 3.59 | 236000 | 2.22 | R-410A | 24.8333
213916485 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.05 | 18.6 | 280000 | 3.54 | 200000 | 2.34 | R-410A | 21
213916486 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.85 | 18.5 | 308000 | 3.54 | 216000 | 2.37 | R-410A | 23
213916487 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.5 | 17.4 | 334000 | 3.52 | 236000 | 2.32 | R-410A | 24.8333
213916488 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 17.65 | 360000 | 3.42 | 268000 | 2.25 | R-410A | 26.6667
213896291 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Non-Ducted Indoor Units | 320000 | 10.1 | 17.4 | 360000 | 3.42 | 268000 | 2.13 | R-410A | 26.6667
213896332 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Ducted Indoor Units | 320000 | 10.9 | 17.9 | 360000 | 3.42 | 268000 | 2.38 | R-410A | 26.6667
213896334 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P360ZSKMU-B | Ducted Indoor Units | 344000 | 10.8 | 17.4 | 386000 | 3.32 | 284000 | 2.32 | R-410A | 28.6667
213916489 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P360ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 17.1 | 386000 | 3.36 | 284000 | 2.18 | R-410A | 28.6667
213916355 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916348 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916891 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916892 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916349 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916356 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916350 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
213916398 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916893 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916895 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916897 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
6687539 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
207742258 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
6687541 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
6687542 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
6687543 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
7850818 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
7850820 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
7850821 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
7850822 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
7850838 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
7850840 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
7850841 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
7850842 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
213894090 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 77000 | 4.46 | 56000 | 2.94 | R-410A | 5.75
213895002 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.23 | 56000 | 2.88 | R-410A | 5.75
213894109 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 22.1 | 77000 | 4.01 | 56000 | 2.82 | R-410A | 5.75
213894116 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Ducted Indoor Units | 92000 | 12 | 21.9 | 103000 | 3.83 | 76000 | 2.61 | R-410A | 7.6667
213895006 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.8 | 103000 | 4.02 | 76000 | 2.66 | R-410A | 7.6667
213894091 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Non-Ducted Indoor Units | 92000 | 11.8 | 23.7 | 103000 | 4.21 | 76000 | 2.72 | R-410A | 7.6667
213894092 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 129000 | 4.09 | 92000 | 2.85 | R-410A | 9.5
213895010 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 22 | 129000 | 3.96 | 92000 | 2.81 | R-410A | 9.5
213894123 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Ducted Indoor Units | 114000 | 11.7 | 21.2 | 129000 | 3.83 | 92000 | 2.78 | R-410A | 9.5
213895004 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.15 | 23.6 | 77000 | 4.37 | 64000 | 2.84 | R-410A | 5.75
213894107 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Non-Ducted Indoor Units | 69000 | 13.6 | 24.4 | 77000 | 4.52 | 64000 | 2.91 | R-410A | 5.75
213894111 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Ducted Indoor Units | 69000 | 12.7 | 22.8 | 77000 | 4.23 | 64000 | 2.78 | R-410A | 5.75
213894114 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Non-Ducted Indoor Units | 92000 | 12.1 | 23.4 | 103000 | 4.49 | 87000 | 2.84 | R-410A | 7.6667
213894118 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Ducted Indoor Units | 92000 | 11.8 | 20 | 103000 | 4.22 | 87000 | 2.73 | R-410A | 7.6667
213895008 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 21.7 | 103000 | 4.35 | 87000 | 2.78 | R-410A | 7.6667
213895012 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.05 | 129000 | 4.02 | 116000 | 2.55 | R-410A | 9.5
213894121 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Non-Ducted Indoor Units | 114000 | 11.2 | 22.7 | 129000 | 4.13 | 116000 | 2.51 | R-410A | 9.5
213894125 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Ducted Indoor Units | 114000 | 12 | 21.4 | 129000 | 3.92 | 116000 | 2.59 | R-410A | 9.5
213894110 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 22.1 | 77000 | 4.01 | 56000 | 2.82 | R-410A | 5.75
213894106 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 77000 | 4.46 | 56000 | 2.94 | R-410A | 5.75
213895003 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.23 | 56000 | 2.88 | R-410A | 5.75
213895007 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.8 | 103000 | 4.02 | 76000 | 2.66 | R-410A | 7.6667
213894117 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Ducted Indoor Units | 92000 | 12 | 21.9 | 103000 | 3.83 | 76000 | 2.61 | R-410A | 7.6667
213894113 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Non-Ducted Indoor Units | 92000 | 11.8 | 23.7 | 103000 | 4.21 | 76000 | 2.72 | R-410A | 7.6667
213894124 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Ducted Indoor Units | 114000 | 11.7 | 21.2 | 129000 | 3.83 | 92000 | 2.78 | R-410A | 9.5
213894120 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 129000 | 4.09 | 92000 | 2.85 | R-410A | 9.5
213895011 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 22 | 129000 | 3.96 | 92000 | 2.81 | R-410A | 9.5
213895005 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.15 | 23.6 | 77000 | 4.37 | 64000 | 2.84 | R-410A | 5.75
213894112 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Ducted Indoor Units | 69000 | 12.7 | 22.8 | 77000 | 4.23 | 64000 | 2.78 | R-410A | 5.75
213894108 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Non-Ducted Indoor Units | 69000 | 13.6 | 24.4 | 77000 | 4.52 | 64000 | 2.91 | R-410A | 5.75
213894115 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Non-Ducted Indoor Units | 92000 | 12.1 | 23.4 | 103000 | 4.49 | 87000 | 2.84 | R-410A | 7.6667
213894119 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Ducted Indoor Units | 92000 | 11.8 | 20 | 103000 | 4.22 | 87000 | 2.73 | R-410A | 7.6667
213895009 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 21.7 | 103000 | 4.35 | 87000 | 2.78 | R-410A | 7.6667
213895013 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.05 | 129000 | 4.02 | 116000 | 2.55 | R-410A | 9.5
213894122 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Non-Ducted Indoor Units | 114000 | 11.2 | 22.7 | 129000 | 4.13 | 116000 | 2.51 | R-410A | 9.5
213894126 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Ducted Indoor Units | 114000 | 12 | 21.4 | 129000 | 3.92 | 116000 | 2.59 | R-410A | 9.5
202583512 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Non-Ducted Indoor Units | 92000 | 11.6 | 23.1 | 103000 | 3.87 | 73000 | 2.52 | R-410A | 7.6667
202583511 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Non-Ducted Indoor Units | 69000 | 12.1 | 23.9 | 77000 | 4.19 | 56000 | 2.64 | R-410A | 5.75
202583513 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Non-Ducted Indoor Units | 114000 | 11.6 | 24.2 | 129000 | 3.77 | 87000 | 2.42 | R-410A | 9.5
202882193 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202882194 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202891635 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918830 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202891636 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202883243 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883244 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202883245 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883246 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202891643 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918941 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918942 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918943 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918938 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918939 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918940 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202891644 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202883247 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883248 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202891633 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891634 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202897134 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918839 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918836 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918837 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918838 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202897135 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202891637 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891638 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202891639 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891640 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202897136 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918947 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918948 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918949 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918944 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918945 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918946 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202897137 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202891641 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891642 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202897138 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897139 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202897176 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918845 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918846 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918847 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918842 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918843 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918844 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897177 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897144 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897145 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202897146 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897147 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202897178 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918953 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918954 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918955 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918950 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918951 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918952 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897179 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897148 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897149 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
213893630 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A |  |  |  | PUHY-P72YNU-A | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213916633 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A |  |  |  | PUHY-P72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916634 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893636 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893637 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213893628 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A |  |  |  | PUHY-P72TNU-A | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213916594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A |  |  |  | PUHY-P72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893632 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893633 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213893526 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893527 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916609 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916610 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893534 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893535 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916570 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893522 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893523 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893530 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893531 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916571 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916627 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893842 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893559 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893564 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893565 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916628 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916629 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893542 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893543 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893558 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893827 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213916588 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916589 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893560 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893561 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893538 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893539 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213916590 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916795 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN |  |  |  | TUHYP0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213893703 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN |  |  |  | TUHYP0724AN40AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893706 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893707 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916799 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916793 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN |  |  |  | TUHYP0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213893702 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN |  |  |  | TUHYP0723AN40AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893704 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893705 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916797 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916700 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893642 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893643 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893646 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893647 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916704 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916698 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893640 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893641 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893644 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893645 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916702 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916774 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893682 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893683 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893686 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893687 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916778 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916782 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893690 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893691 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893688 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893689 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893684 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893685 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893680 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893681 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213916780 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916776 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916772 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213896013 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A |  |  |  | PURY-P72YNU-A | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896149 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A |  |  |  | PURY-P72YNU-A | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896153 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A |  |  |  | PURY-P96YNU-A | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896147 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A |  |  |  | PURY-P72TNU-A | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896011 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A |  |  |  | PURY-P72TNU-A | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896151 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A |  |  |  | PURY-P96TNU-A | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896061 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN40AN |  |  |  | TURYP0724AN40AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896205 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN40AN |  |  |  | TURYP0724AN40AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896209 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN40AN |  |  |  | TURYP0964AN40AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896203 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN40AN |  |  |  | TURYP0723AN40AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896059 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN40AN |  |  |  | TURYP0723AN40AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896207 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN40AN |  |  |  | TURYP0963AN40AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896101 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A |  |  |  | PURY-EP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895981 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A |  |  |  | PURY-EP72YNU-A | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896105 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A |  |  |  | PURY-EP96YNU-A | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896099 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A |  |  |  | PURY-EP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895979 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A |  |  |  | PURY-EP72TNU-A | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896103 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A |  |  |  | PURY-EP96TNU-A | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896157 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN40AN |  |  |  | TURYE0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896021 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN40AN |  |  |  | TURYE0724AN40AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896161 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN |  |  |  | TURYE0964AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896155 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN40AN |  |  |  | TURYE0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896019 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN40AN |  |  |  | TURYE0723AN40AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896159 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN |  |  |  | TURYE0963AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896128 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A |  |  |  | PURY-HP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895997 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A |  |  |  | PURY-HP72YNU-A | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896001 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A |  |  |  | PURY-HP96YNU-A | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896133 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A |  |  |  | PURY-HP96YNU-A | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896125 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A |  |  |  | PURY-HP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895995 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A |  |  |  | PURY-HP72TNU-A | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213895999 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A |  |  |  | PURY-HP96TNU-A | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896131 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A |  |  |  | PURY-HP96TNU-A | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896189 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN |  |  |  | TURYH0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896045 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN |  |  |  | TURYH0724AN40AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896049 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN |  |  |  | TURYH0964AN40AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896193 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN |  |  |  | TURYH0964AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896187 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN |  |  |  | TURYH0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896043 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN |  |  |  | TURYH0723AN40AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896047 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN |  |  |  | TURYH0963AN40AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896191 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN |  |  |  | TURYH0963AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
205818928 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205811858 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205811859 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205811954 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205818832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205818833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205818834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205818835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205811955 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205811860 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205811861 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205818929 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205818930 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205811862 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205811863 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205811956 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205818836 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205818837 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205818838 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205818839 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205811957 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205811864 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205811865 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205818931 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205818932 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205811866 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205811867 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205811958 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205818840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205818841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205818842 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205818843 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205811959 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205811868 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205811869 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205818933 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205818934 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205811870 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205811871 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205811960 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205818844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205818845 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205818846 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205818847 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205811961 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205811872 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205811873 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205818935 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205818936 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205811874 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205811875 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205811962 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205818848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205818849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205818850 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205818851 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205811963 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205811876 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205811877 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205818937 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205818938 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205811878 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205811879 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205811964 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205818852 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205818853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205818854 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205818855 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205811965 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205811880 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205811881 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205818939 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
208811482 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Non-Ducted Indoor Units | 69000 | 14.9 | 29 | 77000 | 4.42 | 56000 | 2.65 | R-410A | 5.75
208812532 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Ducted Indoor Units | 69000 | 12.3 | 21.2 | 77000 | 3.77 | 56000 | 2.45 | R-410A | 5.75
208812533 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Ducted Indoor Units | 92000 | 11.7 | 19.9 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
208811483 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Non-Ducted Indoor Units | 92000 | 13.2 | 28 | 103000 | 4 | 73000 | 2.52 | R-410A | 7.6667
208811484 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Non-Ducted Indoor Units | 115000 | 13.5 | 28.4 | 129000 | 3.69 | 87000 | 2.43 | R-410A | 9.5833
208812534 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Ducted Indoor Units | 115000 | 11.3 | 19.8 | 129000 | 3.65 | 87000 | 2.43 | R-410A | 9.5833
208812537 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Ducted Indoor Units | 69000 | 12.3 | 21.2 | 77000 | 3.77 | 56000 | 2.45 | R-410A | 5.75
208811487 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Non-Ducted Indoor Units | 69000 | 14.9 | 29 | 77000 | 4.42 | 56000 | 2.65 | R-410A | 5.75
208811488 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Non-Ducted Indoor Units | 92000 | 13.2 | 28 | 103000 | 4 | 73000 | 2.52 | R-410A | 7.6667
208812538 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Ducted Indoor Units | 92000 | 11.7 | 19.9 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
208812539 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Ducted Indoor Units | 115000 | 11.3 | 19.8 | 129000 | 3.65 | 87000 | 2.43 | R-410A | 9.5833
208811489 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Non-Ducted Indoor Units | 115000 | 13.5 | 28.4 | 129000 | 3.69 | 87000 | 2.43 | R-410A | 9.5833
201830229 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201830230 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850119 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850120 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850236 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850237 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201994655 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201994656 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
202073585 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.22 | 20.57 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
204723036 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
204723037 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
207591014 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
207591015 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
207591016 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
204723038 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
202073586 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 19.94 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
201994657 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201850238 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201850121 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830231 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830261 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201830262 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850151 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850152 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201994705 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201994707 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850268 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850269 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
202073601 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 20.57 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
204723068 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
204723069 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
207591046 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
207591047 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
207591048 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
204723070 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
202073602 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 19.94 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
201850270 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201994709 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201850153 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830263 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830293 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201830294 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850183 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850184 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850300 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850301 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201994758 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201994759 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
202073617 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.75 | 77000 | 3.77 | 54000 | 2.43 | R-410A | 5.75
204723100 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
204723101 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
207591078 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
207591079 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
207591080 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
204723102 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
202073618 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.7 | 21.1 | 103000 | 3.5 | 72000 | 2.31 | R-410A | 7.6667
201994761 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201850302 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201850185 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201830295 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1* | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201830319 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201830320 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850209 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850210 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201994802 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201994804 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850326 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850327 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
202073630 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.75 | 77000 | 3.77 | 54000 | 2.43 | R-410A | 5.75
204723126 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
204723127 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
207591104 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
207591105 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
207591106 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
204723128 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
202073631 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.7 | 21.1 | 103000 | 3.5 | 72000 | 2.31 | R-410A | 7.6667
201850328 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201994806 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201850211 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201830321 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1* | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
9990279 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
9990277 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
9990278 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
211123650 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
213884896 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 56000 | 2.7 | R-410A | 5.75
213884892 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 56000 | 2.8 | R-410A | 5.75
213885174 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 56000 | 2.75 | R-410A | 5.75
213885178 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL |  |  |  | MMY-MUP0961FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 23.6 | 103000 | 4.16 | 74000 | 2.65 | R-410A | 7.6667
213884900 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL |  |  |  | MMY-MUP0961FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.1 | 26 | 103000 | 4.45 | 74000 | 2.7 | R-410A | 7.6667
213884908 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Non-Ducted Indoor Units | 115000 | 12.1 | 24.6 | 129000 | 4.2 | 92000 | 2.68 | R-410A | 9.5833
213884912 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Ducted Indoor Units | 115000 | 11.6 | 22 | 129000 | 3.84 | 92000 | 2.44 | R-410A | 9.5833
213885182 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.3 | 129000 | 4.02 | 92000 | 2.56 | R-410A | 9.5833
213884898 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 64000 | 2.7 | R-410A | 5.75
213884894 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 64000 | 2.8 | R-410A | 5.75
213885175 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 64000 | 2.75 | R-410A | 5.75
213885179 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 23.45 | 103000 | 4.45 | 86000 | 2.82 | R-410A | 7.6667
213884906 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Ducted Indoor Units | 92000 | 12.2 | 21.6 | 103000 | 4.1 | 86000 | 2.69 | R-410A | 7.6667
213884902 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Non-Ducted Indoor Units | 92000 | 13.3 | 25.3 | 103000 | 4.8 | 86000 | 2.95 | R-410A | 7.6667
213884914 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Ducted Indoor Units | 115000 | 12 | 22.5 | 129000 | 3.91 | 110000 | 2.58 | R-410A | 9.5833
213884910 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24.8 | 129000 | 4.43 | 110000 | 2.8 | R-410A | 9.5833
213885183 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.2 | 23.65 | 129000 | 4.17 | 110000 | 2.69 | R-410A | 9.5833
213885173 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 56000 | 2.75 | R-410A | 5.75
213884897 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 56000 | 2.7 | R-410A | 5.75
213884893 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 56000 | 2.8 | R-410A | 5.75
213884901 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL |  |  |  | MMY-MUP0961FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.1 | 26 | 103000 | 4.45 | 74000 | 2.7 | R-410A | 7.6667
213885177 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL |  |  |  | MMY-MUP0961FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 23.6 | 103000 | 4.16 | 74000 | 2.65 | R-410A | 7.6667
213885181 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.3 | 129000 | 4.02 | 92000 | 2.56 | R-410A | 9.5833
213884909 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Non-Ducted Indoor Units | 115000 | 12.1 | 24.6 | 129000 | 4.2 | 92000 | 2.68 | R-410A | 9.5833
213884913 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Ducted Indoor Units | 115000 | 11.6 | 22 | 129000 | 3.84 | 92000 | 2.44 | R-410A | 9.5833
213884899 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 64000 | 2.7 | R-410A | 5.75
213884895 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 64000 | 2.8 | R-410A | 5.75
213885176 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 64000 | 2.75 | R-410A | 5.75
213885180 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 23.45 | 103000 | 4.45 | 86000 | 2.82 | R-410A | 7.6667
213884907 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Ducted Indoor Units | 92000 | 12.2 | 21.6 | 103000 | 4.1 | 86000 | 2.69 | R-410A | 7.6667
213884903 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Non-Ducted Indoor Units | 92000 | 13.3 | 25.3 | 103000 | 4.8 | 86000 | 2.95 | R-410A | 7.6667
213884915 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Ducted Indoor Units | 115000 | 12 | 22.5 | 129000 | 3.91 | 110000 | 2.58 | R-410A | 9.5833
213884911 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24.8 | 129000 | 4.43 | 110000 | 2.8 | R-410A | 9.5833
213885184 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.2 | 23.65 | 129000 | 4.17 | 110000 | 2.69 | R-410A | 9.5833
213896311 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-A |  |  |  | PURY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 11.4 | 19.8 | 76000 | 3.46 | 56000 | 2.26 | R-410A | 5.75
213896335 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Ducted Indoor Units | 69000 | 12.3 | 20.2 | 76000 | 3.74 | 56000 | 2.59 | R-410A | 5.75
213896280 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 12.4 | 22.2 | 76000 | 3.85 | 56000 | 2.25 | R-410A | 5.75
213916464 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.2 | 76000 | 3.79 | 56000 | 2.42 | R-410A | 5.75
213916465 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12 | 21.15 | 103000 | 3.73 | 76000 | 2.56 | R-410A | 7.6667
213896281 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Non-Ducted Indoor Units | 92000 | 12.1 | 22.2 | 103000 | 3.74 | 76000 | 2.42 | R-410A | 7.6667
213896336 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.73 | 76000 | 2.71 | R-410A | 7.6667
213896315 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A |  |  |  | PUHY-P120ZKMU-A | Ducted Indoor Units | 115000 | 11.4 | 19.5 | 129000 | 3.62 | 92000 | 2.51 | R-410A | 9.5833
208102077 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
9956607 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
9121821 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
9956601 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER120C432Y |  |  |  | VER120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
208102081 | 1/1/2027 | LENNOX | HMSR-A-CB | VER120C432Y |  |  |  | VER120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
9121814 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-F(U) |  |  |  | GMV-Q120WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
9133443 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
204572298 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799420 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799422 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572306 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
9956574 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
10306439 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) |  |  |  | IOV120H3CDC720(A) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
7849630 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
201874038 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
205281456 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
206453538 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
202515434 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
202515520 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202516169 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
202516171 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
206453540 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
205281459 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
205281462 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
206453543 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
202516175 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
202516176 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
205281458 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
206453539 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
202515521 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202515522 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
202524541 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
202524542 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
206453542 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
205281461 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
205281464 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
206453545 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
202524543 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
202524544 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
10103102 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10103123 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10103129 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10103130 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10103124 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10103103 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10103104 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
10103125 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
10103131 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10103135 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Ducted Indoor Units | 69000 | 13.8 | 20.8 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
10103149 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.8 | 22.4 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
10103108 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10103109 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Non-Ducted Indoor Units | 92000 | 14.6 | 25.1 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
10103150 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.45 | 22.2 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
10103136 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Ducted Indoor Units | 92000 | 12.3 | 19.3 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
10103137 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
10103151 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 21.5 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
10103110 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.1 | 23.4 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
10612440 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612547 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612548 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
212511071 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
212511072 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
212512455 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
212512458 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
212511075 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
212511076 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
10612554 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
10612555 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
10612446 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
10612451 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
10612559 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
10612560 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
212511079 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
212511080 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
212512461 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
212512456 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
212511073 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
212511074 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
10612549 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612550 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
10612441 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612447 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
10612556 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
10612557 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
212511077 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
212511078 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
212512459 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
212512462 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
212511081 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
212511082 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
10612561 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
10612562 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
10612452 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
9133488 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC72K/220V |  |  |  | TVRF-SHC72K/220V | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
9133489 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/220V |  |  |  | TVRF-SHC96K/220V | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
205782688 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/220V |  |  |  | TVRF-SHC96K/220V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
205782689 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC120K/220V |  |  |  | TVRF-SHC120K/220V | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.25 | 22.4 | 126000 | 3.4 | 82000 | 2.25 | R-410A | 9.3333
203360783 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-SHC120K/220V |  |  |  | TVRF-SHC120K/220V | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
212512538 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612442 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612551 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612552 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
9990087 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* |  |  |  | RXYQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
9989439 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* |  |  |  | RXYQ72TATJ* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
9990088 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* |  |  |  | RXYQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
9990029 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* |  |  |  | RXYQ72TAYD* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
9990046 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
9990089 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
9989440 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
9990090 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
9990047 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
9990030 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
9990031 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* |  |  |  | RXYQ120TATJ* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
9990091 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* |  |  |  | RXYQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
9990092 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* |  |  |  | RXYQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
9990048 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* |  |  |  | RXYQ120TAYD* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
9990289 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
9990292 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
9990290 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
9990287 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
9990288 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
9990291 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
202607341 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607353 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607926 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607956 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607365 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607377 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607389 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607980 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607463 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607356 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607344 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607929 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607959 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607380 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607368 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607392 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607983 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607466 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607342 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607354 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607927 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607957 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607366 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607378 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607390 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607981 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607464 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607357 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607345 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607930 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607960 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607381 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607369 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607393 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607984 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607467 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607343 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607355 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607928 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607958 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607367 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607379 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607391 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607982 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607465 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607358 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607346 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607931 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607961 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607382 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607370 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607394 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607985 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607468 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607351 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607363 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607936 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607966 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607387 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607375 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607399 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607990 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607473 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607361 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607349 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607934 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607964 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607373 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607385 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607397 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607988 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607471 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607352 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607364 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607937 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607967 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607388 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607376 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607400 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607991 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607474 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607932 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607359 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607347 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607371 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607383 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607962 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607986 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607469 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607395 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607935 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607350 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607362 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607386 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607374 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607965 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607989 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607472 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607398 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607933 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607360 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607348 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607372 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607384 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607963 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607987 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607470 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607396 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
6687540 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
6691437 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
6691438 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
6687544 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
6691439 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
7502109 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7502110 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7465339 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7465340 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
10594255 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
201847169 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2Y |  |  |  | VRA072H4M-2Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847170 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2Y |  |  |  | VRA072H4M-2Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864466 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864467 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864460 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C6000AA |  |  |  | 4TVR0096C6000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864461 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C6000AA |  |  |  | 4TVR0096C6000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
202073573 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
201847173 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y |  |  |  | VRA096H4M-2Y | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847174 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y |  |  |  | VRA096H4M-2Y | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830205 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847177 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y |  |  |  | VRA120H4M-2Y | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
202073574 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.35 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
201864462 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0115C6000AA |  |  |  | 4TVR0115C6000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864474 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C6000AA |  |  |  | 4TVH0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864475 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C6000AA |  |  |  | 4TVH0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
10594257 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
201847111 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2Y |  |  |  | VPA072H4M-2Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847112 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2Y |  |  |  | VPA072H4M-2Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7465345 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7465346 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574204 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574205 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574206 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574228 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574229 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574230 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574252 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574253 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574254 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574276 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574277 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574278 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574279 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574280 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574281 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574255 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574256 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574257 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574231 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574232 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574233 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574207 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574208 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574209 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
201847115 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y |  |  |  | VPA096H4M-2Y | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847116 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y |  |  |  | VPA096H4M-2Y | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830219 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830220 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864476 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C6000AA |  |  |  | 4TVH0096C6000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864477 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C6000AA |  |  |  | 4TVH0096C6000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
202073579 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073580 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
201864478 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0115C6000AA |  |  |  | 4TVH0115C6000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847120 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y |  |  |  | VPA120H4M-2Y | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201830349 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574210 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574212 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574234 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574236 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574258 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574260 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574282 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574284 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
10594256 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
201847171 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2G |  |  |  | VRA072H4M-2G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847172 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2G |  |  |  | VRA072H4M-2G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7499011 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7499012 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7502097 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7502098 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864458 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864459 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864468 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C4000AA |  |  |  | 4TVR0096C4000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864469 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C4000AA |  |  |  | 4TVR0096C4000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
202073576 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
201847175 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G |  |  |  | VRA096H4M-2G | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847176 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G |  |  |  | VRA096H4M-2G | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830213 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830214 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830215 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847179 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G |  |  |  | VRA120H4M-2G | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
202073577 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.35 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
201864470 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0115C4000AA |  |  |  | 4TVR0115C4000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864482 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C4000AA |  |  |  | 4TVH0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864483 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C4000AA |  |  |  | 4TVH0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
10594258 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
201847109 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2G |  |  |  | VPA072H4M-2G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847110 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2G |  |  |  | VPA072H4M-2G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7499016 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7499017 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574264 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574265 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574266 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574288 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574289 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574290 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574240 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574241 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574242 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574216 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574217 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574218 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574219 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574220 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574221 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574243 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574244 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574245 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574291 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574292 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574293 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574267 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574268 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574269 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
201830224 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830225 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847113 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G |  |  |  | VPA096H4M-2G | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847114 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G |  |  |  | VPA096H4M-2G | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864484 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C4000AA |  |  |  | 4TVH0096C4000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864485 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C4000AA |  |  |  | 4TVH0096C4000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
202073582 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073583 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
201864486 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0115C4000AA |  |  |  | 4TVH0115C4000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201830350 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847118 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G |  |  |  | VPA120H4M-2G | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574270 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574272 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574294 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574296 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574246 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574248 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574222 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574224 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
204442713 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH |  |  |  | AM072FXVAFH | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442728 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH |  |  |  | AM072FXVAJH | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442744 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
205000539 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH |  |  |  | AM120FXVAFH | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
205000540 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH |  |  |  | AM120FXVAJH | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
207382954 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
207385922 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 25.85 | 129000 | 3.43 | 84000 | 2.54 | R-410A | 9.5
205000511 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
205000541 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR |  |  |  | AM120FXVAJR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
207382951 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
207385918 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 25.2 | 77000 | 3.58 | 51000 | 2.59 | R-410A | 5.75
204572223 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204442714 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
206799423 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
206799425 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204442729 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
204572238 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572253 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204442745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
206799424 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
207385920 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 26.55 | 103000 | 3.74 | 67000 | 2.63 | R-410A | 7.6667
207382953 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
206799426 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572268 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
208102003 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
7849628 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
9956564 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10306433 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10306436 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
7849629 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
9956571 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
208102009 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
208102015 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
7850819 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
7850858 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
7850859 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
7850823 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
7850860 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
7850868 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
7850839 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
7850869 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
7850870 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
7850843 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
201874148 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
201874151 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
201874042 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
201874028 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
201874140 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
201874147 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
201874036 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
201874040 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
201874150 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
201874139 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
201874026 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
203297560 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.5 | 21.9 | 76000 | 3.59 | 56000 | 2.26 | R-410A | 5.75
203297561 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
203381260 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 23.5 | 76000 | 3.69 | 56000 | 2.26 | R-410A | 5.75
203381269 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 23.85 | 103000 | 3.52 | 71000 | 2.25 | R-410A | 7.6667
203297571 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 3.49 | 71000 | 2.25 | R-410A | 7.6667
203297572 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
203301897 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
203297456 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.5 | 129000 | 3.49 | 87000 | 2.26 | R-410A | 9.5
203381174 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.55 | 129000 | 3.64 | 87000 | 2.26 | R-410A | 9.5
203381256 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 23.5 | 76000 | 3.69 | 56000 | 2.26 | R-410A | 5.75
203297555 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
203300907 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.5 | 21.9 | 76000 | 3.59 | 56000 | 2.26 | R-410A | 5.75
203300877 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 3.49 | 71000 | 2.25 | R-410A | 7.6667
203297567 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
203381265 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 23.85 | 103000 | 3.52 | 71000 | 2.25 | R-410A | 7.6667
203381170 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.55 | 129000 | 3.64 | 87000 | 2.26 | R-410A | 9.5
203301896 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
203297452 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.5 | 129000 | 3.49 | 87000 | 2.26 | R-410A | 9.5
206799419 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204442775 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
204572282 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572290 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204442783 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
206799421 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799427 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204442776 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
204572283 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204572291 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204442784 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
206799429 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
203993607 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606760 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606763 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993614 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993609 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606761 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606764 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993616 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993611 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606762 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606765 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993618 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
212511003 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
212511024 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
212512523 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
10612394 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
10612437 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
10612546 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
10612553 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
10612443 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
10612396 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
212512524 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
212511025 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
212511004 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
212511005 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
212511026 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
212512525 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
10612398 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
10612448 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
10612558 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
10612438 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
10612439 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
10612395 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
212512454 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
212511039 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
212511061 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
212511062 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
212511040 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
212512457 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
10612397 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
10612444 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
10612445 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
10612449 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
10612450 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
10612399 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
212512460 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
212511041 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
212511063 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
202583515 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Ducted Indoor Units | 92000 | 11.6 | 21.1 | 103000 | 3.66 | 73000 | 2.47 | R-410A | 7.6667
202583518 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.1 | 103000 | 3.76 | 73000 | 2.49 | R-410A | 7.6667
202583514 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Ducted Indoor Units | 69000 | 11.9 | 21.5 | 77000 | 4.01 | 56000 | 2.64 | R-410A | 5.75
202583517 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 4.1 | 56000 | 2.64 | R-410A | 5.75
202583519 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.55 | 129000 | 3.7 | 87000 | 2.38 | R-410A | 9.5
202583516 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Ducted Indoor Units | 114000 | 11.6 | 20.9 | 129000 | 3.64 | 87000 | 2.35 | R-410A | 9.5
203364244 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203334936 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203334986 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203334987 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203334937 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203364245 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203364246 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
203334938 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
203334988 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
203335003 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203334953 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203364261 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203364262 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203334954 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203335004 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203335005 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
203334955 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
203364263 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
203335020 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203364278 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203334970 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203334971 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203364279 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203335021 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203335022 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
203364280 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
203334972 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
204268347 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268408 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204269024 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269025 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204268409 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268350 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268352 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268410 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204269026 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204268424 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268375 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204269040 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269041 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204268376 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268425 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268426 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268378 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204269042 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204268441 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268392 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204269056 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269057 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204268393 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268442 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268443 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268394 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204269058 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204268471 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268557 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204269072 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269073 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204268558 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268472 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268473 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268559 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204269074 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204268495 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268580 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204269088 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269089 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204268581 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268497 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268499 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268582 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204269090 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204268530 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204269104 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204268596 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268597 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204269105 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204268531 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268533 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204269106 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204268598 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204793015 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* |  |  |  | MVHP072ME2CA* | Ducted Indoor Units | 69000 | 12.1 | 21 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793016 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* |  |  |  | MVHP072ME2CA* | Non-Ducted Indoor Units | 69000 | 13.5 | 25 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793017 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* |  |  |  | MVHR072ME2CA* | Ducted Indoor Units | 69000 | 11.9 | 20 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793018 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* |  |  |  | MVHR072ME2CA* | Non-Ducted Indoor Units | 69000 | 13 | 24.5 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793019 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* |  |  |  | MVHP096ME2CA* | Ducted Indoor Units | 92000 | 12.1 | 22.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793020 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* |  |  |  | MVHP096ME2CA* | Non-Ducted Indoor Units | 92000 | 12 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793021 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* |  |  |  | MVHR096ME2CA* | Ducted Indoor Units | 92000 | 11.9 | 21.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793022 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* |  |  |  | MVHR096ME2CA* | Non-Ducted Indoor Units | 92000 | 12.3 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793023 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* |  |  |  | MVHP120ME2CA* | Ducted Indoor Units | 115000 | 12.1 | 23 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793024 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* |  |  |  | MVHP120ME2CA* | Non-Ducted Indoor Units | 115000 | 12.1 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793025 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* |  |  |  | MVHR120ME2CA* | Ducted Indoor Units | 115000 | 11.9 | 21.9 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793026 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* |  |  |  | MVHR120ME2CA* | Non-Ducted Indoor Units | 115000 | 11.9 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
205708872 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
205048202 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
205048203 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
205048204 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Ducted Indoor Units | 92000 | 11.2 | 19 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
205048205 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
205708873 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.5 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
205708874 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/460V |  |  |  | TVRF-OC120KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
205048206 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/460V |  |  |  | TVRF-OC120KHP/460V | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
205048213 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC72K/460V |  |  |  | TVRF-SHC72K/460V | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
205048215 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/460V |  |  |  | TVRF-SHC96K/460V | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
205048217 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC120K/460V |  |  |  | TVRF-SHC120K/460V | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205233054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* |  |  |  | RXYQ72XATJ* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
205234814 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* |  |  |  | RXYQ72XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
205233065 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
205234815 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
205233055 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
205233056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* |  |  |  | RXYQ120XATJ* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205234816 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* |  |  |  | RXYQ120XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
205234819 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* |  |  |  | RXYQ72XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
205233059 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* |  |  |  | RXYQ72XAYD* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
205233060 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
205234820 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
205233070 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
205234821 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* |  |  |  | RXYQ120XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
205233061 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* |  |  |  | RXYQ120XAYD* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205234828 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
205234780 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
205234860 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
205234861 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 21.6 | 103000 | 3.97 | 72000 | 2.49 | R-410A | 7.6667
205234781 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Non-Ducted Indoor Units | 92000 | 13.6 | 24.3 | 103000 | 4.33 | 72000 | 2.66 | R-410A | 7.6667
205234829 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Ducted Indoor Units | 92000 | 11.4 | 18.9 | 103000 | 3.61 | 72000 | 2.32 | R-410A | 7.6667
205234830 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Ducted Indoor Units | 114000 | 11.1 | 19 | 129000 | 3.54 | 88000 | 2.3 | R-410A | 9.5
205234782 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Non-Ducted Indoor Units | 114000 | 12.5 | 23.3 | 129000 | 3.89 | 88000 | 2.58 | R-410A | 9.5
205234862 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 21.15 | 129000 | 3.71 | 88000 | 2.44 | R-410A | 9.5
206568879 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* |  |  |  | MVHP072ME4CA* | Ducted Indoor Units | 69000 | 12.1 | 21 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568881 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* |  |  |  | MVHP072ME4CA* | Non-Ducted Indoor Units | 69000 | 13.5 | 25 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568882 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* |  |  |  | MVHR072ME4CA* | Ducted Indoor Units | 69000 | 11.9 | 20 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568883 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* |  |  |  | MVHR072ME4CA* | Non-Ducted Indoor Units | 69000 | 13 | 24.5 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568885 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* |  |  |  | MVHP096ME4CA* | Ducted Indoor Units | 92000 | 12.1 | 22.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568886 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* |  |  |  | MVHP096ME4CA* | Non-Ducted Indoor Units | 92000 | 12 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568887 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* |  |  |  | MVHR096ME4CA* | Ducted Indoor Units | 92000 | 11.9 | 21.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568888 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* |  |  |  | MVHR096ME4CA* | Non-Ducted Indoor Units | 92000 | 12.3 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568890 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* |  |  |  | MVHP120ME4CA* | Ducted Indoor Units | 115000 | 12.1 | 23 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568891 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* |  |  |  | MVHP120ME4CA* | Non-Ducted Indoor Units | 115000 | 12.1 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568892 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* |  |  |  | MVHR120ME4CA* | Ducted Indoor Units | 115000 | 11.9 | 21.9 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568893 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* |  |  |  | MVHR120ME4CA* | Non-Ducted Indoor Units | 115000 | 11.9 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
207172462 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
207172463 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
207172466 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
210845528 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
210845822 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
210720743 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
208812542 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 25.1 | 77000 | 4.09 | 56000 | 2.55 | R-410A | 5.75
208812543 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.45 | 23.95 | 103000 | 3.86 | 73000 | 2.49 | R-410A | 7.6667
208812544 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.4 | 24.1 | 129000 | 3.67 | 87000 | 2.43 | R-410A | 9.5833
208812547 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 25.1 | 77000 | 4.09 | 56000 | 2.55 | R-410A | 5.75
208812548 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.45 | 23.95 | 103000 | 3.86 | 73000 | 2.49 | R-410A | 7.6667
208812549 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.4 | 24.1 | 129000 | 3.67 | 87000 | 2.43 | R-410A | 9.5833
210691220 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
210713380 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
210713381 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
210691221 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
210691222 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
210691223 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
210691224 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
210691225 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
210691226 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
212924814 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Ducted Indoor Units | 72000 | 12 | 19.5 | 81000 | 3.65 | 52500 | 2.45 | R-410A | 6
212924815 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Non-Ducted Indoor Units | 72000 | 12.5 | 23 | 81000 | 4.25 | 52500 | 2.67 | R-410A | 6
212924829 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 12.25 | 21.25 | 81000 | 3.95 | 52500 | 2.56 | R-410A | 6
212924830 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 96000 | 12.1 | 21.15 | 103000 | 3.9 | 70000 | 2.5 | R-410A | 8
212924816 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Ducted Indoor Units | 96000 | 11.7 | 19.7 | 103000 | 3.75 | 70000 | 2.45 | R-410A | 8
212924817 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Non-Ducted Indoor Units | 96000 | 12.5 | 22.6 | 103000 | 4.05 | 70000 | 2.55 | R-410A | 8
212924818 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Ducted Indoor Units | 120000 | 12 | 20.65 | 129000 | 3.71 | 81000 | 2.4 | R-410A | 10
212924819 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Non-Ducted Indoor Units | 120000 | 12 | 22.1 | 129000 | 3.9 | 81000 | 2.53 | R-410A | 10
212924831 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 120000 | 12 | 21.37 | 129000 | 3.8 | 81000 | 2.46 | R-410A | 10
212924832 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 12.25 | 21.25 | 81000 | 3.95 | 52500 | 2.56 | R-410A | 6
212924821 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Ducted Indoor Units | 72000 | 12 | 19.5 | 81000 | 3.65 | 52500 | 2.45 | R-410A | 6
212924822 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Non-Ducted Indoor Units | 72000 | 12.5 | 23 | 81000 | 4.25 | 52500 | 2.67 | R-410A | 6
212924823 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Ducted Indoor Units | 96000 | 11.7 | 19.7 | 103000 | 3.75 | 70000 | 2.45 | R-410A | 8
212924824 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Non-Ducted Indoor Units | 96000 | 12.5 | 22.6 | 103000 | 4.05 | 70000 | 2.55 | R-410A | 8
212924833 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 96000 | 12.1 | 21.15 | 103000 | 3.9 | 70000 | 2.5 | R-410A | 8
212924834 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 120000 | 12 | 21.37 | 129000 | 3.8 | 81000 | 2.46 | R-410A | 10
212924825 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Ducted Indoor Units | 120000 | 12 | 20.65 | 129000 | 3.71 | 81000 | 2.4 | R-410A | 10
212924826 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Non-Ducted Indoor Units | 120000 | 12 | 22.1 | 129000 | 3.9 | 81000 | 2.53 | R-410A | 10
213500519 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-76H8FH3H2 |  |  |  | AVW-76H8FH3H2 | Non-Ducted Indoor Units | 72000 | 11.6 | 26.5 | 81000 | 3.7 | 52500 | 2.6 | R-410A | 6
213500526 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-76H8FH3H2 |  |  |  | AVW-76H8FH3H2 | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 11.35 | 22.55 | 81000 | 3.55 | 52500 | 2.5 | R-410A | 6
213500518 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-96H8FH3H2 |  |  |  | AVW-96H8FH3H2 | Non-Ducted Indoor Units | 92000 | 11.5 | 25.4 | 103000 | 3.6 | 70000 | 2.4 | R-410A | 7.6667
213500525 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-96H8FH3H2 |  |  |  | AVW-96H8FH3H2 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.25 | 21.75 | 103000 | 3.45 | 70000 | 2.35 | R-410A | 7.6667
10479770 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V96W/A-F(U) |  |  |  | GMV-V96W/A-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 20 | 103000 | 3.5 | 70000 | 2.25 | R-410A | 7.6667
10515237 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10515247 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10515227 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10515228 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10515248 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10515238 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10515239 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10515249 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10515229 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10515230 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10515250 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10515240 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10515241 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
10515251 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10515231 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
10515232 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
10515252 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10515242 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
201856718 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) |  |  |  | MV5-RC72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856719 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) |  |  |  | MV5-RC72DXN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862854 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y |  |  |  | VRA072L4M-2Y | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862855 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y |  |  |  | VRA072L4M-2Y | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862856 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y |  |  |  | VRA096L4M-2Y | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201856720 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) |  |  |  | MV5-RC96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201856722 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) |  |  |  | MV5-RC120DXN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862858 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y |  |  |  | VRA120L4M-2Y | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856742 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) |  |  |  | MV5-RC72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856743 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) |  |  |  | MV5-RC72DZN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862878 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G |  |  |  | VRA072L4M-2G | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862879 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G |  |  |  | VRA072L4M-2G | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862880 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G |  |  |  | VRA096L4M-2G | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201856744 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) |  |  |  | MV5-RC96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201856746 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) |  |  |  | MV5-RC120DZN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862882 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G |  |  |  | VRA120L4M-2G | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862902 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y |  |  |  | VPA072L4M-2Y | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862903 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y |  |  |  | VPA072L4M-2Y | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856766 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) |  |  |  | MV5-XC72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856767 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) |  |  |  | MV5-XC72DXN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856768 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) |  |  |  | MV5-XC96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201862904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y |  |  |  | VPA096L4M-2Y | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201862906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y |  |  |  | VPA120L4M-2Y | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856770 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) |  |  |  | MV5-XC120DXN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856788 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) |  |  |  | MV5-XC72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856789 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) |  |  |  | MV5-XC72DZN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862924 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G |  |  |  | VPA072L4M-2G | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862925 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G |  |  |  | VPA072L4M-2G | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862926 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G |  |  |  | VPA096L4M-2G | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201856790 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) |  |  |  | MV5-XC96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201856792 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) |  |  |  | MV5-XC120DZN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862928 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G |  |  |  | VPA120L4M-2G | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201992872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
202022845 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202022846 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
201992873 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Non-Ducted Indoor Units | 92000 | 13.6 | 24.3 | 103000 | 4.33 | 72000 | 2.66 | R-410A | 7.6667
202022800 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 21.6 | 103000 | 3.97 | 72000 | 2.49 | R-410A | 7.6667
202021882 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Ducted Indoor Units | 92000 | 11.4 | 18.9 | 103000 | 3.61 | 72000 | 2.32 | R-410A | 7.6667
202021883 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Ducted Indoor Units | 114000 | 11.1 | 19 | 129000 | 3.54 | 88000 | 2.3 | R-410A | 9.5
202022801 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 21.15 | 129000 | 3.71 | 88000 | 2.44 | R-410A | 9.5
201992874 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Non-Ducted Indoor Units | 114000 | 12.5 | 23.3 | 129000 | 3.89 | 88000 | 2.58 | R-410A | 9.5
202022813 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
201992879 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
202021864 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202021865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
201992880 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
202022814 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202022815 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
201992871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
202021866 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202021867 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
201993477 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
202022816 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
202022817 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
201993478 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
202021868 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
202021869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
201993173 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
202022818 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
202022819 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
201993479 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
202021870 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
202021871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
201993480 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
202022820 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
202022821 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
201993174 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
202021872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
204442792 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
204572299 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
206799428 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
207699044 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 28.85 | 103000 | 3.95 | 103000 | 2.41 | R-410A | 7.6667
207699040 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
206799430 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204572307 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
9133481 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
201902897 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10267502 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10306463 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
208102000 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
202566095 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
206453576 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
205287345 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
205281457 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
205281460 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
206453541 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
202566098 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
202566099 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
202566100 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
202566101 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
206453544 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
205281463 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
203398521 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72W/A-F(U) |  |  |  | GMV-VQ72W/A-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 21 | 77000 | 3.4 | 60000 | 2.25 | R-410A | 5.75
10479769 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V96W/A-F(U) |  |  |  | GMV-V96W/A-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 21 | 103000 | 3.5 | 68000 | 2.25 | R-410A | 7.6667
10479766 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 21 | 77000 | 3.5 | 60000 | 2.25 | R-410A | 5.75
10479767 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.25 | 20.5 | 77000 | 3.55 | 60000 | 2.25 | R-410A | 5.75
203293238 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Ducted Indoor Units | 69000 | 11.2 | 20 | 77000 | 3.4 | 60000 | 2.25 | R-410A | 5.75
208102083 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432G | VER072C432G |  |  | VER144C432G | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
10341439 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-U(U) | GMV-Q72WM/B-U(U) |  |  | GMV-Q144WM/B-U(U) | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
208102075 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432G |  |  |  | VER096C432G | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
203400954 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-U(U) |  |  |  | GMV-Q120WM/B-U(U) | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
201903147 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER072C432G | VER072C432G |  |  | VER144C432G | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
10341435 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-U(U) |  |  |  | GMV-Q96WM/B-U(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
207337153 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
208102001 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10306464 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10306462 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10267500 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10267501 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
201902894 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
201902896 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
204442791 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
203360784 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V |  |  |  | TVRF-OC120KHP/220V | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
9133449 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9133480 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
204442800 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
202519343 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y72WM/C-F(U) |  |  |  | GMV-Y72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
202519344 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y72WM/C-F(U) |  |  |  | GMV-Y72WM/C-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 22 | 77000 | 3.5 | 51000 | 2.4 | R-410A | 5.75
202519346 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/C-F(U) |  |  |  | GMV-Y96WM/C-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 22 | 103000 | 3.5 | 67000 | 2.3 | R-410A | 7.6667
208102016 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
208102010 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
9956572 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
7835428 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
7845593 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
208102008 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9956570 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
10306437 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
10306434 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10306435 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
10509439 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10509440 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10509441 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
10509442 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
10306432 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
9956563 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
9956565 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
208102004 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
7793597 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
7793598 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
204442760 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
204442759 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR |  |  |  | AM072FXVAJR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
208102002 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
201903141 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432G |  |  |  | VER096C432G | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
9133441 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
9133442 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10509445 | 1/1/2027 | AC PRO.COM | HMSR-A-CB | GMV-Q72WM/B-F(U) |  |  |  | GMV-Q72WM/B-F(U) | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
10342541 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-F(U) | GMV-Q72WM/B-F(U) |  |  | GMV-Q144WM/B-F(U) | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
8849290 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-F(U) |  |  |  | GMV-Q72WM/B-F(U) | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
208102073 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432Y |  |  |  | VER072C432Y | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
208102085 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432Y | VER072C432Y |  |  | VER144C432Y | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
203266414 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266443 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) |  |  |  | IOV120H3CDC720(A) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266444 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266445 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
204442799 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
203266412 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-F(U) |  |  |  | GMV-Q120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
10509447 | 1/1/2027 | AC PRO.COM | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
9956605 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER072C432Y |  |  |  | VER072C432Y | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
9956608 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
208102078 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
8849292 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
6687545 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
207742259 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687547 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687549 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
6687551 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6687553 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850824 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850826 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850828 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
7850830 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850832 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850844 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850846 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850848 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
7850850 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850852 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
213895054 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP1921HT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 22.4 | 206000 | 4 | 154000 | 2.51 | R-410A | 15.3333
213895059 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP1921HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 22.3 | 206000 | 4.13 | 154000 | 2.6 | R-410A | 15.3333
213894095 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 232000 | 4.04 | 164000 | 2.76 | R-410A | 17.1667
213894130 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 21.6 | 154000 | 3.64 | 109000 | 2.53 | R-410A | 11.5
213894136 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Ducted Indoor Units | 206000 | 11.6 | 20.9 | 232000 | 4.01 | 164000 | 2.74 | R-410A | 17.1667
213895014 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.25 | 22.15 | 154000 | 3.78 | 109000 | 2.59 | R-410A | 11.5
213895023 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.15 | 232000 | 4.02 | 164000 | 2.74 | R-410A | 17.1667
213895067 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2401HT6P-UL | Ducted Indoor Units | 230000 | 11.2 | 19.9 | 258000 | 3.88 | 182000 | 2.6 | R-410A | 19.1667
213895071 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2401HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 22 | 258000 | 3.93 | 182000 | 2.63 | R-410A | 19.1667
213894093 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Non-Ducted Indoor Units | 138000 | 11.1 | 22.7 | 154000 | 3.93 | 109000 | 2.66 | R-410A | 11.5
213894094 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL |  |  |  | MMY-MUP1681HT6P-UL | Non-Ducted Indoor Units | 160000 | 11.4 | 21.7 | 180000 | 3.63 | 132000 | 2.16 | R-410A | 13.3333
213895020 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL |  |  |  | MMY-MUP1681HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.35 | 180000 | 3.59 | 132000 | 2.25 | R-410A | 13.3333
213895016 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.95 | 23.1 | 154000 | 4.47 | 128000 | 2.74 | R-410A | 11.5
213894132 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Ducted Indoor Units | 138000 | 11.6 | 22.3 | 154000 | 4.21 | 128000 | 2.64 | R-410A | 11.5
213894128 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Non-Ducted Indoor Units | 138000 | 12.3 | 23.9 | 154000 | 4.74 | 128000 | 2.84 | R-410A | 11.5
213895056 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Ducted Indoor Units | 184000 | 10.8 | 21 | 206000 | 4.33 | 174000 | 2.58 | R-410A | 15.3333
213895051 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Non-Ducted Indoor Units | 184000 | 10.8 | 21.6 | 206000 | 4.41 | 174000 | 2.75 | R-410A | 15.3333
213895061 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.3 | 206000 | 4.37 | 174000 | 2.66 | R-410A | 15.3333
213895065 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Non-Ducted Indoor Units | 230000 | 12 | 22.5 | 258000 | 3.92 | 232000 | 2.44 | R-410A | 19.1667
213895073 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.65 | 21.3 | 258000 | 3.95 | 232000 | 2.52 | R-410A | 19.1667
213895069 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Ducted Indoor Units | 230000 | 11.3 | 20.1 | 258000 | 3.99 | 232000 | 2.61 | R-410A | 19.1667
213895060 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP1921HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 22.3 | 206000 | 4.13 | 154000 | 2.6 | R-410A | 15.3333
213895055 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP1921HT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 22.4 | 206000 | 4 | 154000 | 2.51 | R-410A | 15.3333
213895015 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.25 | 22.15 | 154000 | 3.78 | 109000 | 2.59 | R-410A | 11.5
213895024 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.15 | 232000 | 4.02 | 164000 | 2.74 | R-410A | 17.1667
213895068 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2401HT9P-UL | Ducted Indoor Units | 230000 | 11.2 | 19.9 | 258000 | 3.88 | 182000 | 2.6 | R-410A | 19.1667
213895072 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2401HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 20.65 | 258000 | 3.91 | 182000 | 2.63 | R-410A | 19.1667
213894127 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Non-Ducted Indoor Units | 138000 | 11.1 | 22.7 | 154000 | 3.93 | 109000 | 2.66 | R-410A | 11.5
213894131 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 21.6 | 154000 | 3.64 | 109000 | 2.53 | R-410A | 11.5
213894137 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Ducted Indoor Units | 206000 | 11.6 | 20.9 | 232000 | 4.01 | 164000 | 2.74 | R-410A | 17.1667
213894135 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 232000 | 4.04 | 164000 | 2.76 | R-410A | 17.1667
213894134 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL |  |  |  | MMY-MUP1681HT9P-UL | Non-Ducted Indoor Units | 160000 | 11.4 | 21.7 | 180000 | 3.63 | 132000 | 2.16 | R-410A | 13.3333
213895021 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL |  |  |  | MMY-MUP1681HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.35 | 180000 | 3.59 | 132000 | 2.25 | R-410A | 13.3333
213895017 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.95 | 23.1 | 154000 | 4.47 | 128000 | 2.74 | R-410A | 11.5
213894133 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Ducted Indoor Units | 138000 | 11.6 | 22.3 | 154000 | 4.21 | 128000 | 2.64 | R-410A | 11.5
213894129 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Non-Ducted Indoor Units | 138000 | 12.3 | 23.9 | 154000 | 4.74 | 128000 | 2.84 | R-410A | 11.5
213895062 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.3 | 206000 | 4.37 | 174000 | 2.66 | R-410A | 15.3333
213895052 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Non-Ducted Indoor Units | 184000 | 10.8 | 21.6 | 206000 | 4.41 | 174000 | 2.75 | R-410A | 15.3333
213895057 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Ducted Indoor Units | 184000 | 10.8 | 21 | 206000 | 4.33 | 174000 | 2.58 | R-410A | 15.3333
213895066 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Non-Ducted Indoor Units | 230000 | 12 | 22.5 | 258000 | 3.92 | 232000 | 2.44 | R-410A | 19.1667
213895074 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.65 | 21.3 | 258000 | 3.95 | 232000 | 2.52 | R-410A | 19.1667
213895070 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Ducted Indoor Units | 230000 | 11.3 | 20.1 | 258000 | 3.99 | 232000 | 2.61 | R-410A | 19.1667
202897164 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897165 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918869 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918870 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918871 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897234 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897235 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897194 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897195 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918867 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918868 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897203 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R120DXN1 |  |  | MV6-R240DXN1 | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202918977 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918978 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918979 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202918984 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB120H4M-3Y |  |  | VRB240H4M-3Y | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202897196 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897197 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202897236 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202897237 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202897198 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897199 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918981 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB120H4M-3G |  |  | VRB240H4M-3G | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202918974 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918975 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918976 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202897205 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R120DZN1 |  |  | MV6-R240DZN1 | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202897180 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897140 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897141 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918851 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918852 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918853 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918850 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897181 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897150 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897151 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897152 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897153 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897182 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918959 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918960 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918961 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918956 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918957 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918958 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897183 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897154 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897155 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897184 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897142 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897143 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918857 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918858 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918859 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202918854 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918855 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918856 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897185 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897156 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897157 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202897158 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897159 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202897186 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202918965 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918966 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918967 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202918962 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918963 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918964 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897187 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897160 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897161 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
213893574 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P96YNU-A |  |  | PUHY-P192YSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893572 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P96TNU-A |  |  | PUHY-P192TSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213916614 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916616 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  |  | PUHY-EP216YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893472 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  |  | PUHY-EP216YSNU-A | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893466 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893467 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893460 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A |  |  |  | PUHY-EP144YNU-A | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213893470 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  |  | PUHY-EP216TSNU-A | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893462 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893463 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213916575 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  |  | PUHY-EP216TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893458 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A |  |  |  | PUHY-EP144TNU-A | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213916630 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893833 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893844 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893550 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893551 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916631 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893556 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A | PUHY-HP120YNU-A |  |  | PUHY-HP240YSNU-A | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893831 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893835 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213916591 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916592 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893546 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893547 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893554 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A | PUHY-HP120TNU-A |  |  | PUHY-HP240TSNU-A | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893711 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP0964AN40AN |  |  | TUHYP1924BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893710 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP0963AN40AN |  |  | TUHYP1923BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893652 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893653 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893655 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN |  |  | TUHYE2164BN40AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916722 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916730 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN |  |  | TUHYE2164BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893649 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN |  |  |  | TUHYE1444AN40AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213893650 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893651 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893654 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN |  |  | TUHYE2163BN40AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916719 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916726 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN |  |  | TUHYE2163BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893648 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN |  |  |  | TUHYE1443AN40AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213916786 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893694 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893695 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893698 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893699 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916789 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893701 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN | TUHYH1204AN40AN |  |  | TUHYH2404BN40AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893692 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893693 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916784 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916787 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893696 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893697 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893700 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN40AN | TUHYH1203AN40AN |  |  | TUHYH2403BN40AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213896137 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A | PURY-P96YNU-A |  |  | PURY-P192YSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896135 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A | PURY-P96TNU-A |  |  | PURY-P192TSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896213 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN40AN | TURYP0964AN40AN |  |  | TURYP1924BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896211 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN40AN | TURYP0963AN40AN |  |  | TURYP1923BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213895965 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A | PURY-EP96YNU-A |  |  | PURY-EP192YSNU-A | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896077 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A | PURY-EP96YNU-A |  |  | PURY-EP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213895963 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A | PURY-EP96TNU-A |  |  | PURY-EP192TSNU-A | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896075 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A | PURY-EP96TNU-A |  |  | PURY-EP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896029 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN | TURYE0964AN40AN |  |  | TURYE1924BN40AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896165 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN | TURYE0964AN40AN |  |  | TURYE1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896027 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN | TURYE0963AN40AN |  |  | TURYE1923BN40AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896163 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN | TURYE0963AN40AN |  |  | TURYE1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896110 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A | PURY-HP72YNU-A |  |  | PURY-HP144YSNU-A | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895989 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A | PURY-HP72YNU-A |  |  | PURY-HP144YSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213895993 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A | PURY-HP96YNU-A |  |  | PURY-HP192YSNU-A | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896120 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A | PURY-HP96YNU-A |  |  | PURY-HP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896107 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A | PURY-HP72TNU-A |  |  | PURY-HP144TSNU-A | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895987 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A | PURY-HP72TNU-A |  |  | PURY-HP144TSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213895991 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A | PURY-HP96TNU-A |  |  | PURY-HP192TSNU-A | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896115 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A | PURY-HP96TNU-A |  |  | PURY-HP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896197 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN | TURYH0724AN40AN |  |  | TURYH1444BN40AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896053 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN | TURYH0724AN40AN |  |  | TURYH1444BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896057 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN | TURYH0964AN40AN |  |  | TURYH1924BN40AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896201 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN | TURYH0964AN40AN |  |  | TURYH1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896195 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN | TURYH0723AN40AN |  |  | TURYH1443BN40AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896051 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN | TURYH0723AN40AN |  |  | TURYH1443BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896055 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN | TURYH0963AN40AN |  |  | TURYH1923BN40AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896199 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN | TURYH0963AN40AN |  |  | TURYH1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
205818940 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205811882 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205811883 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205811966 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205818856 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205818857 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205818858 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205818859 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205811967 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205811884 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205811885 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205818941 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205818942 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205811886 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205811887 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205811968 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205818860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205818861 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205818862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205818863 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205811969 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205811888 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205811889 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205818943 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205818944 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205811890 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205811891 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205811970 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205818864 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205818865 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205818866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205818867 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205811971 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205811892 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205811893 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205818945 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205818946 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205811894 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205811895 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205811972 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205818868 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205818869 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205818870 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205818871 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205811973 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205811896 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205811897 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205818947 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205818948 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205818952 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205818956 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205811898 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205811899 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205811906 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205811907 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205811914 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205811915 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205811974 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205811978 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205811982 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205818872 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205818873 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205818880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205818881 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205818888 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205818889 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205818890 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205818891 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205818882 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205818883 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205818874 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205818875 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205811983 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205811979 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205811975 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205811916 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205811917 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205811908 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205811909 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205811900 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205811901 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205818957 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205818953 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205818949 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205818950 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205818954 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205818958 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205811902 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205811903 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205811910 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205811911 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205811918 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205811919 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205811976 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205811980 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205811984 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205818876 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205818877 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205818884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205818885 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205818892 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205818893 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205818894 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205818895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205818886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205818887 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205818878 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205818879 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205811985 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205811981 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205811977 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205811920 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205811921 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205811912 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205811913 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205811904 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205811905 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205818959 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205818955 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205818951 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
208811485 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208811486 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Non-Ducted Indoor Units | 230000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208812535 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812536 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Ducted Indoor Units | 230000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931864 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Ducted Indoor Units | 138000 | 12.2 | 20.4 | 154000 | 3.82 | 106000 | 2.4 | R-410A | 11.5
208931709 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Non-Ducted Indoor Units | 138000 | 14.4 | 28.2 | 154000 | 4.07 | 106000 | 2.48 | R-410A | 11.5
208931711 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Non-Ducted Indoor Units | 160000 | 12.2 | 25.7 | 180000 | 3.78 | 124000 | 2.32 | R-410A | 13.3333
208931866 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Ducted Indoor Units | 160000 | 11.5 | 19.9 | 180000 | 3.61 | 124000 | 2.3 | R-410A | 13.3333
208931868 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 206000 | 3.48 | 140000 | 2.23 | R-410A | 15.3333
208931713 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Non-Ducted Indoor Units | 184000 | 11 | 24.6 | 206000 | 3.48 | 140000 | 2.16 | R-410A | 15.3333
208812540 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812541 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Ducted Indoor Units | 230000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208811490 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208811491 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Non-Ducted Indoor Units | 230000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931731 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Non-Ducted Indoor Units | 138000 | 14.4 | 28.2 | 154000 | 4.07 | 106000 | 2.48 | R-410A | 11.5
208931886 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Ducted Indoor Units | 138000 | 12.2 | 20.4 | 154000 | 3.82 | 106000 | 2.4 | R-410A | 11.5
208931888 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Ducted Indoor Units | 160000 | 11.5 | 19.9 | 180000 | 3.61 | 124000 | 2.3 | R-410A | 13.3333
208931732 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Non-Ducted Indoor Units | 160000 | 12.2 | 25.7 | 180000 | 3.78 | 124000 | 2.32 | R-410A | 13.3333
208931734 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Non-Ducted Indoor Units | 184000 | 11 | 24.6 | 206000 | 3.48 | 140000 | 2.16 | R-410A | 15.3333
208931890 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 206000 | 3.48 | 140000 | 2.23 | R-410A | 15.3333
207591022 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
207591023 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
207591024 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
207591025 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
204723044 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
204723045 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
204723046 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
204723047 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
202073589 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.35 | 19.73 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
202073590 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 10.8 | 19.3 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
201994665 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201994667 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201994668 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201994670 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850244 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850245 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850246 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850247 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850127 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850128 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850129 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850130 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201830237 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201830238 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201830239 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201830240 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
207591054 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
207591055 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
207591056 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
207591057 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
204723076 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
204723077 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
204723078 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
204723079 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
202073605 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.35 | 19.73 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
202073606 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 10.8 | 19.3 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
201850276 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850277 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850278 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850279 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201994719 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201994721 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201994723 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201994724 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850159 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850160 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850161 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850162 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201830269 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201830270 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201830271 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201830272 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9990282 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
9990283 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990284 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
9990280 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990281 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
207591094 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
202073625 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 21.05 | 256000 | 3.45 | 172000 | 2.31 | R-410A | 19.1667
201994787 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201830309 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1* | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850316 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850199 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
204723116 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
204723142 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850226 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201830335 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1* | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201994829 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850342 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
202073638 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 21.05 | 256000 | 3.45 | 172000 | 2.31 | R-410A | 19.1667
207591120 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
213884928 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.1 | 24.7 | 206000 | 4.4 | 148000 | 2.48 | R-410A | 15.3333
213884932 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 22 | 206000 | 3.81 | 148000 | 2.45 | R-410A | 15.3333
213885192 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.8 | 23.35 | 206000 | 4.1 | 148000 | 2.46 | R-410A | 15.3333
213885186 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22.95 | 154000 | 3.9 | 100000 | 2.62 | R-410A | 11.5
213884938 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 23.9 | 232000 | 4.33 | 156000 | 2.75 | R-410A | 17.1667
213884940 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Ducted Indoor Units | 206000 | 11.3 | 21.9 | 232000 | 3.63 | 156000 | 2.65 | R-410A | 17.1667
213884942 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 22.9 | 258000 | 4.18 | 174000 | 2.55 | R-410A | 19.1667
213884946 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Ducted Indoor Units | 230000 | 11.2 | 21.8 | 258000 | 3.47 | 174000 | 2.53 | R-410A | 19.1667
213884916 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Non-Ducted Indoor Units | 138000 | 11.9 | 24.3 | 154000 | 4 | 100000 | 2.65 | R-410A | 11.5
213884918 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 21.6 | 154000 | 3.81 | 100000 | 2.6 | R-410A | 11.5
213885197 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 22.9 | 232000 | 3.98 | 156000 | 2.7 | R-410A | 17.1667
213885199 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.55 | 22.35 | 258000 | 3.82 | 174000 | 2.54 | R-410A | 19.1667
213884924 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Non-Ducted Indoor Units | 160000 | 11.2 | 24.2 | 180000 | 3.85 | 122000 | 2.57 | R-410A | 13.3333
213884926 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Ducted Indoor Units | 160000 | 10.7 | 21.5 | 180000 | 3.54 | 122000 | 2.47 | R-410A | 13.3333
213885189 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 22.85 | 180000 | 3.69 | 122000 | 2.52 | R-410A | 13.3333
213884936 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 10.7 | 21.4 | 206000 | 3.64 | 146000 | 2.29 | R-410A | 15.3333
213884937 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.7 | 206000 | 3.37 | 146000 | 2.25 | R-410A | 15.3333
213885195 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.7 | 21.05 | 206000 | 3.5 | 146000 | 2.27 | R-410A | 15.3333
213884920 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Non-Ducted Indoor Units | 138000 | 13.4 | 25 | 154000 | 4.87 | 128000 | 2.77 | R-410A | 11.5
213884922 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Ducted Indoor Units | 138000 | 12.9 | 23.4 | 154000 | 4.12 | 128000 | 2.73 | R-410A | 11.5
213885187 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.15 | 24.2 | 154000 | 4.49 | 128000 | 2.75 | R-410A | 11.5
213884930 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Non-Ducted Indoor Units | 184000 | 13.2 | 23.3 | 206000 | 4.53 | 172000 | 2.63 | R-410A | 15.3333
213884934 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Ducted Indoor Units | 184000 | 12.5 | 22.5 | 206000 | 3.92 | 172000 | 2.62 | R-410A | 15.3333
213885193 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.85 | 22.9 | 206000 | 4.22 | 172000 | 2.62 | R-410A | 15.3333
213885200 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.35 | 22.9 | 258000 | 4 | 220000 | 2.48 | R-410A | 19.1667
213884944 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Non-Ducted Indoor Units | 230000 | 12.6 | 23.3 | 258000 | 4.4 | 220000 | 2.54 | R-410A | 19.1667
213884948 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Ducted Indoor Units | 230000 | 12.1 | 22.5 | 258000 | 3.6 | 220000 | 2.43 | R-410A | 19.1667
213884933 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 22 | 206000 | 3.81 | 148000 | 2.45 | R-410A | 15.3333
213884929 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.1 | 24.7 | 206000 | 4.4 | 148000 | 2.48 | R-410A | 15.3333
213885191 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.8 | 23.35 | 206000 | 4.1 | 148000 | 2.46 | R-410A | 15.3333
213884919 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 21.6 | 154000 | 3.81 | 100000 | 2.6 | R-410A | 11.5
213884917 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Non-Ducted Indoor Units | 138000 | 11.9 | 24.3 | 154000 | 4 | 100000 | 2.65 | R-410A | 11.5
213884939 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 23.9 | 232000 | 4.33 | 156000 | 2.75 | R-410A | 17.1667
213884947 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Ducted Indoor Units | 230000 | 11.2 | 21.8 | 258000 | 3.47 | 174000 | 2.53 | R-410A | 19.1667
213884943 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 22.9 | 258000 | 4.18 | 174000 | 2.55 | R-410A | 19.1667
213884941 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Ducted Indoor Units | 206000 | 11.3 | 21.9 | 232000 | 3.63 | 156000 | 2.65 | R-410A | 17.1667
213885185 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22.95 | 154000 | 3.9 | 100000 | 2.62 | R-410A | 11.5
213885198 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.55 | 22.35 | 258000 | 3.82 | 174000 | 2.54 | R-410A | 19.1667
213885196 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 22.9 | 232000 | 3.98 | 156000 | 2.7 | R-410A | 17.1667
213885190 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 22.85 | 180000 | 3.69 | 122000 | 2.52 | R-410A | 13.3333
213884927 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Ducted Indoor Units | 160000 | 10.7 | 21.5 | 180000 | 3.54 | 122000 | 2.47 | R-410A | 13.3333
213884925 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Non-Ducted Indoor Units | 160000 | 11.2 | 24.2 | 180000 | 3.85 | 122000 | 2.57 | R-410A | 13.3333
213884923 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Ducted Indoor Units | 138000 | 12.9 | 23.4 | 154000 | 4.12 | 128000 | 2.73 | R-410A | 11.5
213884921 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Non-Ducted Indoor Units | 138000 | 13.4 | 25 | 154000 | 4.87 | 128000 | 2.77 | R-410A | 11.5
213885188 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.15 | 24.2 | 154000 | 4.49 | 128000 | 2.75 | R-410A | 11.5
213884931 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Non-Ducted Indoor Units | 184000 | 13.2 | 23.3 | 206000 | 4.53 | 172000 | 2.63 | R-410A | 15.3333
213884935 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Ducted Indoor Units | 184000 | 12.5 | 22.5 | 206000 | 3.92 | 172000 | 2.62 | R-410A | 15.3333
213885194 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.85 | 22.9 | 206000 | 4.22 | 172000 | 2.62 | R-410A | 15.3333
213885201 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.35 | 22.9 | 258000 | 4 | 220000 | 2.48 | R-410A | 19.1667
213884945 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Non-Ducted Indoor Units | 230000 | 12.6 | 23.3 | 258000 | 4.4 | 220000 | 2.54 | R-410A | 19.1667
213884949 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Ducted Indoor Units | 230000 | 12.1 | 22.5 | 258000 | 3.6 | 220000 | 2.43 | R-410A | 19.1667
213916727 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN |  |  | TUHYE2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893744 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN |  |  | TUHYE2163BN41AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893745 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN |  |  | TUHYE2164BN41AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916731 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN |  |  | TUHYE2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213896358 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Non-Ducted Indoor Units | 160000 | 11.4 | 20.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
213896319 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Ducted Indoor Units | 160000 | 11.3 | 19.2 | 178000 | 3.54 | 132000 | 2.6 | R-410A | 13.3333
213896321 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P192ZSKMU-A | Ducted Indoor Units | 184000 | 11 | 18.7 | 204000 | 3.48 | 150000 | 2.45 | R-410A | 15.3333
213916468 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.35 | 19.95 | 178000 | 3.68 | 132000 | 2.39 | R-410A | 13.3333
213916469 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P192ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 18.25 | 204000 | 3.58 | 150000 | 2.31 | R-410A | 15.3333
213916470 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P216ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 18.8 | 232000 | 3.53 | 164000 | 2.28 | R-410A | 17.1667
213896323 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P216ZSKMU-A | Ducted Indoor Units | 206000 | 10.8 | 19.8 | 232000 | 3.51 | 164000 | 2.48 | R-410A | 17.1667
204442793 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204572302 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572303 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
205000513 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
205000507 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
204572300 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799466 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799448 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799440 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799474 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799476 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799468 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799442 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799450 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
204572310 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572311 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572308 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
205000529 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000547 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
205000544 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR |  |  |  | AM168HXVAJR | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
204442716 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAFH |  |  |  | AM192HXVAFH | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
204442731 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH |  |  |  | AM192HXVAJH | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
202516754 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202516755 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
206453546 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
205281465 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
206453549 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
202516758 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
202516761 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202516762 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
206453529 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
205281447 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
206453530 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 |  |  |  | ARUM216BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
202516764 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 |  |  |  | ARUM216BTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
202524545 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
202524546 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
206453548 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
205281467 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
206453551 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
202524547 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
202524549 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
202524550 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
206453532 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
205281450 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
206453533 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 |  |  |  | ARUM216DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
202524551 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 |  |  |  | ARUM216DTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
10103105 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10103132 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10103126 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
10103127 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10103133 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10103106 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10103107 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10103134 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10103128 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
10103113 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.2 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
10103114 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Non-Ducted Indoor Units | 206000 | 12.2 | 22 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
10103154 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.55 | 20.95 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
10103155 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.9 | 20.8 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
10103140 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Ducted Indoor Units | 184000 | 12.6 | 19.7 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
10103141 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Ducted Indoor Units | 206000 | 11.6 | 19.6 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
10103142 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Ducted Indoor Units | 228000 | 11.4 | 18.6 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
10103156 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.5 | 19.85 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
10103115 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Non-Ducted Indoor Units | 228000 | 11.6 | 21.1 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
10103111 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Non-Ducted Indoor Units | 138000 | 11.8 | 22.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
10103152 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
10103138 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Ducted Indoor Units | 138000 | 11.3 | 18.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
212512472 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
212511091 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
212511092 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
10612576 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
10612577 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
10612469 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
10612475 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
10612471 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
10612580 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
10612581 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
10612584 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
10612585 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
10612594 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
212511095 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
212511096 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
212511099 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
212511100 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
212511107 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
212512477 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
212512474 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
212512464 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
212512481 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
212511103 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
212511104 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
212511083 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
212511084 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
10612564 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
10612565 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
10612590 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
10612591 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
10612483 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
10612456 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
10612570 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
212511087 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
10612470 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
10612578 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
10612579 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
212511093 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
212511094 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
212512473 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
212512475 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
212512478 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
212511097 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
212511098 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
212511101 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
212511102 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
212511109 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
10612582 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
10612583 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
10612586 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
10612587 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
10612596 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
10612472 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
10612476 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
10612484 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
10612457 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
10612566 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
10612567 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
10612592 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
10612593 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
212511105 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
212511106 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
212511085 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
212511086 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
212512465 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
212512482 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
212511089 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
10612572 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
212512452 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Non-Ducted Indoor Units | 144000 | 11.8 | 23 | 162000 | 3.77 | 109000 | 2.57 | R-410A | 12
212512453 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Ducted Indoor Units | 144000 | 11.1 | 20 | 162000 | 3.57 | 109000 | 2.54 | R-410A | 12
212512539 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 11.45 | 21.5 | 162000 | 3.67 | 109000 | 2.55 | R-410A | 12
10612458 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.85 | 22.85 | 154000 | 3.67 | 109000 | 2.59 | R-410A | 11.5
10612568 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Non-Ducted Indoor Units | 138000 | 13.5 | 25.7 | 154000 | 3.77 | 109000 | 2.65 | R-410A | 11.5
10612569 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Ducted Indoor Units | 138000 | 12.2 | 20 | 154000 | 3.57 | 109000 | 2.54 | R-410A | 11.5
9989457 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 200000 | 3.85 | 146000 | 2.38 | R-410A | 15.3333
9989794 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Ducted Indoor Units | 184000 | 12.3 | 21.1 | 200000 | 3.67 | 146000 | 2.26 | R-410A | 15.3333
9989849 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 22 | 200000 | 3.76 | 146000 | 2.32 | R-410A | 15.3333
9989850 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 22 | 200000 | 3.76 | 146000 | 2.32 | R-410A | 15.3333
9989782 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 200000 | 3.85 | 146000 | 2.38 | R-410A | 15.3333
9989795 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Ducted Indoor Units | 184000 | 12.3 | 21.1 | 200000 | 3.67 | 146000 | 2.26 | R-410A | 15.3333
9989796 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Ducted Indoor Units | 206000 | 12.2 | 20.8 | 226000 | 3.66 | 160000 | 2.18 | R-410A | 17.1667
9989799 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Non-Ducted Indoor Units | 228000 | 11.9 | 21.9 | 250000 | 3.68 | 178000 | 2.24 | R-410A | 19
9989759 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Non-Ducted Indoor Units | 206000 | 12.5 | 23 | 226000 | 3.74 | 160000 | 2.32 | R-410A | 17.1667
9989819 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Ducted Indoor Units | 228000 | 11.6 | 19.8 | 250000 | 3.51 | 178000 | 2.09 | R-410A | 19
9989851 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 21.9 | 226000 | 3.7 | 160000 | 2.25 | R-410A | 17.1667
9989853 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 20.85 | 250000 | 3.59 | 178000 | 2.16 | R-410A | 19
9989854 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 20.85 | 250000 | 3.59 | 178000 | 2.16 | R-410A | 19
9989852 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 21.9 | 226000 | 3.7 | 160000 | 2.25 | R-410A | 17.1667
9989820 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Ducted Indoor Units | 228000 | 11.6 | 19.8 | 250000 | 3.51 | 178000 | 2.09 | R-410A | 19
9989809 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Non-Ducted Indoor Units | 228000 | 11.9 | 21.9 | 250000 | 3.68 | 178000 | 2.24 | R-410A | 19
9989783 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Non-Ducted Indoor Units | 206000 | 12.5 | 23 | 226000 | 3.74 | 160000 | 2.32 | R-410A | 17.1667
9989797 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Ducted Indoor Units | 206000 | 12.2 | 20.8 | 226000 | 3.66 | 160000 | 2.18 | R-410A | 17.1667
9990034 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
9990067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
9990097 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
9990098 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
9990068 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
9990051 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
9990035 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
9990069 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
9990099 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
9990100 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
9990070 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
9990052 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
9990036 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
9990053 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* |  |  | RXYQ240TAYD* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
9990071 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
9990072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* |  |  | RXYQ240TAYD* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
9990101 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
9990102 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
9990032 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
9990063 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
9990093 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
9990094 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
9990064 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
9990049 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
9990304 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
9990305 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990306 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
9990311 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
9990312 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990313 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
9990302 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990309 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990310 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
9990303 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
207699038 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
207699039 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
207699042 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.35 | 26.4 | 154000 | 3.65 | 154000 | 2.22 | R-410A | 11.5
207699043 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.45 | 26.2 | 180000 | 3.67 | 180000 | 2.2 | R-410A | 13.3333
202607622 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608124 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608094 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607493 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607565 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607577 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202608010 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607401 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607413 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608040 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607523 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202608070 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607425 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607625 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608127 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608097 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607496 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607580 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607568 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202608013 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607404 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607416 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608043 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607526 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202608073 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607428 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607623 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608125 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608095 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607494 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607566 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607578 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202608011 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607402 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607414 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608041 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607524 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202608071 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607426 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607626 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608128 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608098 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607497 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607581 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607569 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202608014 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607405 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607417 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608044 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607527 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202608074 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607429 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607624 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608126 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608096 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607495 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607567 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607579 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202608012 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607403 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607415 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608042 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607525 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202608072 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607427 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607627 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608129 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608099 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607498 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607582 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607570 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202608015 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607406 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607418 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608045 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607528 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202608075 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607430 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607632 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608134 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608104 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607587 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607503 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607575 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202608020 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607411 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607423 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607533 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202608080 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607435 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607630 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608132 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608102 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607501 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607573 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607585 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202608018 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607409 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607421 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608048 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607531 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202608078 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607433 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607633 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608135 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608105 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607588 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607504 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607576 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202608021 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202607412 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607424 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202608051 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607534 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607628 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608130 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202607407 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202608100 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607499 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607571 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607583 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202608016 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608046 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607529 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607419 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607431 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202608076 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607631 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608133 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202607410 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202608103 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607502 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607586 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607574 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202608019 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608049 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607532 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607422 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607434 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202608079 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607629 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608131 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202607408 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202608101 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202607500 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607572 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607584 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202608017 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608047 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202607530 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607420 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607432 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202608077 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608081 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202607436 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
6687546 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
6691440 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
6691441 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687548 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687550 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
6687552 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6687554 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
6691442 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
6691443 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6691444 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
201863381 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863382 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863383 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863384 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095834 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095835 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095842 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095843 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847197 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y |  |  | VRA240H4M-2Y | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847198 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y |  |  | VRA240H4M-2Y | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201847193 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y |  |  | VRA216H4M-2Y | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847194 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y |  |  | VRA216H4M-2Y | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611576 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611577 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611578 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611579 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10612356 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 20.85 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10612357 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.05 | 20.55 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
201863369 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863370 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863371 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863372 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095838 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095839 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095830 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847135 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y |  |  | VPA216H4M-2Y | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847136 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y |  |  | VPA216H4M-2Y | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847139 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y |  |  | VPA240H4M-2Y | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847140 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y |  |  | VPA240H4M-2Y | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611622 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.25 | 20.65 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10611623 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 20.2 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10611541 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611542 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611543 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611544 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201863387 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863388 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863389 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863390 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095836 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095837 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095845 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847195 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G |  |  | VRA216H4M-2G | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847196 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G |  |  | VRA216H4M-2G | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847199 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G |  |  | VRA240H4M-2G | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847200 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G |  |  | VRA240H4M-2G | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611600 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611601 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611602 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611603 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10612368 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 20.85 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10612369 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.05 | 20.55 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
201863375 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863376 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863377 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863378 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847137 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G |  |  | VPA240H4M-2G | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847138 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G |  |  | VPA240H4M-2G | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201847133 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G |  |  | VPA216H4M-2G | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847134 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G |  |  | VPA216H4M-2G | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611637 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.25 | 20.65 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10611638 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 20.2 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10611555 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611556 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611557 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611558 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
204442718 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM168HXVAFH |  |  | AM240JXVAFH | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204442733 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM168HXVAJH |  |  | AM240JXVAJH | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204572224 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204442715 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
206799435 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
206799437 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204442730 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
204572239 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572254 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204442746 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
206799436 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
207385924 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 22.45 | 154000 | 3.62 | 100000 | 2.54 | R-410A | 11.5
207382956 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
206799438 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572269 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
208102018 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
7849631 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-72WM/B-F(U) |  |  | GMV-144WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
9956559 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
9088668 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 | IOV072H3CDC712 |  |  | IOV144H3CDC724 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
10306442 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV072H3CDC712(A) |  |  | IOV144H3CDC725(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
7850825 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850861 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850862 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850827 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850829 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
7850831 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850833 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850863 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
7850864 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850865 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850871 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850845 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850847 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850872 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850873 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
7850874 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850875 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850849 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
7850851 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850853 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
205000542 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH |  |  |  | AM168HXVAFH | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
205000543 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH |  |  |  | AM168HXVAJH | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
205000512 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR |  |  |  | AM168HXVAFR | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
201874162 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
201874163 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
201874092 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
201874074 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  |  | PUHY-P240YSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
201874089 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
201874099 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
201874160 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
201874169 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
201874143 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
201874032 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
201874034 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
201874146 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
201874158 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
201874083 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
201874084 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
201874159 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
201874095 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
201874156 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
201874167 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
201874081 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
201874069 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  |  | PUHY-P240TSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
201874030 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
201874142 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
201874145 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
201874033 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
203301907 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
203381188 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.65 | 152000 | 3.79 | 97000 | 2.17 | R-410A | 11.3333
203381199 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 21.35 | 178000 | 3.55 | 119000 | 2.27 | R-410A | 13.3333
203381207 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 22.8 | 204000 | 3.54 | 142000 | 2.17 | R-410A | 15.1667
203297483 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Ducted Indoor Units | 160000 | 11 | 19 | 178000 | 3.37 | 119000 | 2.21 | R-410A | 13.3333
203297484 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
203297495 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 22.6 | 204000 | 3.51 | 142000 | 2.19 | R-410A | 15.1667
203297496 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
203297509 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 20.8 | 232000 | 3.5 | 158000 | 2.19 | R-410A | 17.1667
203297510 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
203297521 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 18.6 | 258000 | 3.43 | 174000 | 2.14 | R-410A | 19
203381216 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 21.5 | 232000 | 3.53 | 158000 | 2.14 | R-410A | 17.1667
203381225 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.2 | 258000 | 3.52 | 174000 | 2.09 | R-410A | 19
203381184 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 21.55 | 152000 | 3.52 | 97000 | 2.1 | R-410A | 11.3333
203301906 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
203297478 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168YLMU-A |  |  |  | PURY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
203381181 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.65 | 152000 | 3.79 | 97000 | 2.17 | R-410A | 11.3333
203301904 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
203297489 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 22.6 | 204000 | 3.51 | 142000 | 2.19 | R-410A | 15.1667
203297490 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
203297475 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Ducted Indoor Units | 160000 | 11 | 19 | 178000 | 3.37 | 119000 | 2.21 | R-410A | 13.3333
203297476 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
203381194 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 21.35 | 178000 | 3.55 | 119000 | 2.27 | R-410A | 13.3333
203381203 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 22.8 | 204000 | 3.54 | 142000 | 2.17 | R-410A | 15.1667
203381221 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.2 | 258000 | 3.52 | 174000 | 2.09 | R-410A | 19
203381212 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 21.5 | 232000 | 3.53 | 158000 | 2.14 | R-410A | 17.1667
203297503 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 20.8 | 232000 | 3.5 | 158000 | 2.19 | R-410A | 17.1667
203297504 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
203297517 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 18.6 | 258000 | 3.43 | 174000 | 2.14 | R-410A | 19
203301903 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
203381179 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 21.55 | 152000 | 3.52 | 97000 | 2.1 | R-410A | 11.3333
203297470 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168TLMU-A |  |  |  | PURY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
206799473 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799465 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799447 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799439 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
205000527 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000545 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
204442779 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442780 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
204442777 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204572286 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572287 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572284 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572292 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572294 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572295 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204442787 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442788 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
204442785 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
205000546 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
205000528 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799441 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799449 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799475 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799467 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799455 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204442778 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204572285 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572293 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204442786 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
206799457 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
206799463 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
204572314 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
204442807 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Non-Ducted Indoor Units | 206000 | 11 | 24.5 | 230000 | 3.82 | 150000 | 2.7 | R-410A | 17.1667
203993992 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607517 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607520 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993999 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993994 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607518 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607521 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203994001 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993996 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607519 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607522 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203994003 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
10612574 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
10612463 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
10612406 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
212512527 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
212511009 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
212511028 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
212511029 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
212511037 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
212511038 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
212511031 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
212511010 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
212511012 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
212512528 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
212512530 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
212512537 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
10612408 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
10612413 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
10612466 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
10612480 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
10612575 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
10612589 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
10612707 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
10612663 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
10612664 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
10612588 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
10612563 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
10612477 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
10612453 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
10612411 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
10612400 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
212512526 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
212512529 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
212511027 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
212511011 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
212511006 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
212511030 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
212511007 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
212511008 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
212512466 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
10612402 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
10612403 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
10612459 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
212511045 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
212511065 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
212512470 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
10612407 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
10612464 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
10612465 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
10612473 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
10612474 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
10612467 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
10612468 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
10612481 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
10612482 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
10612409 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
10612410 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
10612414 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
212512471 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
212512476 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
212512480 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
212511066 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
212511067 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
212511069 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
212511046 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
212511047 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
212511049 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
212511064 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
212511042 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
212511048 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
212511068 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
212512463 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
212512479 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
10612412 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
10612401 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
10612478 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
10612479 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
10612454 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
10612455 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
10612460 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
10612404 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
10612405 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
212512467 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
212511043 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
212511044 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
203381124 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203378434 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203376873 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203378436 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203381123 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203376884 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203376962 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203381081 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203376896 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203376971 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203381079 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203376908 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203381327 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203378392 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203378442 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203381326 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203378391 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203378441 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203378327 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203378328 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203381284 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203378323 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203378324 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203381282 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203334991 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203334992 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203334941 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334942 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203364249 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364250 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203364251 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
203334943 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203334993 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203334989 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
203334939 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203364247 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
208480482 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* |  |  |  | REYQ168XATJ* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
203364266 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364267 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203335008 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203335009 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203334958 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334959 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203334960 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203335010 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203364268 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
203364264 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
203334956 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203335006 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
208480483 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* |  |  |  | REYQ168XAYD* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
203334975 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334976 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203364283 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364284 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203335025 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203335026 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203335027 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203364285 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
203334977 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203334973 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203364281 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
203335023 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
208480484 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* |  |  |  | REYQ168XAYC* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
204268362 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S | TVAHR120B52S |  |  | TVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204269031 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S | TVAHR120B52S |  |  | TVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269027 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269030 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204268360 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268411 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268414 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268354 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268356 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268412 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204269028 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269029 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S |  |  |  | TVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204268413 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S |  |  |  | TVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268383 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S | HVAHR120B52S |  |  | HVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204269047 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S | HVAHR120B52S |  |  | HVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269046 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269043 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204268379 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268382 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268430 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268427 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268428 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268380 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204269044 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269045 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S |  |  |  | HVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204268429 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S |  |  |  | HVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268399 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S | YVAHR120B52S |  |  | YVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204269063 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S | YVAHR120B52S |  |  | YVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269059 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269062 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204268395 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268445 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268451 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268398 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268447 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268396 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204269060 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269061 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S |  |  |  | YVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204268449 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S |  |  |  | YVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268480 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S | TVAHP120B52S |  |  | TVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204269079 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S | TVAHP120B52S |  |  | TVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269075 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204268567 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204269078 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204268561 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268478 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268474 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268476 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268563 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204269076 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269077 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S |  |  |  | TVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204268565 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S |  |  |  | TVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268511 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S | HVAHP120B52S |  |  | HVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204269095 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S | HVAHP120B52S |  |  | HVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269094 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269091 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204268586 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268509 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268583 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268502 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268504 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268584 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204269092 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269093 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S |  |  |  | HVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204268585 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S |  |  |  | HVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268542 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S | YVAHP120B52S |  |  | YVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204269111 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S | YVAHP120B52S |  |  | YVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204268602 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268540 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268599 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204269110 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269107 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204268535 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268536 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204269108 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204268600 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268601 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S |  |  |  | YVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204269109 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S |  |  |  | YVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
205749941 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* | MVHP096ME2CA* |  |  | MVHP168ME2CA* | Ducted Indoor Units | 161000 | 11.4 | 21.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749966 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* | MVHP096ME2CA* |  |  | MVHP168ME2CA* | Non-Ducted Indoor Units | 161000 | 11.6 | 22.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749967 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* | MVHR096ME2CA* |  |  | MVHR168ME2CA* | Non-Ducted Indoor Units | 161000 | 11.4 | 22 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749942 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* | MVHR096ME2CA* |  |  | MVHR168ME2CA* | Ducted Indoor Units | 161000 | 11.2 | 20.7 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749943 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* | MVHP096ME2CA* |  |  | MVHP192ME2CA* | Ducted Indoor Units | 184000 | 11.1 | 20.6 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749968 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* | MVHP096ME2CA* |  |  | MVHP192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.6 | 21.4 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749969 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* | MVHR096ME2CA* |  |  | MVHR192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.4 | 20.4 | 206000 | 3.4 | 138000 | 2.3 | R-410A | 15.3333
205749944 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* | MVHR096ME2CA* |  |  | MVHR192ME2CA* | Ducted Indoor Units | 184000 | 11.2 | 19.7 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749945 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* | MVHP096ME2CA* |  |  | MVHP216ME2CA* | Ducted Indoor Units | 207000 | 10.9 | 20.7 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749970 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* | MVHP096ME2CA* |  |  | MVHP216ME2CA* | Non-Ducted Indoor Units | 207000 | 11.5 | 20.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749971 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* | MVHR096ME2CA* |  |  | MVHR216ME2CA* | Non-Ducted Indoor Units | 207000 | 11.4 | 19.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749946 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* | MVHR096ME2CA* |  |  | MVHR216ME2CA* | Ducted Indoor Units | 207000 | 10.9 | 19.8 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
204793027 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME2CA* |  |  |  | MVHP144ME2CA* | Ducted Indoor Units | 138000 | 11.7 | 21.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793028 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME2CA* |  |  |  | MVHP144ME2CA* | Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793029 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME2CA* |  |  |  | MVHR144ME2CA* | Ducted Indoor Units | 138000 | 11 | 20.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793030 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME2CA* |  |  |  | MVHR144ME2CA* | Non-Ducted Indoor Units | 138000 | 11.4 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
205234700 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
205234792 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
205234840 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
205234841 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
205234793 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
205234701 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
205234702 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
205234794 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
205234842 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
205234850 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
205234770 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
205234802 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
205234803 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
205234771 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
205234851 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
205234852 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
205234772 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
205234804 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
205234865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 20.55 | 206000 | 3.81 | 150000 | 2.45 | R-410A | 15.3333
205234866 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.55 | 20.4 | 232000 | 3.71 | 164000 | 2.28 | R-410A | 17.1667
205234785 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Non-Ducted Indoor Units | 184000 | 12.4 | 21.9 | 206000 | 3.91 | 150000 | 2.52 | R-410A | 15.3333
205234786 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Non-Ducted Indoor Units | 206000 | 11.8 | 21.7 | 232000 | 3.84 | 164000 | 2.35 | R-410A | 17.1667
205234833 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Ducted Indoor Units | 184000 | 11.8 | 19.2 | 206000 | 3.72 | 150000 | 2.39 | R-410A | 15.3333
205234834 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Ducted Indoor Units | 206000 | 11.3 | 19.1 | 232000 | 3.58 | 164000 | 2.22 | R-410A | 17.1667
205234835 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Ducted Indoor Units | 228000 | 10.7 | 18.1 | 256000 | 3.46 | 182000 | 2.18 | R-410A | 19
205234787 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 256000 | 3.77 | 182000 | 2.39 | R-410A | 19
205234867 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 19.45 | 256000 | 3.61 | 182000 | 2.28 | R-410A | 19
205234863 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.2 | 154000 | 3.65 | 109000 | 2.17 | R-410A | 11.5
205234783 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Non-Ducted Indoor Units | 138000 | 11.5 | 22.2 | 154000 | 3.84 | 109000 | 2.2 | R-410A | 11.5
205234831 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Ducted Indoor Units | 138000 | 10.8 | 18.2 | 154000 | 3.46 | 109000 | 2.14 | R-410A | 11.5
205233067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
205234817 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
205233057 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
205233072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
205234822 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
205233062 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
208685681 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
208685682 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
208685683 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
208758282 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
208758283 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
208758284 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
208758285 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
208758286 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
208758287 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
208685684 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
208685712 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
208685713 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
207168488 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* | MVHP096ME4CA* |  |  | MVHP168ME4CA* | Ducted Indoor Units | 161000 | 11.4 | 21.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168489 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* | MVHP096ME4CA* |  |  | MVHP168ME4CA* | Non-Ducted Indoor Units | 161000 | 11.6 | 22.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168490 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* | MVHR096ME4CA* |  |  | MVHR168ME4CA* | Ducted Indoor Units | 161000 | 11.2 | 20.7 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168491 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* | MVHR096ME4CA* |  |  | MVHR168ME4CA* | Non-Ducted Indoor Units | 161000 | 11.4 | 22 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168492 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* | MVHP096ME4CA* |  |  | MVHP192ME4CA* | Ducted Indoor Units | 184000 | 11.1 | 20.6 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168493 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* | MVHP096ME4CA* |  |  | MVHP192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.6 | 21.4 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168494 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* | MVHR096ME4CA* |  |  | MVHR192ME4CA* | Ducted Indoor Units | 184000 | 11.2 | 19.7 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168495 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* | MVHR096ME4CA* |  |  | MVHR192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.4 | 20.4 | 206000 | 3.4 | 138000 | 2.3 | R-410A | 15.3333
207168496 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* | MVHP096ME4CA* |  |  | MVHP216ME4CA* | Ducted Indoor Units | 207000 | 10.9 | 20.7 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168497 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* | MVHP096ME4CA* |  |  | MVHP216ME4CA* | Non-Ducted Indoor Units | 207000 | 11.5 | 20.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168498 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* | MVHR096ME4CA* |  |  | MVHR216ME4CA* | Ducted Indoor Units | 207000 | 10.9 | 19.8 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168499 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* | MVHR096ME4CA* |  |  | MVHR216ME4CA* | Non-Ducted Indoor Units | 207000 | 11.4 | 19.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
206568895 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME4CA* |  |  |  | MVHP144ME4CA* | Ducted Indoor Units | 138000 | 11.7 | 21.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568896 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME4CA* |  |  |  | MVHP144ME4CA* | Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568897 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME4CA* |  |  |  | MVHR144ME4CA* | Ducted Indoor Units | 138000 | 11 | 20.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568898 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME4CA* |  |  |  | MVHR144ME4CA* | Non-Ducted Indoor Units | 138000 | 11.4 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
208812545 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812546 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931865 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.3 | 24.3 | 154000 | 3.94 | 106000 | 2.44 | R-410A | 11.5
208931867 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.85 | 22.8 | 180000 | 3.69 | 124000 | 2.31 | R-410A | 13.3333
208931869 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.95 | 206000 | 3.48 | 140000 | 2.19 | R-410A | 15.3333
208812550 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812551 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931887 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.3 | 24.3 | 154000 | 3.94 | 106000 | 2.44 | R-410A | 11.5
208931889 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.85 | 22.8 | 180000 | 3.69 | 124000 | 2.31 | R-410A | 13.3333
208931891 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.95 | 206000 | 3.48 | 140000 | 2.19 | R-410A | 15.3333
209842408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209863184 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
213886376 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886448 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
209863185 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH | AM120BXVTFH |  |  | AM240BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209842409 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH | AM120BXVTFH |  |  | AM240BXVTFH | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209842427 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842437 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209863193 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
213886414 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213893863 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893867 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893871 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893875 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886450 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213886410 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886378 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
209863194 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209842438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209842428 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842429 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH | AM120BXVTJH |  |  | AM240BXVTJH | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209863195 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH | AM120BXVTJH |  |  | AM240BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209863173 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209842189 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842199 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209842200 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209842190 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209863174 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209863175 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR | AM120BXVTFR |  |  | AM240BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209842191 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR | AM120BXVTFR |  |  | AM240BXVTFR | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209842457 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209842447 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209863203 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
213886419 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886415 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213893876 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213893872 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893868 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893864 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213886451 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213886379 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886411 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
209863204 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209842448 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842458 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209842449 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR | AM120BXVTJR |  |  | AM240BXVTJR | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209863205 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR | AM120BXVTJR |  |  | AM240BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209863183 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209842407 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842417 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
213886412 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213893861 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213886416 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213893865 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893869 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893873 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
210691236 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
210691237 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
210691238 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
210691239 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
210691240 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
210691241 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
210691228 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA |  |  |  | AVWT-144FHFSHA | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
210691229 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA |  |  |  | AVWT-144FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
210691231 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FHFSHA |  |  |  | AVWT-168FHFSHA | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
210691232 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FHFSHA |  |  |  | AVWT-168FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 22.45 | 170000 | 3.29 | 115000 | 2.16 | R-410A | 13.3333
210691234 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FHFSHA |  |  |  | AVWT-192FHFSHA | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
210691235 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FHFSHA |  |  |  | AVWT-192FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
212924820 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Non-Ducted Indoor Units | 144000 | 12.2 | 20 | 162000 | 4.1 | 105000 | 2.45 | R-410A | 12
212928533 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Ducted Indoor Units | 144000 | 12.5 | 18.5 | 162000 | 3.72 | 105000 | 2.45 | R-410A | 12
212928543 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 12.35 | 19.25 | 162000 | 3.91 | 105000 | 2.45 | R-410A | 12
212928544 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 192000 | 11.65 | 19.25 | 206000 | 3.77 | 140000 | 2.38 | R-410A | 16
212928534 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Ducted Indoor Units | 192000 | 11.5 | 19 | 206000 | 3.6 | 140000 | 2.37 | R-410A | 16
212928535 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Non-Ducted Indoor Units | 192000 | 11.8 | 19.5 | 206000 | 3.94 | 140000 | 2.4 | R-410A | 16
212928546 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 12.35 | 19.25 | 162000 | 3.91 | 105000 | 2.45 | R-410A | 12
212928538 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Ducted Indoor Units | 144000 | 12.5 | 18.5 | 162000 | 3.72 | 105000 | 2.45 | R-410A | 12
212924827 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Non-Ducted Indoor Units | 144000 | 12.2 | 20 | 162000 | 4.1 | 105000 | 2.45 | R-410A | 12
212928539 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Ducted Indoor Units | 192000 | 11.5 | 19 | 206000 | 3.6 | 140000 | 2.37 | R-410A | 16
212928540 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Non-Ducted Indoor Units | 192000 | 11.8 | 19.5 | 206000 | 3.94 | 140000 | 2.4 | R-410A | 16
212928547 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 192000 | 11.65 | 19.25 | 206000 | 3.77 | 140000 | 2.38 | R-410A | 16
213686153 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
213686154 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
213686155 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
213686156 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
213686157 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
213686158 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
10515233 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10515243 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
10515253 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10515254 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10515244 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
10515234 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10515261 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10515257 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10515259 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10515260 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10515258 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10515262 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10515245 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
10515255 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10515235 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10515236 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10515256 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10515246 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
201856724 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC144DXN1-(A) | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856725 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC144DXN1-(A) | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y | VRA072L4M-2Y |  |  | VRA144L4M-2Y | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862861 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y | VRA072L4M-2Y |  |  | VRA144L4M-2Y | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA072L4M-2Y |  |  | VRA168L4M-2Y | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862863 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA072L4M-2Y |  |  | VRA168L4M-2Y | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862864 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y |  |  | VRA192L4M-2Y | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862865 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y |  |  | VRA192L4M-2Y | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856726 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856727 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC168DXN1-(A) | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856728 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856729 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC192DXN1-(A) | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856730 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856731 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC216DXN1-(A) | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201856732 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) |  |  | MV5-RC240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862866 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y |  |  | VRA216L4M-2Y | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862867 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y |  |  | VRA216L4M-2Y | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201862868 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y |  |  | VRA240L4M-2Y | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856748 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC144DZN1-(A) | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856749 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC144DZN1-(A) | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G | VRA072L4M-2G |  |  | VRA144L4M-2G | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862885 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G | VRA072L4M-2G |  |  | VRA144L4M-2G | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA072L4M-2G |  |  | VRA168L4M-2G | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862887 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA072L4M-2G |  |  | VRA168L4M-2G | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862888 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G |  |  | VRA192L4M-2G | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862889 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G |  |  | VRA192L4M-2G | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856750 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856751 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC168DZN1-(A) | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856752 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856753 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC192DZN1-(A) | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856754 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856755 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC216DZN1-(A) | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201856756 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) |  |  | MV5-RC240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862890 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G |  |  | VRA216L4M-2G | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862891 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G |  |  | VRA216L4M-2G | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201862892 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G |  |  | VRA240L4M-2G | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862908 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y | VPA072L4M-2Y |  |  | VPA144L4M-2Y | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862909 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y | VPA072L4M-2Y |  |  | VPA144L4M-2Y | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856772 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC144DXN1-(A) | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856773 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC144DXN1-(A) | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856774 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856775 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC168DXN1-(A) | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856776 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856777 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC192DXN1-(A) | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862910 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA072L4M-2Y |  |  | VPA168L4M-2Y | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862911 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA072L4M-2Y |  |  | VPA168L4M-2Y | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862912 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y |  |  | VPA192L4M-2Y | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862913 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y |  |  | VPA192L4M-2Y | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862914 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y |  |  | VPA216L4M-2Y | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862916 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA120L4M-2Y |  |  | VPA240L4M-2Y | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856778 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856780 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC120DXN1-(A) |  |  | MV5-XC240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856794 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC144DZN1-(A) | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856795 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC144DZN1-(A) | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862930 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G | VPA072L4M-2G |  |  | VPA144L4M-2G | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862931 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G | VPA072L4M-2G |  |  | VPA144L4M-2G | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862932 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA072L4M-2G |  |  | VPA168L4M-2G | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862933 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA072L4M-2G |  |  | VPA168L4M-2G | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862934 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G |  |  | VPA192L4M-2G | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862935 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G |  |  | VPA192L4M-2G | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856796 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856797 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC168DZN1-(A) | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856798 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856799 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC192DZN1-(A) | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856800 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856802 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC120DZN1-(A) |  |  | MV5-XC240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862936 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G |  |  | VPA216L4M-2G | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862938 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA120L4M-2G |  |  | VPA240L4M-2G | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201992875 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Non-Ducted Indoor Units | 138000 | 11.5 | 22.2 | 154000 | 3.84 | 109000 | 2.2 | R-410A | 11.5
202021884 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Ducted Indoor Units | 138000 | 10.8 | 18.2 | 154000 | 3.46 | 109000 | 2.14 | R-410A | 11.5
202022802 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.2 | 154000 | 3.65 | 109000 | 2.17 | R-410A | 11.5
202022804 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 20.55 | 206000 | 3.81 | 150000 | 2.45 | R-410A | 15.3333
202022805 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.55 | 20.4 | 232000 | 3.71 | 164000 | 2.28 | R-410A | 17.1667
202016259 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Non-Ducted Indoor Units | 206000 | 11.8 | 21.7 | 232000 | 3.84 | 164000 | 2.35 | R-410A | 17.1667
202021886 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Ducted Indoor Units | 184000 | 11.8 | 19.2 | 206000 | 3.72 | 150000 | 2.39 | R-410A | 15.3333
202021887 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Ducted Indoor Units | 206000 | 11.3 | 19.1 | 232000 | 3.58 | 164000 | 2.22 | R-410A | 17.1667
202021854 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.4 | 21.9 | 206000 | 3.91 | 150000 | 2.52 | R-410A | 15.3333
202021888 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Ducted Indoor Units | 228000 | 10.7 | 18.1 | 256000 | 3.46 | 182000 | 2.18 | R-410A | 19
202016261 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 256000 | 3.77 | 182000 | 2.39 | R-410A | 19
202022806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 19.45 | 256000 | 3.61 | 182000 | 2.28 | R-410A | 19
202022822 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202021873 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202021860 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202021861 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202021874 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202022823 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202022824 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202021875 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202021855 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202021856 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202021876 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202022825 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202022826 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202021877 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202021857 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202021878 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202016269 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202022827 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202022828 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202021879 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
202021858 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
202021859 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
202021880 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
202022829 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202022830 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202016271 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
202021881 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
204442794 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204572301 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
206799456 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
207699045 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.3 | 25.8 | 206000 | 3.66 | 206000 | 2.2 | R-410A | 15.3333
207699041 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
206799458 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572309 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
9133446 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC96KHP/220V |  |  | TVRF-OC192KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.15 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
9133487 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC240KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 21.7 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
10267483 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-240WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
201903115 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
208102040 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
201902946 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
10267474 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-168WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
10267499 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-72WM/B-U(U) |  |  | GMV-144WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
201902941 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
10306471 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) | IOV072H6CDC712(A) |  |  | IOV144H6CDC725(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
208102025 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
208102022 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
208102030 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
208102035 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
10267477 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-192WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
10267480 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-216WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
201903106 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
201903110 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
206799464 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
204572317 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
205281466 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
206453547 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
202566102 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
202566103 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202566104 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
206453550 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
205281453 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
206453535 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
202566106 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
202566107 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202566108 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 |  |  |  | ARUM216CTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
206453536 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 |  |  |  | ARUM216CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
208102095 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432G | VER120C432G |  |  | VER216C432G | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
201904248 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432G | VER120C432G |  |  | VER216C432G | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
10341446 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-U(U) | GMV-Q120WM/B-U(U) |  |  | GMV-Q216WM/B-U(U) | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
201903109 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
201903105 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10267479 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-216WM/B-U(U) | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
10267476 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-192WM/B-U(U) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
208102036 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
208102031 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
208102024 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
208102021 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10306470 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) | IOV072H6CDC712(A) |  |  | IOV144H6CDC725(A) | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
201902944 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
10267470 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-72WM/B-U(U) |  |  | GMV-144WM/B-U(U) | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10267472 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-168WM/B-U(U) | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
201902938 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
208102041 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
201903113 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
9133486 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC240KHP/220V | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
9133448 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC216KHP/220V | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
204442802 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204442810 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Non-Ducted Indoor Units | 206000 | 11 | 24.5 | 230000 | 3.82 | 150000 | 2.7 | R-410A | 17.1667
208102043 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP120C432Y |  |  | VEP240C432Y | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
208102033 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y |  |  | VEP192C432Y | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
208102038 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP096C432Y |  |  | VEP216C432Y | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
8176006 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  |  | GMV-192WM/B-F(U) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
8176007 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  |  | GMV-216WM/B-F(U) | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
9956567 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y |  |  | VEP192C432Y | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
9956569 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP096C432Y |  |  | VEP216C432Y | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
10306441 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV072H3CDC712(A) |  |  | IOV144H3CDC725(A) | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10306447 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  |  | IOV192H3CDC733(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10306449 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  |  | IOV216H3CDC737(A) | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
10306444 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) |  |  | IOV168H3CDC729(A) | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
8176009 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) |  |  | GMV-168WM/B-F(U) | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
9088667 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 | IOV072H3CDC712 |  |  | IOV144H3CDC724 | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
9956558 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
208102017 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
7793599 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-72WM/B-F(U) |  |  | GMV-144WM/B-F(U) | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
208102027 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y |  |  | VEP168C432Y | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
204442761 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
204442764 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM168HXVAJR |  |  | AM240JXVAJR | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204442749 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM168HXVAFR |  |  | AM240JXVAFR | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204442795 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442796 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
10267482 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-240WM/B-U(U) | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
204442762 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR |  |  |  | AM192HXVAJR | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
201874091 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
204442747 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAFR |  |  |  | AM192HXVAFR | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
10306451 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  |  | IOV240H3CDC741(A) | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
9956577 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP120C432Y |  |  | VEP240C432Y | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
8176008 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  |  | GMV-240WM/B-F(U) | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
204442801 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442803 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442804 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
9133445 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC96KHP/220V |  |  | TVRF-OC192KHP/220V | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10344560 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) | GMV-Q120WM/B-F(U) |  |  | GMV-Q216WM/B-F(U) | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
201866461 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y | VER120C432Y |  |  | VER216C432Y | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
208102097 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y | VER120C432Y |  |  | VER216C432Y | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
6687555 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
6687557 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
7850834 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
7850836 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
7850854 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
7850856 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
213894101 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Non-Ducted Indoor Units | 366000 | 9.6 | 18.4 | 412000 | 3.45 | 294000 | 2.28 | R-410A | 30.5
213894097 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Non-Ducted Indoor Units | 276000 | 9.95 | 20.6 | 308000 | 3.61 | 216000 | 2.27 | R-410A | 23
213894144 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Ducted Indoor Units | 276000 | 10.8 | 21.4 | 308000 | 3.81 | 216000 | 2.56 | R-410A | 23
213894162 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Ducted Indoor Units | 366000 | 11 | 18.9 | 412000 | 3.48 | 294000 | 2.29 | R-410A | 30.5
213895028 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.37 | 21 | 308000 | 3.71 | 216000 | 2.41 | R-410A | 23
213895040 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.3 | 18.65 | 412000 | 3.46 | 294000 | 2.28 | R-410A | 30.5
213895042 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.1 | 18.15 | 438000 | 3.36 | 310000 | 2.29 | R-410A | 32.5
213895036 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.42 | 18.9 | 386000 | 3.47 | 284000 | 2.29 | R-410A | 28.5
213895044 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.95 | 18.05 | 462000 | 3.34 | 328000 | 2.29 | R-410A | 34.3333
213895046 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP1201HT6P-UL |  | MMY-UP4561HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.65 | 17.45 | 488000 | 3.3 | 350000 | 2.28 | R-410A | 36.1667
213895032 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 20.2 | 334000 | 3.57 | 236000 | 2.44 | R-410A | 24.8333
213895034 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.35 | 360000 | 3.47 | 268000 | 2.29 | R-410A | 26.6667
213895026 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.6 | 22.65 | 284000 | 3.76 | 200000 | 2.51 | R-410A | 21
213894165 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Ducted Indoor Units | 390000 | 10.4 | 18.4 | 438000 | 3.38 | 310000 | 2.39 | R-410A | 32.5
213894168 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Ducted Indoor Units | 412000 | 9.9 | 17.6 | 462000 | 3.35 | 328000 | 2.41 | R-410A | 34.3333
213894149 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Ducted Indoor Units | 298000 | 10.1 | 20.4 | 334000 | 3.6 | 236000 | 2.44 | R-410A | 24.8333
213894152 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Ducted Indoor Units | 320000 | 10 | 18.4 | 360000 | 3.46 | 268000 | 2.39 | R-410A | 26.6667
213894157 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Ducted Indoor Units | 342000 | 11.2 | 19.4 | 386000 | 3.5 | 284000 | 2.45 | R-410A | 28.5
213894139 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Ducted Indoor Units | 252000 | 10.3 | 21 | 284000 | 3.82 | 200000 | 2.55 | R-410A | 21
213894098 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Non-Ducted Indoor Units | 298000 | 9.6 | 20 | 334000 | 3.54 | 236000 | 2.44 | R-410A | 24.8333
213894099 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 20.8 | 360000 | 3.53 | 268000 | 2.21 | R-410A | 26.6667
213894100 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Non-Ducted Indoor Units | 342000 | 9.65 | 18.4 | 386000 | 3.44 | 284000 | 2.13 | R-410A | 28.5
213894096 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Non-Ducted Indoor Units | 252000 | 10.3 | 20.2 | 284000 | 3.74 | 200000 | 2.49 | R-410A | 21
213894102 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Non-Ducted Indoor Units | 390000 | 9.8 | 17.9 | 438000 | 3.34 | 310000 | 2.19 | R-410A | 32.5
213894103 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Non-Ducted Indoor Units | 412000 | 10 | 18.5 | 462000 | 3.33 | 328000 | 2.17 | R-410A | 34.3333
213894104 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP1201HT6P-UL |  | MMY-UP4561HT6P-UL | Non-Ducted Indoor Units | 434000 | 9.8 | 17.6 | 488000 | 3.28 | 350000 | 2.21 | R-410A | 36.1667
213894142 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Non-Ducted Indoor Units | 276000 | 11 | 19.3 | 308000 | 3.82 | 260000 | 2.31 | R-410A | 23
213894146 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Ducted Indoor Units | 276000 | 11.2 | 18.8 | 308000 | 4.08 | 260000 | 2.48 | R-410A | 23
213895030 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 19.05 | 308000 | 3.95 | 260000 | 2.39 | R-410A | 23
213895038 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 19.4 | 386000 | 3.75 | 348000 | 2.47 | R-410A | 28.5
213894159 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Ducted Indoor Units | 342000 | 10.8 | 19.5 | 386000 | 3.8 | 348000 | 2.48 | R-410A | 28.5
213894155 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Non-Ducted Indoor Units | 342000 | 10.1 | 19.3 | 386000 | 3.7 | 348000 | 2.46 | R-410A | 28.5
213895029 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.37 | 21 | 308000 | 3.71 | 216000 | 2.41 | R-410A | 23
213895041 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.3 | 18.65 | 412000 | 3.46 | 294000 | 2.28 | R-410A | 30.5
213894145 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Ducted Indoor Units | 276000 | 10.8 | 21.4 | 308000 | 3.81 | 216000 | 2.56 | R-410A | 23
213894141 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Non-Ducted Indoor Units | 276000 | 9.95 | 20.6 | 308000 | 3.61 | 216000 | 2.27 | R-410A | 23
213894163 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Ducted Indoor Units | 366000 | 11 | 18.9 | 412000 | 3.48 | 294000 | 2.29 | R-410A | 30.5
213894161 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Non-Ducted Indoor Units | 366000 | 9.6 | 18.4 | 412000 | 3.45 | 294000 | 2.28 | R-410A | 30.5
213894164 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Non-Ducted Indoor Units | 390000 | 9.8 | 17.9 | 438000 | 3.34 | 310000 | 2.19 | R-410A | 32.5
213894166 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Ducted Indoor Units | 390000 | 10.4 | 18.4 | 438000 | 3.38 | 310000 | 2.39 | R-410A | 32.5
213894167 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Non-Ducted Indoor Units | 412000 | 10 | 18.5 | 462000 | 3.33 | 328000 | 2.17 | R-410A | 34.3333
213894169 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Ducted Indoor Units | 412000 | 9.9 | 17.6 | 462000 | 3.35 | 328000 | 2.41 | R-410A | 34.3333
213894170 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP1201HT9P-UL |  | MMY-UP4561HT9P-UL | Non-Ducted Indoor Units | 434000 | 9.8 | 17.6 | 488000 | 3.28 | 350000 | 2.21 | R-410A | 36.1667
213894148 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Non-Ducted Indoor Units | 298000 | 9.6 | 20 | 334000 | 3.54 | 236000 | 2.44 | R-410A | 24.8333
213894150 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Ducted Indoor Units | 298000 | 10.1 | 20.4 | 334000 | 3.6 | 236000 | 2.44 | R-410A | 24.8333
213894151 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 20.8 | 360000 | 3.53 | 268000 | 2.21 | R-410A | 26.6667
213894153 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Ducted Indoor Units | 320000 | 10 | 18.4 | 360000 | 3.46 | 268000 | 2.39 | R-410A | 26.6667
213894154 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Non-Ducted Indoor Units | 342000 | 9.65 | 18.4 | 386000 | 3.44 | 284000 | 2.13 | R-410A | 28.5
213894158 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Ducted Indoor Units | 342000 | 11.2 | 19.4 | 386000 | 3.5 | 284000 | 2.45 | R-410A | 28.5
213894138 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Non-Ducted Indoor Units | 252000 | 10.3 | 20.2 | 284000 | 3.74 | 200000 | 2.49 | R-410A | 21
213894140 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Ducted Indoor Units | 252000 | 10.3 | 21 | 284000 | 3.82 | 200000 | 2.55 | R-410A | 21
213895043 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.1 | 18.15 | 438000 | 3.36 | 310000 | 2.29 | R-410A | 32.5
213895037 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.42 | 18.9 | 386000 | 3.47 | 284000 | 2.29 | R-410A | 28.5
213895047 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP1201HT9P-UL |  | MMY-UP4561HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.65 | 17.45 | 488000 | 3.3 | 350000 | 2.28 | R-410A | 36.1667
213895045 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.95 | 18.05 | 462000 | 3.34 | 328000 | 2.29 | R-410A | 34.3333
213895027 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.6 | 22.65 | 284000 | 3.76 | 200000 | 2.51 | R-410A | 21
213895035 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 21.6 | 360000 | 3.47 | 268000 | 2.29 | R-410A | 26.6667
213895033 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 20.2 | 334000 | 3.57 | 236000 | 2.44 | R-410A | 24.8333
213894143 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Non-Ducted Indoor Units | 276000 | 11 | 19.3 | 308000 | 3.82 | 260000 | 2.31 | R-410A | 23
213894147 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Ducted Indoor Units | 276000 | 11.2 | 18.8 | 308000 | 4.08 | 260000 | 2.48 | R-410A | 23
213895031 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 19.05 | 308000 | 3.95 | 260000 | 2.39 | R-410A | 23
213895039 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 19.4 | 386000 | 3.75 | 348000 | 2.47 | R-410A | 28.5
213894160 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Ducted Indoor Units | 342000 | 10.8 | 19.5 | 386000 | 3.8 | 348000 | 2.48 | R-410A | 28.5
213894156 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Non-Ducted Indoor Units | 342000 | 10.1 | 19.3 | 386000 | 3.7 | 348000 | 2.46 | R-410A | 28.5
202897168 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202897169 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202897242 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202918881 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202918882 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202918883 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202918878 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202918879 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202918880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202897243 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202897206 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202897207 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202897208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202897209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202897244 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202918989 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202918990 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202918991 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202918986 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202918987 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202918988 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202897245 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202897210 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202897211 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202897174 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202897175 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202897170 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202897171 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202897246 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202897254 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202918887 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202918888 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202918889 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202918899 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202918900 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202918901 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202918896 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202918897 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202918898 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202918884 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202918885 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202918886 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202897255 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202897247 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202897224 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202897225 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202897212 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202897213 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202897214 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202897215 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202897226 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202897227 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202897248 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202897256 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202918995 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202918996 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202918997 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202919007 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202919008 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202919009 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202919004 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202919005 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202919006 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202918992 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202918993 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202918994 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202897257 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202897249 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202897228 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202897229 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202897216 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202897217 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202897172 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202897173 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202897250 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202897259 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X168DXN1 |  |  | MV6-X360DXN1 | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897302 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X168DXN1 |  |  | MV6-X360DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202918906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB168H4M-3Y |  |  | VPB360H4M-3Y | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202918907 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB168H4M-3Y |  |  | VPB360H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202918893 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202918894 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202918895 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202918903 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB168H4M-3G |  |  | VPB360H4M-3G | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202918904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB168H4M-3G |  |  | VPB360H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202918890 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202918891 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202918892 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202897303 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X168DZN1 |  |  | MV6-X360DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202897271 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X168DZN1 |  |  | MV6-X360DZN1 | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897251 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202897218 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202897219 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202897220 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202897221 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202897252 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202897273 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R168DXN1 |  |  | MV6-R360DXN1 | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897304 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R168DXN1 |  |  | MV6-R360DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202919001 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202919002 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202919003 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202919014 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB168H4M-3Y |  |  | VRB360H4M-3Y | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202919015 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB168H4M-3Y |  |  | VRB360H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202919011 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB168H4M-3G |  |  | VRB360H4M-3G | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202919012 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB168H4M-3G |  |  | VRB360H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202918998 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202918999 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202919000 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202897305 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R168DZN1 |  |  | MV6-R360DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202897275 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R168DZN1 |  |  | MV6-R360DZN1 | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897253 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202897222 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202897223 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
213893584 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893585 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893592 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893593 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893600 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P312YSNU-A | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213916640 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916641 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916642 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P312YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916643 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893608 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893609 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893614 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P360YSNU-A | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893618 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P144YNU-A |  | PUHY-P384YSNU-A | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893622 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P408YSNU-A | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213916644 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P360YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893626 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P432YSNU-A | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893588 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893589 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893581 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893596 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P312TSNU-A | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213916601 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916602 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916603 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P312TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916604 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893604 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893605 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893620 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P144TNU-A | PUHY-P144TNU-A |  | PUHY-P408TSNU-A | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893616 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P144TNU-A |  | PUHY-P384TSNU-A | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893612 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P360TSNU-A | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213916605 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P360TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893624 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P144TNU-A | PUHY-P144TNU-A |  | PUHY-P432TSNU-A | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893478 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893479 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893486 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893487 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893494 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893495 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213916619 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916620 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916621 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916622 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893502 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893503 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893520 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP144YNU-A | PUHY-EP144YNU-A |  | PUHY-EP408YSNU-A | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893510 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893511 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893516 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP144YNU-A |  | PUHY-EP384YSNU-A | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213916623 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893838 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP144YNU-A | PUHY-EP144YNU-A |  | PUHY-EP432YSNU-A | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916581 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916582 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893474 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893475 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893482 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893483 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893490 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893491 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893498 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893499 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916583 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916584 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893518 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP144TNU-A | PUHY-EP144TNU-A |  | PUHY-EP408TSNU-A | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893514 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP144TNU-A |  | PUHY-EP384TSNU-A | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893506 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893507 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893836 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP144TNU-A | PUHY-EP144TNU-A |  | PUHY-EP432TSNU-A | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916823 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916827 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916831 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3124BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893716 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893717 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893720 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893721 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893724 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3124BN40AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893728 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893729 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916835 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916839 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3604BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893731 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3604BN40AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893733 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1444AN40AN |  | TUHYP3844BN40AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893735 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1444AN40AN | TUHYP1444AN40AN |  | TUHYP4084BN40AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893737 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1444AN40AN | TUHYP1444AN40AN |  | TUHYP4324BN40AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213916821 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916829 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3123BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916825 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213893718 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893719 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893714 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893715 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893722 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3123BN40AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893726 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893727 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916833 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916837 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3603BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893730 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3603BN40AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893734 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1443AN40AN | TUHYP1443AN40AN |  | TUHYP4083BN40AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893732 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1443AN40AN |  | TUHYP3843BN40AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893736 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1443AN40AN | TUHYP1443AN40AN |  | TUHYP4323BN40AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213916742 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916746 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916750 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893666 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893667 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893658 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893659 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893662 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893663 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893670 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893671 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916754 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916758 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893674 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893675 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893677 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1444AN40AN |  | TUHYE3844BN40AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893679 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1444AN40AN | TUHYE1444AN40AN |  | TUHYE4084BN40AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893841 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1444AN40AN | TUHYE1444AN40AN |  | TUHYE4324BN40AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916740 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916748 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916744 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213893664 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893665 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893660 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893661 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893656 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893657 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893668 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893669 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916752 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916756 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893672 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893673 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893676 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1443AN40AN |  | TUHYE3843BN40AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893678 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1443AN40AN | TUHYE1443AN40AN |  | TUHYE4083BN40AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893840 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1443AN40AN | TUHYE1443AN40AN |  | TUHYE4323BN40AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
205818912 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205818913 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205818920 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205818921 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205818960 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205818964 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205818968 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205818972 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205818976 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205818977 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205818978 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205811922 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205811923 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205811930 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205811931 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205811938 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205811939 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205811946 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205811947 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205811986 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205811990 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205811994 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205811998 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205812002 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205812003 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205812004 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205818896 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205818897 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205818904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205818905 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205818906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205818907 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205818898 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205818899 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205812005 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205812006 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205812007 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205811999 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205811995 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205811991 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205811987 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205811948 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205811949 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205811940 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205811941 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205811932 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205811933 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205811924 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205811925 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205818979 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205818980 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205818981 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205818973 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205818969 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205818965 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205818961 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205818922 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205818923 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205818914 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205818915 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205818916 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205818917 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205818924 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205818925 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205818962 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205818966 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205818970 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205818974 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205818982 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205818983 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205818984 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205811926 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205811927 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205811934 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205811935 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205811942 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205811943 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205811950 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205811951 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205811988 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205811992 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205811996 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205812000 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205812008 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205812009 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205812010 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205818900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205818901 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205818908 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205818909 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205818910 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205818911 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205818902 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205818903 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205812011 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205812012 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205812013 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205812001 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205811997 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205811993 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205811989 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205811952 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205811953 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205811944 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205811945 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205811936 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205811937 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205811928 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205811929 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205818985 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205818986 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205818987 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205818975 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205818971 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205818967 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205818963 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205818926 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205818927 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205818918 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205818919 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
208931715 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931718 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Non-Ducted Indoor Units | 276000 | 9.8 | 22.4 | 308000 | 3.39 | 210000 | 2.16 | R-410A | 23
208931728 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Non-Ducted Indoor Units | 390000 | 11 | 22.7 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931729 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Non-Ducted Indoor Units | 412000 | 10.8 | 22.9 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931870 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Ducted Indoor Units | 252000 | 11.2 | 17.3 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931872 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Ducted Indoor Units | 276000 | 10 | 17.2 | 308000 | 3.37 | 210000 | 2.16 | R-410A | 23
208931882 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Ducted Indoor Units | 390000 | 11 | 17.6 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931884 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Ducted Indoor Units | 412000 | 10.8 | 17.5 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931874 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Ducted Indoor Units | 298000 | 10 | 17.2 | 320000 | 3.37 | 214000 | 2.16 | R-410A | 24.8333
208931876 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Ducted Indoor Units | 320000 | 10 | 17.2 | 338000 | 3.37 | 224000 | 2.16 | R-410A | 26.6667
208931721 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Non-Ducted Indoor Units | 298000 | 9.8 | 22.4 | 320000 | 3.39 | 214000 | 2.16 | R-410A | 24.8333
208931723 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Non-Ducted Indoor Units | 320000 | 9.8 | 22.4 | 338000 | 3.39 | 224000 | 2.16 | R-410A | 26.6667
208931725 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Non-Ducted Indoor Units | 344000 | 9.8 | 22.4 | 346000 | 3.39 | 232000 | 2.16 | R-410A | 28.6667
208931726 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Non-Ducted Indoor Units | 366000 | 9.8 | 22.4 | 354000 | 3.39 | 240000 | 2.16 | R-410A | 30.5
208931878 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Ducted Indoor Units | 344000 | 10 | 17.2 | 346000 | 3.37 | 232000 | 2.16 | R-410A | 28.6667
208931880 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Ducted Indoor Units | 366000 | 10 | 17.2 | 354000 | 3.37 | 240000 | 2.16 | R-410A | 30.5
208931749 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Non-Ducted Indoor Units | 390000 | 11 | 22.7 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931751 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Non-Ducted Indoor Units | 412000 | 10.8 | 22.9 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931736 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931738 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Non-Ducted Indoor Units | 276000 | 9.8 | 22.4 | 308000 | 3.39 | 210000 | 2.16 | R-410A | 23
208931892 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Ducted Indoor Units | 252000 | 11.2 | 17.3 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931894 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Ducted Indoor Units | 276000 | 10 | 17.2 | 308000 | 3.37 | 210000 | 2.16 | R-410A | 23
208931904 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Ducted Indoor Units | 390000 | 11 | 17.6 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931906 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Ducted Indoor Units | 412000 | 10.8 | 17.5 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931896 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Ducted Indoor Units | 298000 | 10 | 17.2 | 320000 | 3.37 | 214000 | 2.16 | R-410A | 24.8333
208931898 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Ducted Indoor Units | 320000 | 10 | 17.2 | 338000 | 3.37 | 224000 | 2.16 | R-410A | 26.6667
208931741 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Non-Ducted Indoor Units | 298000 | 9.8 | 22.4 | 320000 | 3.39 | 214000 | 2.16 | R-410A | 24.8333
208931743 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Non-Ducted Indoor Units | 320000 | 9.8 | 22.4 | 338000 | 3.39 | 224000 | 2.16 | R-410A | 26.6667
208931745 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Non-Ducted Indoor Units | 344000 | 9.8 | 22.4 | 346000 | 3.39 | 232000 | 2.16 | R-410A | 28.6667
208931747 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Non-Ducted Indoor Units | 366000 | 9.8 | 22.4 | 354000 | 3.39 | 240000 | 2.16 | R-410A | 30.5
208931900 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Ducted Indoor Units | 344000 | 10 | 17.2 | 346000 | 3.37 | 232000 | 2.16 | R-410A | 28.6667
208931902 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Ducted Indoor Units | 366000 | 10 | 17.2 | 354000 | 3.37 | 240000 | 2.16 | R-410A | 30.5
201830249 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201830250 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201830251 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201830252 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850139 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850140 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850141 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850142 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201994686 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201994687 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201994689 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201994691 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850256 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850257 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850258 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850259 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
202073595 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.25 | 18.76 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
202073596 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 9.9 | 17.92 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
204723056 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
204723057 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
204723058 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
204723059 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
207591034 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
207591035 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
207591036 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
207591037 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201830281 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201830282 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201830283 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201830284 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850171 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850172 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850173 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850174 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850288 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850289 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850290 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850291 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201994739 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201994741 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201994742 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201994744 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
202073611 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.25 | 18.76 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
202073612 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 9.9 | 17.92 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
204723088 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
204723089 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
204723090 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
204723091 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
207591066 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
207591067 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
207591068 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
207591069 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9990285 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
9990286 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
204723118 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850201 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850318 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201830311 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1* | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201994790 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
202073626 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.1 | 19.9 | 274000 | 3.29 | 186000 | 2.24 | R-410A | 20.6667
207591096 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
207591122 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
202073639 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.1 | 19.9 | 274000 | 3.29 | 186000 | 2.24 | R-410A | 20.6667
201850344 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201994832 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201830337 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1* | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850228 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
204723144 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
213884954 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.6 | 22.8 | 308000 | 3.88 | 200000 | 2.45 | R-410A | 23
213884958 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Ducted Indoor Units | 276000 | 10.6 | 21.7 | 308000 | 3.27 | 200000 | 2.43 | R-410A | 23
213884978 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3841FT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 20.4 | 412000 | 3.53 | 274000 | 2.6 | R-410A | 30.5
213885204 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 22.25 | 308000 | 3.57 | 200000 | 2.44 | R-410A | 23
213885217 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3841FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.4 | 19.5 | 412000 | 3.38 | 274000 | 2.57 | R-410A | 30.5
213885219 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4081FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.15 | 19.2 | 438000 | 3.37 | 296000 | 2.57 | R-410A | 32.5
213885221 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4321FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.85 | 19.1 | 462000 | 3.35 | 318000 | 2.51 | R-410A | 34.3333
213885223 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4561FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.85 | 18.95 | 488000 | 3.34 | 322000 | 2.49 | R-410A | 36.1667
213885210 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL |  |  | MMY-UP3361FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 20.85 | 360000 | 3.4 | 244000 | 2.43 | R-410A | 26.6667
213885212 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3601FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 20.05 | 386000 | 3.39 | 270000 | 2.5 | R-410A | 28.5
213885203 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.2 | 22.35 | 284000 | 3.6 | 196000 | 2.44 | R-410A | 21
213885208 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.95 | 21.6 | 334000 | 3.55 | 222000 | 2.43 | R-410A | 24.8333
213885225 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4801FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 456000 | 9.7 | 18.95 | 514000 | 3.29 | 344000 | 2.47 | R-410A | 38
213884964 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Ducted Indoor Units | 298000 | 10.6 | 21 | 334000 | 3.25 | 222000 | 2.42 | R-410A | 24.8333
213884966 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL |  |  | MMY-UP3361FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 21.4 | 360000 | 3.57 | 244000 | 2.44 | R-410A | 26.6667
213884970 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3601FT6P-UL | Non-Ducted Indoor Units | 342000 | 10.6 | 20.5 | 386000 | 3.54 | 270000 | 2.51 | R-410A | 28.5
213884962 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Non-Ducted Indoor Units | 298000 | 11.3 | 22.2 | 334000 | 3.86 | 222000 | 2.44 | R-410A | 24.8333
213884952 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Ducted Indoor Units | 252000 | 10.7 | 21.8 | 284000 | 3.28 | 196000 | 2.43 | R-410A | 21
213884950 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 284000 | 3.92 | 196000 | 2.46 | R-410A | 21
213884982 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4081FT6P-UL | Non-Ducted Indoor Units | 390000 | 10.3 | 20.2 | 438000 | 3.51 | 296000 | 2.58 | R-410A | 32.5
213884986 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4321FT6P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.48 | 318000 | 2.52 | R-410A | 34.3333
213884990 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4561FT6P-UL | Non-Ducted Indoor Units | 434000 | 9.9 | 19.8 | 488000 | 3.45 | 322000 | 2.5 | R-410A | 36.1667
213884994 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4801FT6P-UL | Non-Ducted Indoor Units | 456000 | 9.7 | 19.8 | 514000 | 3.37 | 344000 | 2.49 | R-410A | 38
213884960 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.59 | 258000 | 2.42 | R-410A | 23
213884956 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Non-Ducted Indoor Units | 276000 | 12.6 | 21 | 308000 | 3.9 | 258000 | 2.48 | R-410A | 23
213885206 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.1 | 20.4 | 308000 | 3.74 | 258000 | 2.45 | R-410A | 23
213885214 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.65 | 20.25 | 386000 | 3.62 | 330000 | 2.42 | R-410A | 28.5
213884972 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Non-Ducted Indoor Units | 342000 | 11.9 | 20.9 | 386000 | 3.69 | 330000 | 2.45 | R-410A | 28.5
213884976 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Ducted Indoor Units | 342000 | 11.4 | 19.6 | 386000 | 3.55 | 330000 | 2.4 | R-410A | 28.5
213884979 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3841FT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 20.4 | 412000 | 3.53 | 274000 | 2.6 | R-410A | 30.5
213884955 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.6 | 22.8 | 308000 | 3.88 | 200000 | 2.45 | R-410A | 23
213884959 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Ducted Indoor Units | 276000 | 10.6 | 21.7 | 308000 | 3.27 | 200000 | 2.43 | R-410A | 23
213885205 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 22.25 | 308000 | 3.57 | 200000 | 2.44 | R-410A | 23
213885216 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3841FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.4 | 19.5 | 412000 | 3.38 | 274000 | 2.57 | R-410A | 30.5
213885213 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3601FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 20.05 | 386000 | 3.39 | 270000 | 2.5 | R-410A | 28.5
213885211 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL |  |  | MMY-UP3361FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 20.85 | 360000 | 3.4 | 244000 | 2.43 | R-410A | 26.6667
213885224 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4801FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 456000 | 9.7 | 18.95 | 514000 | 3.29 | 344000 | 2.47 | R-410A | 38
213885222 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4561FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.85 | 18.95 | 488000 | 3.34 | 322000 | 2.49 | R-410A | 36.1667
213885220 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4321FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.85 | 19.1 | 462000 | 3.35 | 318000 | 2.51 | R-410A | 34.3333
213885218 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4081FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.15 | 19.2 | 438000 | 3.37 | 296000 | 2.57 | R-410A | 32.5
213885202 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.2 | 22.35 | 284000 | 3.6 | 196000 | 2.44 | R-410A | 21
213885209 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.95 | 21.6 | 334000 | 3.55 | 222000 | 2.43 | R-410A | 24.8333
213884963 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Non-Ducted Indoor Units | 298000 | 11.3 | 22.2 | 334000 | 3.86 | 222000 | 2.44 | R-410A | 24.8333
213884953 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Ducted Indoor Units | 252000 | 10.7 | 21.8 | 284000 | 3.28 | 196000 | 2.43 | R-410A | 21
213884951 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 284000 | 3.92 | 196000 | 2.46 | R-410A | 21
213884971 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3601FT9P-UL | Non-Ducted Indoor Units | 342000 | 10.6 | 20.5 | 386000 | 3.54 | 270000 | 2.51 | R-410A | 28.5
213884967 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL |  |  | MMY-UP3361FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 21.4 | 360000 | 3.57 | 244000 | 2.44 | R-410A | 26.6667
213884965 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Ducted Indoor Units | 298000 | 10.6 | 21 | 334000 | 3.25 | 222000 | 2.42 | R-410A | 24.8333
213884983 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4081FT9P-UL | Non-Ducted Indoor Units | 390000 | 10.3 | 20.2 | 438000 | 3.51 | 296000 | 2.58 | R-410A | 32.5
213884987 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4321FT9P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.48 | 318000 | 2.52 | R-410A | 34.3333
213884995 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4801FT9P-UL | Non-Ducted Indoor Units | 456000 | 9.7 | 19.8 | 514000 | 3.37 | 344000 | 2.49 | R-410A | 38
213884991 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4561FT9P-UL | Non-Ducted Indoor Units | 434000 | 9.9 | 19.8 | 488000 | 3.45 | 322000 | 2.5 | R-410A | 36.1667
213884961 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.59 | 258000 | 2.42 | R-410A | 23
213884957 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Non-Ducted Indoor Units | 276000 | 12.6 | 21 | 308000 | 3.9 | 258000 | 2.48 | R-410A | 23
213885207 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.1 | 20.4 | 308000 | 3.74 | 258000 | 2.45 | R-410A | 23
213885215 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.65 | 20.25 | 386000 | 3.62 | 330000 | 2.42 | R-410A | 28.5
213884973 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Non-Ducted Indoor Units | 342000 | 11.9 | 20.9 | 386000 | 3.69 | 330000 | 2.45 | R-410A | 28.5
213884977 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Ducted Indoor Units | 342000 | 11.4 | 19.6 | 386000 | 3.55 | 330000 | 2.4 | R-410A | 28.5
213896359 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Non-Ducted Indoor Units | 252000 | 10.8 | 18.2 | 280000 | 3.62 | 200000 | 2.16 | R-410A | 21
213896365 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Non-Ducted Indoor Units | 276000 | 10.6 | 18.9 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 23
213896366 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Non-Ducted Indoor Units | 298000 | 10 | 17.5 | 334000 | 3.59 | 236000 | 2.22 | R-410A | 24.8333
213896325 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Ducted Indoor Units | 252000 | 11.3 | 19 | 280000 | 3.47 | 200000 | 2.52 | R-410A | 21
213896327 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Ducted Indoor Units | 276000 | 11.1 | 18.1 | 308000 | 3.49 | 216000 | 2.53 | R-410A | 23
213896329 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Ducted Indoor Units | 298000 | 11 | 17.3 | 334000 | 3.46 | 236000 | 2.43 | R-410A | 24.8333
213916472 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.05 | 18.6 | 280000 | 3.54 | 200000 | 2.34 | R-410A | 21
213916473 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.85 | 18.5 | 308000 | 3.54 | 216000 | 2.37 | R-410A | 23
213916474 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.5 | 17.4 | 334000 | 3.52 | 236000 | 2.32 | R-410A | 24.8333
213916475 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 17.65 | 360000 | 3.42 | 268000 | 2.25 | R-410A | 26.6667
213896331 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Ducted Indoor Units | 320000 | 10.9 | 17.4 | 360000 | 3.42 | 268000 | 2.38 | R-410A | 26.6667
213896360 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Non-Ducted Indoor Units | 320000 | 10.1 | 17.9 | 360000 | 3.42 | 268000 | 2.13 | R-410A | 26.6667
213896333 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P360ZSKMU-A | Ducted Indoor Units | 344000 | 10.8 | 16.8 | 386000 | 3.32 | 284000 | 2.32 | R-410A | 28.6667
213916476 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P360ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 17.1 | 386000 | 3.36 | 284000 | 2.18 | R-410A | 28.6667
204572304 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799482 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799484 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572312 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
205000550 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR | AM192HXVAJR |  |  | AM360JXVAJR | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
204442723 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAFH | AM192HXVAFH |  |  | AM384JXVAFH | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442738 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH | AM192HXVAJH |  |  | AM384JXVAJH | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442808 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH | AM216KXVGJH |  |  | AM408KXVGJH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442754 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAFR | AM192HXVAFR |  |  | AM384JXVAFR | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442769 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR | AM192HXVAJR |  |  | AM384JXVAJR | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
205281471 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
206453552 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
202516769 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
202516770 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202519360 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202519361 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202519382 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM121BTE5 | ARUM121BTE5 |  | ARUM432BTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
206453554 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453559 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM121BTE5 | ARUM121BTE5 |  | ARUM432BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
205281473 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
205281474 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
206453555 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453556 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453557 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM168BTE5 |  |  | ARUM384BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453558 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
206453553 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM121BTE5 |  |  | ARUM336BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
202519364 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202519365 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202519368 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM121BTE5 |  |  | ARUM336BTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202519371 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202519374 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM168BTE5 |  |  | ARUM384BTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202519378 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
205281479 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
206453560 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
202524555 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202524556 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
202524557 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202524558 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202524569 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM121DTE5 | ARUM121DTE5 |  | ARUM432DTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
206453561 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453567 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM121DTE5 | ARUM121DTE5 |  | ARUM432DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
205281480 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
205281481 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
206453562 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453563 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM121DTE5 |  |  | ARUM336DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
206453564 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453565 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM168DTE5 |  |  | ARUM384DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453566 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
202524559 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202524560 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202524561 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM121DTE5 |  |  | ARUM336DTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202524563 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202524565 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM168DTE5 |  |  | ARUM384DTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202524567 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
10103157 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ144TAYC* |  |  | REYQ264TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 18.75 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
10103161 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* | REYQ120TAYC* |  | REYQ360TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.65 | 18.6 | 384000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
10103116 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ144TAYC* |  |  | REYQ264TAYC* | Non-Ducted Indoor Units | 252000 | 11.2 | 20.5 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
10103120 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* | REYQ120TAYC* |  | REYQ360TAYC* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 384000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
10103117 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ144TAYC* |  |  | REYQ288TAYC* | Non-Ducted Indoor Units | 274000 | 11 | 20.3 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
10103118 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ168TAYC* |  |  | REYQ312TAYC* | Non-Ducted Indoor Units | 296000 | 10.1 | 19.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
10103158 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ144TAYC* |  |  | REYQ288TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 18.85 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
10103159 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ168TAYC* |  |  | REYQ312TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.9 | 18.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
10103160 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYC* | REYQ168TAYC* |  |  | REYQ336TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 17.9 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
10103119 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYC* | REYQ168TAYC* |  |  | REYQ336TAYC* | Non-Ducted Indoor Units | 320000 | 9.8 | 19 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
10612506 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
10612512 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
10612615 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
10612616 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
10612623 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
212511135 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
212511127 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
212511128 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
212512508 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
212512502 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
212512492 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
212512511 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
212512486 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
212511115 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
212511116 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
212511111 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
212511112 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
10612515 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
10612599 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
10612600 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
10612603 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
10612604 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
10612496 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
10612490 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
10612502 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
10612498 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
10612607 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
10612608 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
10612619 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1686FT6P-UL |  |  | MMY-AP336S6FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
10612611 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
10612612 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
212511131 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1686FT6P-UL |  |  | MMY-AP336S6FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
212511119 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
212511120 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
212511123 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
212511124 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
212512494 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
212512498 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
212512503 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
212512509 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
212511129 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
212511130 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
212511137 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
10612513 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
10612507 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
10612617 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
10612618 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
10612625 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
10612491 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
10612497 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
10612516 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
10612601 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
10612602 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
10612605 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
10612606 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
212511113 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
212511114 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
212511117 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
212511118 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
212512512 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
212512493 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
212512487 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
212512495 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
212512499 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
212511121 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
212511122 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
212511125 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
212511126 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
212511133 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1686FT9P-UL |  |  | MMY-AP336S6FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
10612609 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
10612610 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
10612499 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
10612503 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
10612621 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1686FT9P-UL |  |  | MMY-AP336S6FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
10612613 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
10612614 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
9989800 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ144TATJ* |  |  | REYQ264TATJ* | Non-Ducted Indoor Units | 252000 | 11.6 | 21.6 | 274000 | 3.55 | 196000 | 2.33 | R-410A | 21
9989804 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ120TATJ* | REYQ120TATJ* |  | REYQ360TATJ* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 376000 | 3.52 | 258000 | 2.28 | R-410A | 28.5
9989855 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ144TATJ* |  |  | REYQ264TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.1 | 274000 | 3.37 | 196000 | 2.2 | R-410A | 21
9989863 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ120TATJ* | REYQ120TATJ* |  | REYQ360TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.2 | 376000 | 3.39 | 258000 | 2.16 | R-410A | 28.5
9989864 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ120TAYD* | REYQ120TAYD* |  | REYQ360TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.2 | 376000 | 3.39 | 258000 | 2.16 | R-410A | 28.5
9989856 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ144TAYD* |  |  | REYQ264TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.1 | 274000 | 3.37 | 196000 | 2.2 | R-410A | 21
9989814 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ120TAYD* | REYQ120TAYD* |  | REYQ360TAYD* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 376000 | 3.52 | 258000 | 2.28 | R-410A | 28.5
9989810 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ144TAYD* |  |  | REYQ264TAYD* | Non-Ducted Indoor Units | 252000 | 11.6 | 21.6 | 274000 | 3.55 | 196000 | 2.33 | R-410A | 21
9989857 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ144TATJ* |  |  | REYQ288TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 19.45 | 288000 | 3.35 | 210000 | 2.27 | R-410A | 22.8333
9989859 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ168TATJ* |  |  | REYQ312TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.5 | 19.1 | 306000 | 3.38 | 230000 | 2.22 | R-410A | 24.6667
9989801 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ144TATJ* |  |  | REYQ288TATJ* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 288000 | 3.51 | 210000 | 2.41 | R-410A | 22.8333
9989802 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ168TATJ* |  |  | REYQ312TATJ* | Non-Ducted Indoor Units | 296000 | 11 | 20.2 | 306000 | 3.57 | 230000 | 2.35 | R-410A | 24.6667
9989860 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ168TAYD* |  |  | REYQ312TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.5 | 19.1 | 306000 | 3.38 | 230000 | 2.22 | R-410A | 24.6667
9989858 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ144TAYD* |  |  | REYQ288TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 19.45 | 288000 | 3.35 | 210000 | 2.27 | R-410A | 22.8333
9989811 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ144TAYD* |  |  | REYQ288TAYD* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 288000 | 3.51 | 210000 | 2.41 | R-410A | 22.8333
9989812 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ168TAYD* |  |  | REYQ312TAYD* | Non-Ducted Indoor Units | 296000 | 11 | 20.2 | 306000 | 3.57 | 230000 | 2.35 | R-410A | 24.6667
9989861 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TATJ* | REYQ168TATJ* |  |  | REYQ336TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.95 | 18.15 | 316000 | 3.36 | 244000 | 2.11 | R-410A | 26.6667
9989803 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TATJ* | REYQ168TATJ* |  |  | REYQ336TATJ* | Non-Ducted Indoor Units | 320000 | 10.3 | 19 | 316000 | 3.53 | 244000 | 2.18 | R-410A | 26.6667
9989862 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYD* | REYQ168TAYD* |  |  | REYQ336TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.95 | 18.15 | 316000 | 3.36 | 244000 | 2.11 | R-410A | 26.6667
9989813 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYD* | REYQ168TAYD* |  |  | REYQ336TAYD* | Non-Ducted Indoor Units | 320000 | 10.3 | 19 | 316000 | 3.53 | 244000 | 2.18 | R-410A | 26.6667
9990037 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ144TATJ* |  |  | RXYQ264TATJ* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
9990041 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* | RXYQ120TATJ* |  | RXYQ360TATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
9990103 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ144TATJ* |  |  | RXYQ264TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
9990111 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* | RXYQ120TATJ* |  | RXYQ360TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
9990112 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* | RXYQ120TAYD* |  | RXYQ360TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
9990104 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ144TAYD* |  |  | RXYQ264TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
9990058 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* | RXYQ120TAYD* |  | RXYQ360TAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
9990054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ144TAYD* |  |  | RXYQ264TAYD* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
9990038 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
9990039 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ168TATJ* |  |  | RXYQ312TATJ* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
9990075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
9990105 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
9990107 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ168TATJ* |  |  | RXYQ312TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
9990108 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ168TAYD* |  |  | RXYQ312TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
9990106 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
9990076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
9990055 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
9990056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ168TAYD* |  |  | RXYQ312TAYD* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
9990307 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
9990308 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
9990314 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
9990315 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
202608148 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608178 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202607646 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607688 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607658 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206773 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S | TVAHP144B32S |  | TVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10207486 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S | TVAHP120B32S |  | TVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
202607736 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608202 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608238 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607808 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608181 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608151 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202607649 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607691 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607661 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10207492 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S | TVAHP120B42S |  | TVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10206815 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S | TVAHP144B42S |  | TVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
202607739 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608205 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608241 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607811 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608149 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608179 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202607647 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607659 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607689 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206787 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S | HVAHP144B32S |  | HVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10207488 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S | HVAHP120B32S |  | HVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
202607737 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608203 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608239 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607809 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608182 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608152 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202607650 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607662 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10207494 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S | HVAHP120B42S |  | HVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10206829 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S | HVAHP144B42S |  | HVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
202607740 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608206 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608242 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607812 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608150 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608180 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202607648 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607660 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607690 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S | YVAHP144B32S |  | YVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10207490 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S | YVAHP120B32S |  | YVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
202607738 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608204 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608240 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608183 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608153 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202607651 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607693 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607663 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10207496 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S | YVAHP120B42S |  | YVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10206843 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S | YVAHP144B42S |  | YVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
202607741 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608207 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608243 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607813 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608188 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608158 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202607656 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607668 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607698 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323611 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S | HVAHR120B42S |  | HVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323709 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S | HVAHR144B42S |  | HVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
202607746 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608212 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608248 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607818 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608186 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608156 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202607654 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607696 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607666 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323677 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S | YVAHR144B32S |  | YVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323579 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S | YVAHR120B32S |  | YVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
202607744 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608210 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608246 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607816 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608189 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608159 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202607657 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607669 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607699 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323627 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S | YVAHR120B42S |  | YVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323725 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S | YVAHR144B42S |  | YVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
202607747 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608213 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608154 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608184 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202607652 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607694 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607664 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323645 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S | TVAHR144B32S |  | TVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323547 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S | TVAHR120B32S |  | TVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
202607742 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608208 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608244 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607814 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608187 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608157 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202607655 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607667 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607697 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323595 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S | TVAHR120B42S |  | TVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323693 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S | TVAHR144B42S |  | TVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
202607745 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608211 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608247 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607817 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608155 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608185 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202607653 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607695 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607665 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323661 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S | HVAHR144B32S |  | HVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323563 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S | HVAHR120B32S |  | HVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
202607743 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202608209 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608245 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202607815 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607819 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202608249 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204442767 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM168HXVAJR |  |  | AM312JXVAJR | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
6687556 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
6687558 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
6691445 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
6691446 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
201847213 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y | VRA096H4M-2Y |  | VRA336H4M-2Y | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847214 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y | VRA096H4M-2Y |  | VRA336H4M-2Y | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611586 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611587 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10612361 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.65 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
202095850 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095851 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863385 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863386 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A)* | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202095846 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095847 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863373 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863374 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A)* | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847155 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y | VPA096H4M-2Y |  | VPA336H4M-2Y | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847156 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y | VPA096H4M-2Y |  | VPA336H4M-2Y | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611629 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 19.3 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10611547 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611548 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201847215 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G | VRA096H4M-2G |  | VRA336H4M-2G | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847216 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G | VRA096H4M-2G |  | VRA336H4M-2G | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611610 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611611 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10612373 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.65 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
202095852 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863391 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863392 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A)* | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202095848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863379 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863380 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A)* | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847153 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G | VPA096H4M-2G |  | VPA336H4M-2G | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847154 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G | VPA096H4M-2G |  | VPA336H4M-2G | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611644 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 19.3 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10611561 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611562 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
204442719 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442724 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM144FXVAFH | AM192HXVAFH |  | AM408JXVAFH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204572228 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799477 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799479 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572243 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204442734 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442739 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM144FXVAJH | AM192HXVAJH |  | AM408JXVAJH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204572229 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204442720 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442721 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM168HXVAFH |  |  | AM312JXVAFH | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
206799485 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
206799487 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204442735 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442736 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM168HXVAJH |  |  | AM312JXVAJH | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204572244 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572259 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572258 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799478 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799480 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572273 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204442752 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM168HXVAFR |  |  | AM312JXVAFR | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
206799486 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
206799488 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572274 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204442750 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442765 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
208102048 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10032811 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-264WM/B-F(U) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10257465 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10306453 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV264H3CDC745(A) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10255984 | 1/1/2027 | INNOVAIR | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10257462 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10306455 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV288H3CDC749(A) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10035095 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-288WM/B-F(U) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
208102053 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
7850866 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
7850867 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
7850835 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
7850837 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
7850855 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
7850857 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
7850876 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
7850877 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
205000548 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH | AM192HXVAFH |  |  | AM360JXVAFH | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
204442722 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH | AM168HXVAFH |  |  | AM336JXVAFH | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
204442737 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH | AM168HXVAJH |  |  | AM336JXVAJH | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
205000549 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH | AM192HXVAJH |  |  | AM360JXVAJH | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
205000514 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR | AM192HXVAFR |  |  | AM360JXVAFR | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
201874075 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
201874076 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
201874077 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  | PUHY-P360YSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
201874090 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
201874100 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
201874161 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
201874170 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
201874789 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Non-Ducted Indoor Units | 282000 | 13.4 | 22.1 | 316000 | 3.66 | 236000 | 2.22 | R-410A | 23.5
201874790 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Non-Ducted Indoor Units | 304000 | 13.2 | 20.9 | 342000 | 3.52 | 268000 | 2.13 | R-410A | 25.3333
201874096 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
201874157 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
201874786 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Non-Ducted Indoor Units | 282000 | 13.4 | 22.1 | 316000 | 3.66 | 236000 | 2.22 | R-410A | 23.5
201874787 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Non-Ducted Indoor Units | 304000 | 13.2 | 20.9 | 342000 | 3.52 | 268000 | 2.13 | R-410A | 25.3333
201874168 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
201874082 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
201874070 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
201874071 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
201874072 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  | PUHY-P360TSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
206799481 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204442781 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204572288 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572296 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204442789 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
206799483 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799489 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204442782 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204572289 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204572297 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204442790 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
206799491 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204442809 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH | AM216KXVGJH |  |  | AM432KXVGJH | Non-Ducted Indoor Units | 416000 | 9.8 | 21 | 460000 | 3.3 | 300000 | 2.4 | R-410A | 34.6667
203994166 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994694 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202607682 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202608172 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608175 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202607685 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994697 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994169 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994167 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994695 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202607683 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202608173 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608176 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202607686 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994170 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994168 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994696 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202607684 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202608174 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608177 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202607687 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994699 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994171 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
212511022 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
212511023 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
212512506 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
10612433 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
10612434 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
10612510 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
10612665 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
10612666 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 434000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
10612635 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
10612636 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 435000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
10612627 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
10612628 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
10612598 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
10612492 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
10612487 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
10612415 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
10612417 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
10612418 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
212512488 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
212511151 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 436000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
212511152 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 436000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
212512531 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
212512532 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
212512533 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 436000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
212511013 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
212511014 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
212511015 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
212511032 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
212511033 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
212511034 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
212511035 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
212511036 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
212511155 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 436000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
212511156 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 436000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
212511164 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4566HT6P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 488000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
212511016 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
212511017 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
212511018 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
212511019 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
212511020 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
212511021 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
212512534 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 436000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
212512535 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
212512490 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
212512496 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
212512500 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
10612429 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
10612430 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
10612421 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
10612422 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
10612425 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
10612426 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
10612494 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
10612500 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
10612504 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
10612639 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
10612640 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 435000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
10612667 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 434000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
10612668 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
10612647 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
10612648 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
10612656 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4566HT6P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 485000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
10612511 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
10612435 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
10612436 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
212512507 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
212511059 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
212511060 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
212511050 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
212511051 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
212511052 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
212511070 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
212511139 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
212511140 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
212512510 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
212512513 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 436000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
212512489 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
212511153 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 436000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
212511154 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 436000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
212512485 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
10612416 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
10612419 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
10612420 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
10612488 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
10612489 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
10612493 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
10612514 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
10612517 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 434000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
10612637 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
10612638 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 435000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
10612629 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
10612630 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
10612641 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
10612642 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 435000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
10612658 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4566HT9P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 485000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
10612649 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
10612650 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
10612518 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 434000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
10612521 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
10612501 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
10612505 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
10612495 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
10612431 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
10612432 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
10612427 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
10612428 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
10612423 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
10612424 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
212512491 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
212512501 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
212512497 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
212512514 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 436000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
212512517 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
212511145 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
212511146 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
212511166 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4566HT9P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 488000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
212511157 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 436000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
212511158 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 436000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
212511053 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
212511054 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
212511055 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
212511056 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
212511057 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
212511058 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
203376929 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203378290 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203381142 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203378291 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203376933 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203381141 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203381098 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203376937 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378292 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203381097 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203376941 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378293 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378452 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203378420 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203381346 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203378419 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203378451 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203381344 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203378450 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378354 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203381301 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381300 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203378353 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378449 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203364252 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ144XATJ* |  |  | REYQ264XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203364256 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* | REYQ120XATJ* |  | REYQ360XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
203334944 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ144XATJ* |  |  | REYQ264XATJ* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334948 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* | REYQ120XATJ* |  | REYQ360XATJ* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203334945 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ144XATJ* |  |  | REYQ288XATJ* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334946 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ168XATJ* |  |  | REYQ312XATJ* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203364253 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ144XATJ* |  |  | REYQ288XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364254 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ168XATJ* |  |  | REYQ312XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203364255 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* | REYQ168XATJ* |  |  | REYQ336XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203334947 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* | REYQ168XATJ* |  |  | REYQ336XATJ* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
203334961 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ144XAYD* |  |  | REYQ264XAYD* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334965 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* | REYQ120XAYD* |  | REYQ360XAYD* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203364269 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ144XAYD* |  |  | REYQ264XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203364273 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* | REYQ120XAYD* |  | REYQ360XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
203364270 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ144XAYD* |  |  | REYQ288XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364271 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ168XAYD* |  |  | REYQ312XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203334962 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ144XAYD* |  |  | REYQ288XAYD* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334963 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ168XAYD* |  |  | REYQ312XAYD* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203334964 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* | REYQ168XAYD* |  |  | REYQ336XAYD* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
203364272 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* | REYQ168XAYD* |  |  | REYQ336XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203364286 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ144XAYC* |  |  | REYQ264XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203334982 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* | REYQ120XAYC* |  | REYQ360XAYC* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203364290 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* | REYQ120XAYC* |  | REYQ360XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
203334978 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ144XAYC* |  |  | REYQ264XAYC* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334979 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ144XAYC* |  |  | REYQ288XAYC* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334980 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ168XAYC* |  |  | REYQ312XAYC* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203364287 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ144XAYC* |  |  | REYQ288XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364288 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ168XAYC* |  |  | REYQ312XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203364289 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* | REYQ168XAYC* |  |  | REYQ336XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203334981 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* | REYQ168XAYC* |  |  | REYQ336XAYC* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
204269032 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269033 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S |  |  | TVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204268364 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268371 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S | TVAHR120B52S |  | TVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268416 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268417 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S |  |  | TVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268423 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S | TVAHR144B52S |  | TVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268418 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S | TVAHR144B52S |  |  | TVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204269034 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S | TVAHR144B52S |  |  | TVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269035 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204268419 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204269048 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269049 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S |  |  | HVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204268384 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268389 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S | HVAHR120B52S |  | HVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268432 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268433 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S |  |  | HVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268439 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S | HVAHR144B52S |  | HVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268434 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S | HVAHR144B52S |  |  | HVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204269050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S | HVAHR144B52S |  |  | HVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269051 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204268435 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204269064 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269065 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S |  |  | YVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204268456 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268458 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S |  |  | YVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268470 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S | YVAHR144B52S |  | YVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268400 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268405 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S | YVAHR120B52S |  | YVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268460 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S | YVAHR144B52S |  |  | YVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204269066 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S | YVAHR144B52S |  |  | YVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269067 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204268462 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204269080 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269081 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S |  |  | TVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204268569 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268570 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S |  |  | TVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268579 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S | TVAHP144B52S |  | TVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268481 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268489 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S | TVAHP120B52S |  | TVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268572 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S | TVAHP144B52S |  |  | TVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204269082 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S | TVAHP144B52S |  |  | TVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269083 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204268574 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204269096 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269097 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S |  |  | HVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204268595 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S | HVAHP144B52S |  | HVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268513 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268588 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268589 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S |  |  | HVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268525 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S | HVAHP120B52S |  | HVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268590 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S | HVAHP144B52S |  |  | HVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204269098 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S | HVAHP144B52S |  |  | HVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269099 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204268591 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268604 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268606 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S |  |  | YVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268616 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S | YVAHP144B52S |  | YVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204269112 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269113 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S |  |  | YVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204268545 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268553 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S | YVAHP120B52S |  | YVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204269114 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S | YVAHP144B52S |  |  | YVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204268607 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S | YVAHP144B52S |  |  | YVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268609 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204269115 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
205234707 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* | RXYQ120XATJ* |  | RXYQ360XATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
205234703 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ144XATJ* |  |  | RXYQ264XATJ* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
205234843 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ144XATJ* |  |  | RXYQ264XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
205234847 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* | RXYQ120XATJ* |  | RXYQ360XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
205234853 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ144XAYD* |  |  | RXYQ264XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
205234857 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* | RXYQ120XAYD* |  | RXYQ360XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
205234773 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ144XAYD* |  |  | RXYQ264XAYD* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
205234777 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* | RXYQ120XAYD* |  | RXYQ360XAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
205234788 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ144XAYC* |  |  | RXYQ264XAYC* | Non-Ducted Indoor Units | 252000 | 10.8 | 20.1 | 282000 | 3.71 | 200000 | 2.27 | R-410A | 21
205234710 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ120XAYC* |  | RXYQ360XAYC* | Non-Ducted Indoor Units | 342000 | 10.5 | 19.1 | 384000 | 3.62 | 270000 | 2.28 | R-410A | 28.5
205234711 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ144XAYC* |  | RXYQ384XAYC* | Non-Ducted Indoor Units | 352000 | 9.6 | 18.3 | 398000 | 3.26 | 280000 | 2.24 | R-410A | 29.3333
205234868 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ144XAYC* |  |  | RXYQ264XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.2 | 18.3 | 282000 | 3.47 | 200000 | 2.18 | R-410A | 21
205234872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ120XAYC* |  | RXYQ360XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.1 | 384000 | 3.42 | 270000 | 2.19 | R-410A | 28.5
205234869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* | RXYQ144XAYC* |  |  | RXYQ288XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 18.6 | 306000 | 3.34 | 216000 | 2.16 | R-410A | 22.8333
205234789 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* | RXYQ144XAYC* |  |  | RXYQ288XAYC* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.1 | 306000 | 3.48 | 216000 | 2.24 | R-410A | 22.8333
205234791 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168XAYC* | RXYQ168XAYC* |  |  | RXYQ336XAYC* | Non-Ducted Indoor Units | 308000 | 9.8 | 18.9 | 338000 | 3.6 | 228000 | 2.11 | R-410A | 25.6667
205234871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168XAYC* | RXYQ168XAYC* |  |  | RXYQ336XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 308000 | 9.65 | 17.8 | 338000 | 3.4 | 228000 | 2.08 | R-410A | 25.6667
205234844 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
205234845 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ168XATJ* |  |  | RXYQ312XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
205234796 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
205234704 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
205234705 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ168XATJ* |  |  | RXYQ312XATJ* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
205234854 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
205234855 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ168XAYD* |  |  | RXYQ312XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
205234774 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
205234775 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ168XAYD* |  |  | RXYQ312XAYD* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
205234806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
208758288 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
208758289 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
208758290 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
208685685 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
208685686 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
208685687 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
208758307 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB | CHV6-144URB |  | CHV6-408URB | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
208758308 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB | CHV6-144URB |  | CHV6-408URB | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
208685704 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-408FFFH | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
208685705 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-408FFFH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
208685707 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-432FFFH | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
208685708 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-432FFFH | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
208685710 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-168FFFH |  | AVWT-456FFFH | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
208758310 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-144URB |  | CHV6-432URB | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
208758311 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-144URB |  | CHV6-432URB | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
208758313 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-168URB |  | CHV6-456URB | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
208685689 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH |  |  | AVWT-288FFFH | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
208685690 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH |  |  | AVWT-288FFFH | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
208685692 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-168FFFH |  |  | AVWT-312FFFH | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
208758292 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB |  |  | CHV6-288URB | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
208758293 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB |  |  | CHV6-288URB | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
208758295 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-168URB |  |  | CHV6-312URB | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
207826725 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH | AM216BXVGFH |  |  | AM432BXVGFH | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826729 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH | AM216BXVGFH |  |  | AM432BXVGFH | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207827292 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM432BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207826733 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH | AM216BXVGJH |  |  | AM432BXVGJH | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826737 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH | AM216BXVGJH |  |  | AM432BXVGJH | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207827296 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM432BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207826251 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR | AM216BXVGFR |  |  | AM432BXVGFR | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826256 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR | AM216BXVGFR |  |  | AM432BXVGFR | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207827277 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM432BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207826741 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR | AM216BXVGJR |  |  | AM432BXVGJR | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR | AM216BXVGJR |  |  | AM432BXVGJR | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207827300 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM432BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
208931871 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.45 | 20.1 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931873 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 19.8 | 308000 | 3.38 | 210000 | 2.16 | R-410A | 23
208931883 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 11 | 20.15 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931885 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 10.8 | 20.2 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931875 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.9 | 19.8 | 320000 | 3.38 | 214000 | 2.16 | R-410A | 24.8333
208931877 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.9 | 19.8 | 338000 | 3.38 | 224000 | 2.16 | R-410A | 26.6667
208931879 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 19.8 | 346000 | 3.38 | 232000 | 2.16 | R-410A | 28.6667
208931881 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.8 | 354000 | 3.38 | 240000 | 2.16 | R-410A | 30.5
208931893 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.45 | 20.1 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931895 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 19.8 | 308000 | 3.38 | 210000 | 2.16 | R-410A | 23
208931905 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 11 | 20.15 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931907 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 10.8 | 20.2 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931897 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.9 | 19.8 | 320000 | 3.38 | 214000 | 2.16 | R-410A | 24.8333
208931899 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.9 | 19.8 | 338000 | 3.38 | 224000 | 2.16 | R-410A | 26.6667
208931901 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 19.8 | 346000 | 3.38 | 232000 | 2.16 | R-410A | 28.6667
208931903 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.8 | 354000 | 3.38 | 240000 | 2.16 | R-410A | 30.5
209842413 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842423 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209863189 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209842432 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842442 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209863198 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209863199 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209842443 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209842433 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209863178 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209842204 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842194 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842195 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842205 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209863179 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209842462 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842452 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209863208 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209863209 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209842453 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842463 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209863188 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209842412 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842422 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
210691242 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
210691243 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
210691244 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
210691261 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-408FHFSHA | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
210691262 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-408FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
210691264 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-432FHFSHA | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
210691265 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-432FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
210691267 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-168FHFSHA |  | AVWT-456FHFSHA | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
210691246 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA |  |  | AVWT-288FHFSHA | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
210691247 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA |  |  | AVWT-288FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
210691249 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-168FHFSHA |  |  | AVWT-312FHFSHA | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
212928536 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Ducted Indoor Units | 240000 | 11.4 | 18.7 | 258000 | 3.5 | 162000 | 2.36 | R-410A | 20
212928537 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Non-Ducted Indoor Units | 240000 | 11.8 | 19 | 258000 | 3.8 | 162000 | 2.38 | R-410A | 20
212928545 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 240000 | 11.6 | 18.85 | 258000 | 3.65 | 162000 | 2.37 | R-410A | 20
212928548 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 240000 | 11.6 | 18.85 | 258000 | 3.65 | 162000 | 2.37 | R-410A | 20
212928541 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Ducted Indoor Units | 240000 | 11.4 | 18.7 | 258000 | 3.5 | 162000 | 2.36 | R-410A | 20
212928542 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Non-Ducted Indoor Units | 240000 | 11.8 | 19 | 258000 | 3.8 | 162000 | 2.38 | R-410A | 20
213686159 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
213686160 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
213686161 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
213686178 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-408FLFSH | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
213686179 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-408FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
213686181 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-432FLFSH | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
213686182 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-432FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
213686184 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-168FLFSH |  | AVWT-456FLFSH | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
213686163 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH |  |  | AVWT-288FLFSH | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
213686164 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH |  |  | AVWT-288FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
213686166 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-168FLFSH |  |  | AVWT-312FLFSH | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
201856734 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC264DXN1-(A) | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856735 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC264DXN1-(A) | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862870 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA264L4M-2Y | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862871 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA264L4M-2Y | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862872 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA288L4M-2Y | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862873 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA288L4M-2Y | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862874 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA096L4M-2Y |  | VRA312L4M-2Y | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862875 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA096L4M-2Y |  | VRA312L4M-2Y | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201862876 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y | VRA096L4M-2Y |  | VRA336L4M-2Y | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201862877 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y | VRA096L4M-2Y |  | VRA336L4M-2Y | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201856736 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC288DXN1-(A) | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856737 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC288DXN1-(A) | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856738 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856739 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC312DXN1-(A) | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201856740 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201856741 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC336DXN1-(A) | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201862894 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA264L4M-2G | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA264L4M-2G | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856758 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC264DZN1-(A) | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856759 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC264DZN1-(A) | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856760 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC288DZN1-(A) | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856761 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC288DZN1-(A) | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856762 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856763 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC312DZN1-(A) | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201856764 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201856765 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC336DZN1-(A) | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201862896 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA288L4M-2G | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862897 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA288L4M-2G | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862898 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA096L4M-2G |  | VRA312L4M-2G | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862899 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA096L4M-2G |  | VRA312L4M-2G | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201862900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G | VRA096L4M-2G |  | VRA336L4M-2G | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201862901 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G | VRA096L4M-2G |  | VRA336L4M-2G | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201856782 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC264DXN1-(A) | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856783 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC264DXN1-(A) | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862918 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA264L4M-2Y | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862919 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA264L4M-2Y | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862920 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA288L4M-2Y | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862921 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA288L4M-2Y | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862922 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA096L4M-2Y |  | VPA312L4M-2Y | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856784 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC288DXN1-(A) | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856785 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC288DXN1-(A) | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856786 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  | MV5-XC312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862940 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA264L4M-2G | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862941 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA264L4M-2G | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856804 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC264DZN1-(A) | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856805 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC264DZN1-(A) | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856806 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC288DZN1-(A) | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856807 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC288DZN1-(A) | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856808 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  | MV5-XC312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862942 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA288L4M-2G | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862943 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA288L4M-2G | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862944 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA096L4M-2G |  | VPA312L4M-2G | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201992877 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* | RXYQ144TAYC* |  |  | RXYQ288TAYC* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.1 | 306000 | 3.48 | 216000 | 2.24 | R-410A | 22.8333
202022808 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* | RXYQ144TAYC* |  |  | RXYQ288TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 18.6 | 306000 | 3.34 | 216000 | 2.16 | R-410A | 22.8333
202022810 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168TAYC* | RXYQ168TAYC* |  |  | RXYQ336TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 308000 | 9.65 | 17.8 | 338000 | 3.4 | 228000 | 2.08 | R-410A | 25.6667
202016263 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168TAYC* | RXYQ168TAYC* |  |  | RXYQ336TAYC* | Non-Ducted Indoor Units | 308000 | 9.8 | 18.9 | 338000 | 3.6 | 228000 | 2.11 | R-410A | 25.6667
202016265 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ120TAYC* |  | RXYQ360TAYC* | Non-Ducted Indoor Units | 342000 | 10.5 | 19.1 | 384000 | 3.62 | 270000 | 2.28 | R-410A | 28.5
201992876 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ144TAYC* |  |  | RXYQ264TAYC* | Non-Ducted Indoor Units | 252000 | 10.8 | 20.1 | 282000 | 3.71 | 200000 | 2.27 | R-410A | 21
201992870 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ144TAYC* |  | RXYQ384TAYC* | Non-Ducted Indoor Units | 352000 | 9.6 | 18.3 | 398000 | 3.26 | 280000 | 2.24 | R-410A | 29.3333
202022807 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ144TAYC* |  |  | RXYQ264TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.2 | 18.3 | 282000 | 3.47 | 200000 | 2.18 | R-410A | 21
202022811 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ120TAYC* |  | RXYQ360TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.1 | 384000 | 3.42 | 270000 | 2.19 | R-410A | 28.5
204572305 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
206799490 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
206799492 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204572313 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204442797 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204442805 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
10267498 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903135 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903117 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
201903119 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
208102065 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10267485 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10267486 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
208102045 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
208102046 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
208102050 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
208102051 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
208102055 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10267488 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10267489 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
10267492 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
201903122 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
201903123 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
201903127 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
202566112 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202566113 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
206453568 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
205281487 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
205281488 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
206453569 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453575 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM121CTE5 | ARUM121CTE5 |  | ARUM432CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
202566114 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202566115 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202566126 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM121CTE5 | ARUM121CTE5 |  | ARUM432CTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
202566116 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202566117 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202566118 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM121CTE5 |  |  | ARUM336CTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202566120 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202566122 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM168CTE5 |  |  | ARUM384CTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202566124 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
206453570 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453571 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM121CTE5 |  |  | ARUM336CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
206453572 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453573 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM168CTE5 |  |  | ARUM384CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453574 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
205281489 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
201903128 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G | VEP120C432G |  | VEP336C432G | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
201903120 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
201903124 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
201903126 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10267493 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-336WM/B-U(U) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
10267487 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10267490 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10267491 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102054 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102056 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102059 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G | VEP120C432G |  | VEP336C432G | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
208102049 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
208102044 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10267484 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
208102066 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102064 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903132 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903134 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10267496 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10267497 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
204442798 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442806 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442813 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR | AM216KXVGJR |  |  | AM432KXVGJR | Non-Ducted Indoor Units | 416000 | 9.8 | 21 | 460000 | 3.3 | 300000 | 2.4 | R-410A | 34.6667
10306454 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV288H3CDC749(A) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
204442753 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR | AM168HXVAFR |  |  | AM336JXVAFR | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
208102067 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP120C432Y | VEP120C432Y |  | VEP360C432Y | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102057 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102052 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10035096 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-312WM/B-F(U) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10257466 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10035094 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-288WM/B-F(U) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10257463 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10324126 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  | IOV312H3CDC753(A) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10306452 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV264H3CDC745(A) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10257464 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10032555 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-264WM/B-F(U) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
208102047 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
204442770 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM144FXVAJR | AM192HXVAJR |  | AM408JXVAJR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442755 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM144FXVAFR | AM192HXVAFR |  | AM408JXVAFR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442766 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442751 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
201903116 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
204442812 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR | AM216KXVGJR |  |  | AM408KXVGJR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442768 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR | AM168HXVAJR |  |  | AM336JXVAJR | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
10306460 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  | IOV360H3CDC761(A) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
9964029 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-360WM/B-F(U) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10257470 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP120C432Y | VEP120C432Y |  | VEP360C432Y | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10324127 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  | IOV312H3CDC753(A) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10306458 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  | IOV336H3CDC758(A) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
10035097 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-312WM/B-F(U) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10035098 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-336WM/B-F(U) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
208102058 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102062 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP120C432Y | VEP120C432Y |  | VEP336C432Y | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667

## Commercial Water Loop HP
AHRI Certified Reference Number | Date No Longer Eligible | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage | Tax Credit (IRA) Eligibility
202211049 |  | Water Loop | WaterFurnace | URD049*0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211050 |  | Water Loop | WaterFurnace | URD049*0*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211051 |  | Water Loop | WaterFurnace | URD049*3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211052 |  | Water Loop | WaterFurnace | URD049*3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211053 |  | Water Loop | WaterFurnace | URD049*3*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7167538 |  | Water Loop | CARRIER | 50PTD/H/V024***3/CA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167539 |  | Water Loop | CARRIER | 50PTD/H/V024***5/EA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167540 |  | Water Loop | CARRIER | 50PTD/H/V024***4/DA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167541 |  | Water Loop | CARRIER | 50PTD/H/V024***6/FA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167542 |  | Water Loop | CARRIER | 50PTD/H/V036***3/CA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167543 |  | Water Loop | CARRIER | 50PTD/H/V036***5/EA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167544 |  | Water Loop | CARRIER | 50PTD/H/V036***4/DA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167545 |  | Water Loop | CARRIER | 50PTD/H/V036***6/FA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
217752680 |  | Water Loop | DAIKIN | WSSH030K1*B*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217752682 |  | Water Loop | DAIKIN | WSSH030K1*B*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217752684 |  | Water Loop | DAIKIN | WSSH036K1*B*T |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
217752686 |  | Water Loop | DAIKIN | WSSH036K1*B*C |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
217752688 |  | Water Loop | DAIKIN | WSSH042K1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
7499552 |  | Water Loop | FHP | LM036-2VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499553 |  | Water Loop | FHP | LM036-3VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499554 |  | Water Loop | FHP | LM036-4VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499702 |  | Water Loop | BOSCH | SM036-1CF/HZ/VT |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
7519727 |  | Water Loop | GEOCOMFORT | GVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
7519748 |  | Water Loop | HYDRON MODULE | HVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
7519756 |  | Water Loop | TETCO | TVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
203380966 |  | Water Loop | BOSCH | EP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203380967 |  | Water Loop | BOSCH | EP042-3HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203380968 |  | Water Loop | BOSCH | EP042-4HZ*******B |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
215837877 |  | Water Loop | DAIKIN | WSSH048F3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837879 |  | Water Loop | DAIKIN | WSSH048K3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837880 |  | Water Loop | DAIKIN | WSSH048L3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837886 |  | Water Loop | DAIKIN | WSSH048F3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837887 |  | Water Loop | DAIKIN | WSSH048K3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837889 |  | Water Loop | DAIKIN | WSSH048L3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837895 |  | Water Loop | DAIKIN | WSSH060F3*C/S*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837896 |  | Water Loop | DAIKIN | WSSH060K3*C/S*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837904 |  | Water Loop | DAIKIN | WSSH060F3*C/S*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837905 |  | Water Loop | DAIKIN | WSSH060K3*C/S*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
10259059 |  | Water Loop | TETCO | TZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
7411231 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411380 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411778 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411949 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7412057 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7412253 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7412381 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7414142 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414232 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414335 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
215400080 |  | Water Loop | DAIKIN | WSMV015E1*C/S*T |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215400082 |  | Water Loop | DAIKIN | WSMV015E1*C/S*C |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215400094 |  | Water Loop | DAIKIN | WSMV024E1*C/S*T |  | 24700 | 18.03 | 28600 | 5.25 | 2.0583 | No
215400095 |  | Water Loop | DAIKIN | WSMV024F3*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215400098 |  | Water Loop | DAIKIN | WSMV024E1*C/S*C |  | 24700 | 18.03 | 28600 | 5.25 | 2.0583 | No
215400099 |  | Water Loop | DAIKIN | WSMV024F3*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215400114 |  | Water Loop | DAIKIN | WSMV036E1*C/S*P |  | 37300 | 17.25 | 43000 | 5.02 | 3.1083 | No
215400118 |  | Water Loop | DAIKIN | WSMV036E1*C/S*T |  | 37200 | 17.68 | 43100 | 5.17 | 3.1 | No
215400119 |  | Water Loop | DAIKIN | WSMV036F3*C/S*T |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
215400122 |  | Water Loop | DAIKIN | WSMV036E1*C/S*C |  | 37200 | 17.68 | 43100 | 5.17 | 3.1 | No
215400123 |  | Water Loop | DAIKIN | WSMV036F3*C/S*C |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
217754417 |  | Water Loop | DAIKIN | WSSH070F1*B*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217754421 |  | Water Loop | DAIKIN | WSSH070F1*B*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217754425 |  | Water Loop | DAIKIN | WSSV024F1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
216739926 |  | Water Loop | DAIKIN | WSNH036E1*C/S*C |  | 35200 | 17.4 | 42500 | 5.3 | 2.9333 | No
216739927 |  | Water Loop | DAIKIN | WSNH036F3*C/S*C |  | 35200 | 17.1 | 42500 | 5.2 | 2.9333 | No
216739928 |  | Water Loop | DAIKIN | WSNH036J1*C/S*C |  | 35200 | 17.1 | 42500 | 5.2 | 2.9333 | No
207200598 |  | Water Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
217967019 |  | Water Loop | TRANE | VSVK024A |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967021 |  | Water Loop | TRANE | VSVK033A |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967022 |  | Water Loop | TRANE | VSHK042A |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967023 |  | Water Loop | TRANE | VSVK042A |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
217967025 |  | Water Loop | TRANE | VSVK050A |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
217967028 |  | Water Loop | TRANE | VSHK024B |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217967029 |  | Water Loop | TRANE | VSVK024B |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967031 |  | Water Loop | TRANE | VSVK033B |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967032 |  | Water Loop | TRANE | VSHK042B |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967033 |  | Water Loop | TRANE | VSVK042B |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
217967035 |  | Water Loop | TRANE | VSVK050B |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
217967038 |  | Water Loop | TRANE | VSHK0244 |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217967039 |  | Water Loop | TRANE | VSVK0244 |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967041 |  | Water Loop | TRANE | VSVK0334 |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967042 |  | Water Loop | TRANE | VSHK0424 |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967043 |  | Water Loop | TRANE | VSVK0424 |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
9111998 |  | Water Loop | BOSCH | SM036-1VT/CF*-*****B |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | No
9113183 |  | Water Loop | BOSCH | SM036-1VT/CF*-*****B |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | Yes
207337513 |  | Water Loop | GEOSTAR | 103J036**1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | No
207337514 |  | Water Loop | GEOSTAR | 103J036**1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | No
207338127 |  | Water Loop | GEOSTAR | 141/142C036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
215399877 |  | Water Loop | DAIKIN | WSSV048L3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399880 |  | Water Loop | DAIKIN | WSSV048K3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399881 |  | Water Loop | DAIKIN | WSSV048L3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399884 |  | Water Loop | DAIKIN | WSSV060K3*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215399886 |  | Water Loop | DAIKIN | WSSV060K3*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217752690 |  | Water Loop | DAIKIN | WSSH042K1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217752692 |  | Water Loop | DAIKIN | WSSH048K1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217754501 |  | Water Loop | DAIKIN | WSTV024E1*B*C |  | 24300 | 17.59 | 28000 | 5.81 | 2.025 | No
217754502 |  | Water Loop | DAIKIN | WSTV024F1*B*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
217754509 |  | Water Loop | DAIKIN | WSTV036E1*B*C |  | 38100 | 18.45 | 41100 | 5.18 | 3.175 | No
217754510 |  | Water Loop | DAIKIN | WSTV036F1*B*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
217754513 |  | Water Loop | DAIKIN | WSTV042E1*B*C |  | 43500 | 17.3 | 50000 | 5.06 | 3.625 | No
217754517 |  | Water Loop | DAIKIN | WSTV048E1*B*C |  | 50800 | 17.62 | 58500 | 5.52 | 4.2333 | No
217754518 |  | Water Loop | DAIKIN | WSTV048F1*B*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
217754521 |  | Water Loop | DAIKIN | WSTV060E1*B*C |  | 60500 | 17.3 | 74700 | 5.5 | 5.0417 | No
8560938 |  | Water Loop | GEOCOMFORT | GVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560939 |  | Water Loop | HYDRON MODULE | HVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560940 |  | Water Loop | TETCO | TVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560941 |  | Water Loop | GEOCOMFORT | GVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560942 |  | Water Loop | HYDRON MODULE | HVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560943 |  | Water Loop | TETCO | TVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560946 |  | Water Loop | GEOCOMFORT | GVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
8560947 |  | Water Loop | HYDRON MODULE | HVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
8560948 |  | Water Loop | TETCO | TVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
8560949 |  | Water Loop | GEOCOMFORT | GVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
8560950 |  | Water Loop | HYDRON MODULE | HVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
8560951 |  | Water Loop | TETCO | TVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
203113888 |  | Water Loop | GEOSTAR | 103J036**1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
218158031 |  | Water Loop | YORK | Y5SS036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
218158036 |  | Water Loop | YORK | Y5SZ036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
218158041 |  | Water Loop | YORK | Y5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
218158046 |  | Water Loop | YORK | Y5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
9910757 |  | Water Loop | TETCO | TZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910758 |  | Water Loop | GEOCOMFORT | GZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910759 |  | Water Loop | HYDRON MODULE | HZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910760 |  | Water Loop | TETCO | TZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
216625542 |  | Water Loop | GEOSTAR | G5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625543 |  | Water Loop | GEOSTAR | G5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625770 |  | Water Loop | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625771 |  | Water Loop | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625772 |  | Water Loop | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625773 |  | Water Loop | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
5699505 |  | Water Loop | TRANE | VSVE0421 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699525 |  | Water Loop | TRANE | VSVE0422 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699526 |  | Water Loop | TRANE | VSVE0424 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699628 |  | Water Loop | TRANE | VSHE0241 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699631 |  | Water Loop | TRANE | VSHE0242 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699633 |  | Water Loop | TRANE | VSHE0244 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699639 |  | Water Loop | TRANE | VSHE0421 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
5699644 |  | Water Loop | TRANE | VSHE0422 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
5699650 |  | Water Loop | TRANE | VSHE0424 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
214771931 |  | Water Loop | TRANE | EXVK009A |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214771932 |  | Water Loop | TRANE | EXVK012A |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214771934 |  | Water Loop | TRANE | EXVK018A |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214771935 |  | Water Loop | TRANE | EXVK024A |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214771936 |  | Water Loop | TRANE | EXVK030A |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214771937 |  | Water Loop | TRANE | EXVK036A |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214771938 |  | Water Loop | TRANE | EXVK042A |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214771939 |  | Water Loop | TRANE | EXVK048A |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
217754537 |  | Water Loop | DAIKIN | WSMH024F1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754538 |  | Water Loop | DAIKIN | WSMH024K1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754541 |  | Water Loop | DAIKIN | WSMH024F1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754542 |  | Water Loop | DAIKIN | WSMH024K1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754549 |  | Water Loop | DAIKIN | WSMH030F1*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754550 |  | Water Loop | DAIKIN | WSMH030K1*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754553 |  | Water Loop | DAIKIN | WSMH030F1*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754554 |  | Water Loop | DAIKIN | WSMH030K1*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754575 |  | Water Loop | DAIKIN | WSMH042E1*C/S*T |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
217754581 |  | Water Loop | DAIKIN | WSMH042E1*C/S*C |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
202330563 |  | Water Loop | AAON, Inc. | M2-006-2-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
202330567 |  | Water Loop | AAON, Inc. | M2-006-3-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
202330571 |  | Water Loop | AAON, Inc. | M2-006-4-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
216772594 |  | Water Loop | Enertech | EZS018* |  | 19725 | 18 | 21900 | 5.5 | 1.6438 | Yes
213154467 |  | Water Loop | GeoSmart Energy | GS030**1*1********L |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
206342120 |  | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206342121 |  | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206342122 |  | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206345837 |  | Water Loop | HYDROTECH | WSS6006*7* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
216687114 |  | Water Loop | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
203238019 |  | Water Loop | BOSCH-GEO | BP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203253412 |  | Water Loop | BOSCH | BP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254606 |  | Water Loop | CARRIER | GB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203254607 |  | Water Loop | BRYANT | GB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254608 |  | Water Loop | ARCOAIRE | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203254609 |  | Water Loop | HEIL | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254610 |  | Water Loop | KEEPRITE | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254611 |  | Water Loop | TEMPSTAR | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254612 |  | Water Loop | COMFORTMAKER | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254614 |  | Water Loop | DAY & NIGHT | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
214771940 |  | Water Loop | TRANE | EXVK060A |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214771941 |  | Water Loop | TRANE | EXVK070A |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
217735426 |  | Water Loop | DAIKIN | WSSH024J1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217735427 |  | Water Loop | DAIKIN | WSSH024J1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217735428 |  | Water Loop | DAIKIN | WSSH030J1*B*T |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
217735429 |  | Water Loop | DAIKIN | WSSH030J1*B*C |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
217735430 |  | Water Loop | DAIKIN | WSSH036J1*B*T |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
217735431 |  | Water Loop | DAIKIN | WSSH036J1*B*C |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
217735432 |  | Water Loop | DAIKIN | WSSH042J1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217735433 |  | Water Loop | DAIKIN | WSSH042J1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217735434 |  | Water Loop | DAIKIN | WSTH024J1*B*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
217735438 |  | Water Loop | DAIKIN | WSTH036J1*B*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
217735440 |  | Water Loop | DAIKIN | WSTV024J1*B*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
217735444 |  | Water Loop | DAIKIN | WSTV036J1*B*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
7422309 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
6501918 |  | Water Loop | GEOSTAR | GBV/GBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501919 |  | Water Loop | GEOSTAR | GBV/GBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501920 |  | Water Loop | GEOSTAR | GBV/GBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501921 |  | Water Loop | GEOSTAR | GBV/GBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501922 |  | Water Loop | GEOSTAR | GBV/GBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501923 |  | Water Loop | GEOSTAR | GBV/GBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501924 |  | Water Loop | GEOSTAR | GBV/GBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501925 |  | Water Loop | GEOSTAR | GBV/GBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501926 |  | Water Loop | GEOSTAR | GBV/GBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501927 |  | Water Loop | GEOSTAR | GBV/GBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501928 |  | Water Loop | GEOSTAR | GBV/GBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501929 |  | Water Loop | GEOSTAR | GBV/GBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
9910548 |  | Water Loop | GEOCOMFORT | GZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910549 |  | Water Loop | HYDRON MODULE | HZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910550 |  | Water Loop | TETCO | TZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910551 |  | Water Loop | GEOCOMFORT | GZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910552 |  | Water Loop | HYDRON MODULE | HZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910553 |  | Water Loop | TETCO | TZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910554 |  | Water Loop | GEOCOMFORT | GZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910555 |  | Water Loop | HYDRON MODULE | HZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910556 |  | Water Loop | TETCO | TZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910557 |  | Water Loop | GEOCOMFORT | GZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910558 |  | Water Loop | HYDRON MODULE | HZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910559 |  | Water Loop | TETCO | TZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
205788285 |  | Water Loop | Johnson Controls | JSH/V/D036C*K B |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | No
205788286 |  | Water Loop | SKYMARK | JSH/V/D036C*K C |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | No
205788287 |  | Water Loop | Johnson Controls | JSH/V/D042C B |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | No
205788288 |  | Water Loop | SKYMARK | JSH/V/D042C C |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | No
205788289 |  | Water Loop | Johnson Controls | JSH/V/D042C*K B |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
205788290 |  | Water Loop | SKYMARK | JSH/V/D042C*K C |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
214772142 |  | Water Loop | TRANE | DXHK036A |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772143 |  | Water Loop | TRANE | DXHK048A |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772144 |  | Water Loop | TRANE | DXHK060A |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772146 |  | Water Loop | TRANE | DXVK024B |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772147 |  | Water Loop | TRANE | DXVK0244 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772148 |  | Water Loop | TRANE | DXVK036B |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
209156974 |  | Water Loop | AE Air | WSS6006*6* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
209156993 |  | Water Loop | AE Air | WSS6006*7* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
200083642 |  | Water Loop | COMFORT-AIRE | HZV/H/D036B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
200083643 |  | Water Loop | CENTURY | HZV/H/D036B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
200083644 |  | Water Loop | COMFORT-AIRE | HZV/H/D024B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
200083645 |  | Water Loop | CENTURY | HZV/H/D024B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
206346927 |  | Water Loop | DAIKIN | WVFC*030*K***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
216625774 |  | Water Loop | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625775 |  | Water Loop | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625776 |  | Water Loop | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625777 |  | Water Loop | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625778 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625779 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625780 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625781 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625782 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625783 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625784 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625785 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625786 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625787 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625788 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625789 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625790 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625791 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625792 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625793 |  | Water Loop | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625794 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625795 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625796 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625797 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625798 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625799 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625800 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625801 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625802 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625803 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625804 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625805 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625806 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625807 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625808 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625809 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625810 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625811 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625812 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625813 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625814 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625815 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625816 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625817 |  | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
207312172 |  | Water Loop | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207312173 |  | Water Loop | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207312225 |  | Water Loop | WaterFurnace | NSV/NSH030J1*(1,4) |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207312226 |  | Water Loop | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207312227 |  | Water Loop | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207312265 |  | Water Loop | WaterFurnace | NSV/NSH030J1*(0,3) |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | Yes
213502523 |  | Water Loop | DAIKIN | WSMH015A1*C/S*T |  | 15500 | 17.8 | 19900 | 5.9 | 1.2917 | No
213502524 |  | Water Loop | DAIKIN | WSMH015A1*C/S*C |  | 15500 | 17.8 | 19900 | 5.9 | 1.2917 | No
213502529 |  | Water Loop | DAIKIN | WSMH015E1*C/S*T |  | 15500 | 17.8 | 20000 | 5.9 | 1.2917 | No
213502530 |  | Water Loop | DAIKIN | WSMH015E1*C/S*C |  | 15500 | 17.8 | 20000 | 5.9 | 1.2917 | No
213502535 |  | Water Loop | DAIKIN | WSMH015J1*C/S*T |  | 15400 | 17 | 20000 | 5.8 | 1.2833 | No
213502536 |  | Water Loop | DAIKIN | WSMH015J1*C/S*C |  | 15400 | 17 | 20000 | 5.8 | 1.2833 | No
213502541 |  | Water Loop | DAIKIN | WSMH019E1*C/S*T |  | 19700 | 17 | 24200 | 5.2 | 1.6417 | No
213502542 |  | Water Loop | DAIKIN | WSMH019E1*C/S*C |  | 19700 | 17 | 24200 | 5.2 | 1.6417 | No
213502547 |  | Water Loop | DAIKIN | WSMH019J1*C/S*T |  | 19700 | 17 | 24200 | 5.1 | 1.6417 | No
213502548 |  | Water Loop | DAIKIN | WSMH019J1*C/S*C |  | 19700 | 17 | 24200 | 5.1 | 1.6417 | No
213502553 |  | Water Loop | DAIKIN | WSMH024E1*C/S*T |  | 24800 | 17.5 | 30700 | 5.6 | 2.0667 | No
213502554 |  | Water Loop | DAIKIN | WSMH024E1*C/S*C |  | 24800 | 17.5 | 30700 | 5.6 | 2.0667 | No
213502559 |  | Water Loop | DAIKIN | WSMH030E1*C/S*T |  | 28300 | 17.6 | 35300 | 5.7 | 2.3583 | No
213502560 |  | Water Loop | DAIKIN | WSMH030E1*C/S*C |  | 28300 | 17.6 | 35300 | 5.7 | 2.3583 | No
9035993 |  | Water Loop | GEOCOMFORT | GZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
9035994 |  | Water Loop | HYDRON MODULE | HZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
205767467 |  | Water Loop | ClimateMaster | QEV/H/D1860 |  | 48000 | 17.3 | 60000 | 5.5 | 4 | Yes
205767473 |  | Water Loop | ClimateMaster | TEV/H/D026B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
205767474 |  | Water Loop | ClimateMaster | TEV/H/D038B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
215400192 |  | Water Loop | DAIKIN | WSSV030J1*B*C |  | 29200 | 18.02 | 34500 | 5.67 | 2.4333 | No
215400193 |  | Water Loop | DAIKIN | WSSV030K3*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215400196 |  | Water Loop | DAIKIN | WSSV036J1*B*T |  | 39000 | 17.94 | 44100 | 5.35 | 3.25 | No
215400197 |  | Water Loop | DAIKIN | WSSV036K3*B*T |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
215400200 |  | Water Loop | DAIKIN | WSSV036J1*B*C |  | 39000 | 17.94 | 44100 | 5.35 | 3.25 | No
215400201 |  | Water Loop | DAIKIN | WSSV036K3*B*C |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
215400204 |  | Water Loop | DAIKIN | WSSV042E1*B*T |  | 43000 | 18.36 | 47600 | 5.43 | 3.5833 | No
215400205 |  | Water Loop | DAIKIN | WSSV042F3*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215400208 |  | Water Loop | DAIKIN | WSSV042E1*B*C |  | 43000 | 18.36 | 47600 | 5.43 | 3.5833 | No
215400209 |  | Water Loop | DAIKIN | WSSV042F3*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215400212 |  | Water Loop | DAIKIN | WSSV048E1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400213 |  | Water Loop | DAIKIN | WSSV048F3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400216 |  | Water Loop | DAIKIN | WSSV048E1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400217 |  | Water Loop | DAIKIN | WSSV048F3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400220 |  | Water Loop | DAIKIN | WSSV060E1*B*T |  | 64000 | 17.4 | 78000 | 5.3 | 5.3333 | No
215400221 |  | Water Loop | DAIKIN | WSSV060F3*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215400222 |  | Water Loop | DAIKIN | WSSV060E1*B*C |  | 64000 | 17.4 | 78000 | 5.3 | 5.3333 | No
215400223 |  | Water Loop | DAIKIN | WSSV060F3*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215402546 |  | Water Loop | DAIKIN | WSSV007E1*B*T |  | 7100 | 17.99 | 8100 | 5.49 | 0.59167 | No
215402548 |  | Water Loop | DAIKIN | WSSV009E1*B*T |  | 9200 | 17.49 | 11000 | 4.98 | 0.76667 | No
215402550 |  | Water Loop | DAIKIN | WSSV024E1*B*T |  | 24400 | 18.37 | 28000 | 5.79 | 2.0333 | No
215402551 |  | Water Loop | DAIKIN | WSSV024F3*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215402554 |  | Water Loop | DAIKIN | WSSV024E1*B*C |  | 24400 | 18.37 | 28000 | 5.79 | 2.0333 | No
215402555 |  | Water Loop | DAIKIN | WSSV024F3*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215402558 |  | Water Loop | DAIKIN | WSSV030E1*B*T |  | 29200 | 19.17 | 34500 | 5.67 | 2.4333 | No
215402559 |  | Water Loop | DAIKIN | WSSV030F3*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215837673 |  | Water Loop | DAIKIN | WSMH024F3*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837675 |  | Water Loop | DAIKIN | WSMH024J1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837676 |  | Water Loop | DAIKIN | WSMH024K3*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837681 |  | Water Loop | DAIKIN | WSMH024F3*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837683 |  | Water Loop | DAIKIN | WSMH024J1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837685 |  | Water Loop | DAIKIN | WSMH024K3*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837698 |  | Water Loop | DAIKIN | WSMH030F3*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
215837701 |  | Water Loop | DAIKIN | WSMH030K3*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
215837707 |  | Water Loop | DAIKIN | WSMH030F3*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
215837709 |  | Water Loop | DAIKIN | WSMH030K3*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
218157959 |  | Water Loop | YORK | Y5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157960 |  | Water Loop | YORK | Y5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157961 |  | Water Loop | YORK | Y5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157962 |  | Water Loop | YORK | Y5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157963 |  | Water Loop | YORK | Y5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157964 |  | Water Loop | YORK | Y5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157965 |  | Water Loop | YORK | Y5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157976 |  | Water Loop | YORK | Y5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157977 |  | Water Loop | YORK | Y5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157978 |  | Water Loop | YORK | Y5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157979 |  | Water Loop | YORK | Y5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157980 |  | Water Loop | YORK | Y5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157981 |  | Water Loop | YORK | Y5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157982 |  | Water Loop | YORK | Y5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157983 |  | Water Loop | YORK | Y5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157984 |  | Water Loop | YORK | Y5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
218157985 |  | Water Loop | YORK | Y5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
8740368 |  | Water Loop | GEOCOMFORT | GVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
216439574 |  | Water Loop | GeoSmart Energy | S5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
216687119 |  | Water Loop | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216687732 |  | Water Loop | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216687737 |  | Water Loop | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216621313 |  | Water Loop | GEOSTAR | G5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216621314 |  | Water Loop | GEOSTAR | G5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216621315 |  | Water Loop | GEOSTAR | G5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216621316 |  | Water Loop | GEOSTAR | G5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216621333 |  | Water Loop | GEOSTAR | G5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621334 |  | Water Loop | GEOSTAR | G5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621335 |  | Water Loop | GEOSTAR | G5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621336 |  | Water Loop | GEOSTAR | G5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621337 |  | Water Loop | GEOSTAR | G5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621338 |  | Water Loop | GEOSTAR | G5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621339 |  | Water Loop | GEOSTAR | G5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621340 |  | Water Loop | GEOSTAR | G5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621341 |  | Water Loop | GEOSTAR | G5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621342 |  | Water Loop | GEOSTAR | G5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215415909 |  | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215415910 |  | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215415911 |  | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 38000 | 17.5 | 43100 | 5.5 | 3.1667 | Yes
215415912 |  | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 38000 | 17.5 | 43100 | 5.5 | 3.1667 | Yes
215415913 |  | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 51000 | 18 | 58700 | 5.6 | 4.25 | Yes
215415914 |  | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 51000 | 18 | 58700 | 5.6 | 4.25 | Yes
215285739 |  | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215285740 |  | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 38000 | 17.5 | 43100 | 5.5 | 3.1667 | Yes
215285741 |  | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 51000 | 18 | 58700 | 5.6 | 4.25 | Yes
217531660 |  | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)006A |  | 6300 | 17 | 7600 | 5.5 | 0.525 | Yes
215399856 |  | Water Loop | DAIKIN | WSSV015A1*B*T |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215399857 |  | Water Loop | DAIKIN | WSSV015J1*B*T |  | 16100 | 18.01 | 18600 | 5.72 | 1.3417 | No
215399860 |  | Water Loop | DAIKIN | WSSV015A1*B*C |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215399861 |  | Water Loop | DAIKIN | WSSV015J1*B*C |  | 16100 | 18.01 | 18600 | 5.72 | 1.3417 | No
215399864 |  | Water Loop | DAIKIN | WSSV019J1*B*T |  | 19600 | 17.18 | 23500 | 5.23 | 1.6333 | No
215399866 |  | Water Loop | DAIKIN | WSSV019J1*B*C |  | 19600 | 17.18 | 23500 | 5.23 | 1.6333 | No
215399868 |  | Water Loop | DAIKIN | WSSV042J1*B*T |  | 42570 | 18.17 | 47124 | 5.38 | 3.5475 | No
215399869 |  | Water Loop | DAIKIN | WSSV042K3*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215399872 |  | Water Loop | DAIKIN | WSSV042J1*B*C |  | 42570 | 18.17 | 47124 | 5.38 | 3.5475 | No
215399873 |  | Water Loop | DAIKIN | WSSV042K3*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215399876 |  | Water Loop | DAIKIN | WSSV048K3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752676 |  | Water Loop | DAIKIN | WSSH024K1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217752678 |  | Water Loop | DAIKIN | WSSH024K1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
216759817 |  | Water Loop | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216759822 |  | Water Loop | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216759827 |  | Water Loop | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216759832 |  | Water Loop | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
214063753 |  | Water Loop | GeoSmart Energy | GBV/GBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063754 |  | Water Loop | GeoSmart Energy | GBV/GBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063756 |  | Water Loop | GeoSmart Energy | GBV/GBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063757 |  | Water Loop | GeoSmart Energy | GBV/GBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063762 |  | Water Loop | GeoSmart Energy | GBV/GBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214063763 |  | Water Loop | GeoSmart Energy | GBV/GBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063764 |  | Water Loop | GeoSmart Energy | GBV/GBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063765 |  | Water Loop | GeoSmart Energy | GBV/GBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214063766 |  | Water Loop | GeoSmart Energy | GBV/GBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063767 |  | Water Loop | GeoSmart Energy | GBV/GBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063769 |  | Water Loop | GeoSmart Energy | GBV/GBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063770 |  | Water Loop | GeoSmart Energy | GBV/GBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063772 |  | Water Loop | GeoSmart Energy | GBV/GBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063773 |  | Water Loop | GeoSmart Energy | GBV/GBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063774 |  | Water Loop | GeoSmart Energy | GBV/GBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063775 |  | Water Loop | GeoSmart Energy | GBV/GBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063776 |  | Water Loop | GeoSmart Energy | GBV/GBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063777 |  | Water Loop | GeoSmart Energy | GBV/GBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063778 |  | Water Loop | GeoSmart Energy | GBV/GBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214063779 |  | Water Loop | GeoSmart Energy | GBV/GBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214063780 |  | Water Loop | GeoSmart Energy | GBV/GBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214063781 |  | Water Loop | GeoSmart Energy | GBV/GBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
215837835 |  | Water Loop | DAIKIN | WSSH030F3*C/S*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837836 |  | Water Loop | DAIKIN | WSSH030J1*C/S*C |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
215837837 |  | Water Loop | DAIKIN | WSSH030K3*C/S*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837843 |  | Water Loop | DAIKIN | WSSH036F3*C/S*T |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
215837844 |  | Water Loop | DAIKIN | WSSH036J1*C/S*T |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
215837845 |  | Water Loop | DAIKIN | WSSH036K3*C/S*T |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
215837851 |  | Water Loop | DAIKIN | WSSH036F3*C/S*C |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
215837853 |  | Water Loop | DAIKIN | WSSH036J1*C/S*C |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
215837854 |  | Water Loop | DAIKIN | WSSH036K3*C/S*C |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
215837859 |  | Water Loop | DAIKIN | WSSH042F3*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837860 |  | Water Loop | DAIKIN | WSSH042J1*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837862 |  | Water Loop | DAIKIN | WSSH042K3*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837867 |  | Water Loop | DAIKIN | WSSH042F3*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837869 |  | Water Loop | DAIKIN | WSSH042J1*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837870 |  | Water Loop | DAIKIN | WSSH042K3*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
7411100 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
207348707 |  | Water Loop | WaterFurnace | URD038*0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348708 |  | Water Loop | WaterFurnace | URD038*0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348709 |  | Water Loop | WaterFurnace | URD038*0*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348710 |  | Water Loop | WaterFurnace | URD038*3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348711 |  | Water Loop | WaterFurnace | URD038*3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348712 |  | Water Loop | WaterFurnace | URD038*3*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348713 |  | Water Loop | WaterFurnace | URD038*4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348714 |  | Water Loop | WaterFurnace | URD038*4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348715 |  | Water Loop | WaterFurnace | URD038*4*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348716 |  | Water Loop | WaterFurnace | URD049*0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348717 |  | Water Loop | WaterFurnace | URD049*0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348718 |  | Water Loop | WaterFurnace | URD049*0*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348719 |  | Water Loop | WaterFurnace | URD049*3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348720 |  | Water Loop | WaterFurnace | URD049*3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348721 |  | Water Loop | WaterFurnace | URD049*3*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348722 |  | Water Loop | WaterFurnace | URD049*4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348723 |  | Water Loop | WaterFurnace | URD049*4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348724 |  | Water Loop | WaterFurnace | URD049*4*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207323903 |  | Water Loop | WaterFurnace | NSZ036J1* | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207323912 |  | Water Loop | WaterFurnace | NSZ036J1* | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207324064 |  | Water Loop | WaterFurnace | NVV/NVH036C1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
211594262 |  | Water Loop | TRANE | EXHG0704 |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
211594266 |  | Water Loop | TRANE | DXHG036B |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594267 |  | Water Loop | TRANE | DXHG0364 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594268 |  | Water Loop | TRANE | DXHG0367 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594269 |  | Water Loop | TRANE | DXHG048B |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594270 |  | Water Loop | TRANE | DXHG0484 |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594271 |  | Water Loop | TRANE | DXHG060B |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
211594272 |  | Water Loop | TRANE | DXHG0604 |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
215748227 |  | Water Loop | ClimateMaster | SMT(S,M)24A*Q |  | 25000 | 17.6 | 28000 | 5.1 | 2.0833 | No
215748230 |  | Water Loop | ClimateMaster | SMT(S,M)30A*Q |  | 30000 | 17 | 35500 | 5.3 | 2.5 | No
218157947 |  | Water Loop | YORK | Y5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157948 |  | Water Loop | YORK | Y5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157949 |  | Water Loop | YORK | Y5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157950 |  | Water Loop | YORK | Y5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157951 |  | Water Loop | YORK | Y5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157952 |  | Water Loop | YORK | Y5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157953 |  | Water Loop | YORK | Y5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157954 |  | Water Loop | YORK | Y5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157955 |  | Water Loop | YORK | Y5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157956 |  | Water Loop | YORK | Y5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157957 |  | Water Loop | YORK | Y5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
218157958 |  | Water Loop | YORK | Y5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
9910584 |  | Water Loop | GEOCOMFORT | GZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910585 |  | Water Loop | HYDRON MODULE | HZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910586 |  | Water Loop | TETCO | TZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910587 |  | Water Loop | GEOCOMFORT | GZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910588 |  | Water Loop | HYDRON MODULE | HZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910589 |  | Water Loop | TETCO | TZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910590 |  | Water Loop | GEOCOMFORT | GZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910591 |  | Water Loop | HYDRON MODULE | HZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910592 |  | Water Loop | TETCO | TZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910593 |  | Water Loop | GEOCOMFORT | GZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910594 |  | Water Loop | HYDRON MODULE | HZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910595 |  | Water Loop | TETCO | TZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910756 |  | Water Loop | HYDRON MODULE | HZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
5220675 |  | Water Loop | DAIKIN | WGSV/WGSH030B*E |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220676 |  | Water Loop | DAIKIN | WGSV/WGSH030B*F |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220677 |  | Water Loop | DAIKIN | WGSV/WGSH030B*J |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220678 |  | Water Loop | DAIKIN | WGSV/WGSH030B*K |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220681 |  | Water Loop | DAIKIN | WGSV/WGSH036B*E |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
201907628 |  | Water Loop | WaterFurnace | URD038*4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907629 |  | Water Loop | WaterFurnace | URD038*4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907630 |  | Water Loop | WaterFurnace | URD038*4*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907631 |  | Water Loop | WaterFurnace | URD049*4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
201907632 |  | Water Loop | WaterFurnace | URD049*4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
201907633 |  | Water Loop | WaterFurnace | URD049*4*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
211594132 |  | Water Loop | TRANE | EXHG018A |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
211594133 |  | Water Loop | TRANE | EXHG024A |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594134 |  | Water Loop | TRANE | EXHG030A |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594135 |  | Water Loop | TRANE | EXHG036A |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594136 |  | Water Loop | TRANE | EXHG042A |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594137 |  | Water Loop | TRANE | EXHG048A |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594138 |  | Water Loop | TRANE | EXHG060A |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594139 |  | Water Loop | TRANE | EXHG070A |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
202921957 |  | Water Loop | FHP | EP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921958 |  | Water Loop | FHP | EP036-3VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921959 |  | Water Loop | FHP | EP036-4VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921960 |  | Water Loop | BOSCH | BP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
207349388 |  | Water Loop | WaterFurnace | NBV/NBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349389 |  | Water Loop | WaterFurnace | NBV/NBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349390 |  | Water Loop | WaterFurnace | NBV/NBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349391 |  | Water Loop | WaterFurnace | NBV/NBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349392 |  | Water Loop | WaterFurnace | NBV/NBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349393 |  | Water Loop | WaterFurnace | NBV/NBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349394 |  | Water Loop | WaterFurnace | NBV/NBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349395 |  | Water Loop | WaterFurnace | NBV/NBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349396 |  | Water Loop | WaterFurnace | NBV/NBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349397 |  | Water Loop | WaterFurnace | NBV/NBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349398 |  | Water Loop | WaterFurnace | NBV/NBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349399 |  | Water Loop | WaterFurnace | NBV/NBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349400 |  | Water Loop | WaterFurnace | NBV/NBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349409 |  | Water Loop | WaterFurnace | NBV/NBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
215400184 |  | Water Loop | DAIKIN | WSSV024J1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400185 |  | Water Loop | DAIKIN | WSSV024K3*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400188 |  | Water Loop | DAIKIN | WSSV030J1*B*T |  | 29200 | 18.02 | 34500 | 5.67 | 2.4333 | No
215400189 |  | Water Loop | DAIKIN | WSSV030K3*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
216625485 |  | Water Loop | GEOSTAR | G5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625486 |  | Water Loop | GEOSTAR | G5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625487 |  | Water Loop | GEOSTAR | G5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625488 |  | Water Loop | GEOSTAR | G5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625489 |  | Water Loop | GEOSTAR | G5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625490 |  | Water Loop | GEOSTAR | G5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625491 |  | Water Loop | GEOSTAR | G5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625492 |  | Water Loop | GEOSTAR | G5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625493 |  | Water Loop | GEOSTAR | G5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625494 |  | Water Loop | GEOSTAR | G5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625495 |  | Water Loop | GEOSTAR | G5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625496 |  | Water Loop | GEOSTAR | G5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625497 |  | Water Loop | GEOSTAR | G5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625498 |  | Water Loop | GEOSTAR | G5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625499 |  | Water Loop | GEOSTAR | G5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625500 |  | Water Loop | GEOSTAR | G5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625501 |  | Water Loop | GEOSTAR | G5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625502 |  | Water Loop | GEOSTAR | G5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625503 |  | Water Loop | GEOSTAR | G5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625504 |  | Water Loop | GEOSTAR | G5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
207335136 |  | Water Loop | GEOSTAR | 101/102J030**1*(1,4)***** |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335137 |  | Water Loop | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207335138 |  | Water Loop | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
215399772 |  | Water Loop | DAIKIN | WSMV015A1*C/S*T |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215399776 |  | Water Loop | DAIKIN | WSMV015A1*C/S*C |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215399790 |  | Water Loop | DAIKIN | WSMV024J1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399791 |  | Water Loop | DAIKIN | WSMV024K3*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399794 |  | Water Loop | DAIKIN | WSMV024J1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399795 |  | Water Loop | DAIKIN | WSMV024K3*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399815 |  | Water Loop | DAIKIN | WSMV036K3*C/S*T |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
215399819 |  | Water Loop | DAIKIN | WSMV036K3*C/S*C |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
215268667 |  | Water Loop | WaterFurnace | V5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268668 |  | Water Loop | WaterFurnace | V5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268669 |  | Water Loop | WaterFurnace | V5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268670 |  | Water Loop | WaterFurnace | V5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268682 |  | Water Loop | WaterFurnace | V5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268683 |  | Water Loop | WaterFurnace | V5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268684 |  | Water Loop | WaterFurnace | V5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268685 |  | Water Loop | WaterFurnace | V5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268686 |  | Water Loop | WaterFurnace | V5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268687 |  | Water Loop | WaterFurnace | V5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268688 |  | Water Loop | WaterFurnace | V5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268689 |  | Water Loop | WaterFurnace | V5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268690 |  | Water Loop | WaterFurnace | V5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268691 |  | Water Loop | WaterFurnace | V5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268692 |  | Water Loop | WaterFurnace | V5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268693 |  | Water Loop | WaterFurnace | V5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268694 |  | Water Loop | WaterFurnace | V5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268695 |  | Water Loop | WaterFurnace | V5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268696 |  | Water Loop | WaterFurnace | V5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268697 |  | Water Loop | WaterFurnace | V5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268698 |  | Water Loop | WaterFurnace | V5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268699 |  | Water Loop | WaterFurnace | V5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268700 |  | Water Loop | WaterFurnace | V5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268701 |  | Water Loop | WaterFurnace | V5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
206726680 |  | Water Loop | WaterFurnace | UVV/UVH024**0*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
206726691 |  | Water Loop | WaterFurnace | UVV/UVH024**3*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
206726692 |  | Water Loop | WaterFurnace | UVV/UVH024**4*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
206726812 |  | Water Loop | GEOCOMFORT | GBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726813 |  | Water Loop | GEOCOMFORT | GBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726814 |  | Water Loop | HYDRON MODULE | HBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726815 |  | Water Loop | HYDRON MODULE | HBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726816 |  | Water Loop | TETCO | TBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726817 |  | Water Loop | TETCO | TBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726818 |  | Water Loop | GEOCOMFORT | GBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726819 |  | Water Loop | GEOCOMFORT | GBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
206726820 |  | Water Loop | HYDRON MODULE | HBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726821 |  | Water Loop | HYDRON MODULE | HBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
206726822 |  | Water Loop | TETCO | TBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726823 |  | Water Loop | TETCO | TBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
218157885 |  | Water Loop | YORK | Y5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
218157886 |  | Water Loop | YORK | Y5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
9910449 |  | Water Loop | GEOCOMFORT | GZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
9910450 |  | Water Loop | HYDRON MODULE | HZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
9910451 |  | Water Loop | TETCO | TZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
9910452 |  | Water Loop | GEOCOMFORT | GZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
9910453 |  | Water Loop | HYDRON MODULE | HZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
9910454 |  | Water Loop | TETCO | TZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
201907610 |  | Water Loop | WaterFurnace | URS036*0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907611 |  | Water Loop | WaterFurnace | URS036*0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907612 |  | Water Loop | WaterFurnace | URS036*0*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907613 |  | Water Loop | WaterFurnace | URS036*3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7414470 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414553 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414651 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414828 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414896 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415098 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415209 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7415301 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415373 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415878 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416559 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416782 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416889 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417060 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417146 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417329 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417419 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417586 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417698 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417776 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417867 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417918 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417992 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418047 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418154 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418360 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418435 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418635 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418715 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418887 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418965 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7421327 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421397 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421438 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421969 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421970 |  | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
216014181 |  | Water Loop | RHEEM | RPVV/H/D036D |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
216054107 |  | Water Loop | WaterFurnace | W5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
215852846 |  | Water Loop | DAIKIN | WSTH024E1*C/S*C |  | 24500 | 17.53 | 26100 | 5.29 | 2.0417 | No
215852847 |  | Water Loop | DAIKIN | WSTH024F3*C/S*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
215852850 |  | Water Loop | DAIKIN | WSTH030E1*C/S*C |  | 31400 | 17.12 | 34900 | 5.36 | 2.6167 | No
215852854 |  | Water Loop | DAIKIN | WSTH036E1*C/S*C |  | 38000 | 18.43 | 42900 | 5.36 | 3.1667 | No
215852855 |  | Water Loop | DAIKIN | WSTH036F3*C/S*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
215852858 |  | Water Loop | DAIKIN | WSTH042E1*C/S*C |  | 44000 | 17.59 | 50300 | 5.12 | 3.6667 | No
215852859 |  | Water Loop | DAIKIN | WSTH042F3*C/S*C |  | 44000 | 17.24 | 50300 | 5.02 | 3.6667 | No
215852868 |  | Water Loop | DAIKIN | WSTV024E1*C/S*C |  | 24300 | 17.59 | 28000 | 5.81 | 2.025 | No
215852869 |  | Water Loop | DAIKIN | WSTV024F3*C/S*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
215852874 |  | Water Loop | DAIKIN | WSTV036E1*C/S*C |  | 38100 | 18.45 | 41100 | 5.18 | 3.175 | No
215852875 |  | Water Loop | DAIKIN | WSTV036F3*C/S*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
215852878 |  | Water Loop | DAIKIN | WSTV042E1*C/S*C |  | 43500 | 17.3 | 50000 | 5.06 | 3.625 | No
215852882 |  | Water Loop | DAIKIN | WSTV048E1*C/S*C |  | 50800 | 17.62 | 58500 | 5.52 | 4.2333 | No
215852883 |  | Water Loop | DAIKIN | WSTV048F3*C/S*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
215852884 |  | Water Loop | DAIKIN | WSTV060E1*C/S*C |  | 60500 | 17.3 | 74700 | 5.5 | 5.0417 | No
215866231 |  | Water Loop | ClimateMaster | SMT24A*L |  | 25000 | 17.6 | 28000 | 5.1 | 2.0833 | No
215866538 |  | Water Loop | DAIKIN | WSTH048E1*C/S*C |  | 48200 | 17.34 | 56900 | 5.08 | 4.0167 | No
215268745 |  | Water Loop | WaterFurnace | V5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268746 |  | Water Loop | WaterFurnace | V5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268747 |  | Water Loop | WaterFurnace | V5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268748 |  | Water Loop | WaterFurnace | V5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268749 |  | Water Loop | WaterFurnace | V5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268750 |  | Water Loop | WaterFurnace | V5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268751 |  | Water Loop | WaterFurnace | V5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268752 |  | Water Loop | WaterFurnace | V5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268753 |  | Water Loop | WaterFurnace | V5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268754 |  | Water Loop | WaterFurnace | V5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215746915 |  | Water Loop | TRANE | GSK036A3 |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746916 |  | Water Loop | TRANE | GSK048A3 |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746918 |  | Water Loop | TRANE | GSK060A3 |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746919 |  | Water Loop | TRANE | GSK072A3 |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746920 |  | Water Loop | TRANE | GSK090A3 |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
215746922 |  | Water Loop | TRANE | GSK120A3 |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
215746923 |  | Water Loop | TRANE | GSK036A4 |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746924 |  | Water Loop | TRANE | GSK036AW |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746925 |  | Water Loop | TRANE | GSK048A4 |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746926 |  | Water Loop | TRANE | GSK048AW |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746927 |  | Water Loop | TRANE | GSK060A4 |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746928 |  | Water Loop | TRANE | GSK060AW |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746929 |  | Water Loop | TRANE | GSK072A4 |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746930 |  | Water Loop | TRANE | GSK072AW |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746931 |  | Water Loop | TRANE | GSK090A4 |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
215746932 |  | Water Loop | TRANE | GSK090AW |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
215746935 |  | Water Loop | TRANE | GSK120A4 |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
215746936 |  | Water Loop | TRANE | GSK120AW |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
217754428 |  | Water Loop | DAIKIN | WSSV024F1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217754431 |  | Water Loop | DAIKIN | WSSV030F1*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217754434 |  | Water Loop | DAIKIN | WSSV030F1*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217754437 |  | Water Loop | DAIKIN | WSSV036F1*B*T |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
217754440 |  | Water Loop | DAIKIN | WSSV036F1*B*C |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
217754443 |  | Water Loop | DAIKIN | WSSV042F1*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217754446 |  | Water Loop | DAIKIN | WSSV042F1*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217754449 |  | Water Loop | DAIKIN | WSSV048F1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217754453 |  | Water Loop | DAIKIN | WSSV048F1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217754457 |  | Water Loop | DAIKIN | WSSV060F1*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217754461 |  | Water Loop | DAIKIN | WSSV060F1*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
207177466 |  | Water Loop | TRANE | EXVG018A |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
207177467 |  | Water Loop | TRANE | EXVG0187 |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
207177468 |  | Water Loop | TRANE | EXVG024A |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177469 |  | Water Loop | TRANE | EXVG024B |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177470 |  | Water Loop | TRANE | EXVG0244 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177471 |  | Water Loop | TRANE | EXVG0247 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177472 |  | Water Loop | TRANE | EXVG030A |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177473 |  | Water Loop | TRANE | EXVG030B |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177474 |  | Water Loop | TRANE | EXVG0304 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177475 |  | Water Loop | TRANE | EXVG0307 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177476 |  | Water Loop | TRANE | EXVG036A |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177477 |  | Water Loop | TRANE | EXVG036B |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177478 |  | Water Loop | TRANE | EXVG0364 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177479 |  | Water Loop | TRANE | EXVG0367 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177480 |  | Water Loop | TRANE | EXVG042A |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177481 |  | Water Loop | TRANE | EXVG042B |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177482 |  | Water Loop | TRANE | EXVG0424 |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177483 |  | Water Loop | TRANE | EXVG048A |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177484 |  | Water Loop | TRANE | EXVG048B |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177485 |  | Water Loop | TRANE | EXVG0484 |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177486 |  | Water Loop | TRANE | EXVG060A |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177487 |  | Water Loop | TRANE | EXVG060B |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177488 |  | Water Loop | TRANE | EXVG0604 |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177489 |  | Water Loop | TRANE | EXVG070A |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177490 |  | Water Loop | TRANE | EXVG070B |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177491 |  | Water Loop | TRANE | EXVG0704 |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177496 |  | Water Loop | TRANE | DXVG036A |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177497 |  | Water Loop | TRANE | DXVG036B |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177498 |  | Water Loop | TRANE | DXVG0364 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177499 |  | Water Loop | TRANE | DXVG0367 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177500 |  | Water Loop | TRANE | DXVG048A |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207177501 |  | Water Loop | TRANE | DXVG048B |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207177502 |  | Water Loop | TRANE | DXVG0484 |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207200605 |  | Water Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207200614 |  | Water Loop | GeoSmart Energy | VI036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
206347035 |  | Water Loop | DAIKIN | WCCH*015*J***14* |  | 15600 | 17.6 | 17200 | 5.6 | 1.3 | No
206347037 |  | Water Loop | DAIKIN | WCCH*015*E***14* |  | 16000 | 17.6 | 18100 | 5.6 | 1.3333 | No
206347960 |  | Water Loop | HYDROTECH | WSS6006*6* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
202262237 |  | Water Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205996643 |  | Water Loop | Johnson Controls | JEV/H/D026B B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | No
205996644 |  | Water Loop | Johnson Controls | JEV/H/D038B B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | No
203383883 |  | Water Loop | CARRIER | 50PSH042***3/CA |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383884 |  | Water Loop | CARRIER | 50PSH042***5/EA |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383885 |  | Water Loop | CARRIER | 50PSH042***6/FA |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
203383899 |  | Water Loop | FHP | EP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383900 |  | Water Loop | FHP | EP042-3HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383901 |  | Water Loop | FHP | EP042-4HZ*******B |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
211594213 |  | Water Loop | TRANE | DXHG036A |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594214 |  | Water Loop | TRANE | DXHG048A |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594215 |  | Water Loop | TRANE | DXHG060A |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
211594216 |  | Water Loop | TRANE | DXHG070A |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
211594245 |  | Water Loop | TRANE | EXHG0187 |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
211594246 |  | Water Loop | TRANE | EXHG024B |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594247 |  | Water Loop | TRANE | EXHG0244 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594248 |  | Water Loop | TRANE | EXHG0247 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594249 |  | Water Loop | TRANE | EXHG030B |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594250 |  | Water Loop | TRANE | EXHG0304 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594251 |  | Water Loop | TRANE | EXHG0307 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594252 |  | Water Loop | TRANE | EXHG036B |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594253 |  | Water Loop | TRANE | EXHG0364 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594254 |  | Water Loop | TRANE | EXHG0367 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594255 |  | Water Loop | TRANE | EXHG042B |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594256 |  | Water Loop | TRANE | EXHG0424 |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594257 |  | Water Loop | TRANE | EXHG048B |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594258 |  | Water Loop | TRANE | EXHG0484 |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594259 |  | Water Loop | TRANE | EXHG060B |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594260 |  | Water Loop | TRANE | EXHG0604 |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594261 |  | Water Loop | TRANE | EXHG070B |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
5295984 |  | Water Loop | WaterFurnace | NBV/NBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295985 |  | Water Loop | WaterFurnace | NBV/NBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295986 |  | Water Loop | WaterFurnace | NBV/NBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295987 |  | Water Loop | WaterFurnace | NBV/NBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295988 |  | Water Loop | WaterFurnace | NBV/NBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295989 |  | Water Loop | WaterFurnace | NBV/NBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295990 |  | Water Loop | WaterFurnace | NBV/NBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295991 |  | Water Loop | WaterFurnace | NBV/NBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295992 |  | Water Loop | WaterFurnace | NBV/NBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295993 |  | Water Loop | WaterFurnace | NBV/NBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295994 |  | Water Loop | WaterFurnace | NBV/NBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295995 |  | Water Loop | WaterFurnace | NBV/NBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295996 |  | Water Loop | WaterFurnace | NBV/NBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5295997 |  | Water Loop | WaterFurnace | NBV/NBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5295998 |  | Water Loop | WaterFurnace | NBV/NBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5295999 |  | Water Loop | WaterFurnace | NBV/NBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296000 |  | Water Loop | WaterFurnace | NBV/NBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296001 |  | Water Loop | WaterFurnace | NBV/NBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296002 |  | Water Loop | WaterFurnace | NBV/NBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296003 |  | Water Loop | WaterFurnace | NBV/NBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296008 |  | Water Loop | WaterFurnace | NBV/NBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296009 |  | Water Loop | WaterFurnace | NBV/NBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296010 |  | Water Loop | WaterFurnace | NBV/NBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296011 |  | Water Loop | WaterFurnace | NBV/NBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296012 |  | Water Loop | WaterFurnace | NBV/NBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296013 |  | Water Loop | WaterFurnace | NBV/NBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296014 |  | Water Loop | WaterFurnace | NBV/NBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296015 |  | Water Loop | WaterFurnace | NBV/NBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296225 |  | Water Loop | WaterFurnace | NBV/NBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296226 |  | Water Loop | WaterFurnace | NBV/NBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296227 |  | Water Loop | WaterFurnace | NBV/NBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296228 |  | Water Loop | WaterFurnace | NBV/NBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296229 |  | Water Loop | WaterFurnace | NBV/NBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296230 |  | Water Loop | WaterFurnace | NBV/NBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
10298936 |  | Water Loop | WaterFurnace | UVV/UVH036**0*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
10298937 |  | Water Loop | WaterFurnace | UVV/UVH036**3*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
10298938 |  | Water Loop | WaterFurnace | UVV/UVH036**4*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
216739949 |  | Water Loop | DAIKIN | WSNV024E1*C/S*C |  | 23900 | 17 | 27100 | 5.2 | 1.9917 | No
216739961 |  | Water Loop | DAIKIN | WSNV036E1*C/S*C |  | 36700 | 18.2 | 39400 | 5.1 | 3.0583 | No
216739962 |  | Water Loop | DAIKIN | WSNV036F3*C/S*C |  | 36700 | 17.8 | 39400 | 5 | 3.0583 | No
216739963 |  | Water Loop | DAIKIN | WSNV036J1*C/S*C |  | 36700 | 17.8 | 39400 | 5 | 3.0583 | No
216739964 |  | Water Loop | DAIKIN | WSNV036K3*C/S*C |  | 36700 | 17.6 | 39400 | 5 | 3.0583 | No
216739969 |  | Water Loop | DAIKIN | WSNV042E1*C/S*C |  | 43300 | 17.1 | 49900 | 5 | 3.6083 | No
216739975 |  | Water Loop | DAIKIN | WSNV048E1*C/S*C |  | 49300 | 17.2 | 55800 | 5.2 | 4.1083 | No
213154468 |  | Water Loop | GeoSmart Energy | GS036**1*1********L |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
213154469 |  | Water Loop | GeoSmart Energy | GS042**1*1********L |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
213154474 |  | Water Loop | GeoSmart Energy | GT038**1*1********L |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
213154475 |  | Water Loop | GeoSmart Energy | GT049**1*1********L |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
217903432 |  | Water Loop | WaterFurnace | V5R036*S3**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903433 |  | Water Loop | WaterFurnace | V5R036*S4**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903434 |  | Water Loop | WaterFurnace | V5R036*S4**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903435 |  | Water Loop | WaterFurnace | V5R036*S4**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
202211042 |  | Water Loop | WaterFurnace | URD038*0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211043 |  | Water Loop | WaterFurnace | URD038*0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211044 |  | Water Loop | WaterFurnace | URD038*0*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067548 |  | Water Loop | GeoSmart Energy | GBV/GBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067549 |  | Water Loop | GeoSmart Energy | GBV/GBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067551 |  | Water Loop | GeoSmart Energy | GBV/GBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067552 |  | Water Loop | GeoSmart Energy | GBV/GBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067557 |  | Water Loop | GeoSmart Energy | GBV/GBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214067558 |  | Water Loop | GeoSmart Energy | GBV/GBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067559 |  | Water Loop | GeoSmart Energy | GBV/GBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067560 |  | Water Loop | GeoSmart Energy | GBV/GBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214067561 |  | Water Loop | GeoSmart Energy | GBV/GBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067562 |  | Water Loop | GeoSmart Energy | GBV/GBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067564 |  | Water Loop | GeoSmart Energy | GBV/GBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067565 |  | Water Loop | GeoSmart Energy | GBV/GBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067567 |  | Water Loop | GeoSmart Energy | GBV/GBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067568 |  | Water Loop | GeoSmart Energy | GBV/GBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067569 |  | Water Loop | GeoSmart Energy | GBV/GBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067570 |  | Water Loop | GeoSmart Energy | GBV/GBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067571 |  | Water Loop | GeoSmart Energy | GBV/GBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067572 |  | Water Loop | GeoSmart Energy | GBV/GBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067574 |  | Water Loop | GeoSmart Energy | GBV/GBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067575 |  | Water Loop | GeoSmart Energy | GBV/GBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067577 |  | Water Loop | GeoSmart Energy | GBV/GBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067578 |  | Water Loop | GeoSmart Energy | GBV/GBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067584 |  | Water Loop | GeoSmart Energy | GBV/GBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067585 |  | Water Loop | GeoSmart Energy | GBV/GBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067586 |  | Water Loop | GeoSmart Energy | GBV/GBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067587 |  | Water Loop | GeoSmart Energy | GBV/GBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
208106952 |  | Water Loop | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
208106953 |  | Water Loop | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
214771953 |  | Water Loop | TRANE | EXHK009A |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214771954 |  | Water Loop | TRANE | EXHK012A |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214771956 |  | Water Loop | TRANE | EXHK018A |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214771957 |  | Water Loop | TRANE | EXHK024A |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214771958 |  | Water Loop | TRANE | EXHK030A |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214771959 |  | Water Loop | TRANE | EXHK036A |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214771960 |  | Water Loop | TRANE | EXHK042A |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214771961 |  | Water Loop | TRANE | EXHK048A |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214771962 |  | Water Loop | TRANE | EXHK060A |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214771963 |  | Water Loop | TRANE | EXHK070A |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772074 |  | Water Loop | TRANE | EXVK0097 |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214772075 |  | Water Loop | TRANE | EXVK0127 |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214772077 |  | Water Loop | TRANE | EXVK0187 |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214772078 |  | Water Loop | TRANE | EXVK024B |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772079 |  | Water Loop | TRANE | EXVK0244 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772080 |  | Water Loop | TRANE | EXVK0247 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772081 |  | Water Loop | TRANE | EXVK030B |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772082 |  | Water Loop | TRANE | EXVK0304 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772083 |  | Water Loop | TRANE | EXVK0307 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772084 |  | Water Loop | TRANE | EXVK036B |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772085 |  | Water Loop | TRANE | EXVK0364 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
202443461 |  | Water Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
202443470 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
217752748 |  | Water Loop | DAIKIN | WSTV036K1*B*C |  | 38100 | 17.89 | 41100 | 5.03 | 3.175 | No
217752752 |  | Water Loop | DAIKIN | WSTV048K1*B*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
217752753 |  | Water Loop | DAIKIN | WSTV048L1*B*C |  | 50800 | 17.09 | 58500 | 5.35 | 4.2333 | No
217754377 |  | Water Loop | DAIKIN | WSSH024F1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217754380 |  | Water Loop | DAIKIN | WSSH024F1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217754383 |  | Water Loop | DAIKIN | WSSH030F1*B*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217754386 |  | Water Loop | DAIKIN | WSSH030F1*B*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217754389 |  | Water Loop | DAIKIN | WSSH036F1*B*T |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
217754392 |  | Water Loop | DAIKIN | WSSH036F1*B*C |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
215268775 |  | Water Loop | WaterFurnace | V5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268776 |  | Water Loop | WaterFurnace | V5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268777 |  | Water Loop | WaterFurnace | V5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268778 |  | Water Loop | WaterFurnace | V5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268779 |  | Water Loop | WaterFurnace | V5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268780 |  | Water Loop | WaterFurnace | V5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268781 |  | Water Loop | WaterFurnace | V5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268782 |  | Water Loop | WaterFurnace | V5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268783 |  | Water Loop | WaterFurnace | V5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268784 |  | Water Loop | WaterFurnace | V5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
9910660 |  | Water Loop | GEOCOMFORT | GZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910661 |  | Water Loop | HYDRON MODULE | HZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910662 |  | Water Loop | TETCO | TZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910663 |  | Water Loop | GEOCOMFORT | GZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910664 |  | Water Loop | HYDRON MODULE | HZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910665 |  | Water Loop | TETCO | TZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910666 |  | Water Loop | GEOCOMFORT | GZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910667 |  | Water Loop | HYDRON MODULE | HZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910668 |  | Water Loop | TETCO | TZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910752 |  | Water Loop | GEOCOMFORT | GZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910753 |  | Water Loop | HYDRON MODULE | HZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910754 |  | Water Loop | TETCO | TZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910755 |  | Water Loop | GEOCOMFORT | GZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
4947178 |  | Water Loop | TRANE | VSVE0241 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
4947179 |  | Water Loop | TRANE | VSVE0242 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
4947180 |  | Water Loop | TRANE | VSVE0244 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
5220663 |  | Water Loop | DAIKIN | WGSV/WGSH015B*E |  | 15300 | 18.1 | 19100 | 5.9 | 1.275 | No
201907614 |  | Water Loop | WaterFurnace | URS036*3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907615 |  | Water Loop | WaterFurnace | URS036*3*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907616 |  | Water Loop | WaterFurnace | URS036*4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907617 |  | Water Loop | WaterFurnace | URS036*4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907618 |  | Water Loop | WaterFurnace | URS036*4*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7499543 |  | Water Loop | FHP | LM024-1CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499546 |  | Water Loop | FHP | LM024-2CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499547 |  | Water Loop | FHP | LM024-3CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499548 |  | Water Loop | FHP | LM024-4CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499550 |  | Water Loop | FHP | LM036-1VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6501931 |  | Water Loop | GEOSTAR | GBV/GBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501932 |  | Water Loop | GEOSTAR | GBV/GBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501934 |  | Water Loop | GEOSTAR | GBV/GBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501935 |  | Water Loop | GEOSTAR | GBV/GBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501937 |  | Water Loop | GEOSTAR | GBV/GBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501938 |  | Water Loop | GEOSTAR | GBV/GBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501940 |  | Water Loop | GEOSTAR | GBV/GBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501941 |  | Water Loop | GEOSTAR | GBV/GBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501942 |  | Water Loop | GEOSTAR | GBV/GBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501943 |  | Water Loop | GEOSTAR | GBV/GBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501944 |  | Water Loop | GEOSTAR | GBV/GBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501945 |  | Water Loop | GEOSTAR | GBV/GBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501946 |  | Water Loop | GEOSTAR | GBV/GBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501947 |  | Water Loop | GEOSTAR | GBV/GBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501948 |  | Water Loop | GEOSTAR | GBV/GBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501949 |  | Water Loop | GEOSTAR | GBV/GBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501951 |  | Water Loop | GEOSTAR | GBV/GBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501952 |  | Water Loop | GEOSTAR | GBV/GBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501954 |  | Water Loop | GEOSTAR | GBV/GBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501955 |  | Water Loop | GEOSTAR | GBV/GBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501957 |  | Water Loop | GEOSTAR | GBV/GBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501958 |  | Water Loop | GEOSTAR | GBV/GBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
202835053 |  | Water Loop | BOSCH | SM036-1HZ*-*****C |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
202836307 |  | Water Loop | BOSCH | SM036-1VT*-*****C |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | Yes
202921908 |  | Water Loop | BOSCH | EP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921909 |  | Water Loop | BOSCH | EP036-3VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921910 |  | Water Loop | BOSCH | EP036-4VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921911 |  | Water Loop | BOSCH-GEO | BP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
216772568 |  | Water Loop | Enertech | EVS018* |  | 21300 | 20.5 | 23700 | 6.3 | 1.775 | Yes
216772569 |  | Water Loop | Enertech | EVT024* |  | 24650 | 17.5 | 29100 | 5.6 | 2.0542 | Yes
216772586 |  | Water Loop | Enertech | EVS015* |  | 15775 | 19.9 | 17700 | 6.4 | 1.3146 | Yes
214772149 |  | Water Loop | TRANE | DXVK0364 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772150 |  | Water Loop | TRANE | DXVK048B |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772151 |  | Water Loop | TRANE | DXVK0484 |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772152 |  | Water Loop | TRANE | DXVK060B |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772153 |  | Water Loop | TRANE | DXVK0604 |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772156 |  | Water Loop | TRANE | DXHK024B |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772157 |  | Water Loop | TRANE | DXHK0244 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772158 |  | Water Loop | TRANE | DXHK036B |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772159 |  | Water Loop | TRANE | DXHK0364 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772160 |  | Water Loop | TRANE | DXHK048B |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772161 |  | Water Loop | TRANE | DXHK0484 |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772162 |  | Water Loop | TRANE | DXHK060B |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772163 |  | Water Loop | TRANE | DXHK0604 |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772166 |  | Water Loop | TRANE | DXVK0247 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772167 |  | Water Loop | TRANE | DXVK0367 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772168 |  | Water Loop | TRANE | DXHK0247 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772169 |  | Water Loop | TRANE | DXHK0367 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
216625463 |  | Water Loop | GEOSTAR | G5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625464 |  | Water Loop | GEOSTAR | G5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625465 |  | Water Loop | GEOSTAR | G5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625466 |  | Water Loop | GEOSTAR | G5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625467 |  | Water Loop | GEOSTAR | G5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625468 |  | Water Loop | GEOSTAR | G5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625469 |  | Water Loop | GEOSTAR | G5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625470 |  | Water Loop | GEOSTAR | G5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625471 |  | Water Loop | GEOSTAR | G5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625472 |  | Water Loop | GEOSTAR | G5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625473 |  | Water Loop | GEOSTAR | G5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625474 |  | Water Loop | GEOSTAR | G5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625475 |  | Water Loop | GEOSTAR | G5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625476 |  | Water Loop | GEOSTAR | G5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625477 |  | Water Loop | GEOSTAR | G5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625478 |  | Water Loop | GEOSTAR | G5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625479 |  | Water Loop | GEOSTAR | G5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625480 |  | Water Loop | GEOSTAR | G5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625481 |  | Water Loop | GEOSTAR | G5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625482 |  | Water Loop | GEOSTAR | G5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625483 |  | Water Loop | GEOSTAR | G5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625484 |  | Water Loop | GEOSTAR | G5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
211127895 |  | Water Loop | WaterFurnace | NVV/NVH036D1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
211127898 |  | Water Loop | GEOSTAR | 141/142D036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
215415919 |  | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | No
215415920 |  | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | No
215415921 |  | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 38000 | 17.5 | 43100 | 5.5 | 3.1667 | No
215415922 |  | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 38000 | 17.5 | 43100 | 5.5 | 3.1667 | No
215415923 |  | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 51000 | 18 | 58700 | 5.6 | 4.25 | No
215415924 |  | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 51000 | 18 | 58700 | 5.6 | 4.25 | No
206346951 |  | Water Loop | DAIKIN | WVFC*030*E***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
206346952 |  | Water Loop | DAIKIN | WVFC*030*F***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
206346953 |  | Water Loop | DAIKIN | WVFC*030*J***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
206194171 |  | Water Loop | Johnson Controls | JSH/V/D030C*K B |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
206194172 |  | Water Loop | SKYMARK | JSH/V/D030C*K C |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
206194173 |  | Water Loop | Johnson Controls | JSH/V/D048C*K B |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | No
206194174 |  | Water Loop | SKYMARK | JSH/V/D048C*K C |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | No
206194175 |  | Water Loop | Johnson Controls | JSH/V/D060C*K B |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | No
206194176 |  | Water Loop | SKYMARK | JSH/V/D060C*K C |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | No
216625828 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625829 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
213502565 |  | Water Loop | DAIKIN | WSMH036E1*C/S*T |  | 36500 | 17.2 | 48300 | 5.4 | 3.0417 | No
213502566 |  | Water Loop | DAIKIN | WSMH036E1*C/S*C |  | 36500 | 17.2 | 48300 | 5.4 | 3.0417 | No
213502571 |  | Water Loop | DAIKIN | WSCH042E1*C/S*T |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
213502572 |  | Water Loop | DAIKIN | WSCH042E1*C/S*C |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
217967045 |  | Water Loop | TRANE | VSVK0504 |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
4218842 |  | Water Loop | DAIKIN | WVFC1030*E***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
4218843 |  | Water Loop | DAIKIN | WVFC1030*F***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
4218844 |  | Water Loop | DAIKIN | WVFC1030*J***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
214595646 |  | Water Loop | AAON, Inc. | M2-006-2-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
214595648 |  | Water Loop | AAON, Inc. | M2-006-3-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
214595650 |  | Water Loop | AAON, Inc. | M2-006-4-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
214067608 |  | Water Loop | GeoSmart Energy | GBV/GBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
215268713 |  | Water Loop | WaterFurnace | V5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268714 |  | Water Loop | WaterFurnace | V5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268715 |  | Water Loop | WaterFurnace | V5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268716 |  | Water Loop | WaterFurnace | V5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268717 |  | Water Loop | WaterFurnace | V5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268718 |  | Water Loop | WaterFurnace | V5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268719 |  | Water Loop | WaterFurnace | V5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268720 |  | Water Loop | WaterFurnace | V5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268721 |  | Water Loop | WaterFurnace | V5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268722 |  | Water Loop | WaterFurnace | V5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268723 |  | Water Loop | WaterFurnace | V5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268724 |  | Water Loop | WaterFurnace | V5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268725 |  | Water Loop | WaterFurnace | V5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268734 |  | Water Loop | WaterFurnace | V5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215402562 |  | Water Loop | DAIKIN | WSSV030E1*B*C |  | 29200 | 19.17 | 34500 | 5.67 | 2.4333 | No
215402563 |  | Water Loop | DAIKIN | WSSV030F3*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215402566 |  | Water Loop | DAIKIN | WSSV036E1*B*T |  | 39000 | 19.02 | 44100 | 5.35 | 3.25 | No
215402567 |  | Water Loop | DAIKIN | WSSV036F3*B*T |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
215402570 |  | Water Loop | DAIKIN | WSSV036E1*B*C |  | 39000 | 19.02 | 44100 | 5.35 | 3.25 | No
215402571 |  | Water Loop | DAIKIN | WSSV036F3*B*C |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
10259035 |  | Water Loop | GEOCOMFORT | GZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259036 |  | Water Loop | HYDRON MODULE | HZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259037 |  | Water Loop | TETCO | TZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259038 |  | Water Loop | GEOCOMFORT | GZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259039 |  | Water Loop | HYDRON MODULE | HZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259040 |  | Water Loop | TETCO | TZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259054 |  | Water Loop | GEOCOMFORT | GZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259055 |  | Water Loop | HYDRON MODULE | HZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259056 |  | Water Loop | TETCO | TZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259057 |  | Water Loop | GEOCOMFORT | GZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
10259058 |  | Water Loop | HYDRON MODULE | HZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
7519776 |  | Water Loop | HYDRON MODULE | HVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519777 |  | Water Loop | TETCO | TVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7520238 |  | Water Loop | GEOCOMFORT | GVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520239 |  | Water Loop | HYDRON MODULE | HVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520240 |  | Water Loop | TETCO | TVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520241 |  | Water Loop | GEOCOMFORT | GVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520242 |  | Water Loop | HYDRON MODULE | HVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520243 |  | Water Loop | TETCO | TVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520244 |  | Water Loop | TETCO | TVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520245 |  | Water Loop | HYDRON MODULE | HVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520246 |  | Water Loop | GEOCOMFORT | GVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520247 |  | Water Loop | HYDRON MODULE | HVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520248 |  | Water Loop | TETCO | TVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520249 |  | Water Loop | GEOCOMFORT | GVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7523956 |  | Water Loop | GEOCOMFORT | GVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
7523957 |  | Water Loop | HYDRON MODULE | HVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
7523958 |  | Water Loop | TETCO | TVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
7523959 |  | Water Loop | GEOCOMFORT | GVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
7523960 |  | Water Loop | HYDRON MODULE | HVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
7523961 |  | Water Loop | TETCO | TVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
217193306 |  | Water Loop | WaterFurnace | V7A(V/H)024*V0**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193307 |  | Water Loop | WaterFurnace | V7A(V/H)036*V0**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
217193552 |  | Water Loop | WaterFurnace | V7A(V/H)024*V3**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193553 |  | Water Loop | WaterFurnace | V7A(V/H)024*V4**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193554 |  | Water Loop | WaterFurnace | V7A(V/H)036*V3**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
217193555 |  | Water Loop | WaterFurnace | V7A(V/H)036*V4**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
963510 |  | Water Loop | WaterFurnace | NLV/NXV095T*3 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
963511 |  | Water Loop | WaterFurnace | NLV/NXV095T*4 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
963512 |  | Water Loop | WaterFurnace | NLV/NXV095T*5 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
218494310 |  | Water Loop | ClimateMaster | SMT(S,M)24A*L |  | 25000 | 17.6 | 28000 | 5.1 | 2.0833 | No
5317193 |  | Water Loop | WaterFurnace | NBV/NBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317194 |  | Water Loop | WaterFurnace | NBV/NBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317195 |  | Water Loop | WaterFurnace | NBV/NBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317196 |  | Water Loop | WaterFurnace | NBV/NBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317197 |  | Water Loop | WaterFurnace | NBV/NBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317198 |  | Water Loop | WaterFurnace | NBV/NBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317199 |  | Water Loop | WaterFurnace | NBV/NBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317200 |  | Water Loop | WaterFurnace | NBV/NBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317201 |  | Water Loop | WaterFurnace | NBV/NBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317202 |  | Water Loop | WaterFurnace | NBV/NBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317203 |  | Water Loop | WaterFurnace | NBV/NBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317205 |  | Water Loop | WaterFurnace | NBV/NBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317206 |  | Water Loop | WaterFurnace | NBV/NBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317207 |  | Water Loop | WaterFurnace | NBV/NBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317332 |  | Water Loop | WaterFurnace | NBV/NBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
6501900 |  | Water Loop | GEOSTAR | GBV/GBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501901 |  | Water Loop | GEOSTAR | GBV/GBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501903 |  | Water Loop | GEOSTAR | GBV/GBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501904 |  | Water Loop | GEOSTAR | GBV/GBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501906 |  | Water Loop | GEOSTAR | GBV/GBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501907 |  | Water Loop | GEOSTAR | GBV/GBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501909 |  | Water Loop | GEOSTAR | GBV/GBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501910 |  | Water Loop | GEOSTAR | GBV/GBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
205129920 |  | Water Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205129921 |  | Water Loop | GEOSTAR | 103J036**1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
213710618 |  | Water Loop | DAIKIN | WSSH015A1*B*T |  | 16100 | 19.7 | 18000 | 5.76 | 1.3417 | No
213710619 |  | Water Loop | DAIKIN | WSSH015A1*B*C |  | 16100 | 19.7 | 18000 | 5.76 | 1.3417 | No
213710626 |  | Water Loop | DAIKIN | WSSH015J1*B*T |  | 16100 | 18.2 | 18000 | 5.7 | 1.3417 | No
213710627 |  | Water Loop | DAIKIN | WSSH015J1*B*C |  | 16100 | 18.2 | 18000 | 5.7 | 1.3417 | No
213710636 |  | Water Loop | DAIKIN | WSSH019J1*B*T |  | 19900 | 17.7 | 23300 | 5.3 | 1.6583 | No
213710637 |  | Water Loop | DAIKIN | WSSH019J1*B*C |  | 19900 | 17.7 | 23300 | 5.3 | 1.6583 | No
213711957 |  | Water Loop | DAIKIN | WSSH007E1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
5220682 |  | Water Loop | DAIKIN | WGSV/WGSH036B*F |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220683 |  | Water Loop | DAIKIN | WGSV/WGSH036B*J |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220684 |  | Water Loop | DAIKIN | WGSV/WGSH036B*K |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220686 |  | Water Loop | DAIKIN | WGSV/WGSH042B*E |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220687 |  | Water Loop | DAIKIN | WGSV/WGSH042B*F |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220688 |  | Water Loop | DAIKIN | WGSV/WGSH042B*K |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220690 |  | Water Loop | DAIKIN | WGSV/WGSH048B*E |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220691 |  | Water Loop | DAIKIN | WGSV/WGSH048B*F |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220693 |  | Water Loop | DAIKIN | WGSV/WGSH048B*K |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220700 |  | Water Loop | DAIKIN | WGSV/WGSH060B*E |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
5220701 |  | Water Loop | DAIKIN | WGSV/WGSH060B*F |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
5220702 |  | Water Loop | DAIKIN | WGSV/WGSH060B*K |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
5220980 |  | Water Loop | DAIKIN | WGTV/WGTH038B*E |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220981 |  | Water Loop | DAIKIN | WGTV/WGTH038B*F |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220982 |  | Water Loop | DAIKIN | WGTV/WGTH038B*K |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220983 |  | Water Loop | DAIKIN | WGTV/WGTH044B*E |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220984 |  | Water Loop | DAIKIN | WGTV/WGTH044B*F |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220985 |  | Water Loop | DAIKIN | WGTV/WGTH044B*K |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220990 |  | Water Loop | DAIKIN | WGTV/WGTH064B*E |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
5220991 |  | Water Loop | DAIKIN | WGTV/WGTH064B*F |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
5220992 |  | Water Loop | DAIKIN | WGTV/WGTH064B*K |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
205767605 |  | Water Loop | ClimateMaster | VEV/H/D1860 |  | 48000 | 17.3 | 60000 | 5.5 | 4 | Yes
205767606 |  | Water Loop | ClimateMaster | VEV/H/D0930 |  | 24000 | 19.3 | 30000 | 6.6 | 2 | Yes
205767615 |  | Water Loop | ClimateMaster | QEV/H/D0930 |  | 24000 | 19.3 | 30000 | 6.6 | 2 | Yes
205782239 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205782243 |  | Water Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205788279 |  | Water Loop | Johnson Controls | JSH/V/D024C*K B |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | No
205788280 |  | Water Loop | SKYMARK | JSH/V/D024C*K C |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | No
205788283 |  | Water Loop | Johnson Controls | JSH/V/D036C B |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | No
205788284 |  | Water Loop | SKYMARK | JSH/V/D036C C |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | No
214772086 |  | Water Loop | TRANE | EXVK0367 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772087 |  | Water Loop | TRANE | EXVK042B |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772088 |  | Water Loop | TRANE | EXVK0424 |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772089 |  | Water Loop | TRANE | EXVK048B |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772090 |  | Water Loop | TRANE | EXVK0484 |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772091 |  | Water Loop | TRANE | EXVK060B |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772092 |  | Water Loop | TRANE | EXVK0604 |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772093 |  | Water Loop | TRANE | EXVK070B |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772094 |  | Water Loop | TRANE | EXVK0704 |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772095 |  | Water Loop | TRANE | DXVK024A |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772096 |  | Water Loop | TRANE | DXVK036A |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772097 |  | Water Loop | TRANE | DXVK048A |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772098 |  | Water Loop | TRANE | DXVK060A |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
213710594 |  | Water Loop | DAIKIN | WSSH007A1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
213710599 |  | Water Loop | DAIKIN | WSSH007J1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
213710602 |  | Water Loop | DAIKIN | WSSH009A1*B*T |  | 9100 | 18 | 11200 | 5.6 | 0.75833 | No
213710607 |  | Water Loop | DAIKIN | WSSH009J1*B*T |  | 9100 | 17 | 11200 | 5.4 | 0.75833 | No
207177503 |  | Water Loop | TRANE | DXVG060A |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177504 |  | Water Loop | TRANE | DXVG060B |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177505 |  | Water Loop | TRANE | DXVG0604 |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177506 |  | Water Loop | TRANE | DXVG070A |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
207177507 |  | Water Loop | TRANE | DXVG070B |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
207177508 |  | Water Loop | TRANE | DXVG0704 |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
217897465 |  | Water Loop | CENTURY | MJN036A | MAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
217897466 |  | Water Loop | COMFORT-AIRE | MJN036A | MAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
217903418 |  | Water Loop | WaterFurnace | V5R036*S0**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903419 |  | Water Loop | WaterFurnace | V5R036*S0**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903420 |  | Water Loop | WaterFurnace | V5R036*S0**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903430 |  | Water Loop | WaterFurnace | V5R036*S3**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903431 |  | Water Loop | WaterFurnace | V5R036*S3**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
9035995 |  | Water Loop | TETCO | TZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
9035996 |  | Water Loop | GEOCOMFORT | GZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035997 |  | Water Loop | HYDRON MODULE | HZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035998 |  | Water Loop | TETCO | TZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035999 |  | Water Loop | GEOCOMFORT | GZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036000 |  | Water Loop | HYDRON MODULE | HZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036001 |  | Water Loop | TETCO | TZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036002 |  | Water Loop | GEOCOMFORT | GZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036003 |  | Water Loop | HYDRON MODULE | HZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036004 |  | Water Loop | TETCO | TZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036975 |  | Water Loop | GEOCOMFORT | GZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9036998 |  | Water Loop | HYDRON MODULE | HZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9037017 |  | Water Loop | TETCO | TZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9037062 |  | Water Loop | GEOCOMFORT | GZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037081 |  | Water Loop | HYDRON MODULE | HZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037097 |  | Water Loop | TETCO | TZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037137 |  | Water Loop | GEOCOMFORT | GZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037158 |  | Water Loop | HYDRON MODULE | HZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037175 |  | Water Loop | TETCO | TZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037215 |  | Water Loop | GEOCOMFORT | GZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
207348654 |  | Water Loop | WaterFurnace | URS036*0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348655 |  | Water Loop | WaterFurnace | URS036*0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348656 |  | Water Loop | WaterFurnace | URS036*0*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348657 |  | Water Loop | WaterFurnace | URS036*3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348658 |  | Water Loop | WaterFurnace | URS036*3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348659 |  | Water Loop | WaterFurnace | URS036*3*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348660 |  | Water Loop | WaterFurnace | URS036*4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348661 |  | Water Loop | WaterFurnace | URS036*4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348662 |  | Water Loop | WaterFurnace | URS036*4*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5599272 |  | Water Loop | BOSCH-GEO | SM036-1CF/HZ/VT |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
207335143 |  | Water Loop | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335144 |  | Water Loop | GEOSTAR | 101/102K049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335251 |  | Water Loop | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335253 |  | Water Loop | GEOSTAR | 161/162K049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335398 |  | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335399 |  | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335407 |  | Water Loop | GeoSmart Energy | GS030**1*(0,3)*J |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | Yes
207335408 |  | Water Loop | GeoSmart Energy | GS030**1*(1,4)*J |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335409 |  | Water Loop | GeoSmart Energy | GS036**1*(0,3)*K |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207335514 |  | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207335573 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335575 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207335580 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335581 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335585 |  | Water Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335586 |  | Water Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335590 |  | Water Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
217752693 |  | Water Loop | DAIKIN | WSSH048L1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752694 |  | Water Loop | DAIKIN | WSSH048K1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752695 |  | Water Loop | DAIKIN | WSSH048L1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752696 |  | Water Loop | DAIKIN | WSSH060K1*B*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217752698 |  | Water Loop | DAIKIN | WSSH060K1*B*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217752700 |  | Water Loop | DAIKIN | WSSH070K1*B*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217752702 |  | Water Loop | DAIKIN | WSSH070K1*B*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217752704 |  | Water Loop | DAIKIN | WSSV024K1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217752705 |  | Water Loop | DAIKIN | WSSV024K1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217752706 |  | Water Loop | DAIKIN | WSSV030K1*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217752707 |  | Water Loop | DAIKIN | WSSV030K1*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217752708 |  | Water Loop | DAIKIN | WSSV036K1*B*T |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
217752709 |  | Water Loop | DAIKIN | WSSV036K1*B*C |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
217752710 |  | Water Loop | DAIKIN | WSSV042K1*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217752711 |  | Water Loop | DAIKIN | WSSV042K1*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217752712 |  | Water Loop | DAIKIN | WSSV048K1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752713 |  | Water Loop | DAIKIN | WSSV048L1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752714 |  | Water Loop | DAIKIN | WSSV048K1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752715 |  | Water Loop | DAIKIN | WSSV048L1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752716 |  | Water Loop | DAIKIN | WSSV060K1*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217752718 |  | Water Loop | DAIKIN | WSSV060K1*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217752724 |  | Water Loop | DAIKIN | WSTH024K1*B*C |  | 24500 | 17 | 26100 | 5.14 | 2.0417 | No
217752728 |  | Water Loop | DAIKIN | WSTH036K1*B*C |  | 38000 | 17.88 | 42900 | 5.2 | 3.1667 | No
217752730 |  | Water Loop | DAIKIN | WSTH042K1*B*C |  | 44000 | 17.07 | 50300 | 4.97 | 3.6667 | No
217752744 |  | Water Loop | DAIKIN | WSTV024K1*B*C |  | 24300 | 17.06 | 28000 | 5.64 | 2.025 | No
7519769 |  | Water Loop | GEOCOMFORT | GVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519770 |  | Water Loop | HYDRON MODULE | HVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519771 |  | Water Loop | TETCO | TVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519772 |  | Water Loop | GEOCOMFORT | GVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519773 |  | Water Loop | HYDRON MODULE | HVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519774 |  | Water Loop | TETCO | TVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519775 |  | Water Loop | GEOCOMFORT | GVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
215837913 |  | Water Loop | DAIKIN | WSSH070F3*C/S*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837914 |  | Water Loop | DAIKIN | WSSH070K3*C/S*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837922 |  | Water Loop | DAIKIN | WSSH070F3*C/S*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837923 |  | Water Loop | DAIKIN | WSSH070K3*C/S*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215851754 |  | Water Loop | DAIKIN | WSTH024J1*C/S*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
215851756 |  | Water Loop | DAIKIN | WSTH024K3*C/S*C |  | 24500 | 17 | 26100 | 5.14 | 2.0417 | No
215851767 |  | Water Loop | DAIKIN | WSTH036J1*C/S*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
215851769 |  | Water Loop | DAIKIN | WSTH036K3*C/S*C |  | 38000 | 17.88 | 42900 | 5.2 | 3.1667 | No
215851773 |  | Water Loop | DAIKIN | WSTH042K3*C/S*C |  | 44000 | 17.07 | 50300 | 4.97 | 3.6667 | No
215851795 |  | Water Loop | DAIKIN | WSTV024J1*C/S*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
215851796 |  | Water Loop | DAIKIN | WSTV024K3*C/S*C |  | 24300 | 17.06 | 28000 | 5.64 | 2.025 | No
215851809 |  | Water Loop | DAIKIN | WSTV036J1*C/S*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
215851810 |  | Water Loop | DAIKIN | WSTV036K3*C/S*C |  | 38100 | 17.89 | 41100 | 5.03 | 3.175 | No
215851818 |  | Water Loop | DAIKIN | WSTV048K3*C/S*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
215851820 |  | Water Loop | DAIKIN | WSTV048L3*C/S*C |  | 50800 | 17.09 | 58500 | 5.35 | 4.2333 | No
213711959 |  | Water Loop | DAIKIN | WSSH009E1*B*T |  | 9100 | 18 | 11200 | 5.6 | 0.75833 | No
213711963 |  | Water Loop | DAIKIN | WSSH015E1*B*T |  | 16100 | 19.95 | 18000 | 5.76 | 1.3417 | No
213711964 |  | Water Loop | DAIKIN | WSSH015E1*B*C |  | 16100 | 19.95 | 18000 | 5.76 | 1.3417 | No
213711966 |  | Water Loop | DAIKIN | WSSH019E1*B*T |  | 19900 | 18 | 23300 | 5.3 | 1.6583 | No
213711967 |  | Water Loop | DAIKIN | WSSH019E1*B*C |  | 19900 | 18 | 23300 | 5.3 | 1.6583 | No
213711969 |  | Water Loop | DAIKIN | WSSH024E1*B*T |  | 24500 | 18.1 | 28000 | 5.8 | 2.0417 | No
213711970 |  | Water Loop | DAIKIN | WSSH024E1*B*C |  | 24500 | 18.1 | 28000 | 5.8 | 2.0417 | No
213711972 |  | Water Loop | DAIKIN | WSSH030E1*B*T |  | 29500 | 19.3 | 34500 | 6 | 2.4583 | No
213711974 |  | Water Loop | DAIKIN | WSSH030E1*B*C |  | 29500 | 19.3 | 34500 | 6 | 2.4583 | No
213711975 |  | Water Loop | DAIKIN | WSSH036E1*B*T |  | 39000 | 19.3 | 44600 | 5.2 | 3.25 | No
213711976 |  | Water Loop | DAIKIN | WSSH036E1*B*C |  | 39000 | 19.3 | 44600 | 5.2 | 3.25 | No
213711978 |  | Water Loop | DAIKIN | WSSH042E1*B*T |  | 42600 | 18.4 | 47000 | 5.4 | 3.55 | No
213711979 |  | Water Loop | DAIKIN | WSSH042E1*B*C |  | 42600 | 18.4 | 47000 | 5.4 | 3.55 | No
213711981 |  | Water Loop | DAIKIN | WSSH048E1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
213711982 |  | Water Loop | DAIKIN | WSSH048E1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
213711984 |  | Water Loop | DAIKIN | WSSH060E1*B*T |  | 60872 | 17.4 | 78027 | 5.72 | 5.0727 | No
213711986 |  | Water Loop | DAIKIN | WSSH060E1*B*C |  | 60872 | 17.4 | 78027 | 5.72 | 5.0727 | No
213714593 |  | Water Loop | DAIKIN | WSSH070E1*B*T |  | 70700 | 17.29 | 83100 | 4.81 | 5.8917 | No
213714595 |  | Water Loop | DAIKIN | WSSH070E1*B*C |  | 70700 | 17.29 | 83100 | 4.81 | 5.8917 | No
215837810 |  | Water Loop | DAIKIN | WSSH024F3*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837811 |  | Water Loop | DAIKIN | WSSH024J1*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837813 |  | Water Loop | DAIKIN | WSSH024K3*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837818 |  | Water Loop | DAIKIN | WSSH024F3*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837820 |  | Water Loop | DAIKIN | WSSH024J1*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837821 |  | Water Loop | DAIKIN | WSSH024K3*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837827 |  | Water Loop | DAIKIN | WSSH030F3*C/S*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837828 |  | Water Loop | DAIKIN | WSSH030J1*C/S*T |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
215837829 |  | Water Loop | DAIKIN | WSSH030K3*C/S*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
214772120 |  | Water Loop | TRANE | EXHK0097 |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214772121 |  | Water Loop | TRANE | EXHK0127 |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214772123 |  | Water Loop | TRANE | EXHK0187 |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214772124 |  | Water Loop | TRANE | EXHK024B |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772125 |  | Water Loop | TRANE | EXHK0244 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772126 |  | Water Loop | TRANE | EXHK0247 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772127 |  | Water Loop | TRANE | EXHK030B |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772128 |  | Water Loop | TRANE | EXHK0304 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772129 |  | Water Loop | TRANE | EXHK0307 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772130 |  | Water Loop | TRANE | EXHK036B |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772131 |  | Water Loop | TRANE | EXHK0364 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772132 |  | Water Loop | TRANE | EXHK0367 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772133 |  | Water Loop | TRANE | EXHK042B |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772134 |  | Water Loop | TRANE | EXHK0424 |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772135 |  | Water Loop | TRANE | EXHK048B |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772136 |  | Water Loop | TRANE | EXHK0484 |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772137 |  | Water Loop | TRANE | EXHK060B |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772138 |  | Water Loop | TRANE | EXHK0604 |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772139 |  | Water Loop | TRANE | EXHK070B |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772140 |  | Water Loop | TRANE | EXHK0704 |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772141 |  | Water Loop | TRANE | DXHK024A |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214796344 |  | Water Loop | WaterFurnace | W5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214796345 |  | Water Loop | WaterFurnace | W5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
214810493 |  | Water Loop | GEOSTAR | G5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214810494 |  | Water Loop | GEOSTAR | G5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
214823446 |  | Water Loop | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214823447 |  | Water Loop | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
9037240 |  | Water Loop | HYDRON MODULE | HZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037275 |  | Water Loop | TETCO | TZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9063207 |  | Water Loop | DAIKIN | WVFC1030*K***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
205767514 |  | Water Loop | ClimateMaster | TSH/V/D024C*K |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | Yes
205767516 |  | Water Loop | ClimateMaster | TSH/V/D030C*K |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
205767517 |  | Water Loop | ClimateMaster | TSH/V/D036C |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | Yes
205767518 |  | Water Loop | ClimateMaster | TSH/V/D036C*K |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | Yes
205767519 |  | Water Loop | ClimateMaster | TSH/V/D042C |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | Yes
205767520 |  | Water Loop | ClimateMaster | TSH/V/D042C*K |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
205767521 |  | Water Loop | ClimateMaster | TSH/V/D048C*K |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | Yes
205767523 |  | Water Loop | ClimateMaster | TSH/V/D060C*K |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | Yes
216128491 |  | Water Loop | GEOSTAR | G5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
216411470 |  | Water Loop | ClimateMaster | SJ/PN036A | SAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
217754655 |  | Water Loop | DAIKIN | WSMV036F1*C/S*T |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
217754656 |  | Water Loop | DAIKIN | WSMV036K1*C/S*T |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
217754659 |  | Water Loop | DAIKIN | WSMV036F1*C/S*C |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
217754660 |  | Water Loop | DAIKIN | WSMV036K1*C/S*C |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
8740369 |  | Water Loop | HYDRON MODULE | HVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
8740370 |  | Water Loop | TETCO | TVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
8740371 |  | Water Loop | GEOCOMFORT | GVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740372 |  | Water Loop | HYDRON MODULE | HVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740373 |  | Water Loop | TETCO | TVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740374 |  | Water Loop | GEOCOMFORT | GVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740375 |  | Water Loop | HYDRON MODULE | HVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740376 |  | Water Loop | TETCO | TVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8964157 |  | Water Loop | BRYANT | GC036C/H/V******1*X1 + UI |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
8964158 |  | Water Loop | CARRIER | GC036C/H/V******1**1 + UI |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
218157918 |  | Water Loop | YORK | Y5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
218157919 |  | Water Loop | YORK | Y5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
218157920 |  | Water Loop | YORK | Y5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
218157921 |  | Water Loop | YORK | Y5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
218157922 |  | Water Loop | YORK | Y5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
218157923 |  | Water Loop | YORK | Y5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
218157924 |  | Water Loop | YORK | Y5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
218157925 |  | Water Loop | YORK | Y5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
218157926 |  | Water Loop | YORK | Y5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
218157927 |  | Water Loop | YORK | Y5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
218157928 |  | Water Loop | YORK | Y5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
218157929 |  | Water Loop | YORK | Y5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
218157930 |  | Water Loop | YORK | Y5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
218157931 |  | Water Loop | YORK | Y5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
218157932 |  | Water Loop | YORK | Y5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
218157933 |  | Water Loop | YORK | Y5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
218157934 |  | Water Loop | YORK | Y5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
218157935 |  | Water Loop | YORK | Y5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
218157936 |  | Water Loop | YORK | Y5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
218157937 |  | Water Loop | YORK | Y5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
218157938 |  | Water Loop | YORK | Y5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
218157939 |  | Water Loop | YORK | Y5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
218157940 |  | Water Loop | YORK | Y5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
218157941 |  | Water Loop | YORK | Y5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
218157942 |  | Water Loop | YORK | Y5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157943 |  | Water Loop | YORK | Y5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157944 |  | Water Loop | YORK | Y5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157945 |  | Water Loop | YORK | Y5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
218157946 |  | Water Loop | YORK | Y5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215827093 |  | Water Loop | DAIKIN | WSLV072F1*C/S |  | 74000 | 17 | 87000 | 5.2 | 6.1667 | No
215827095 |  | Water Loop | DAIKIN | WSLV072K1*C/S |  | 74000 | 17 | 87000 | 5.2 | 6.1667 | No
215827097 |  | Water Loop | DAIKIN | WSLV072L1*C/S |  | 74000 | 17 | 87000 | 5.1 | 6.1667 | No
217967018 |  | Water Loop | TRANE | VSHK024A |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217754631 |  | Water Loop | DAIKIN | WSMV024F1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754632 |  | Water Loop | DAIKIN | WSMV024K1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754635 |  | Water Loop | DAIKIN | WSMV024F1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754636 |  | Water Loop | DAIKIN | WSMV024K1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
203495469 |  | Water Loop | GEOSTAR | 101/102J049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
211594273 |  | Water Loop | TRANE | DXHG070B |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
211594274 |  | Water Loop | TRANE | DXHG0704 |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
8735903 |  | Water Loop | GEOCOMFORT | GVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735904 |  | Water Loop | HYDRON MODULE | HVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735905 |  | Water Loop | TETCO | TVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735906 |  | Water Loop | GEOCOMFORT | GVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735907 |  | Water Loop | HYDRON MODULE | HVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735908 |  | Water Loop | TETCO | TVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735909 |  | Water Loop | GEOCOMFORT | GVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735910 |  | Water Loop | HYDRON MODULE | HVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735911 |  | Water Loop | TETCO | TVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
207335591 |  | Water Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
206570649 |  | Water Loop | 7 SERIES | NVV/NVH036C1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
206570652 |  | Water Loop | GEOSTAR | 141/142C036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
206598629 |  | Water Loop | GeoSmart Energy | VI036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
206598632 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
207349387 |  | Water Loop | WaterFurnace | NBV/NBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
215400130 |  | Water Loop | DAIKIN | WSMV042E1*C/S*T |  | 41200 | 17.13 | 49300 | 5.36 | 3.4333 | No
215400134 |  | Water Loop | DAIKIN | WSMV042E1*C/S*C |  | 41200 | 17.13 | 49300 | 5.36 | 3.4333 | No
215400162 |  | Water Loop | DAIKIN | WSSV007A1*B*T |  | 7100 | 17.99 | 8100 | 5.49 | 0.59167 | No
215400166 |  | Water Loop | DAIKIN | WSSV009A1*B*T |  | 9200 | 17.49 | 11000 | 4.98 | 0.76667 | No
215400172 |  | Water Loop | DAIKIN | WSSV015E1*B*T |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215400174 |  | Water Loop | DAIKIN | WSSV015E1*B*C |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215400176 |  | Water Loop | DAIKIN | WSSV019E1*B*T |  | 19700 | 17.98 | 23500 | 5.33 | 1.6417 | No
215400178 |  | Water Loop | DAIKIN | WSSV019E1*B*C |  | 19700 | 17.98 | 23500 | 5.33 | 1.6417 | No
215400180 |  | Water Loop | DAIKIN | WSSV024J1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400181 |  | Water Loop | DAIKIN | WSSV024K3*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217754473 |  | Water Loop | DAIKIN | WSTH024E1*B*C |  | 24500 | 17.53 | 26100 | 5.29 | 2.0417 | No
217754474 |  | Water Loop | DAIKIN | WSTH024F1*B*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
217754477 |  | Water Loop | DAIKIN | WSTH030E1*B*C |  | 31400 | 17.12 | 34900 | 5.36 | 2.6167 | No
217754481 |  | Water Loop | DAIKIN | WSTH036E1*B*C |  | 38000 | 18.43 | 42900 | 5.36 | 3.1667 | No
217754482 |  | Water Loop | DAIKIN | WSTH036F1*B*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
217754485 |  | Water Loop | DAIKIN | WSTH042E1*B*C |  | 44000 | 17.59 | 50300 | 5.12 | 3.6667 | No
217754486 |  | Water Loop | DAIKIN | WSTH042F1*B*C |  | 44000 | 17.24 | 50300 | 5.02 | 3.6667 | No
217754489 |  | Water Loop | DAIKIN | WSTH048E1*B*C |  | 48200 | 17.34 | 56900 | 5.08 | 4.0167 | No
217754395 |  | Water Loop | DAIKIN | WSSH042F1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217754398 |  | Water Loop | DAIKIN | WSSH042F1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217754401 |  | Water Loop | DAIKIN | WSSH048F1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217754405 |  | Water Loop | DAIKIN | WSSH048F1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217754409 |  | Water Loop | DAIKIN | WSSH060F1*B*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217754413 |  | Water Loop | DAIKIN | WSSH060F1*B*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217037812 |  | Water Loop | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037817 |  | Water Loop | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037822 |  | Water Loop | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037827 |  | Water Loop | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217903454 |  | Water Loop | WaterFurnace | V5R036*D4**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903455 |  | Water Loop | WaterFurnace | V5R036*D4**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903456 |  | Water Loop | WaterFurnace | V5R036*D4**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903468 |  | Water Loop | WaterFurnace | V5R036*D0**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903469 |  | Water Loop | WaterFurnace | V5R036*D0**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903470 |  | Water Loop | WaterFurnace | V5R036*D0**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903471 |  | Water Loop | WaterFurnace | V5R036*D3**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903472 |  | Water Loop | WaterFurnace | V5R036*D3**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903473 |  | Water Loop | WaterFurnace | V5R036*D3**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
6501970 |  | Water Loop | GEOSTAR | GBV/GBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501971 |  | Water Loop | GEOSTAR | GBV/GBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501972 |  | Water Loop | GEOSTAR | GBV/GBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501973 |  | Water Loop | GEOSTAR | GBV/GBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501974 |  | Water Loop | GEOSTAR | GBV/GBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501975 |  | Water Loop | GEOSTAR | GBV/GBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6502006 |  | Water Loop | GEOSTAR | GBV/GBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
6674620 |  | Water Loop | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674621 |  | Water Loop | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674622 |  | Water Loop | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674623 |  | Water Loop | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6676515 |  | Water Loop | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676516 |  | Water Loop | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676518 |  | Water Loop | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676519 |  | Water Loop | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
202922716 |  | Water Loop | CARRIER | 50PSV036***3/CA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922719 |  | Water Loop | CARRIER | 50PSV036***5/EA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922722 |  | Water Loop | CARRIER | 50PSV036***6/FA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922725 |  | Water Loop | CARRIER | GB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922728 |  | Water Loop | BRYANT | GB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922731 |  | Water Loop | HEIL | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922734 |  | Water Loop | ARCOAIRE | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922737 |  | Water Loop | KEEPRITE | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922740 |  | Water Loop | TEMPSTAR | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922742 |  | Water Loop | COMFORTMAKER | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922745 |  | Water Loop | DAY & NIGHT | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202211045 |  | Water Loop | WaterFurnace | URD038*3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211046 |  | Water Loop | WaterFurnace | URD038*3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211047 |  | Water Loop | WaterFurnace | URD038*3*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211048 |  | Water Loop | WaterFurnace | URD049*0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
216625830 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625831 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625832 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625833 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625834 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625835 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625836 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625837 |  | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
202923075 |  | Water Loop | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
10581119 |  | Water Loop | GEOSTAR | 107H038**1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
214855067 |  | Water Loop | WHALEN | CASH*036AB**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855068 |  | Water Loop | WHALEN | CASH*036AD**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855069 |  | Water Loop | WHALEN | CASH*036AJ**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855070 |  | Water Loop | WHALEN | CASH*036AM**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855071 |  | Water Loop | WHALEN | CASV*036AB**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
204031802 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
203363090 |  | Water Loop | WILLIAMS | EW010H1D*A |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
5343143 |  | Water Loop | DAIKIN | WVFC1030*E***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
5343144 |  | Water Loop | DAIKIN | WVFC1030*F***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
5343145 |  | Water Loop | DAIKIN | WVFC1030*J***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
207200624 |  | Water Loop | GeoSmart Energy | VI048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
10268238 |  | Water Loop | TETCO | TBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
207334459 |  | Water Loop | WaterFurnace | NDP038H1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
202443457 |  | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
204344184 |  | Water Loop | 7 SERIES | NVV/NVH036B1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
204452547 |  | Water Loop | GeoSmart Energy | VI036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
204457696 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
5708463 |  | Water Loop | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708493 |  | Water Loop | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708550 |  | Water Loop | GEOSTAR | 101/102A022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708623 |  | Water Loop | GeoSmart Energy | GS022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5295956 |  | Water Loop | TRANE | EXHF0363 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295957 |  | Water Loop | TRANE | EXHF0368 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295958 |  | Water Loop | TRANE | EXHF0364 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
8560787 |  | Water Loop | 5 SERIES | NSV/NSH030H1*(0,3) |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8103479 |  | Water Loop | TRANE | DXHF0241 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105907 |  | Water Loop | TRANE | DXHF0242 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105909 |  | Water Loop | TRANE | DXHF0243 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
207200556 |  | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207200557 |  | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
4217883 |  | Water Loop | DAIKIN | WCCH4015*E*04* |  | 16000 | 17.6 | 18100 | 5.6 | 1.3333 | No
4217885 |  | Water Loop | DAIKIN | WCCH4015*J*04* |  | 15600 | 17.6 | 17200 | 5.6 | 1.3 | No
8105950 |  | Water Loop | TRANE | DXVF0241 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105955 |  | Water Loop | TRANE | DXVF0242 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
207200563 |  | Water Loop | GeoSmart Energy | GS030**1*(0,3)*H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
207200564 |  | Water Loop | GeoSmart Energy | GS030**1*(1,4)*H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
202330748 |  | Water Loop | WHALEN | CASH*036AD**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330749 |  | Water Loop | WHALEN | CASV*036AD**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
203362374 |  | Water Loop | WHALEN | VP-H-1004-*DD |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
202443459 |  | Water Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202443460 |  | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
202443465 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202330771 |  | Water Loop | WHALEN | CASH*036AJ**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330772 |  | Water Loop | WHALEN | CASV*036AJ**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330773 |  | Water Loop | WHALEN | CASH*036AM**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330774 |  | Water Loop | WHALEN | CASV*036AM**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
204474784 |  | Water Loop | GEOSTAR | 141/142B036**1*(1,2) |  | 32000 | 18 | 50000 | 5.3 | 2.6667 | No
8105926 |  | Water Loop | TRANE | DXHF0481 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105927 |  | Water Loop | TRANE | DXHF0482 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105928 |  | Water Loop | TRANE | DXHF0483 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105929 |  | Water Loop | TRANE | DXHF0484 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105930 |  | Water Loop | TRANE | DXHF0488 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
207178494 |  | Water Loop | GEOSTAR | 161/162J049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207178527 |  | Water Loop | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214855043 |  | Water Loop | WHALEN | CASH*015AB**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
8105956 |  | Water Loop | TRANE | DXVF0243 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105960 |  | Water Loop | TRANE | DXVF0244 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105965 |  | Water Loop | TRANE | DXVF0247 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105966 |  | Water Loop | TRANE | DXVF0248 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
5696567 |  | Water Loop | 5 SERIES | NSV/NSH022G1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
9063208 |  | Water Loop | DAIKIN | WVFC1030*K***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
8560801 |  | Water Loop | 5 SERIES | NSV/NSH030H1*(1,4) |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8105911 |  | Water Loop | TRANE | DXHF0244 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105912 |  | Water Loop | TRANE | DXHF0247 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105913 |  | Water Loop | TRANE | DXHF0248 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
202350098 |  | Water Loop | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5613676 |  | Water Loop | GEOSTAR | 141/142A048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
202330280 |  | Water Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 14200 | 17 | 17900 | 6.3 | 1.1833 | No
5440741 |  | Water Loop | 7 SERIES | NVV/NVH048A1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
5612204 |  | Water Loop | GeoSmart Energy | VI048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
5295953 |  | Water Loop | TRANE | EXHF0361 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295954 |  | Water Loop | TRANE | EXHF0362 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295955 |  | Water Loop | TRANE | EXHF0367 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
202330279 |  | Water Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 14200 | 17 | 17900 | 6.3 | 1.1833 | No
202607208 |  | Water Loop | WHALEN | VP-A-1004-*DD |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
8789591 |  | Water Loop | GEOSTAR | 101/102H030**1*(0,3)***** |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789592 |  | Water Loop | GeoSmart Energy | GS030**1*(0,3)********H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789593 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789596 |  | Water Loop | GEOSTAR | 101/102H030**1*(1,4)***** |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8789597 |  | Water Loop | GeoSmart Energy | GS030**1*(1,4)********H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8789598 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8105973 |  | Water Loop | TRANE | DXVF0481 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105974 |  | Water Loop | TRANE | DXVF0482 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105975 |  | Water Loop | TRANE | DXVF0483 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105976 |  | Water Loop | TRANE | DXVF0484 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
202350095 |  | Water Loop | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202350096 |  | Water Loop | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214855044 |  | Water Loop | WHALEN | CASH*015AD**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855045 |  | Water Loop | WHALEN | CASV*015AB**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855046 |  | Water Loop | WHALEN | CASV*015AD**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855047 |  | Water Loop | WHALEN | CASH*018AB**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
214855048 |  | Water Loop | WHALEN | CASH*018AD**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
214855049 |  | Water Loop | WHALEN | CASV*018AB**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
214855050 |  | Water Loop | WHALEN | CASV*018AD**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
6580833 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
6581203 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
10581109 |  | Water Loop | 5 SERIES | NDP038H1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
10581114 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
214855072 |  | Water Loop | WHALEN | CASV*036AD**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855073 |  | Water Loop | WHALEN | CASV*036AJ**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855074 |  | Water Loop | WHALEN | CASV*036AM**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
203113882 |  | Water Loop | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
206199262 |  | Water Loop | RHEEM | RPVV/H/D026D |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | No
8105977 |  | Water Loop | TRANE | DXVF0488 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
207200571 |  | Water Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207200572 |  | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
207200617 |  | Water Loop | GeoSmart Energy | VI036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
203466716 |  | Water Loop | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202443468 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202443469 |  | Water Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
202330359 |  | Water Loop | AAON, Inc. | WV-016-1-H-ACAC-C0-10-200-A |  | 14000 | 17.5 | 18400 | 5.1 | 1.1667 | No
202330360 |  | Water Loop | AAON, Inc. | WV-016-A-H-ACAC-C0-10-200-A |  | 14000 | 17.5 | 18400 | 5.1 | 1.1667 | No
202330746 |  | Water Loop | WHALEN | CASH*036AB**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330747 |  | Water Loop | WHALEN | CASV*036AB**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
203363069 |  | Water Loop | WILLIAMS | EW010A1D*A |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
203113887 |  | Water Loop | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
206315251 |  | Water Loop | WHALEN | CASH*015AD**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315252 |  | Water Loop | WHALEN | CASV*015AD**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315253 |  | Water Loop | WHALEN | CASH*018AB**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
206315254 |  | Water Loop | WHALEN | CASV*018AB**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
206315255 |  | Water Loop | WHALEN | CASH*018AD**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
206315256 |  | Water Loop | WHALEN | CASV*018AD**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
205536344 |  | Water Loop | AAON, Inc. | WV-072-2-0-DCAC-C0-10-200-A |  | 81000 | 17 | 96200 | 5.4 | 6.75 | No
10268233 |  | Water Loop | GEOCOMFORT | GBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268234 |  | Water Loop | HYDRON MODULE | HBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268235 |  | Water Loop | TETCO | TBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268236 |  | Water Loop | GEOCOMFORT | GBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268237 |  | Water Loop | HYDRON MODULE | HBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
206315249 |  | Water Loop | WHALEN | CASH*015AB**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315250 |  | Water Loop | WHALEN | CASV*015AB**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
205536348 |  | Water Loop | AAON, Inc. | WV-072-3-0-DCAC-C0-10-200-A |  | 81000 | 17 | 96200 | 5.4 | 6.75 | No
203490410 |  | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No

## Commercial Ground Water HP
AHRI Certified Reference Number | Date No Longer Eligible | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage | Tax Credit (IRA) Eligibility
216714642 |  | Ground Water | GEOSTAR | G3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714643 |  | Ground Water | GEOSTAR | G3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714644 |  | Ground Water | GEOSTAR | G3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
202211049 |  | Ground Water | WaterFurnace | URD049*0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211050 |  | Ground Water | WaterFurnace | URD049*0*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211051 |  | Ground Water | WaterFurnace | URD049*3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211052 |  | Ground Water | WaterFurnace | URD049*3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211053 |  | Ground Water | WaterFurnace | URD049*3*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211054 |  | Ground Water | WaterFurnace | URD064*0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211055 |  | Ground Water | WaterFurnace | URD064*0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211056 |  | Ground Water | WaterFurnace | URD064*0*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211057 |  | Ground Water | WaterFurnace | URD064*3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211058 |  | Ground Water | WaterFurnace | URD064*3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211059 |  | Ground Water | WaterFurnace | URD064*3*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211060 |  | Ground Water | WaterFurnace | URD072*0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211061 |  | Ground Water | WaterFurnace | URD072*0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211062 |  | Ground Water | WaterFurnace | URD072*0*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211063 |  | Ground Water | WaterFurnace | URD072*3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211064 |  | Ground Water | WaterFurnace | URD072*3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211065 |  | Ground Water | WaterFurnace | URD072*3*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
217351675 |  | Ground Water | BOSCH | RP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
217351676 |  | Ground Water | BOSCH | RP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
217351677 |  | Ground Water | BOSCH | RP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
217351678 |  | Ground Water | BOSCH | RP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
217351679 |  | Ground Water | BOSCH | RP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | Yes
217351680 |  | Ground Water | BOSCH | RP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | Yes
217351681 |  | Ground Water | BOSCH | RP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | Yes
217351682 |  | Ground Water | BOSCH | RP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | Yes
217351683 |  | Ground Water | BOSCH | RP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | Yes
217351684 |  | Ground Water | BOSCH | RP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | Yes
217351686 |  | Ground Water | BOSCH | RP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | Yes
217351687 |  | Ground Water | BOSCH | TW025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351689 |  | Ground Water | BOSCH | TW049-1***-*****C |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351692 |  | Ground Water | FHP | CP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
217351693 |  | Ground Water | FHP | CP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
217351694 |  | Ground Water | FHP | CP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
217351695 |  | Ground Water | FHP | CP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
217351696 |  | Ground Water | FHP | CP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
217351697 |  | Ground Water | FHP | CP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
217351698 |  | Ground Water | FHP | CP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
217351699 |  | Ground Water | FHP | CP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
217351700 |  | Ground Water | FHP | CP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | No
217351701 |  | Ground Water | FHP | CP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | No
217351702 |  | Ground Water | FHP | CP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | No
217351703 |  | Ground Water | FHP | CP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | No
217351704 |  | Ground Water | FHP | CP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | No
217351705 |  | Ground Water | FHP | CP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | No
217351707 |  | Ground Water | FHP | CP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | No
217351708 |  | Ground Water | FHP | WT025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351709 |  | Ground Water | FHP | WT025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216621350 |  | Ground Water | GEOSTAR | G5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621351 |  | Ground Water | GEOSTAR | G5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621352 |  | Ground Water | GEOSTAR | G5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621353 |  | Ground Water | GEOSTAR | G5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621354 |  | Ground Water | GEOSTAR | G5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621355 |  | Ground Water | GEOSTAR | G5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621356 |  | Ground Water | GEOSTAR | G5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621357 |  | Ground Water | GEOSTAR | G5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621358 |  | Ground Water | GEOSTAR | G5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621359 |  | Ground Water | GEOSTAR | G5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
202084059 |  | Ground Water | GEOCOMFORT | GZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
202084060 |  | Ground Water | HYDRON MODULE | HZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
202084061 |  | Ground Water | HYDRON MODULE | HZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
202084062 |  | Ground Water | TETCO | TZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
202084063 |  | Ground Water | TETCO | TZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
3628355 |  | Ground Water | WaterFurnace | USV/USH070**0*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628356 |  | Ground Water | WaterFurnace | USV/USH070**3*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628357 |  | Ground Water | WaterFurnace | USV/USH070**4*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628359 |  | Ground Water | WaterFurnace | USV/USH060**0*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628360 |  | Ground Water | WaterFurnace | USV/USH060**3*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628361 |  | Ground Water | WaterFurnace | USV/USH060**4*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628363 |  | Ground Water | WaterFurnace | USV/USH048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628364 |  | Ground Water | WaterFurnace | USV/USH048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628365 |  | Ground Water | WaterFurnace | USV/USH048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628367 |  | Ground Water | WaterFurnace | USV/USH042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628368 |  | Ground Water | WaterFurnace | USV/USH042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628369 |  | Ground Water | WaterFurnace | USV/USH042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628403 |  | Ground Water | WaterFurnace | USV/USH030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628404 |  | Ground Water | WaterFurnace | USV/USH030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628405 |  | Ground Water | WaterFurnace | USV/USH030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628406 |  | Ground Water | WaterFurnace | USV/USH030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628407 |  | Ground Water | WaterFurnace | USH023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628408 |  | Ground Water | WaterFurnace | USV/USH036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628409 |  | Ground Water | WaterFurnace | USV/USH036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628410 |  | Ground Water | WaterFurnace | USV/USH036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628411 |  | Ground Water | WaterFurnace | USH023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628412 |  | Ground Water | WaterFurnace | USH023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628413 |  | Ground Water | WaterFurnace | USH023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
7022707 |  | Ground Water | GeoSmart Energy | ZS060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
7022708 |  | Ground Water | GEOSTAR | ZS060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
7137597 |  | Ground Water | GEO-THERMAL SPLIT | GS024**1**1 | FE/V****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
7167375 |  | Ground Water | BRYANT | GB024H/V******1*X1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
7167376 |  | Ground Water | CARRIER | GB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
7167377 |  | Ground Water | BRYANT | GB030H/V******1*X1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
7167378 |  | Ground Water | CARRIER | GB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
7167412 |  | Ground Water | BRYANT | GT072C/H/V******1*X1 |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167413 |  | Ground Water | CARRIER | GT072C/H/V******1**1 |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167538 |  | Ground Water | CARRIER | 50PTD/H/V024***3/CA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167539 |  | Ground Water | CARRIER | 50PTD/H/V024***5/EA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167540 |  | Ground Water | CARRIER | 50PTD/H/V024***4/DA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167541 |  | Ground Water | CARRIER | 50PTD/H/V024***6/FA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167542 |  | Ground Water | CARRIER | 50PTD/H/V036***3/CA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167543 |  | Ground Water | CARRIER | 50PTD/H/V036***5/EA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167544 |  | Ground Water | CARRIER | 50PTD/H/V036***4/DA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167545 |  | Ground Water | CARRIER | 50PTD/H/V036***6/FA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167546 |  | Ground Water | CARRIER | 50PTD/H/V048***3/CA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167547 |  | Ground Water | CARRIER | 50PTD/H/V048***5/EA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167548 |  | Ground Water | CARRIER | 50PTD/H/V048***6/FA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167549 |  | Ground Water | CARRIER | 50PTD/H/V060***3/CA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7167550 |  | Ground Water | CARRIER | 50PTD/H/V060***5/EA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7167551 |  | Ground Water | CARRIER | 50PTD/H/V060***6/FA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7167552 |  | Ground Water | CARRIER | 50PTD/H/V070***3/CA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167553 |  | Ground Water | CARRIER | 50PTD/H/V070***5/EA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167554 |  | Ground Water | CARRIER | 50PTD/H/V070***6/FA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7170602 |  | Ground Water | GEOCOMFORT | GVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
7170603 |  | Ground Water | HYDRON MODULE | HVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
7170604 |  | Ground Water | TETCO | TVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
7499552 |  | Ground Water | FHP | LM036-2VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499553 |  | Ground Water | FHP | LM036-3VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499554 |  | Ground Water | FHP | LM036-4VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499556 |  | Ground Water | FHP | LM048-1VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499559 |  | Ground Water | FHP | LM048-3VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499560 |  | Ground Water | FHP | LM048-4VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499562 |  | Ground Water | FHP | LM060-1VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7499565 |  | Ground Water | FHP | LM060-3VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7499566 |  | Ground Water | FHP | LM060-4VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7499569 |  | Ground Water | FHP | LM070-1VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499571 |  | Ground Water | FHP | LM070-3VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499572 |  | Ground Water | FHP | LM070-4VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499702 |  | Ground Water | BOSCH | SM036-1CF/HZ/VT |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
7499719 |  | Ground Water | BOSCH | SM070-1CF/HZ/VT |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7519546 |  | Ground Water | GEOCOMFORT | GVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519547 |  | Ground Water | HYDRON MODULE | HVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519548 |  | Ground Water | TETCO | TVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519549 |  | Ground Water | GEOCOMFORT | GVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519550 |  | Ground Water | HYDRON MODULE | HVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519551 |  | Ground Water | TETCO | TVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519552 |  | Ground Water | GEOCOMFORT | GVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519553 |  | Ground Water | HYDRON MODULE | HVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519554 |  | Ground Water | TETCO | TVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519555 |  | Ground Water | GEOCOMFORT | GVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519556 |  | Ground Water | HYDRON MODULE | HVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519557 |  | Ground Water | TETCO | TVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519558 |  | Ground Water | GEOCOMFORT | GVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519559 |  | Ground Water | HYDRON MODULE | HVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519560 |  | Ground Water | TETCO | TVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519561 |  | Ground Water | GEOCOMFORT | GVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519562 |  | Ground Water | HYDRON MODULE | HVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519563 |  | Ground Water | TETCO | TVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519564 |  | Ground Water | GEOCOMFORT | GVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519565 |  | Ground Water | HYDRON MODULE | HVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519566 |  | Ground Water | TETCO | TVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519567 |  | Ground Water | GEOCOMFORT | GVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519568 |  | Ground Water | HYDRON MODULE | HVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519569 |  | Ground Water | TETCO | TVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519570 |  | Ground Water | GEOCOMFORT | GVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519571 |  | Ground Water | HYDRON MODULE | HVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519572 |  | Ground Water | TETCO | TVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519573 |  | Ground Water | GEOCOMFORT | GVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519574 |  | Ground Water | HYDRON MODULE | HVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519575 |  | Ground Water | TETCO | TVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519576 |  | Ground Water | GEOCOMFORT | GVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519577 |  | Ground Water | HYDRON MODULE | HVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519578 |  | Ground Water | TETCO | TVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519579 |  | Ground Water | GEOCOMFORT | GVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519580 |  | Ground Water | HYDRON MODULE | HVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519581 |  | Ground Water | TETCO | TVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519582 |  | Ground Water | GEOCOMFORT | GVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519583 |  | Ground Water | HYDRON MODULE | HVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519584 |  | Ground Water | TETCO | TVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519727 |  | Ground Water | GEOCOMFORT | GVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
7519748 |  | Ground Water | HYDRON MODULE | HVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
7519756 |  | Ground Water | TETCO | TVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
203372406 |  | Ground Water | TEMPSTAR | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372407 |  | Ground Water | COMFORTMAKER | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372408 |  | Ground Water | DAY & NIGHT | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372993 |  | Ground Water | BOSCH | SM060-1HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
203372994 |  | Ground Water | BOSCH | SM070-1HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
203372995 |  | Ground Water | BOSCH | SM070-1HZ*-*****C |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
203380957 |  | Ground Water | BOSCH | EP018-1VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203380958 |  | Ground Water | BOSCH | EP018-2VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203380959 |  | Ground Water | BOSCH | EP018-1HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203380960 |  | Ground Water | BOSCH | EP018-2HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203380963 |  | Ground Water | BOSCH | EP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380964 |  | Ground Water | BOSCH | EP042-3VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380965 |  | Ground Water | BOSCH | EP042-4VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380966 |  | Ground Water | BOSCH | EP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380967 |  | Ground Water | BOSCH | EP042-3HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380968 |  | Ground Water | BOSCH | EP042-4HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380969 |  | Ground Water | BOSCH | EP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203380970 |  | Ground Water | BOSCH | EP048-3VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
218353572 |  | Ground Water | JOHNSON CONTROLS | DA042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353576 |  | Ground Water | JOHNSON CONTROLS | DA042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353580 |  | Ground Water | JOHNSON CONTROLS | DA042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353584 |  | Ground Water | JOHNSON CONTROLS | DA042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353588 |  | Ground Water | JOHNSON CONTROLS | DA042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353592 |  | Ground Water | JOHNSON CONTROLS | DA042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
202330438 |  | Ground Water | AAON, Inc. | RQ-003-2-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330439 |  | Ground Water | AAON, Inc. | RQ-003-3-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330440 |  | Ground Water | AAON, Inc. | RQ-003-4-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330444 |  | Ground Water | AAON, Inc. | RQ-004-1-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330445 |  | Ground Water | AAON, Inc. | RQ-004-1-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330446 |  | Ground Water | AAON, Inc. | RQ-004-2-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330447 |  | Ground Water | AAON, Inc. | RQ-004-3-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330448 |  | Ground Water | AAON, Inc. | RQ-004-4-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330449 |  | Ground Water | AAON, Inc. | RQ-004-2-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330450 |  | Ground Water | AAON, Inc. | RQ-004-3-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330451 |  | Ground Water | AAON, Inc. | RQ-004-4-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
218158071 |  | Ground Water | YORK | Y3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
218158074 |  | Ground Water | YORK | Y3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
218158076 |  | Ground Water | YORK | Y3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
218158078 |  | Ground Water | YORK | Y3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
218158079 |  | Ground Water | YORK | Y3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
218158081 |  | Ground Water | YORK | Y3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
218158083 |  | Ground Water | YORK | Y3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
218158086 |  | Ground Water | YORK | Y3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
218158087 |  | Ground Water | YORK | Y3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
218158088 |  | Ground Water | YORK | Y3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
218158092 |  | Ground Water | YORK | Y3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
218158093 |  | Ground Water | YORK | Y3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
218158094 |  | Ground Water | YORK | Y3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
218158095 |  | Ground Water | YORK | Y3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
218158096 |  | Ground Water | YORK | Y3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
218158097 |  | Ground Water | YORK | Y3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
218158098 |  | Ground Water | YORK | Y3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
218158106 |  | Ground Water | YORK | Y3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
218158107 |  | Ground Water | YORK | Y3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
218158108 |  | Ground Water | YORK | Y3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
218158109 |  | Ground Water | YORK | Y3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
218158110 |  | Ground Water | YORK | Y3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
218158111 |  | Ground Water | YORK | Y3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
218158112 |  | Ground Water | YORK | Y3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
218158113 |  | Ground Water | YORK | Y3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
218158114 |  | Ground Water | YORK | Y3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
218158115 |  | Ground Water | YORK | Y3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
218158116 |  | Ground Water | YORK | Y3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
218158117 |  | Ground Water | YORK | Y3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
218158123 |  | Ground Water | YORK | Y3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
218158124 |  | Ground Water | YORK | Y3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
218158125 |  | Ground Water | YORK | Y3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
218158126 |  | Ground Water | YORK | Y3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
218353673 |  | Ground Water | JOHNSON CONTROLS | DQ036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218353674 |  | Ground Water | JOHNSON CONTROLS | DQ036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218353675 |  | Ground Water | JOHNSON CONTROLS | DQ048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
218353676 |  | Ground Water | JOHNSON CONTROLS | DQ048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218353677 |  | Ground Water | JOHNSON CONTROLS | DQ048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
218353678 |  | Ground Water | JOHNSON CONTROLS | DQ048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218353679 |  | Ground Water | JOHNSON CONTROLS | DQ048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
218353680 |  | Ground Water | JOHNSON CONTROLS | DQ048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218353681 |  | Ground Water | JOHNSON CONTROLS | DQ060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218353682 |  | Ground Water | JOHNSON CONTROLS | DQ060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
218353683 |  | Ground Water | JOHNSON CONTROLS | DQ060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218353684 |  | Ground Water | JOHNSON CONTROLS | DQ060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
218353685 |  | Ground Water | JOHNSON CONTROLS | DQ060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218471838 |  | Ground Water | YORK | AQ024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218471839 |  | Ground Water | YORK | QQ024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
218471840 |  | Ground Water | YORK | AQ024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218471841 |  | Ground Water | YORK | AQ024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218471842 |  | Ground Water | YORK | QQ036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
218471843 |  | Ground Water | YORK | AQ036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218471844 |  | Ground Water | YORK | AQ036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218471845 |  | Ground Water | YORK | QQ036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
218471846 |  | Ground Water | YORK | AQ036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218471847 |  | Ground Water | YORK | AQ036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218471848 |  | Ground Water | YORK | QQ048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
218471849 |  | Ground Water | YORK | AQ048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
218471850 |  | Ground Water | YORK | AQ048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
218471851 |  | Ground Water | YORK | QQ048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
218471852 |  | Ground Water | YORK | AQ048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218471853 |  | Ground Water | YORK | AQ048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218471854 |  | Ground Water | YORK | QQ060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
218471855 |  | Ground Water | YORK | AQ060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218471856 |  | Ground Water | YORK | AQ060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218471857 |  | Ground Water | YORK | QQ060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
218471858 |  | Ground Water | YORK | AQ060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
218471859 |  | Ground Water | YORK | AQ060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
218471860 |  | Ground Water | YORK | QQ070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
218471861 |  | Ground Water | YORK | AQ070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218471862 |  | Ground Water | YORK | AQ070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218471863 |  | Ground Water | YORK | QQ070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
218471864 |  | Ground Water | YORK | AQ070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218471865 |  | Ground Water | YORK | AQ070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218471866 |  | Ground Water | YORK | QQ070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
218471867 |  | Ground Water | YORK | AQ070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218471868 |  | Ground Water | YORK | AQ070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218471869 |  | Ground Water | YORK | QQ070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
218471870 |  | Ground Water | YORK | AQ070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218471871 |  | Ground Water | YORK | AQ070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218471872 |  | Ground Water | YORK | AH025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218471877 |  | Ground Water | YORK | QW025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
218471879 |  | Ground Water | YORK | QW049-1***-*****C |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
218471881 |  | Ground Water | YORK | AH025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218471891 |  | Ground Water | YORK | QZ024-1CSC-*****A | CDM24B5XXS1A | 27400 | 23.2 | 23800 | 5 | 2.2833 | Yes
218471892 |  | Ground Water | YORK | QZ024-1CSN-*****A | CDM24B5XXS1A | 27600 | 24.3 | 23800 | 5.1 | 2.3 | Yes
218471893 |  | Ground Water | YORK | QZ036-1CSC-*****A | CDM30B5XXS1A | 39600 | 21.5 | 37800 | 4.8 | 3.3 | Yes
217351843 |  | Ground Water | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351844 |  | Ground Water | DAY & NIGHT | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351846 |  | Ground Water | DAY & NIGHT | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
7411231 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411301 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7411380 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411778 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411875 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7411949 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412057 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412158 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7412253 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412381 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412626 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412712 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412777 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412856 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412926 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7413034 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7413487 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7414142 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414232 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414335 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
203337768 |  | Ground Water | BOSCH-GEO | CE025-1VT/HZ/CF*-*****B |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337769 |  | Ground Water | BOSCH | CE025-1VT/HZ/CF*-*****B |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337770 |  | Ground Water | CARRIER | GP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337771 |  | Ground Water | BRYANT | GP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337772 |  | Ground Water | HEIL | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337773 |  | Ground Water | ARCOAIRE | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337774 |  | Ground Water | KEEPRITE | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337775 |  | Ground Water | TEMPSTAR | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337776 |  | Ground Water | COMFORTMAKER | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337777 |  | Ground Water | DAY & NIGHT | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203343532 |  | Ground Water | BOSCH-GEO | SM024-1CS*******A | SM024-1AV/AH*-*****A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | Yes
203343535 |  | Ground Water | BOSCH | SM024-1CS*******A | SM024-1AV/AH*-*****A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | Yes
203344888 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
203344891 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
4651405 |  | Ground Water | WaterFurnace | USV/USH030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651407 |  | Ground Water | WaterFurnace | USV/USH030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651417 |  | Ground Water | WaterFurnace | USV/USH036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651418 |  | Ground Water | WaterFurnace | USV/USH036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651419 |  | Ground Water | WaterFurnace | USV/USH036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651420 |  | Ground Water | WaterFurnace | USV/USH036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651530 |  | Ground Water | WaterFurnace | USV/USH042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651532 |  | Ground Water | WaterFurnace | USV/USH042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651533 |  | Ground Water | WaterFurnace | USV/USH042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651546 |  | Ground Water | WaterFurnace | USV/USH048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651547 |  | Ground Water | WaterFurnace | USV/USH048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651548 |  | Ground Water | WaterFurnace | USV/USH048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651574 |  | Ground Water | WaterFurnace | USV/USH060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651575 |  | Ground Water | WaterFurnace | USV/USH060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651576 |  | Ground Water | WaterFurnace | USV/USH060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651577 |  | Ground Water | WaterFurnace | USV/USH070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651578 |  | Ground Water | WaterFurnace | USV/USH070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651579 |  | Ground Water | WaterFurnace | USV/USH070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651610 |  | Ground Water | GEOSTAR | ZS023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651611 |  | Ground Water | GeoSmart Energy | ZS023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651614 |  | Ground Water | GEOSTAR | ZS024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651615 |  | Ground Water | GeoSmart Energy | ZS024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651618 |  | Ground Water | GEOSTAR | ZS024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651619 |  | Ground Water | GeoSmart Energy | ZS024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651622 |  | Ground Water | GEOSTAR | ZS024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651623 |  | Ground Water | GeoSmart Energy | ZS024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651626 |  | Ground Water | GEOSTAR | ZS024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651627 |  | Ground Water | GeoSmart Energy | ZS024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651630 |  | Ground Water | GEOSTAR | ZS030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651631 |  | Ground Water | GeoSmart Energy | ZS030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651634 |  | Ground Water | GEOSTAR | ZS030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651635 |  | Ground Water | GeoSmart Energy | ZS030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651639 |  | Ground Water | GEOSTAR | ZS030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651640 |  | Ground Water | GeoSmart Energy | ZS030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651644 |  | Ground Water | GEOSTAR | ZS030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651645 |  | Ground Water | GeoSmart Energy | ZS030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651657 |  | Ground Water | GEOSTAR | ZS036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651658 |  | Ground Water | GeoSmart Energy | ZS036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651665 |  | Ground Water | GEOSTAR | ZS036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651666 |  | Ground Water | GeoSmart Energy | ZS036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651726 |  | Ground Water | GEOSTAR | ZS036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651727 |  | Ground Water | GeoSmart Energy | ZS036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651732 |  | Ground Water | GEOSTAR | ZS036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651733 |  | Ground Water | GeoSmart Energy | ZS036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651865 |  | Ground Water | GEOSTAR | ZS023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651866 |  | Ground Water | GeoSmart Energy | ZS023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651869 |  | Ground Water | GEOSTAR | ZS023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
216801983 |  | Ground Water | CARRIER | 50WT*024(G-K;N-R)**3*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801984 |  | Ground Water | CARRIER | 50WT*024(G-K;N-R)**3*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801985 |  | Ground Water | CARRIER | 50WT*024(L/M/S/T)**3*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801986 |  | Ground Water | CARRIER | 50WT*024(L/M/S/T)**3*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801987 |  | Ground Water | CARRIER | 50WT*024(G-K;N-R)**4*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801988 |  | Ground Water | CARRIER | 50WT*024(G-K;N-R)**4*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801989 |  | Ground Water | CARRIER | 50WT*024(L/M/S/T)**4*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801990 |  | Ground Water | CARRIER | 50WT*024(L/M/S/T)**4*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801991 |  | Ground Water | CARRIER | 50WT*024(G-K;N-R)**5*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801992 |  | Ground Water | CARRIER | 50WT*024(G-K;N-R)**5*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801993 |  | Ground Water | CARRIER | 50WT*024(L/M/S/T)**5*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801994 |  | Ground Water | CARRIER | 50WT*024(L/M/S/T)**5*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801995 |  | Ground Water | CARRIER | 50WT*024(G-K;N-R)**6*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801996 |  | Ground Water | CARRIER | 50WT*024(G-K;N-R)**6*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801997 |  | Ground Water | CARRIER | 50WT*024(L/M/S/T)**6*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801998 |  | Ground Water | CARRIER | 50WT*024(L/M/S/T)**6*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801999 |  | Ground Water | CARRIER | 50WT*036***3*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802000 |  | Ground Water | CARRIER | 50WT*036***3*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802001 |  | Ground Water | CARRIER | 50WT*036***4*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802002 |  | Ground Water | CARRIER | 50WT*036***4*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802003 |  | Ground Water | CARRIER | 50WT*036***5*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802004 |  | Ground Water | CARRIER | 50WT*036***5*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802005 |  | Ground Water | CARRIER | 50WT*036***6*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802006 |  | Ground Water | CARRIER | 50WT*036***6*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802007 |  | Ground Water | CARRIER | 50WT*048***3*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802008 |  | Ground Water | CARRIER | 50WT*048***3*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216802009 |  | Ground Water | CARRIER | 50WT*048***5*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802010 |  | Ground Water | CARRIER | 50WT*048***5*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216802011 |  | Ground Water | CARRIER | 50WT*048***6*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802012 |  | Ground Water | CARRIER | 50WT*048***6*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216802013 |  | Ground Water | CARRIER | 50WT*060***3*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802014 |  | Ground Water | CARRIER | 50WT*060***3*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802015 |  | Ground Water | CARRIER | 50WT*060***5*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802016 |  | Ground Water | CARRIER | 50WT*060***5*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802017 |  | Ground Water | CARRIER | 50WT*060***6*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802018 |  | Ground Water | CARRIER | 50WT*060***6*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802019 |  | Ground Water | CARRIER | 50WT*070(G-K;N-R)**3*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802020 |  | Ground Water | CARRIER | 50WT*070(G-K;N-R)**3*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802021 |  | Ground Water | CARRIER | 50WT*070(L/M/S/T)**3*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802022 |  | Ground Water | CARRIER | 50WT*070(L/M/S/T)**3*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802023 |  | Ground Water | CARRIER | 50WT*070(G-K;N-R)**5*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802024 |  | Ground Water | CARRIER | 50WT*070(G-K;N-R)**5*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218471894 |  | Ground Water | YORK | QZ036-1CSN-*****A | CDM30B5XXS1A | 40200 | 22.2 | 38800 | 5 | 3.35 | Yes
218471895 |  | Ground Water | YORK | QZ048-1CSC-*****A | CDM48C5XXS1A | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | Yes
218471896 |  | Ground Water | YORK | QZ048-1CSN-*****A | CDM48C5XXS1A | 53400 | 22.5 | 46600 | 4.7 | 4.45 | Yes
218471898 |  | Ground Water | YORK | QZ060-1CSN-*****A | CDM60C5XXS1A | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | Yes
218471899 |  | Ground Water | YORK | AZ024-1CSC-*****A | JDE24E5XX2DS1 | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
218471900 |  | Ground Water | YORK | AZ024-1CSN-*****A | JDE24E5XX2DS1 | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
218471901 |  | Ground Water | YORK | QZ024-1CSC-*****A | JDE24E5XX2DS1 | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
218471902 |  | Ground Water | YORK | QZ024-1CSN-*****A | JDE24E5XX2DS1 | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
218471903 |  | Ground Water | YORK | AZ036-1CSC-*****A | JDE36E5XX2DS1 | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
218471904 |  | Ground Water | YORK | AZ036-1CSN-*****A | JDE36E5XX2DS1 | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
218471905 |  | Ground Water | YORK | QZ036-1CSC-*****A | JDE36E5XX2DS1 | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
218471906 |  | Ground Water | YORK | QZ036-1CSN-*****A | JDE36E5XX2DS1 | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
218471907 |  | Ground Water | YORK | AZ048-1CSC-*****A | JDE48F5XX2DS1 | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
218471908 |  | Ground Water | YORK | AZ048-1CSN-*****A | JDE48F5XX2DS1 | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
218471909 |  | Ground Water | YORK | QZ048-1CSC-*****A | JDE48F5XX2DS1 | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
218471910 |  | Ground Water | YORK | QZ048-1CSN-*****A | JDE48F5XX2DS1 | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
5646384 |  | Ground Water | GEOCOMFORT | GCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646385 |  | Ground Water | HYDRON MODULE | HCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646386 |  | Ground Water | TETCO | TCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646387 |  | Ground Water | GEOCOMFORT | GCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646388 |  | Ground Water | HYDRON MODULE | HCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646389 |  | Ground Water | TETCO | TCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646391 |  | Ground Water | GEOCOMFORT | GXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646392 |  | Ground Water | HYDRON MODULE | HXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646393 |  | Ground Water | TETCO | TXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646394 |  | Ground Water | GEOCOMFORT | GXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646395 |  | Ground Water | HYDRON MODULE | HXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646396 |  | Ground Water | TETCO | TXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646397 |  | Ground Water | GEOCOMFORT | GXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646398 |  | Ground Water | HYDRON MODULE | HXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646399 |  | Ground Water | TETCO | TXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646765 |  | Ground Water | GEOCOMFORT | GCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
5646766 |  | Ground Water | HYDRON MODULE | HCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
5646767 |  | Ground Water | TETCO | TCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
218471654 |  | Ground Water | YORK | AA042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218471655 |  | Ground Water | YORK | QA042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218471656 |  | Ground Water | YORK | AA042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218471657 |  | Ground Water | YORK | QA042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218471658 |  | Ground Water | YORK | AA042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218471659 |  | Ground Water | YORK | QA042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218471660 |  | Ground Water | YORK | AA042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218471661 |  | Ground Water | YORK | QA042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839496 |  | Ground Water | CARRIER | 50WC*042(G-K;N-R)**3*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839497 |  | Ground Water | CARRIER | 50WC*042(L/M/S/T)**3*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839498 |  | Ground Water | CARRIER | 50WC*042(G-K;N-R)**5*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839499 |  | Ground Water | CARRIER | 50WC*042(L/M/S/T)**5*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839500 |  | Ground Water | CARRIER | 50WC*042(G-K;N-R)**6*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839501 |  | Ground Water | CARRIER | 50WC*042(L/M/S/T)**6*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
202146892 |  | Ground Water | TETCO | TZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146893 |  | Ground Water | GEOCOMFORT | GZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146894 |  | Ground Water | GEOCOMFORT | GZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146895 |  | Ground Water | GEOCOMFORT | GZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146896 |  | Ground Water | GEOCOMFORT | GZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146897 |  | Ground Water | HYDRON MODULE | HZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146898 |  | Ground Water | HYDRON MODULE | HZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146899 |  | Ground Water | HYDRON MODULE | HZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146900 |  | Ground Water | HYDRON MODULE | HZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146901 |  | Ground Water | TETCO | TZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146902 |  | Ground Water | TETCO | TZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146903 |  | Ground Water | TETCO | TZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146904 |  | Ground Water | GEOCOMFORT | GZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146905 |  | Ground Water | GEOCOMFORT | GZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146906 |  | Ground Water | GEOCOMFORT | GZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146907 |  | Ground Water | HYDRON MODULE | HZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146908 |  | Ground Water | HYDRON MODULE | HZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146909 |  | Ground Water | HYDRON MODULE | HZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146910 |  | Ground Water | TETCO | TZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146911 |  | Ground Water | TETCO | TZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146912 |  | Ground Water | TETCO | TZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146913 |  | Ground Water | GEOCOMFORT | GZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
218353078 |  | Ground Water | SKYMARK | PQ048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218353079 |  | Ground Water | SKYMARK | PQ060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218353080 |  | Ground Water | SKYMARK | PQ060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
218353081 |  | Ground Water | SKYMARK | PQ060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218353082 |  | Ground Water | SKYMARK | PQ060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
218353083 |  | Ground Water | SKYMARK | PQ070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353084 |  | Ground Water | SKYMARK | PQ070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353085 |  | Ground Water | SKYMARK | PQ070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353086 |  | Ground Water | SKYMARK | PQ070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353087 |  | Ground Water | SKYMARK | PQ070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353088 |  | Ground Water | SKYMARK | PQ070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353089 |  | Ground Water | SKYMARK | PQ070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353090 |  | Ground Water | SKYMARK | PQ070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353144 |  | Ground Water | SKYMARK | PD007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218353145 |  | Ground Water | SKYMARK | PD007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218353146 |  | Ground Water | SKYMARK | PD007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218353147 |  | Ground Water | SKYMARK | PD007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218353148 |  | Ground Water | SKYMARK | PD009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218353149 |  | Ground Water | SKYMARK | PD009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218353150 |  | Ground Water | SKYMARK | PD009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218353151 |  | Ground Water | SKYMARK | PD009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218353152 |  | Ground Water | SKYMARK | PD012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
218396736 |  | Ground Water | SKYMARK | PH025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218396737 |  | Ground Water | SKYMARK | PH025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217755022 |  | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755023 |  | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755024 |  | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217893588 |  | Ground Water | Engineered Comfort | 44VHB/VCB-19 |  | 21000 | 21.1 | 18500 | 4.1 | 1.75 | Yes
217897411 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
217897412 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
217897413 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
217897414 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
217897417 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
217897418 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
217897421 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
217897422 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
217897425 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
217897426 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
217897427 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
217897428 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
217897429 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
217897430 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
217897433 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
217897434 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
207200558 |  | Ground Water | GeoSmart Energy | GT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207200565 |  | Ground Water | GeoSmart Energy | GS060**1*(1,4)*H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207200566 |  | Ground Water | GeoSmart Energy | GS060**1*0*H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
207200576 |  | Ground Water | GeoSmart Energy | GTZ026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207200577 |  | Ground Water | GeoSmart Energy | GTZ026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207200578 |  | Ground Water | GeoSmart Energy | GTS026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207200579 |  | Ground Water | GeoSmart Energy | GTS026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207200580 |  | Ground Water | GeoSmart Energy | GTS049*1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207200581 |  | Ground Water | GeoSmart Energy | GTS049*1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207200582 |  | Ground Water | GeoSmart Energy | GTS064*1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207200583 |  | Ground Water | GeoSmart Energy | GTS064*1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207200584 |  | Ground Water | GeoSmart Energy | GTS072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200585 |  | Ground Water | GeoSmart Energy | GTZ072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200586 |  | Ground Water | GeoSmart Energy | GSZ022*1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
207200587 |  | Ground Water | GeoSmart Energy | GSZ022*1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207200588 |  | Ground Water | GeoSmart Energy | GSZ030*1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207200589 |  | Ground Water | GeoSmart Energy | GSZ030*1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207200590 |  | Ground Water | GeoSmart Energy | GSZ048*1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
207200591 |  | Ground Water | GeoSmart Energy | GSZ048*1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207200592 |  | Ground Water | GeoSmart Energy | GSZ060*1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
207200593 |  | Ground Water | GeoSmart Energy | GSZ060*1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207200594 |  | Ground Water | GeoSmart Energy | GSZ070*1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207200595 |  | Ground Water | GeoSmart Energy | GTZ072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207200596 |  | Ground Water | GeoSmart Energy | GSZ070*1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
207200597 |  | Ground Water | GeoSmart Energy | GTS072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200598 |  | Ground Water | GeoSmart Energy | GSZ036*1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207200599 |  | Ground Water | GeoSmart Energy | GSZ042*1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207200600 |  | Ground Water | GeoSmart Energy | GTZ038*1*J | SAH038* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207200601 |  | Ground Water | GeoSmart Energy | GTZ049*1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
217967019 |  | Ground Water | TRANE | VSVK024A |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967020 |  | Ground Water | TRANE | VSHK033A |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967021 |  | Ground Water | TRANE | VSVK033A |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967022 |  | Ground Water | TRANE | VSHK042A |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967023 |  | Ground Water | TRANE | VSVK042A |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
217967024 |  | Ground Water | TRANE | VSHK050A |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967025 |  | Ground Water | TRANE | VSVK050A |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967026 |  | Ground Water | TRANE | VSHK060A |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967027 |  | Ground Water | TRANE | VSVK060A |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
217967028 |  | Ground Water | TRANE | VSHK024B |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
217967029 |  | Ground Water | TRANE | VSVK024B |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967030 |  | Ground Water | TRANE | VSHK033B |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967031 |  | Ground Water | TRANE | VSVK033B |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967032 |  | Ground Water | TRANE | VSHK042B |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967033 |  | Ground Water | TRANE | VSVK042B |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
217967034 |  | Ground Water | TRANE | VSHK050B |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967035 |  | Ground Water | TRANE | VSVK050B |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967036 |  | Ground Water | TRANE | VSHK060B |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967037 |  | Ground Water | TRANE | VSVK060B |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
217967038 |  | Ground Water | TRANE | VSHK0244 |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
217967039 |  | Ground Water | TRANE | VSVK0244 |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967040 |  | Ground Water | TRANE | VSHK0334 |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967041 |  | Ground Water | TRANE | VSVK0334 |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967042 |  | Ground Water | TRANE | VSHK0424 |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967043 |  | Ground Water | TRANE | VSVK0424 |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
9100383 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100384 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100390 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100391 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100393 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100394 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100396 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100397 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100400 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100401 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100403 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100404 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100417 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100431 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9105364 |  | Ground Water | GEOCOMFORT | GVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
9105366 |  | Ground Water | HYDRON MODULE | HVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
9105367 |  | Ground Water | TETCO | TVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
9105368 |  | Ground Water | GEOCOMFORT | GVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105369 |  | Ground Water | HYDRON MODULE | HVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105370 |  | Ground Water | TETCO | TVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105371 |  | Ground Water | GEOCOMFORT | GVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105372 |  | Ground Water | HYDRON MODULE | HVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105373 |  | Ground Water | TETCO | TVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9111997 |  | Ground Water | BOSCH | SM024-1VT/CF*-*****B |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | No
9111998 |  | Ground Water | BOSCH | SM036-1VT/CF*-*****B |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | No
9113111 |  | Ground Water | BOSCH | SM048-1VT/CF*-*****B* |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | No
9113180 |  | Ground Water | BOSCH | SM060-1VT/CF*-*****B |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | No
9113181 |  | Ground Water | BOSCH | SM070-1VT/CF*-*****B |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | No
9113182 |  | Ground Water | BOSCH | SM024-1VT/CF*-*****B |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | Yes
9113183 |  | Ground Water | BOSCH | SM036-1VT/CF*-*****B |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | Yes
9113184 |  | Ground Water | BOSCH | SM048-1VT/CF*-*****B* |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | Yes
9113185 |  | Ground Water | BOSCH | SM060-1VT/CF*-*****B |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | Yes
9113186 |  | Ground Water | BOSCH | SM070-1VT/CF*-*****B |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
212505511 |  | Ground Water | HYDROTECH | WSH6048AM* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212505513 |  | Ground Water | AE Air | WSH6036AM* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212505514 |  | Ground Water | AE Air | WSH6042AM* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212505515 |  | Ground Water | AE Air | WSH6048AM* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508382 |  | Ground Water | HYDROTECH | WSH6036AN* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212508384 |  | Ground Water | HYDROTECH | WSH6042AN* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212508386 |  | Ground Water | HYDROTECH | WSH6048AN* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508387 |  | Ground Water | HYDROTECH | WSH6060AM* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
212508388 |  | Ground Water | HYDROTECH | WSH6060AN* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
212508389 |  | Ground Water | HYDROTECH | WSH6072AM* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508390 |  | Ground Water | HYDROTECH | WSH6072AN* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508399 |  | Ground Water | AE Air | WSH6036AN* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212508401 |  | Ground Water | AE Air | WSH6042AN* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212508403 |  | Ground Water | AE Air | WSH6048AN* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508404 |  | Ground Water | AE Air | WSH6072AM* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508405 |  | Ground Water | AE Air | WSH6072AN* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212509300 |  | Ground Water | AE Air | WSH6060AM* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
212509301 |  | Ground Water | AE Air | WSH6060AN* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
215811946 |  | Ground Water | HYDROTECH | WSV6009D* |  | 11000 | 26 | 8800 | 4.3 | 0.91667 | No
215811947 |  | Ground Water | AE Air | WSV6009D* |  | 11000 | 26 | 8800 | 4.3 | 0.91667 | No
215811948 |  | Ground Water | HYDROTECH | WSV6012D* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | No
215811950 |  | Ground Water | AE Air | WSV6012D* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | No
215811951 |  | Ground Water | HYDROTECH | WSV6018D* |  | 20000 | 21.1 | 16000 | 4.1 | 1.6667 | No
215811952 |  | Ground Water | AE Air | WSV6018D* |  | 20000 | 21.1 | 16000 | 4.1 | 1.6667 | No
215811953 |  | Ground Water | HYDROTECH | WSV6024D* |  | 24000 | 23 | 22000 | 4.1 | 2 | No
215811954 |  | Ground Water | AE Air | WSV6024D* |  | 24000 | 23 | 22000 | 4.1 | 2 | No
215811955 |  | Ground Water | HYDROTECH | WSV6030D* |  | 30000 | 22.5 | 24000 | 4.1 | 2.5 | No
215811957 |  | Ground Water | AE Air | WSV6030D* |  | 30000 | 22.5 | 24000 | 4.1 | 2.5 | No
215811958 |  | Ground Water | HYDROTECH | WSV6036D* |  | 39000 | 22 | 35000 | 4.1 | 3.25 | No
215811959 |  | Ground Water | AE Air | WSV6036D* |  | 39000 | 22 | 35000 | 4.1 | 3.25 | No
215811960 |  | Ground Water | HYDROTECH | WSV6042D* |  | 44000 | 24 | 37000 | 4.3 | 3.6667 | No
215811961 |  | Ground Water | AE Air | WSV6042D* |  | 44000 | 24 | 37000 | 4.3 | 3.6667 | No
215811962 |  | Ground Water | HYDROTECH | WSV6048D* |  | 55000 | 23 | 38000 | 4.1 | 4.5833 | No
215811964 |  | Ground Water | AE Air | WSV6048D* |  | 55000 | 23 | 38000 | 4.1 | 4.5833 | No
215815841 |  | Ground Water | HYDROTECH | WSV6060D* |  | 67000 | 23.8 | 53500 | 4.3 | 5.5833 | No
215815842 |  | Ground Water | AE Air | WSV6060D* |  | 67000 | 23.8 | 53500 | 4.3 | 5.5833 | No
215815843 |  | Ground Water | HYDROTECH | WSV6072D* |  | 77000 | 22.1 | 63500 | 4.1 | 6.4167 | No
215815844 |  | Ground Water | AE Air | WSV6072D* |  | 77000 | 22.1 | 63500 | 4.1 | 6.4167 | No
207337502 |  | Ground Water | GEOSTAR | 103H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337503 |  | Ground Water | GEOSTAR | 163H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337504 |  | Ground Water | GEOSTAR | 163H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337505 |  | Ground Water | GEOSTAR | 104H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337506 |  | Ground Water | GEOSTAR | 104H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337507 |  | Ground Water | GEOSTAR | 164H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337508 |  | Ground Water | GEOSTAR | 164H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337509 |  | Ground Water | GEOSTAR | 103H022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
207337510 |  | Ground Water | GEOSTAR | 103H022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
207337511 |  | Ground Water | GEOSTAR | 103H030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207337512 |  | Ground Water | GEOSTAR | 103H030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207337513 |  | Ground Water | GEOSTAR | 103J036**1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | No
207337514 |  | Ground Water | GEOSTAR | 103J036**1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | No
207337515 |  | Ground Water | GEOSTAR | 103J042**1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207337516 |  | Ground Water | GEOSTAR | 103J042**1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207337517 |  | Ground Water | GEOSTAR | 103H048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
207337518 |  | Ground Water | GEOSTAR | 103H048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
207337521 |  | Ground Water | GEOSTAR | 103H070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207337522 |  | Ground Water | GEOSTAR | 103H070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207338127 |  | Ground Water | GEOSTAR | 141/142C036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
207338129 |  | Ground Water | GEOSTAR | 141/142C060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | No
207338249 |  | Ground Water | TRANE | GETE0241-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207338250 |  | Ground Water | TRANE | GETE0242-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207338251 |  | Ground Water | TRANE | GETE0247-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207337481 |  | Ground Water | GEOSTAR | 104J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337482 |  | Ground Water | GEOSTAR | 104J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337483 |  | Ground Water | GEOSTAR | 164J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337484 |  | Ground Water | GEOSTAR | 164J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337485 |  | Ground Water | GEOSTAR | 103J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337486 |  | Ground Water | GEOSTAR | 103J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337487 |  | Ground Water | GEOSTAR | 163J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337488 |  | Ground Water | GEOSTAR | 163J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337489 |  | Ground Water | GEOSTAR | 104H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337490 |  | Ground Water | GEOSTAR | 104H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337491 |  | Ground Water | GEOSTAR | 164H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337492 |  | Ground Water | GEOSTAR | 164H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337493 |  | Ground Water | GEOSTAR | 103J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337494 |  | Ground Water | GEOSTAR | 103J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337495 |  | Ground Water | GEOSTAR | 163J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337496 |  | Ground Water | GEOSTAR | 163J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337497 |  | Ground Water | GEOSTAR | 104H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337498 |  | Ground Water | GEOSTAR | 104H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337499 |  | Ground Water | GEOSTAR | 164H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337500 |  | Ground Water | GEOSTAR | 164H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337501 |  | Ground Water | GEOSTAR | 103H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
214841657 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
214841658 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
214841660 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
214841662 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
214841664 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
214841665 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
214841666 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
214841668 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
214841675 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
214841676 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
214841677 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
214841678 |  | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
214841679 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
214841680 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
214841682 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
214841684 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
214841686 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
214841687 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
214841688 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
8560916 |  | Ground Water | GEOCOMFORT | GVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560917 |  | Ground Water | HYDRON MODULE | HVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560918 |  | Ground Water | TETCO | TVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560919 |  | Ground Water | GEOCOMFORT | GVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560920 |  | Ground Water | HYDRON MODULE | HVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560921 |  | Ground Water | TETCO | TVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560930 |  | Ground Water | GEOCOMFORT | GVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560931 |  | Ground Water | HYDRON MODULE | HVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560932 |  | Ground Water | TETCO | TVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560938 |  | Ground Water | GEOCOMFORT | GVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560939 |  | Ground Water | HYDRON MODULE | HVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560940 |  | Ground Water | TETCO | TVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560941 |  | Ground Water | GEOCOMFORT | GVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560942 |  | Ground Water | HYDRON MODULE | HVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560943 |  | Ground Water | TETCO | TVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560946 |  | Ground Water | GEOCOMFORT | GVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
8560947 |  | Ground Water | HYDRON MODULE | HVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
8560948 |  | Ground Water | TETCO | TVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
8560949 |  | Ground Water | GEOCOMFORT | GVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
8560950 |  | Ground Water | HYDRON MODULE | HVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
8560951 |  | Ground Water | TETCO | TVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
8077727 |  | Ground Water | HYDRON MODULE | HYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077728 |  | Ground Water | TETCO | TYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077729 |  | Ground Water | GEOCOMFORT | GYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077730 |  | Ground Water | HYDRON MODULE | HYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077731 |  | Ground Water | TETCO | TYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077735 |  | Ground Water | GEOCOMFORT | GYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077736 |  | Ground Water | HYDRON MODULE | HYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077737 |  | Ground Water | TETCO | TYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077738 |  | Ground Water | GEOCOMFORT | GYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077739 |  | Ground Water | HYDRON MODULE | HYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077740 |  | Ground Water | TETCO | TYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077741 |  | Ground Water | GEOCOMFORT | GYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077742 |  | Ground Water | HYDRON MODULE | HYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077743 |  | Ground Water | TETCO | TYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8332268 |  | Ground Water | GEOCOMFORT | GYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332358 |  | Ground Water | HYDRON MODULE | HYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332380 |  | Ground Water | TETCO | TYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332431 |  | Ground Water | GEOCOMFORT | GYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332452 |  | Ground Water | HYDRON MODULE | HYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332472 |  | Ground Water | TETCO | TYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332525 |  | Ground Water | GEOCOMFORT | GYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332545 |  | Ground Water | HYDRON MODULE | HYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332563 |  | Ground Water | TETCO | TYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8560797 |  | Ground Water | 5 SERIES | NSV/NSH060H1*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8560805 |  | Ground Water | 5 SERIES | NSV/NSH060H1*(1,4) |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8560913 |  | Ground Water | GEOCOMFORT | GVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
8560914 |  | Ground Water | HYDRON MODULE | HVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
8560915 |  | Ground Water | TETCO | TVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
203113888 |  | Ground Water | GEOSTAR | 103J036**1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
203113890 |  | Ground Water | GEOSTAR | 103J042**1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
203113892 |  | Ground Water | GEOSTAR | 103J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
203113894 |  | Ground Water | GEOSTAR | 104J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
203143108 |  | Ground Water | GEOCOMFORT | GVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143111 |  | Ground Water | GEOCOMFORT | GVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143114 |  | Ground Water | GEOCOMFORT | GVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143119 |  | Ground Water | GEOCOMFORT | GVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143124 |  | Ground Water | HYDRON MODULE | HVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143129 |  | Ground Water | HYDRON MODULE | HVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143133 |  | Ground Water | HYDRON MODULE | HVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143138 |  | Ground Water | HYDRON MODULE | HVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143143 |  | Ground Water | TETCO | TVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143148 |  | Ground Water | TETCO | TVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143153 |  | Ground Water | TETCO | TVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143157 |  | Ground Water | TETCO | TVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143746 |  | Ground Water | GEOCOMFORT | GVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
203143749 |  | Ground Water | GEOCOMFORT | GVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143752 |  | Ground Water | GEOCOMFORT | GVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143764 |  | Ground Water | HYDRON MODULE | HVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
203143767 |  | Ground Water | HYDRON MODULE | HVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143770 |  | Ground Water | HYDRON MODULE | HVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143781 |  | Ground Water | TETCO | TVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
218158022 |  | Ground Water | YORK | Y5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
218158023 |  | Ground Water | YORK | Y5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
218158024 |  | Ground Water | YORK | Y5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
218158025 |  | Ground Water | YORK | Y5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
218158026 |  | Ground Water | YORK | Y5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
218158027 |  | Ground Water | YORK | Y5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
218158028 |  | Ground Water | YORK | Y5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
218158029 |  | Ground Water | YORK | Y5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
218158030 |  | Ground Water | YORK | Y5SS024BD1 | Y5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
218158031 |  | Ground Water | YORK | Y5SS036BD1 | Y5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
218158032 |  | Ground Water | YORK | Y5SS048BD1 | Y5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
218158033 |  | Ground Water | YORK | Y5SS060BD1 | Y5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
218158034 |  | Ground Water | YORK | Y5SS066BD1 | Y5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
218158035 |  | Ground Water | YORK | Y5SZ024BD1 | Y5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
218158036 |  | Ground Water | YORK | Y5SZ036BD1 | Y5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
218158037 |  | Ground Water | YORK | Y5SZ048BD1 | Y5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
218158038 |  | Ground Water | YORK | Y5SZ060BD1 | Y5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
218158039 |  | Ground Water | YORK | Y5SZ066BD1 | Y5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
218158040 |  | Ground Water | YORK | Y5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
218158041 |  | Ground Water | YORK | Y5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
218158042 |  | Ground Water | YORK | Y5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
218158043 |  | Ground Water | YORK | Y5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
218158044 |  | Ground Water | YORK | Y5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
218158045 |  | Ground Water | YORK | Y5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
218158046 |  | Ground Water | YORK | Y5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
218158047 |  | Ground Water | YORK | Y5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
218158048 |  | Ground Water | YORK | Y5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
218158049 |  | Ground Water | YORK | Y5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
10581121 |  | Ground Water | GEOSTAR | 107H064**1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
200083572 |  | Ground Water | COMFORT-AIRE | HBH/V015 |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
200083573 |  | Ground Water | CENTURY | HBH/V015 |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
200083574 |  | Ground Water | COMFORT-AIRE | HBH/V018 |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
200083575 |  | Ground Water | CENTURY | HBH/V018 |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
3628414 |  | Ground Water | WaterFurnace | USV/USH018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3628415 |  | Ground Water | WaterFurnace | USV/USH018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3628416 |  | Ground Water | WaterFurnace | USV/USH015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3628417 |  | Ground Water | WaterFurnace | USV/USH015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3655222 |  | Ground Water | GEOSTAR | GCC/GCW/GCS/GCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3655223 |  | Ground Water | GEOSTAR | GCC/GCW/GCS/GCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3696260 |  | Ground Water | GEOSTAR | ZS015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
3696261 |  | Ground Water | GEOSTAR | ZS015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
217212097 |  | Ground Water | FHP | CP070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212098 |  | Ground Water | FHP | CP070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212099 |  | Ground Water | FHP | CP070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212101 |  | Ground Water | FHP | CP070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212102 |  | Ground Water | BOSCH | RP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
217212103 |  | Ground Water | BOSCH | RP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
217212105 |  | Ground Water | BOSCH | RP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
217212106 |  | Ground Water | BOSCH | RP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
217212107 |  | Ground Water | BOSCH | RP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
217212108 |  | Ground Water | BOSCH | RP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
217212109 |  | Ground Water | BOSCH | RP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
217212111 |  | Ground Water | BOSCH | RP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
217212112 |  | Ground Water | BOSCH | RP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
217212113 |  | Ground Water | BOSCH | RP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
217212114 |  | Ground Water | BOSCH | RP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217212115 |  | Ground Water | BOSCH | RP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217212116 |  | Ground Water | BOSCH | RP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217212117 |  | Ground Water | BOSCH | RP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217351071 |  | Ground Water | BOSCH | CP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
217351072 |  | Ground Water | BOSCH | CP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
218472180 |  | Ground Water | YORK | AQ070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218472181 |  | Ground Water | YORK | AQ070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218472182 |  | Ground Water | YORK | AQ070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218472183 |  | Ground Water | YORK | AQ070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218472190 |  | Ground Water | YORK | AH025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218472192 |  | Ground Water | YORK | AH025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218472198 |  | Ground Water | YORK | AZ024-1CSC-*****A | CDM24B5XXS1A | 27400 | 23.2 | 23800 | 5 | 2.2833 | No
218472199 |  | Ground Water | YORK | AZ024-1CSN-*****A | CDM24B5XXS1A | 27600 | 24.3 | 23800 | 5.1 | 2.3 | No
218472200 |  | Ground Water | YORK | AZ036-1CSC-*****A | CDM30B5XXS1A | 39600 | 21.5 | 37800 | 4.8 | 3.3 | No
218472201 |  | Ground Water | YORK | AZ036-1CSN-*****A | CDM30B5XXS1A | 40200 | 22.2 | 38800 | 5 | 3.35 | No
218472202 |  | Ground Water | YORK | AZ048-1CSC-*****A | CDM48C5XXS1A | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | No
218472203 |  | Ground Water | YORK | AZ048-1CSN-*****A | CDM48C5XXS1A | 53400 | 22.5 | 46600 | 4.7 | 4.45 | No
218472205 |  | Ground Water | YORK | AZ060-1CSN-*****A | CDM60C5XXS1A | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | No
214837742 |  | Ground Water | CARRIER | 50H/VQP072***3C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837743 |  | Ground Water | CARRIER | 50H/VQP072***5C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837744 |  | Ground Water | CARRIER | 50H/VQP072***6C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837745 |  | Ground Water | CARRIER | 50H/VQP096***3C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837746 |  | Ground Water | CARRIER | 50H/VQP096***5C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837747 |  | Ground Water | CARRIER | 50H/VQP096***6C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
216625508 |  | Ground Water | GEOSTAR | G5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625509 |  | Ground Water | GEOSTAR | G5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625510 |  | Ground Water | GEOSTAR | G5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625511 |  | Ground Water | GEOSTAR | G5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625512 |  | Ground Water | GEOSTAR | G5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625513 |  | Ground Water | GEOSTAR | G5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625514 |  | Ground Water | GEOSTAR | G5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625515 |  | Ground Water | GEOSTAR | G5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625516 |  | Ground Water | GEOSTAR | G5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625517 |  | Ground Water | GEOSTAR | G5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625518 |  | Ground Water | GEOSTAR | G5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625519 |  | Ground Water | GEOSTAR | G5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625520 |  | Ground Water | GEOSTAR | G5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625521 |  | Ground Water | GEOSTAR | G5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625522 |  | Ground Water | GEOSTAR | G5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625523 |  | Ground Water | GEOSTAR | G5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625524 |  | Ground Water | GEOSTAR | G5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625525 |  | Ground Water | GEOSTAR | G5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625526 |  | Ground Water | GEOSTAR | G5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625527 |  | Ground Water | GEOSTAR | G5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625528 |  | Ground Water | GEOSTAR | G5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625529 |  | Ground Water | GEOSTAR | G5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625530 |  | Ground Water | GEOSTAR | G5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625531 |  | Ground Water | GEOSTAR | G5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625532 |  | Ground Water | GEOSTAR | G5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625533 |  | Ground Water | GEOSTAR | G5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625534 |  | Ground Water | GEOSTAR | G5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625535 |  | Ground Water | GEOSTAR | G5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625542 |  | Ground Water | GEOSTAR | G5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625543 |  | Ground Water | GEOSTAR | G5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625748 |  | Ground Water | GeoSmart Energy | S5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625749 |  | Ground Water | GeoSmart Energy | S5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625750 |  | Ground Water | GeoSmart Energy | S5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625751 |  | Ground Water | GeoSmart Energy | S5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625752 |  | Ground Water | GeoSmart Energy | S5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625753 |  | Ground Water | GeoSmart Energy | S5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625754 |  | Ground Water | GeoSmart Energy | S5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625755 |  | Ground Water | GeoSmart Energy | S5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625756 |  | Ground Water | GeoSmart Energy | S5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625757 |  | Ground Water | GeoSmart Energy | S5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625758 |  | Ground Water | GeoSmart Energy | S5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625759 |  | Ground Water | GeoSmart Energy | S5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625760 |  | Ground Water | GeoSmart Energy | S5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625761 |  | Ground Water | GeoSmart Energy | S5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625762 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625763 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625764 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625765 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625766 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625767 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625768 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625769 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625770 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625771 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625772 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625773 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218353322 |  | Ground Water | SKYMARK | PQ070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353323 |  | Ground Water | SKYMARK | PQ070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353324 |  | Ground Water | SKYMARK | PQ070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353325 |  | Ground Water | SKYMARK | PQ070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353349 |  | Ground Water | JOHNSON CONTROLS | DD007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218353350 |  | Ground Water | JOHNSON CONTROLS | DD007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218353351 |  | Ground Water | JOHNSON CONTROLS | DD007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218353352 |  | Ground Water | JOHNSON CONTROLS | DD007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218353353 |  | Ground Water | JOHNSON CONTROLS | DD009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218353354 |  | Ground Water | JOHNSON CONTROLS | DD009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
202667081 |  | Ground Water | BOSCH-GEO | BP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
202679205 |  | Ground Water | BOSCH-GEO | SM036-1CSC-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202679208 |  | Ground Water | BOSCH | SM036-1CSC-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202729320 |  | Ground Water | HEIL | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202729321 |  | Ground Water | ARCOAIRE | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729322 |  | Ground Water | KEEPRITE | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729323 |  | Ground Water | TEMPSTAR | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729324 |  | Ground Water | COMFORTMAKER | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729325 |  | Ground Water | DAY & NIGHT | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729332 |  | Ground Water | HEIL | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202729333 |  | Ground Water | ARCOAIRE | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729334 |  | Ground Water | KEEPRITE | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729335 |  | Ground Water | TEMPSTAR | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729336 |  | Ground Water | COMFORTMAKER | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729337 |  | Ground Water | DAY & NIGHT | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202732300 |  | Ground Water | BOSCH | BP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732301 |  | Ground Water | CARRIER | GB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
202732302 |  | Ground Water | BRYANT | GB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732303 |  | Ground Water | ARCOAIRE | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
202732304 |  | Ground Water | HEIL | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732305 |  | Ground Water | KEEPRITE | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732306 |  | Ground Water | TEMPSTAR | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732307 |  | Ground Water | COMFORTMAKER | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732308 |  | Ground Water | DAY & NIGHT | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732913 |  | Ground Water | BOSCH-GEO | SM036-1CSN-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202732914 |  | Ground Water | BOSCH-GEO | BP018-1HZ*******C |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732915 |  | Ground Water | BOSCH | SM036-1CSN-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202732916 |  | Ground Water | BOSCH | BP018-1HZ*******C |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732917 |  | Ground Water | CARRIER | GB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732918 |  | Ground Water | BRYANT | GB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732919 |  | Ground Water | HEIL | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732920 |  | Ground Water | ARCOAIRE | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732921 |  | Ground Water | KEEPRITE | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732922 |  | Ground Water | TEMPSTAR | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732923 |  | Ground Water | COMFORTMAKER | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732924 |  | Ground Water | DAY & NIGHT | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732934 |  | Ground Water | TRANE | GWSC036H3 |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
202732935 |  | Ground Water | TRANE | GWSC036H4 |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
202732936 |  | Ground Water | TRANE | GWSC036HW |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
202732937 |  | Ground Water | TRANE | GWSC048H3 |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
202732938 |  | Ground Water | TRANE | GWSC048H4 |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
202732939 |  | Ground Water | TRANE | GWSC048HW |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
5646768 |  | Ground Water | GEOCOMFORT | GCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646769 |  | Ground Water | HYDRON MODULE | HCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646770 |  | Ground Water | TETCO | TCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646771 |  | Ground Water | GEOCOMFORT | GCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646772 |  | Ground Water | HYDRON MODULE | HCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646773 |  | Ground Water | TETCO | TCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5699505 |  | Ground Water | TRANE | VSVE0421 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699525 |  | Ground Water | TRANE | VSVE0422 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699526 |  | Ground Water | TRANE | VSVE0424 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699527 |  | Ground Water | TRANE | VSVE0601 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699534 |  | Ground Water | TRANE | VSVE0602 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699535 |  | Ground Water | TRANE | VSVE0604 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699628 |  | Ground Water | TRANE | VSHE0241 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699631 |  | Ground Water | TRANE | VSHE0242 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699633 |  | Ground Water | TRANE | VSHE0244 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699634 |  | Ground Water | TRANE | VSHE0331 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699635 |  | Ground Water | TRANE | VSHE0332 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699637 |  | Ground Water | TRANE | VSHE0334 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699639 |  | Ground Water | TRANE | VSHE0421 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699644 |  | Ground Water | TRANE | VSHE0422 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699650 |  | Ground Water | TRANE | VSHE0424 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699652 |  | Ground Water | TRANE | VSHE0501 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699653 |  | Ground Water | TRANE | VSHE0502 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699654 |  | Ground Water | TRANE | VSHE0504 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699655 |  | Ground Water | TRANE | VSHE0601 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
5699656 |  | Ground Water | TRANE | VSHE0602 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
5699657 |  | Ground Water | TRANE | VSHE0604 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
6501883 |  | Ground Water | GEOSTAR | GBV/GBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
6501884 |  | Ground Water | GEOSTAR | GBV/GBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
6501885 |  | Ground Water | GEOSTAR | GBV/GBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
6501886 |  | Ground Water | GEOSTAR | GBV/GBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
205767541 |  | Ground Water | ClimateMaster | TCH/V018A*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205767542 |  | Ground Water | ClimateMaster | TCH/V024A*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205767543 |  | Ground Water | ClimateMaster | TCH/V030A*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
214595715 |  | Ground Water | AAON, Inc. | M2-014-2-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214595716 |  | Ground Water | AAON, Inc. | M2-014-3-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214595717 |  | Ground Water | AAON, Inc. | M2-014-4-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214771921 |  | Ground Water | TRANE | GEVK009A |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214771922 |  | Ground Water | TRANE | GEVK012A |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214771923 |  | Ground Water | TRANE | GEVK015A |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214771924 |  | Ground Water | TRANE | GEVK018A |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214771925 |  | Ground Water | TRANE | GEVK024A |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214771926 |  | Ground Water | TRANE | GEVK030A |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214771927 |  | Ground Water | TRANE | GEVK036A |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214771928 |  | Ground Water | TRANE | GEVK042A |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214771929 |  | Ground Water | TRANE | GEVK048A |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214771930 |  | Ground Water | TRANE | GEVK060A |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214771931 |  | Ground Water | TRANE | EXVK009A |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214771932 |  | Ground Water | TRANE | EXVK012A |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214771933 |  | Ground Water | TRANE | EXVK015A |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214771934 |  | Ground Water | TRANE | EXVK018A |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214771935 |  | Ground Water | TRANE | EXVK024A |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214771936 |  | Ground Water | TRANE | EXVK030A |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214771937 |  | Ground Water | TRANE | EXVK036A |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214771938 |  | Ground Water | TRANE | EXVK042A |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214771939 |  | Ground Water | TRANE | EXVK048A |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
216054482 |  | Ground Water | GEOCOMFORT | GVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
216054483 |  | Ground Water | GEOCOMFORT | GVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216054484 |  | Ground Water | GEOCOMFORT | GVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216054485 |  | Ground Water | GEOCOMFORT | GVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216054486 |  | Ground Water | GEOCOMFORT | GVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216054487 |  | Ground Water | GEOCOMFORT | GYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216054488 |  | Ground Water | GEOCOMFORT | GYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216419863 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
216419865 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
216419867 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
216419868 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
216419871 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
205652455 |  | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | Yes
205652457 |  | Ground Water | BOSCH-GEO | LM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | No
205652458 |  | Ground Water | BOSCH-GEO | LM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | No
205652459 |  | Ground Water | BOSCH-GEO | LM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | No
205652461 |  | Ground Water | BOSCH | SM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | Yes
205652462 |  | Ground Water | BOSCH | SM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | Yes
205652463 |  | Ground Water | BOSCH | SM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | Yes
205652465 |  | Ground Water | FHP | LM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | No
205652466 |  | Ground Water | FHP | LM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | No
205652467 |  | Ground Water | FHP | LM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | No
205752888 |  | Ground Water | ClimateMaster | TCH/V006A*W/K |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
205754885 |  | Ground Water | Johnson Controls | JCH/V015A*W/K B |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205754886 |  | Ground Water | SKYMARK | JCH/V015A*W/K C |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205754887 |  | Ground Water | Johnson Controls | JCH/V018A B |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205754888 |  | Ground Water | SKYMARK | JCH/V018A C |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205754889 |  | Ground Water | Johnson Controls | JCH/V018A*W/K B |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205754890 |  | Ground Water | SKYMARK | JCH/V018A*W/K C |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
214595581 |  | Ground Water | AAON, Inc. | SB-004-2-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
214595583 |  | Ground Water | AAON, Inc. | SB-004-3-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
214595585 |  | Ground Water | AAON, Inc. | SB-004-4-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
4651870 |  | Ground Water | GeoSmart Energy | ZS023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651873 |  | Ground Water | GEOSTAR | ZS023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651874 |  | Ground Water | GeoSmart Energy | ZS023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651882 |  | Ground Water | GEOSTAR | ZS042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651883 |  | Ground Water | GeoSmart Energy | ZS042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651888 |  | Ground Water | GEOSTAR | ZS042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651889 |  | Ground Water | GeoSmart Energy | ZS042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651894 |  | Ground Water | GEOSTAR | ZS042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651895 |  | Ground Water | GeoSmart Energy | ZS042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651936 |  | Ground Water | GEOSTAR | ZS048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651937 |  | Ground Water | GeoSmart Energy | ZS048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651942 |  | Ground Water | GeoSmart Energy | ZS048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651943 |  | Ground Water | GEOSTAR | ZS048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651948 |  | Ground Water | GEOSTAR | ZS048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651949 |  | Ground Water | GeoSmart Energy | ZS048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651954 |  | Ground Water | GEOSTAR | ZS060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651955 |  | Ground Water | GeoSmart Energy | ZS060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651966 |  | Ground Water | GEOSTAR | ZS060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651967 |  | Ground Water | GeoSmart Energy | ZS060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651972 |  | Ground Water | GEOSTAR | ZS070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651973 |  | Ground Water | GeoSmart Energy | ZS070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651978 |  | Ground Water | GEOSTAR | ZS070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651979 |  | Ground Water | GeoSmart Energy | ZS070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651984 |  | Ground Water | GEOSTAR | ZS070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651985 |  | Ground Water | GeoSmart Energy | ZS070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4659826 |  | Ground Water | TRANE | GEVE0721 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659827 |  | Ground Water | TRANE | GEVE0722 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659829 |  | Ground Water | TRANE | GEVE0724 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659831 |  | Ground Water | TRANE | GEVE0904 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
4659834 |  | Ground Water | TRANE | GEHE0721 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659835 |  | Ground Water | TRANE | GEHE0722 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659836 |  | Ground Water | TRANE | GEHE0728 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659837 |  | Ground Water | TRANE | GEHE0724 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
215268758 |  | Ground Water | WaterFurnace | V5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268759 |  | Ground Water | WaterFurnace | V5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268760 |  | Ground Water | WaterFurnace | V5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268761 |  | Ground Water | WaterFurnace | V5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268762 |  | Ground Water | WaterFurnace | V5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218396714 |  | Ground Water | SKYMARK | PH025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218396715 |  | Ground Water | SKYMARK | PH025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218396728 |  | Ground Water | JOHNSON CONTROLS | DH025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218396729 |  | Ground Water | JOHNSON CONTROLS | DH025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
963498 |  | Ground Water | WaterFurnace | NLH/NXH080**3 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
963499 |  | Ground Water | WaterFurnace | NLH/NXH080**4 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
963500 |  | Ground Water | WaterFurnace | NLH/NXH080**5 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
202330556 |  | Ground Water | AAON, Inc. | M2-005-3-H-DCBC-S0-10-000-A |  | 65000 | 21.74 | 50400 | 4.1 | 5.4167 | No
202330559 |  | Ground Water | AAON, Inc. | M2-005-4-H-DCAC-S0-10-000-A |  | 62100 | 21.93 | 50000 | 4.1 | 5.175 | No
202330560 |  | Ground Water | AAON, Inc. | M2-005-4-H-DCBC-S0-10-000-A |  | 65000 | 21.74 | 50400 | 4.1 | 5.4167 | No
202330562 |  | Ground Water | AAON, Inc. | M2-006-2-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
202330564 |  | Ground Water | AAON, Inc. | M2-006-2-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
202330566 |  | Ground Water | AAON, Inc. | M2-006-3-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
202330568 |  | Ground Water | AAON, Inc. | M2-006-3-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
202330570 |  | Ground Water | AAON, Inc. | M2-006-4-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
202330572 |  | Ground Water | AAON, Inc. | M2-006-4-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
202350417 |  | Ground Water | AAON, Inc. | RN-009-2-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350418 |  | Ground Water | AAON, Inc. | RN-009-3-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350419 |  | Ground Water | AAON, Inc. | RN-009-4-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350429 |  | Ground Water | AAON, Inc. | RN-011-2-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
202350430 |  | Ground Water | AAON, Inc. | RN-011-3-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
202350431 |  | Ground Water | AAON, Inc. | RN-011-4-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
202350445 |  | Ground Water | AAON, Inc. | M2-007-2-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350447 |  | Ground Water | AAON, Inc. | M2-007-2-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
202350449 |  | Ground Water | AAON, Inc. | M2-007-3-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350451 |  | Ground Water | AAON, Inc. | M2-007-3-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
215224034 |  | Ground Water | BOSCH | CF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224035 |  | Ground Water | BOSCH | CF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224036 |  | Ground Water | BOSCH | CF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224037 |  | Ground Water | BOSCH | CF007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224038 |  | Ground Water | BOSCH | CF007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224039 |  | Ground Water | BOSCH | CF009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224040 |  | Ground Water | BOSCH | CF009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224041 |  | Ground Water | BOSCH | CF012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224042 |  | Ground Water | BOSCH | CF012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224043 |  | Ground Water | BOSCH | CF015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224044 |  | Ground Water | BOSCH | CF015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224045 |  | Ground Water | BOSCH | CF018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224046 |  | Ground Water | BOSCH | CF018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
216772588 |  | Ground Water | Enertech | EBT060* | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
216772590 |  | Ground Water | Enertech | EVT060* |  | 64200 | 22 | 58550 | 4.49 | 5.35 | Yes
216772591 |  | Ground Water | Enertech | EYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216772592 |  | Ground Water | Enertech | EZS015* |  | 16000 | 26.3 | 14300 | 4.8 | 1.3333 | Yes
216772593 |  | Ground Water | Enertech | EZS017* |  | 18475 | 22.2 | 15950 | 4.38 | 1.5396 | Yes
216772594 |  | Ground Water | Enertech | EZS018* |  | 21500 | 30.1 | 17500 | 4.7 | 1.7917 | Yes
216772596 |  | Ground Water | Enertech | EYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216772598 |  | Ground Water | Enertech | EWS036* |  | 35600 | 22.9 | 38300 | 4.1 | 2.9667 | Yes
216772599 |  | Ground Water | Enertech | EWS048* |  | 52500 | 22.9 | 58700 | 4.2 | 4.375 | Yes
216772602 |  | Ground Water | Enertech | EWT048* |  | 52700 | 21.2 | 61100 | 4.2 | 4.3917 | Yes
216801023 |  | Ground Water | CARRIER | 50PEC09****3/CG |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801024 |  | Ground Water | CARRIER | 50PEC09****4/DG |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801031 |  | Ground Water | FHP | CA009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801032 |  | Ground Water | FHP | CA009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801911 |  | Ground Water | BOSCH | WT025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801912 |  | Ground Water | BOSCH | WT025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
204031812 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
212587993 |  | Ground Water | HYDROTECH | HRCX09*-7 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
212587994 |  | Ground Water | AE Air | HRCX09*-7 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
213087558 |  | Ground Water | WaterFurnace | NDS049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213087559 |  | Ground Water | WaterFurnace | NDS049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213087562 |  | Ground Water | WaterFurnace | NDS064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213087563 |  | Ground Water | WaterFurnace | NDS064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213154439 |  | Ground Water | GeoSmart Energy | GTS026*1******K | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
213154440 |  | Ground Water | GeoSmart Energy | GTS026*1******K | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
213154441 |  | Ground Water | GeoSmart Energy | GTS049*1******K | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213154442 |  | Ground Water | GeoSmart Energy | GTS049*1******K | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213154443 |  | Ground Water | GeoSmart Energy | GTS072*1******K | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
213154444 |  | Ground Water | GeoSmart Energy | GTS072*1******K | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
213154445 |  | Ground Water | GeoSmart Energy | GTS064*1******K | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213154446 |  | Ground Water | GeoSmart Energy | GTS064*1******K | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213154447 |  | Ground Water | GeoSmart Energy | GTS038*1******K | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
213154448 |  | Ground Water | GeoSmart Energy | GTS038*1******K | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154451 |  | Ground Water | GeoSmart Energy | YT048**1*4********C |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
213154454 |  | Ground Water | GeoSmart Energy | GTZ026*1******K | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
213154455 |  | Ground Water | GeoSmart Energy | GTZ026*1******K | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
213154456 |  | Ground Water | GeoSmart Energy | GTZ038*1******K | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154457 |  | Ground Water | GeoSmart Energy | GTZ038*1******K | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154458 |  | Ground Water | GeoSmart Energy | GTZ049*1******K | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
213154459 |  | Ground Water | GeoSmart Energy | GTZ049*1******K | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
213154460 |  | Ground Water | GeoSmart Energy | GTZ064*1******K | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
213154461 |  | Ground Water | GeoSmart Energy | GTZ064*1******K | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
213154462 |  | Ground Water | GeoSmart Energy | GTZ072*1******K | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
213154463 |  | Ground Water | GeoSmart Energy | GTZ072*1******K | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
213154464 |  | Ground Water | GeoSmart Energy | GS012**1*0********L |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
213154465 |  | Ground Water | GeoSmart Energy | GS018**1*1********L |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
213154466 |  | Ground Water | GeoSmart Energy | GS022**1*1********L |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
213154467 |  | Ground Water | GeoSmart Energy | GS030**1*1********L |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
206229678 |  | Ground Water | FHP | EP024-1HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229679 |  | Ground Water | FHP | EP024-2HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229680 |  | Ground Water | FHP | EP024-3HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229681 |  | Ground Water | FHP | EP024-4HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229682 |  | Ground Water | CARRIER | 50PSH/V024**C3/CA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229683 |  | Ground Water | CARRIER | 50PSH/V024**C4/DA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229684 |  | Ground Water | CARRIER | 50PSH/V024**C5/EA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229685 |  | Ground Water | CARRIER | 50PSH/V024**C6/FA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229686 |  | Ground Water | CARRIER | 50PSH/V024**N3/CA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229687 |  | Ground Water | CARRIER | 50PSH/V024**N4/DA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229688 |  | Ground Water | CARRIER | 50PSH/V024**N5/EA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229689 |  | Ground Water | CARRIER | 50PSH/V024**N6/FA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206262126 |  | Ground Water | HYDROTECH | WSV6090A |  | 101000 | 22 | 73000 | 4.1 | 8.4167 | No
206342108 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**3 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206342109 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**4 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206342110 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**5 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206342111 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**3 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342112 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**4 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342113 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**5 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342114 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**3 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342115 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**4 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342116 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**5 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342117 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*3 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342118 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*4 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342119 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*5 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342120 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342121 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342122 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342123 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*3 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206342124 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*5 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206342125 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*4 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206345837 |  | Ground Water | HYDROTECH | WSS6006*7* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
206345838 |  | Ground Water | HYDROTECH | WSS6009*7* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
206345839 |  | Ground Water | HYDROTECH | WSS6012*7* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
206345840 |  | Ground Water | HYDROTECH | WSS6015*7* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
216625838 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625839 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625840 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625841 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625842 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625843 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625844 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625845 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625846 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625847 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625848 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625849 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625850 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625851 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625852 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625853 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625854 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625855 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625856 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625857 |  | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625858 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625859 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625860 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625861 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625862 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625863 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625864 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625865 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625866 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625867 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625868 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625869 |  | Ground Water | GeoSmart Energy | S5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625870 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625871 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625872 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625873 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625874 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625875 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625876 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625877 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625878 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625879 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625880 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625881 |  | Ground Water | GeoSmart Energy | S5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216687113 |  | Ground Water | WaterFurnace | W5SS024BD1 | W5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687114 |  | Ground Water | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687115 |  | Ground Water | WaterFurnace | W5SS048BD1 | W5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687116 |  | Ground Water | WaterFurnace | W5SS060BD1 | W5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
218353471 |  | Ground Water | JOHNSON CONTROLS | DK009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
218353472 |  | Ground Water | JOHNSON CONTROLS | DK009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
203143785 |  | Ground Water | TETCO | TVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143790 |  | Ground Water | TETCO | TVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203238019 |  | Ground Water | BOSCH-GEO | BP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203238020 |  | Ground Water | GEO-THERMAL SPLIT | GZ036***C***1**2 | FE/V****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203238919 |  | Ground Water | BOSCH-GEO | SM024-1VT/CFN-*****A |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203238923 |  | Ground Water | BOSCH-GEO | SM024-1HZC-*****A |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | No
203238926 |  | Ground Water | BOSCH-GEO | SM024-1HZN-*****A |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | No
203253412 |  | Ground Water | BOSCH | BP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203253413 |  | Ground Water | BOSCH | SM024-1HZC-*****A |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203253414 |  | Ground Water | BOSCH | SM024-1HZC-*****C |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203253415 |  | Ground Water | BOSCH | SM024-1HZN-*****A |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203253416 |  | Ground Water | BOSCH | SM024-1HZN-*****C |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203254061 |  | Ground Water | BOSCH-GEO | SM070-1VT*-*****C |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
203254465 |  | Ground Water | BOSCH | SM070-1VT*******C |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
203254574 |  | Ground Water | CARRIER | GZ036***C***1**2 | FE/V****005 | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
203254575 |  | Ground Water | BRYANT | GZ036***C***1**2 | FE/V****005 | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254576 |  | Ground Water | HEIL | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
203254577 |  | Ground Water | ARCOAIRE | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254578 |  | Ground Water | KEEPRITE | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254579 |  | Ground Water | TEMPSTAR | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254580 |  | Ground Water | COMFORTMAKER | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254581 |  | Ground Water | DAY & NIGHT | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254606 |  | Ground Water | CARRIER | GB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203254607 |  | Ground Water | BRYANT | GB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254608 |  | Ground Water | ARCOAIRE | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203254609 |  | Ground Water | HEIL | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254610 |  | Ground Water | KEEPRITE | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254611 |  | Ground Water | TEMPSTAR | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254612 |  | Ground Water | COMFORTMAKER | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254614 |  | Ground Water | DAY & NIGHT | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254620 |  | Ground Water | BRYANT | GC024V/C**N***1*X1 |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203254624 |  | Ground Water | BRYANT | GC024H**C***1*X1 |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203254626 |  | Ground Water | BRYANT | GC024H**N***1*X1 |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203254744 |  | Ground Water | CARRIER | GC024V/C**N***1**1 |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203254748 |  | Ground Water | CARRIER | GC024H**C***1**1 |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203254752 |  | Ground Water | CARRIER | GC024H**N***1**1 |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203260718 |  | Ground Water | BOSCH-GEO | SM024-1VT/CFC******A |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
203260866 |  | Ground Water | CARRIER | GC024V/C**C***1**1 + UI |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
203260867 |  | Ground Water | BRYANT | GC024V/C**C***1*X1 + UI |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
216979817 |  | Ground Water | CARRIER | GCA36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979818 |  | Ground Water | BRYANT | GCA36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979819 |  | Ground Water | CARRIER | GCA36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216979820 |  | Ground Water | BRYANT | GCA36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979821 |  | Ground Water | CARRIER | GCA48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979822 |  | Ground Water | BRYANT | GCA48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979823 |  | Ground Water | CARRIER | GCA48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979824 |  | Ground Water | BRYANT | GCA48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979825 |  | Ground Water | CARRIER | GCA60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979826 |  | Ground Water | BRYANT | GCA60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979827 |  | Ground Water | CARRIER | GCA60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979828 |  | Ground Water | BRYANT | GCA60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979837 |  | Ground Water | HEIL | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979838 |  | Ground Water | ARCOAIRE | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979839 |  | Ground Water | KEEPRITE | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979840 |  | Ground Water | TEMPSTAR | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979841 |  | Ground Water | COMFORTMAKER | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979842 |  | Ground Water | DAY & NIGHT | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979843 |  | Ground Water | HEIL | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979844 |  | Ground Water | ARCOAIRE | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979845 |  | Ground Water | KEEPRITE | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979846 |  | Ground Water | TEMPSTAR | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979847 |  | Ground Water | COMFORTMAKER | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979848 |  | Ground Water | DAY & NIGHT | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979849 |  | Ground Water | HEIL | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979850 |  | Ground Water | ARCOAIRE | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979851 |  | Ground Water | KEEPRITE | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979852 |  | Ground Water | TEMPSTAR | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979853 |  | Ground Water | COMFORTMAKER | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979854 |  | Ground Water | DAY & NIGHT | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979855 |  | Ground Water | HEIL | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979856 |  | Ground Water | ARCOAIRE | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979857 |  | Ground Water | KEEPRITE | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979858 |  | Ground Water | TEMPSTAR | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979859 |  | Ground Water | COMFORTMAKER | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979860 |  | Ground Water | DAY & NIGHT | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979861 |  | Ground Water | HEIL | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979862 |  | Ground Water | ARCOAIRE | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979863 |  | Ground Water | KEEPRITE | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979864 |  | Ground Water | TEMPSTAR | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979865 |  | Ground Water | COMFORTMAKER | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979866 |  | Ground Water | DAY & NIGHT | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
9100368 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100370 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100371 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100373 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100374 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100377 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100378 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100380 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100381 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
205767548 |  | Ground Water | ClimateMaster | TRH/V018A*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205767549 |  | Ground Water | ClimateMaster | TRH/V024A*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205767550 |  | Ground Water | ClimateMaster | TRH/V030A*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205767554 |  | Ground Water | ClimateMaster | TZV/H024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205767556 |  | Ground Water | ClimateMaster | TZV/H036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
205767557 |  | Ground Water | ClimateMaster | TZV/H042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205767559 |  | Ground Water | ClimateMaster | TZV/H060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205767582 |  | Ground Water | ClimateMaster | TES/P038B | TAH038C | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
205767583 |  | Ground Water | ClimateMaster | TES/P049B | TAH049C | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
205767586 |  | Ground Water | ClimateMaster | TES/P026B | TAH026C***A* | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
205767587 |  | Ground Water | ClimateMaster | TES/P026B | TAH026C***B* | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
205767588 |  | Ground Water | ClimateMaster | TES/P026B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
205767589 |  | Ground Water | ClimateMaster | TES/P026B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
205767590 |  | Ground Water | ClimateMaster | TRE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205767591 |  | Ground Water | ClimateMaster | TRE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205767592 |  | Ground Water | ClimateMaster | TRE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205767593 |  | Ground Water | ClimateMaster | TRE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
214771940 |  | Ground Water | TRANE | EXVK060A |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214771941 |  | Ground Water | TRANE | EXVK070A |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214771943 |  | Ground Water | TRANE | GEHK009A |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214771944 |  | Ground Water | TRANE | GEHK012A |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214771945 |  | Ground Water | TRANE | GEHK015A |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214771946 |  | Ground Water | TRANE | GEHK018A |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
7421973 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421974 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421975 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421976 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421977 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421980 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421989 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421999 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7422020 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422043 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422058 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422072 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422083 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422093 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422134 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422147 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422187 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422202 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422225 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422234 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422268 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422280 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422290 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422299 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422309 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422322 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7423168 |  | Ground Water | WaterFurnace | NBV/NBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7423169 |  | Ground Water | GEOSTAR | GBV/GBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7423171 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7487652 |  | Ground Water | GEOCOMFORT | GYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
7487653 |  | Ground Water | HYDRON MODULE | HYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
7487654 |  | Ground Water | TETCO | TYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
7487655 |  | Ground Water | TETCO | TYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487656 |  | Ground Water | GEOCOMFORT | GYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487657 |  | Ground Water | HYDRON MODULE | HYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487658 |  | Ground Water | HYDRON MODULE | HYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487659 |  | Ground Water | GEOCOMFORT | GYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487660 |  | Ground Water | TETCO | TYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487661 |  | Ground Water | GEOCOMFORT | GYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487662 |  | Ground Water | HYDRON MODULE | HYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487663 |  | Ground Water | TETCO | TYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487664 |  | Ground Water | TETCO | TYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487665 |  | Ground Water | HYDRON MODULE | HYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487666 |  | Ground Water | GEOCOMFORT | GYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487667 |  | Ground Water | GEOCOMFORT | GYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487668 |  | Ground Water | HYDRON MODULE | HYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
217351789 |  | Ground Water | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351790 |  | Ground Water | ARCOAIRE | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351792 |  | Ground Water | ARCOAIRE | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351793 |  | Ground Water | ARCOAIRE | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351795 |  | Ground Water | ARCOAIRE | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351796 |  | Ground Water | ARCOAIRE | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351797 |  | Ground Water | ARCOAIRE | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351798 |  | Ground Water | ARCOAIRE | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351799 |  | Ground Water | ARCOAIRE | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351800 |  | Ground Water | ARCOAIRE | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351801 |  | Ground Water | ARCOAIRE | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351803 |  | Ground Water | ARCOAIRE | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351804 |  | Ground Water | ARCOAIRE | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351806 |  | Ground Water | ARCOAIRE | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351808 |  | Ground Water | ARCOAIRE | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351811 |  | Ground Water | COMFORTMAKER | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351812 |  | Ground Water | COMFORTMAKER | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351813 |  | Ground Water | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351814 |  | Ground Water | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351815 |  | Ground Water | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351816 |  | Ground Water | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351817 |  | Ground Water | COMFORTMAKER | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351819 |  | Ground Water | COMFORTMAKER | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351820 |  | Ground Water | COMFORTMAKER | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351822 |  | Ground Water | COMFORTMAKER | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351823 |  | Ground Water | COMFORTMAKER | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351824 |  | Ground Water | COMFORTMAKER | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351825 |  | Ground Water | COMFORTMAKER | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351826 |  | Ground Water | COMFORTMAKER | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351827 |  | Ground Water | COMFORTMAKER | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351828 |  | Ground Water | COMFORTMAKER | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351830 |  | Ground Water | COMFORTMAKER | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351831 |  | Ground Water | COMFORTMAKER | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351833 |  | Ground Water | COMFORTMAKER | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351835 |  | Ground Water | COMFORTMAKER | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351838 |  | Ground Water | DAY & NIGHT | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351839 |  | Ground Water | DAY & NIGHT | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351840 |  | Ground Water | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351841 |  | Ground Water | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351842 |  | Ground Water | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
6501912 |  | Ground Water | GEOSTAR | GBV/GBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501913 |  | Ground Water | GEOSTAR | GBV/GBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501914 |  | Ground Water | GEOSTAR | GBV/GBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501915 |  | Ground Water | GEOSTAR | GBV/GBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501916 |  | Ground Water | GEOSTAR | GBV/GBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501917 |  | Ground Water | GEOSTAR | GBV/GBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501918 |  | Ground Water | GEOSTAR | GBV/GBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501919 |  | Ground Water | GEOSTAR | GBV/GBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501920 |  | Ground Water | GEOSTAR | GBV/GBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501921 |  | Ground Water | GEOSTAR | GBV/GBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501922 |  | Ground Water | GEOSTAR | GBV/GBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501923 |  | Ground Water | GEOSTAR | GBV/GBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501924 |  | Ground Water | GEOSTAR | GBV/GBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501925 |  | Ground Water | GEOSTAR | GBV/GBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501926 |  | Ground Water | GEOSTAR | GBV/GBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501927 |  | Ground Water | GEOSTAR | GBV/GBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501928 |  | Ground Water | GEOSTAR | GBV/GBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501929 |  | Ground Water | GEOSTAR | GBV/GBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501930 |  | Ground Water | GEOSTAR | GBV/GBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
206726827 |  | Ground Water | HYDRON MODULE | HBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726828 |  | Ground Water | TETCO | TBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
206726829 |  | Ground Water | TETCO | TBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726830 |  | Ground Water | GEOCOMFORT | GBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726831 |  | Ground Water | GEOCOMFORT | GBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726832 |  | Ground Water | HYDRON MODULE | HBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726833 |  | Ground Water | HYDRON MODULE | HBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726834 |  | Ground Water | TETCO | TBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726835 |  | Ground Water | TETCO | TBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726836 |  | Ground Water | GEOCOMFORT | GBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726837 |  | Ground Water | GEOCOMFORT | GBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726838 |  | Ground Water | HYDRON MODULE | HBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726839 |  | Ground Water | HYDRON MODULE | HBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726840 |  | Ground Water | TETCO | TBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726841 |  | Ground Water | TETCO | TBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726842 |  | Ground Water | GEOCOMFORT | GBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726843 |  | Ground Water | GEOCOMFORT | GBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726844 |  | Ground Water | HYDRON MODULE | HBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726845 |  | Ground Water | HYDRON MODULE | HBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726846 |  | Ground Water | TETCO | TBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726847 |  | Ground Water | TETCO | TBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726848 |  | Ground Water | GEOCOMFORT | GBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
206726849 |  | Ground Water | HYDRON MODULE | HBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
214841690 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
214841697 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
214841698 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
214841699 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
214841700 |  | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
214841701 |  | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
214841702 |  | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
214841704 |  | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
214841705 |  | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
214841706 |  | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
214841707 |  | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
214841708 |  | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
214841710 |  | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
214841711 |  | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
214841712 |  | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
214844588 |  | Ground Water | WaterFurnace | W7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
214844645 |  | Ground Water | WaterFurnace | W7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
214844646 |  | Ground Water | WaterFurnace | W7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
214844647 |  | Ground Water | WaterFurnace | W7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
215223342 |  | Ground Water | WaterFurnace | V5C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215223348 |  | Ground Water | WaterFurnace | V3C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215223349 |  | Ground Water | WaterFurnace | V3C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215223354 |  | Ground Water | WaterFurnace | V5C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
205788285 |  | Ground Water | Johnson Controls | JSH/V/D036C*K B |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | No
205788286 |  | Ground Water | SKYMARK | JSH/V/D036C*K C |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | No
205788287 |  | Ground Water | Johnson Controls | JSH/V/D042C B |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | No
205788288 |  | Ground Water | SKYMARK | JSH/V/D042C C |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | No
205788289 |  | Ground Water | Johnson Controls | JSH/V/D042C*K B |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205788290 |  | Ground Water | SKYMARK | JSH/V/D042C*K C |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205788293 |  | Ground Water | Johnson Controls | JSH/V/D060C B |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | No
205788294 |  | Ground Water | SKYMARK | JSH/V/D060C C |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | No
205901399 |  | Ground Water | Johnson Controls | JCH/V015A B |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205901400 |  | Ground Water | SKYMARK | JCH/V015A C |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205958295 |  | Ground Water | BOSCH-GEO | SM036-1CS*-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205958297 |  | Ground Water | BOSCH | SM036-1CS*-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205961527 |  | Ground Water | Johnson Controls | JRE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205961528 |  | Ground Water | Johnson Controls | JRE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205961529 |  | Ground Water | Johnson Controls | JRE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205961530 |  | Ground Water | Johnson Controls | JRE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
214772142 |  | Ground Water | TRANE | DXHK036A |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772143 |  | Ground Water | TRANE | DXHK048A |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772144 |  | Ground Water | TRANE | DXHK060A |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772145 |  | Ground Water | TRANE | DXHK070A |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772146 |  | Ground Water | TRANE | DXVK024B |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772147 |  | Ground Water | TRANE | DXVK0244 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772148 |  | Ground Water | TRANE | DXVK036B |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
7421971 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421972 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
203363126 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**0*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363127 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**0*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363129 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**2*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363130 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**2*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363132 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**3*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363133 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**3*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363135 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**4*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363136 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**4*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363137 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363138 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363139 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363140 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363141 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363142 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363143 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363144 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363145 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363146 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363147 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363148 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363150 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**0*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363151 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**0*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363153 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**3*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363154 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**3*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363156 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**4*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363157 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**4*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
209156972 |  | Ground Water | AE Air | WSV6090A |  | 101000 | 22 | 73000 | 4.1 | 8.4167 | No
209156974 |  | Ground Water | AE Air | WSS6006*6* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
209156975 |  | Ground Water | AE Air | WSS6009*6* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
209156976 |  | Ground Water | AE Air | WSS6012*6* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
209156977 |  | Ground Water | AE Air | WSS6015*6* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
209156981 |  | Ground Water | AE Air | WSHXE06A6* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
209156987 |  | Ground Water | AE Air | WSHXE06A7* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
209156993 |  | Ground Water | AE Air | WSS6006*7* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
209156994 |  | Ground Water | AE Air | WSS6009*7* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
209156995 |  | Ground Water | AE Air | WSS6012*7* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
200083642 |  | Ground Water | COMFORT-AIRE | HZV/H/D036B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
200083643 |  | Ground Water | CENTURY | HZV/H/D036B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
200083644 |  | Ground Water | COMFORT-AIRE | HZV/H/D024B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
200083645 |  | Ground Water | CENTURY | HZV/H/D024B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
200083646 |  | Ground Water | COMFORT-AIRE | HZV/H/D048B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
200083647 |  | Ground Water | CENTURY | HZV/H/D048B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
200083648 |  | Ground Water | COMFORT-AIRE | HZV/H/D060B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
200083649 |  | Ground Water | CENTURY | HZV/H/D060B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
200083650 |  | Ground Water | COMFORT-AIRE | HZV/H/D070B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
200083651 |  | Ground Water | CENTURY | HZV/H/D070B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
200083684 |  | Ground Water | COMFORT-AIRE | HZS024B | WDG024**A-*B | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
200083685 |  | Ground Water | CENTURY | HZS024B | WDG024**A-*B | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
200083686 |  | Ground Water | COMFORT-AIRE | HZS024B | WDG024**B-*B | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
200083687 |  | Ground Water | CENTURY | HZS024B | WDG024**B-*B | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
200083688 |  | Ground Water | COMFORT-AIRE | HZS024B | MWG24*A-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083689 |  | Ground Water | CENTURY | HZS024B | MWG24*A-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083690 |  | Ground Water | COMFORT-AIRE | HZS024B | MWG24*C-B | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
200083691 |  | Ground Water | CENTURY | HZS024B | MWG24*C-B | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
200083692 |  | Ground Water | COMFORT-AIRE | HZS024B | MWG24*B-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083693 |  | Ground Water | CENTURY | HZS024B | MWG24*B-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083694 |  | Ground Water | COMFORT-AIRE | HZS036B | MWG36**-B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | No
200083695 |  | Ground Water | CENTURY | HZS036B | MWG36**-B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
200083696 |  | Ground Water | COMFORT-AIRE | HZS036B | WDG036***-*B | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
200083697 |  | Ground Water | CENTURY | HZS036B | WDG036***-*B | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
200083700 |  | Ground Water | COMFORT-AIRE | HZS048B | WDG048***-*B | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
200083701 |  | Ground Water | CENTURY | HZS048B | WDG048***-*B | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
200083804 |  | Ground Water | NORTHERN HEAT PUMP | RA-VE-061-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
200083805 |  | Ground Water | NORTHSTAR SERIES | RA-VE-061-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
218338500 |  | Ground Water | YORK | Y5C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
218338506 |  | Ground Water | YORK | Y3C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
218338507 |  | Ground Water | YORK | Y3C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
218338512 |  | Ground Water | YORK | Y5C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
10346272 |  | Ground Water | GEOCOMFORT | GZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346273 |  | Ground Water | HYDRON MODULE | HZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346274 |  | Ground Water | TETCO | TZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346276 |  | Ground Water | GEOCOMFORT | GZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346277 |  | Ground Water | HYDRON MODULE | HZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346278 |  | Ground Water | TETCO | TZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346377 |  | Ground Water | GEOCOMFORT | GZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346378 |  | Ground Water | HYDRON MODULE | HZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346379 |  | Ground Water | TETCO | TZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346380 |  | Ground Water | GEOCOMFORT | GZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346381 |  | Ground Water | HYDRON MODULE | HZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346382 |  | Ground Water | TETCO | TZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10384616 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ070H1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10384620 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
10384621 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435611 |  | Ground Water | GEOSTAR | 103H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
10435612 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435613 |  | Ground Water | GeoSmart Energy | GTZ072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
10435614 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10435615 |  | Ground Water | GEOSTAR | 103H070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10435616 |  | Ground Water | GeoSmart Energy | GSZ070*1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10435617 |  | Ground Water | GEOSTAR | 104H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435618 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435619 |  | Ground Water | GeoSmart Energy | GTS072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
202330469 |  | Ground Water | AAON, Inc. | RN-006-2-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
202330470 |  | Ground Water | AAON, Inc. | RN-006-3-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
202330471 |  | Ground Water | AAON, Inc. | RN-006-4-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
202330486 |  | Ground Water | AAON, Inc. | SB-004-1-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330488 |  | Ground Water | AAON, Inc. | SB-004-2-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330490 |  | Ground Water | AAON, Inc. | SB-004-3-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330492 |  | Ground Water | AAON, Inc. | SB-004-4-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
216625774 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625775 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625776 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625777 |  | Ground Water | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625778 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625779 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625780 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625781 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625782 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625783 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625784 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625785 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625786 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625787 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625788 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625789 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625790 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625791 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625792 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625793 |  | Ground Water | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625794 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625795 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625796 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625797 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625798 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625799 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625800 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625801 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625802 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625803 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625804 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625805 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625806 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625807 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625808 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625809 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625810 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625811 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625812 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625813 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625814 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625815 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625816 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625817 |  | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625818 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625819 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625820 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625821 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625822 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625823 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
207312016 |  | Ground Water | WaterFurnace | SDV049J1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
207312019 |  | Ground Water | WaterFurnace | SDV038K1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
207312171 |  | Ground Water | WaterFurnace | NDV/NDH026J1*(1,4) |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207312172 |  | Ground Water | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207312173 |  | Ground Water | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207312174 |  | Ground Water | WaterFurnace | NDV/NDH072J1*(1,4) |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207312176 |  | Ground Water | WaterFurnace | NDV/NDH064K1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207312224 |  | Ground Water | WaterFurnace | NSV/NSH018J1*(1,4) |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207312225 |  | Ground Water | WaterFurnace | NSV/NSH030J1*(1,4) |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207312226 |  | Ground Water | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207312227 |  | Ground Water | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207312228 |  | Ground Water | WaterFurnace | NSV/NSH048K1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207312229 |  | Ground Water | WaterFurnace | NSV/NSH060K1*(1,4)* |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207312230 |  | Ground Water | WaterFurnace | NSV/NSH070J1*(1,4) |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207312262 |  | Ground Water | WaterFurnace | NSV/NSH012J1*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207312263 |  | Ground Water | WaterFurnace | NSV/NSH018J1*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | Yes
207312265 |  | Ground Water | WaterFurnace | NSV/NSH030J1*(0,3) |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | Yes
207312266 |  | Ground Water | WaterFurnace | NSV/NSH036K1*(0,3) |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207312267 |  | Ground Water | WaterFurnace | NSV/NSH042K1*(0,3) |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | Yes
207312268 |  | Ground Water | WaterFurnace | NSV/NSH048K1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | Yes
207312269 |  | Ground Water | WaterFurnace | NSV/NSH060K1*0* |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | Yes
207312271 |  | Ground Water | WaterFurnace | NSV/NSH022J1*(1,4) |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
207318098 |  | Ground Water | WaterFurnace | LD(V,H)048A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
206438732 |  | Ground Water | BOSCH | EP012-2VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438733 |  | Ground Water | BOSCH | EP015-2HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438734 |  | Ground Water | BOSCH | EP030-1HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438735 |  | Ground Water | BOSCH | EP030-2HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438736 |  | Ground Water | BOSCH | EP030-3HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438737 |  | Ground Water | BOSCH | EP030-4HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438738 |  | Ground Water | BOSCH | EP060-3HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438739 |  | Ground Water | BOSCH | EP060-4HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438740 |  | Ground Water | BOSCH | EP070-3HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438741 |  | Ground Water | BOSCH | EP070-4HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
9009391 |  | Ground Water | FHP | ES035-4CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9011292 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
9032648 |  | Ground Water | HYDROTECH | HRCX18*-6 |  | 20000 | 22.5 | 16000 | 4.1 | 1.6667 | Yes
9033424 |  | Ground Water | HYDROTECH | HRCX09*-6 |  | 11500 | 26.5 | 8800 | 4.5 | 0.95833 | Yes
9033758 |  | Ground Water | HYDROTECH | HRCX24*-6 |  | 26000 | 26.5 | 22000 | 4.4 | 2.1667 | Yes
9033759 |  | Ground Water | HYDROTECH | HRCX12*-6 |  | 13000 | 25 | 10500 | 4.1 | 1.0833 | Yes
205754895 |  | Ground Water | Johnson Controls | JCH/V030A*W/K B |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205754896 |  | Ground Water | SKYMARK | JCH/V030A*W/K C |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205754919 |  | Ground Water | Johnson Controls | JSH/V006A B |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205754920 |  | Ground Water | SKYMARK | JSH/V006A C |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205754921 |  | Ground Water | Johnson Controls | JSH/V009A B |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
205754922 |  | Ground Water | SKYMARK | JSH/V009A C |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
205767467 |  | Ground Water | ClimateMaster | QEV/H/D1860 |  | 48000 | 35.5 | 60000 | 4.3 | 4 | Yes
205767468 |  | Ground Water | ClimateMaster | TYV/H024B |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | No
205767470 |  | Ground Water | ClimateMaster | TYV/H036B |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | No
205767471 |  | Ground Water | ClimateMaster | TYV/H042 |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | No
205767473 |  | Ground Water | ClimateMaster | TEV/H/D026B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
205767474 |  | Ground Water | ClimateMaster | TEV/H/D038B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
205767475 |  | Ground Water | ClimateMaster | TEV/H/D049B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
205767476 |  | Ground Water | ClimateMaster | TEV/H/D064B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
205767477 |  | Ground Water | ClimateMaster | TEV/H/D072B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
205767488 |  | Ground Water | ClimateMaster | TSH/V006A |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205767489 |  | Ground Water | ClimateMaster | TSH/V/D018B |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
214595631 |  | Ground Water | AAON, Inc. | M2-004-4-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
4219426 |  | Ground Water | NORDIC | R65HACW-P-1T-*-SDE** |  | 62600 | 21.5 | 58700 | 4.5 | 5.2167 | Yes
4219434 |  | Ground Water | NORDIC | TF55HACW-P-1T-*-SDE** |  | 51100 | 22.5 | 47100 | 4.4 | 4.2583 | Yes
4219443 |  | Ground Water | NORDIC | RS45HACW-P-1T-* | AH-45-P-1-***** | 38500 | 21.3 | 35700 | 4.3 | 3.2083 | Yes
4219444 |  | Ground Water | NORDIC | RS55HACW-P-1T-* | AH-55-P-1-***** | 50200 | 22.5 | 47200 | 4.5 | 4.1833 | Yes
4219445 |  | Ground Water | NORDIC | RS65HACW-P-1T-* | AH-65-P-1-***** | 62600 | 21.5 | 58700 | 4.5 | 5.2167 | Yes
4230749 |  | Ground Water | DAIKIN | WCCW4024*E*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
4230751 |  | Ground Water | DAIKIN | WCCW4024*F*01* |  | 0 | 22.8 | 23500 | 4.2 | 0 | No
4230753 |  | Ground Water | DAIKIN | WCCW4024*J*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
4230922 |  | Ground Water | DAIKIN | WCCW4024*K*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
218157959 |  | Ground Water | YORK | Y5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157960 |  | Ground Water | YORK | Y5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157961 |  | Ground Water | YORK | Y5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157962 |  | Ground Water | YORK | Y5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157963 |  | Ground Water | YORK | Y5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157964 |  | Ground Water | YORK | Y5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157965 |  | Ground Water | YORK | Y5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157966 |  | Ground Water | YORK | Y5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157967 |  | Ground Water | YORK | Y5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157968 |  | Ground Water | YORK | Y5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157969 |  | Ground Water | YORK | Y5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157970 |  | Ground Water | YORK | Y5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157971 |  | Ground Water | YORK | Y5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157972 |  | Ground Water | YORK | Y5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157973 |  | Ground Water | YORK | Y5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157974 |  | Ground Water | YORK | Y5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157975 |  | Ground Water | YORK | Y5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
218157976 |  | Ground Water | YORK | Y5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157977 |  | Ground Water | YORK | Y5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157978 |  | Ground Water | YORK | Y5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157979 |  | Ground Water | YORK | Y5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157980 |  | Ground Water | YORK | Y5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157981 |  | Ground Water | YORK | Y5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157982 |  | Ground Water | YORK | Y5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157983 |  | Ground Water | YORK | Y5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157984 |  | Ground Water | YORK | Y5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157985 |  | Ground Water | YORK | Y5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
218157986 |  | Ground Water | YORK | Y5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215224478 |  | Ground Water | FHP | CF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224479 |  | Ground Water | FHP | CF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224480 |  | Ground Water | FHP | CF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224481 |  | Ground Water | FHP | CF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224482 |  | Ground Water | FHP | CF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224483 |  | Ground Water | FHP | CF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224484 |  | Ground Water | FHP | CF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224485 |  | Ground Water | FHP | CF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224486 |  | Ground Water | FHP | CF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224487 |  | Ground Water | FHP | CF007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224488 |  | Ground Water | FHP | CF007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224489 |  | Ground Water | FHP | CF009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224490 |  | Ground Water | FHP | CF009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224491 |  | Ground Water | FHP | CF012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224492 |  | Ground Water | FHP | CF012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224493 |  | Ground Water | FHP | CF015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224494 |  | Ground Water | FHP | CF015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224495 |  | Ground Water | FHP | CF018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
8738074 |  | Ground Water | HYDRON MODULE | HVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738075 |  | Ground Water | TETCO | TVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738076 |  | Ground Water | GEOCOMFORT | GVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738077 |  | Ground Water | HYDRON MODULE | HVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738078 |  | Ground Water | TETCO | TVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8740368 |  | Ground Water | GEOCOMFORT | GVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
216419879 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
216419880 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
216419882 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
216419883 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
216419898 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
216419899 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
216419902 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
216419904 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
216419907 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
216419908 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
216419909 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
216419912 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
216419920 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
216419921 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
216419922 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
216419924 |  | Ground Water | Whalen | WR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
216419941 |  | Ground Water | Whalen | WZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
216419942 |  | Ground Water | Whalen | WZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
216419945 |  | Ground Water | Whalen | WZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
216419946 |  | Ground Water | Whalen | WZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
216419947 |  | Ground Water | Whalen | WZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
216439574 |  | Ground Water | GeoSmart Energy | S5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216439575 |  | Ground Water | GeoSmart Energy | S5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216439576 |  | Ground Water | GeoSmart Energy | S5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216439577 |  | Ground Water | GeoSmart Energy | S5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216727177 |  | Ground Water | CARRIER | GZ024*******1**1 | FE*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
216727179 |  | Ground Water | CARRIER | GZ036*******1**2 | FE*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
214839009 |  | Ground Water | FHP | EC072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839010 |  | Ground Water | FHP | EC072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839011 |  | Ground Water | FHP | EC072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839012 |  | Ground Water | FHP | EC096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214839013 |  | Ground Water | FHP | EC096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214839014 |  | Ground Water | FHP | EC096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
216687117 |  | Ground Water | WaterFurnace | W5SS066BD1 | W5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216687118 |  | Ground Water | WaterFurnace | W5SZ024BD1 | W5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687119 |  | Ground Water | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687120 |  | Ground Water | WaterFurnace | W5SZ048BD1 | W5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687121 |  | Ground Water | WaterFurnace | W5SZ060BD1 | W5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687122 |  | Ground Water | WaterFurnace | W5SZ066BD1 | W5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216687731 |  | Ground Water | GEOSTAR | G5SS024BD1 | G5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687732 |  | Ground Water | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687733 |  | Ground Water | GEOSTAR | G5SS048BD1 | G5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687734 |  | Ground Water | GEOSTAR | G5SS060BD1 | G5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687735 |  | Ground Water | GEOSTAR | G5SS066BD1 | G5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216687736 |  | Ground Water | GEOSTAR | G5SZ024BD1 | G5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687737 |  | Ground Water | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687738 |  | Ground Water | GEOSTAR | G5SZ048BD1 | G5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687739 |  | Ground Water | GEOSTAR | G5SZ060BD1 | G5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687740 |  | Ground Water | GEOSTAR | G5SZ066BD1 | G5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216714606 |  | Ground Water | GEOSTAR | G3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
216714607 |  | Ground Water | GEOSTAR | G3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
216714612 |  | Ground Water | GEOSTAR | G3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714613 |  | Ground Water | GEOSTAR | G3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714614 |  | Ground Water | GEOSTAR | G3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714615 |  | Ground Water | GEOSTAR | G3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714620 |  | Ground Water | GEOSTAR | G3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714621 |  | Ground Water | GEOSTAR | G3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714622 |  | Ground Water | GEOSTAR | G3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714623 |  | Ground Water | GEOSTAR | G3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714624 |  | Ground Water | GEOSTAR | G3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714625 |  | Ground Water | GEOSTAR | G3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714626 |  | Ground Water | GEOSTAR | G3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714627 |  | Ground Water | GEOSTAR | G3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714636 |  | Ground Water | GEOSTAR | G3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714637 |  | Ground Water | GEOSTAR | G3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714638 |  | Ground Water | GEOSTAR | G3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714639 |  | Ground Water | GEOSTAR | G3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714640 |  | Ground Water | GEOSTAR | G3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714641 |  | Ground Water | GEOSTAR | G3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216569713 |  | Ground Water | GeoCool | GCHPV/H/D024BT**A*** |  | 28500 | 27.4 | 24500 | 4.8 | 2.375 | No
216569714 |  | Ground Water | GeoCool | GCHPV/H/D036BT**A*** |  | 41500 | 27.2 | 36600 | 4.9 | 3.4583 | No
216569715 |  | Ground Water | GeoCool | GCHPV/H/D048BT**A*** |  | 54800 | 26 | 48200 | 4.9 | 4.5667 | No
216569813 |  | Ground Water | GeoCool | GCHPV/H/D060BT**A*** |  | 69500 | 24 | 61600 | 4.9 | 5.7917 | No
216621309 |  | Ground Water | GEOSTAR | G5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216621310 |  | Ground Water | GEOSTAR | G5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216621311 |  | Ground Water | GEOSTAR | G5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216621312 |  | Ground Water | GEOSTAR | G5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216621313 |  | Ground Water | GEOSTAR | G5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216621314 |  | Ground Water | GEOSTAR | G5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216621315 |  | Ground Water | GEOSTAR | G5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216621316 |  | Ground Water | GEOSTAR | G5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216621317 |  | Ground Water | GEOSTAR | G5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216621318 |  | Ground Water | GEOSTAR | G5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216621319 |  | Ground Water | GEOSTAR | G5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216621323 |  | Ground Water | GEOSTAR | G5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216621324 |  | Ground Water | GEOSTAR | G5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216621325 |  | Ground Water | GEOSTAR | G5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621326 |  | Ground Water | GEOSTAR | G5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621327 |  | Ground Water | GEOSTAR | G5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621328 |  | Ground Water | GEOSTAR | G5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621329 |  | Ground Water | GEOSTAR | G5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621330 |  | Ground Water | GEOSTAR | G5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621331 |  | Ground Water | GEOSTAR | G5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621332 |  | Ground Water | GEOSTAR | G5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621333 |  | Ground Water | GEOSTAR | G5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621334 |  | Ground Water | GEOSTAR | G5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621335 |  | Ground Water | GEOSTAR | G5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621336 |  | Ground Water | GEOSTAR | G5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621337 |  | Ground Water | GEOSTAR | G5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621338 |  | Ground Water | GEOSTAR | G5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621339 |  | Ground Water | GEOSTAR | G5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621340 |  | Ground Water | GEOSTAR | G5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621341 |  | Ground Water | GEOSTAR | G5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621342 |  | Ground Water | GEOSTAR | G5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621343 |  | Ground Water | GEOSTAR | G5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621344 |  | Ground Water | GEOSTAR | G5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621345 |  | Ground Water | GEOSTAR | G5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621346 |  | Ground Water | GEOSTAR | G5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621347 |  | Ground Water | GEOSTAR | G5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621348 |  | Ground Water | GEOSTAR | G5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621349 |  | Ground Water | GEOSTAR | G5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218353294 |  | Ground Water | SKYMARK | PE072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218353295 |  | Ground Water | SKYMARK | PE096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
218353298 |  | Ground Water | SKYMARK | PK009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
218353299 |  | Ground Water | SKYMARK | PK009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
218353306 |  | Ground Water | SKYMARK | PQ024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353307 |  | Ground Water | SKYMARK | PQ024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218353308 |  | Ground Water | SKYMARK | PQ024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353309 |  | Ground Water | SKYMARK | PQ024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218353310 |  | Ground Water | SKYMARK | PQ024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353311 |  | Ground Water | SKYMARK | PQ024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218353312 |  | Ground Water | SKYMARK | PQ024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353313 |  | Ground Water | SKYMARK | PQ024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218353314 |  | Ground Water | SKYMARK | PQ036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218353315 |  | Ground Water | SKYMARK | PQ036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218353316 |  | Ground Water | SKYMARK | PQ036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218353317 |  | Ground Water | SKYMARK | PQ036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218353318 |  | Ground Water | SKYMARK | PQ048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
218353319 |  | Ground Water | SKYMARK | PQ048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218353320 |  | Ground Water | SKYMARK | PQ060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218353321 |  | Ground Water | SKYMARK | PQ060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
215415870 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415871 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415872 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415873 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415874 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415875 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415876 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415877 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415878 |  | Ground Water | CENTURY | MZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
215415879 |  | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
215415880 |  | Ground Water | CENTURY | MZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
215415881 |  | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
215415884 |  | Ground Water | CENTURY | MZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
215415885 |  | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
215415886 |  | Ground Water | CENTURY | MZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
215415887 |  | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
215415888 |  | Ground Water | CENTURY | MZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
215415889 |  | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
215415909 |  | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215415910 |  | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215415911 |  | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 42000 | 25 | 36000 | 4.9 | 3.5 | Yes
215415912 |  | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 42000 | 25 | 36000 | 4.9 | 3.5 | Yes
215415913 |  | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 56000 | 27 | 47300 | 4.9 | 4.6667 | Yes
215415914 |  | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 56000 | 27 | 47300 | 4.9 | 4.6667 | Yes
215415915 |  | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
215415916 |  | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
215270421 |  | Ground Water | CARRIER | GZ024*******1**1 | FE****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270423 |  | Ground Water | CARRIER | GZ036*******1**2 | FE****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215270427 |  | Ground Water | BRYANT | GZ024*******1**1 | FE****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270429 |  | Ground Water | BRYANT | GZ036*******1**2 | FE****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215278610 |  | Ground Water | WaterFurnace | W3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215285739 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215285740 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 42000 | 25 | 36000 | 4.9 | 3.5 | Yes
215285741 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 56000 | 27 | 47300 | 4.9 | 4.6667 | Yes
215285742 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
215285743 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
215287172 |  | Ground Water | GEOSTAR | G3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215287179 |  | Ground Water | GeoSmart Energy | S3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215310891 |  | Ground Water | GEOSTAR | G7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
215310892 |  | Ground Water | GEOSTAR | G7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
215310893 |  | Ground Water | GEOSTAR | G7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
215310895 |  | Ground Water | GEOSTAR | G7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
215310990 |  | Ground Water | GeoSmart Energy | S7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
215310991 |  | Ground Water | GeoSmart Energy | S7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
215310992 |  | Ground Water | GeoSmart Energy | S7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
215310994 |  | Ground Water | GeoSmart Energy | S7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
217531660 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)006A |  | 7600 | 30 | 6200 | 4.8 | 0.63333 | Yes
217531661 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)009A |  | 10500 | 28 | 9000 | 4.6 | 0.875 | Yes
217531662 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)012A |  | 13600 | 26.2 | 12200 | 4.3 | 1.1333 | Yes
217531663 |  | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)018A |  | 22000 | 28.1 | 18900 | 4.9 | 1.8333 | Yes
207177436 |  | Ground Water | TRANE | GEVG0157 |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
207177437 |  | Ground Water | TRANE | GEVG018A |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
207177438 |  | Ground Water | TRANE | GEVG0187 |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
207177439 |  | Ground Water | TRANE | GEVG024A |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177440 |  | Ground Water | TRANE | GEVG024B |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177441 |  | Ground Water | TRANE | GEVG0244 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177442 |  | Ground Water | TRANE | GEVG0247 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177443 |  | Ground Water | TRANE | GEVG030A |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177444 |  | Ground Water | TRANE | GEVG030B |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177445 |  | Ground Water | TRANE | GEVG0304 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177446 |  | Ground Water | TRANE | GEVG0307 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
3059237 |  | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3093286 |  | Ground Water | TRANE | GEHE072 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
3093289 |  | Ground Water | TRANE | GEVE072 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
3093290 |  | Ground Water | TRANE | GEVE090 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
3627926 |  | Ground Water | WaterFurnace | USV/USH015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
3627927 |  | Ground Water | WaterFurnace | USV/USH015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
202350481 |  | Ground Water | AAON, Inc. | M2-011-2-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350484 |  | Ground Water | AAON, Inc. | M2-011-3-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350487 |  | Ground Water | AAON, Inc. | M2-011-4-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350489 |  | Ground Water | AAON, Inc. | M2-014-2-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350490 |  | Ground Water | AAON, Inc. | M2-014-2-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350491 |  | Ground Water | AAON, Inc. | M2-014-3-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350492 |  | Ground Water | AAON, Inc. | M2-014-3-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350493 |  | Ground Water | AAON, Inc. | M2-014-4-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350494 |  | Ground Water | AAON, Inc. | M2-014-4-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350495 |  | Ground Water | AAON, Inc. | M2-011-2-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
202350496 |  | Ground Water | AAON, Inc. | M2-011-3-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
202350497 |  | Ground Water | AAON, Inc. | M2-011-4-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
202350498 |  | Ground Water | AAON, Inc. | M2-014-2-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
202350499 |  | Ground Water | AAON, Inc. | M2-014-2-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
202350500 |  | Ground Water | AAON, Inc. | M2-014-3-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
202350501 |  | Ground Water | AAON, Inc. | M2-014-3-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
202350502 |  | Ground Water | AAON, Inc. | M2-014-4-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
216743662 |  | Ground Water | BOSCH | CP060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216743663 |  | Ground Water | BOSCH-GEO | RP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
216743664 |  | Ground Water | BOSCH | CP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743665 |  | Ground Water | BOSCH | CP070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743666 |  | Ground Water | BOSCH | CP070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743667 |  | Ground Water | BOSCH-GEO | RP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
216743668 |  | Ground Water | BOSCH | CP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743669 |  | Ground Water | BOSCH | CP070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743670 |  | Ground Water | BOSCH | CP070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743671 |  | Ground Water | BOSCH-GEO | RP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
216743672 |  | Ground Water | BOSCH | CP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743673 |  | Ground Water | BOSCH | CP070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743674 |  | Ground Water | BOSCH | CP070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743675 |  | Ground Water | BOSCH-GEO | RP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
216743676 |  | Ground Water | BOSCH | CP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743677 |  | Ground Water | BOSCH | CP070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743678 |  | Ground Water | BOSCH | CP070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216759673 |  | Ground Water | WaterFurnace | W7SZ030BV1**F | W7BM030BN1**2 | 35800 | 27.8 | 40700 | 4.5 | 2.9833 | Yes
216759674 |  | Ground Water | WaterFurnace | W7SZ042BV1**F | W7BM042BN1**2 | 44400 | 28.8 | 51300 | 4.4 | 3.7 | Yes
216759816 |  | Ground Water | WaterFurnace | W5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759817 |  | Ground Water | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759818 |  | Ground Water | WaterFurnace | W5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759819 |  | Ground Water | WaterFurnace | W5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759820 |  | Ground Water | WaterFurnace | W5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759821 |  | Ground Water | GEOSTAR | G5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759822 |  | Ground Water | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759823 |  | Ground Water | GEOSTAR | G5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759824 |  | Ground Water | GEOSTAR | G5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759825 |  | Ground Water | GEOSTAR | G5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759826 |  | Ground Water | WaterFurnace | W5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759827 |  | Ground Water | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759828 |  | Ground Water | WaterFurnace | W5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759829 |  | Ground Water | WaterFurnace | W5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759830 |  | Ground Water | WaterFurnace | W5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759831 |  | Ground Water | GEOSTAR | G5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759832 |  | Ground Water | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759833 |  | Ground Water | GEOSTAR | G5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759834 |  | Ground Water | GEOSTAR | G5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759835 |  | Ground Water | GEOSTAR | G5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216767321 |  | Ground Water | TETCO | TVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
216767322 |  | Ground Water | TETCO | TVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216767323 |  | Ground Water | TETCO | TVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216767324 |  | Ground Water | TETCO | TVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216767325 |  | Ground Water | TETCO | TVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216767326 |  | Ground Water | TETCO | TYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216767327 |  | Ground Water | TETCO | TYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216767328 |  | Ground Water | TETCO | TYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216767329 |  | Ground Water | TETCO | TVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216767330 |  | Ground Water | TETCO | TYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
214063739 |  | Ground Water | GeoSmart Energy | GBV/GBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
214063740 |  | Ground Water | GeoSmart Energy | GBV/GBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
214063741 |  | Ground Water | GeoSmart Energy | GBV/GBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063742 |  | Ground Water | GeoSmart Energy | GBV/GBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063743 |  | Ground Water | GeoSmart Energy | GBV/GBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
214063744 |  | Ground Water | GeoSmart Energy | GBV/GBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063745 |  | Ground Water | GeoSmart Energy | GBV/GBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063746 |  | Ground Water | GeoSmart Energy | GBV/GBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
214063747 |  | Ground Water | GeoSmart Energy | GBV/GBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063748 |  | Ground Water | GeoSmart Energy | GBV/GBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063749 |  | Ground Water | GeoSmart Energy | GBV/GBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
214063750 |  | Ground Water | GeoSmart Energy | GBV/GBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063751 |  | Ground Water | GeoSmart Energy | GBV/GBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063752 |  | Ground Water | GeoSmart Energy | GBV/GBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214063753 |  | Ground Water | GeoSmart Energy | GBV/GBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063754 |  | Ground Water | GeoSmart Energy | GBV/GBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063755 |  | Ground Water | GeoSmart Energy | GBV/GBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214063756 |  | Ground Water | GeoSmart Energy | GBV/GBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063757 |  | Ground Water | GeoSmart Energy | GBV/GBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063758 |  | Ground Water | GeoSmart Energy | GBV/GBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063759 |  | Ground Water | GeoSmart Energy | GBV/GBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063760 |  | Ground Water | GeoSmart Energy | GBV/GBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063761 |  | Ground Water | GeoSmart Energy | GBV/GBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063762 |  | Ground Water | GeoSmart Energy | GBV/GBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214063763 |  | Ground Water | GeoSmart Energy | GBV/GBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063764 |  | Ground Water | GeoSmart Energy | GBV/GBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063765 |  | Ground Water | GeoSmart Energy | GBV/GBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214063766 |  | Ground Water | GeoSmart Energy | GBV/GBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063767 |  | Ground Water | GeoSmart Energy | GBV/GBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063768 |  | Ground Water | GeoSmart Energy | GBV/GBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214063769 |  | Ground Water | GeoSmart Energy | GBV/GBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063770 |  | Ground Water | GeoSmart Energy | GBV/GBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063771 |  | Ground Water | GeoSmart Energy | GBV/GBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214063772 |  | Ground Water | GeoSmart Energy | GBV/GBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063773 |  | Ground Water | GeoSmart Energy | GBV/GBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063774 |  | Ground Water | GeoSmart Energy | GBV/GBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063775 |  | Ground Water | GeoSmart Energy | GBV/GBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063776 |  | Ground Water | GeoSmart Energy | GBV/GBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063777 |  | Ground Water | GeoSmart Energy | GBV/GBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063778 |  | Ground Water | GeoSmart Energy | GBV/GBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214063779 |  | Ground Water | GeoSmart Energy | GBV/GBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214063780 |  | Ground Water | GeoSmart Energy | GBV/GBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214063781 |  | Ground Water | GeoSmart Energy | GBV/GBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214063782 |  | Ground Water | GeoSmart Energy | GBV/GBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214063783 |  | Ground Water | GeoSmart Energy | GBV/GBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214063784 |  | Ground Water | GeoSmart Energy | GBV/GBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214063785 |  | Ground Water | GeoSmart Energy | GBV/GBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214063786 |  | Ground Water | GeoSmart Energy | GBV/GBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214063788 |  | Ground Water | GeoSmart Energy | GBV/GBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214063789 |  | Ground Water | GeoSmart Energy | GBV/GBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214063790 |  | Ground Water | GeoSmart Energy | GBV/GBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
218472100 |  | Ground Water | YORK | AD007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218472101 |  | Ground Water | YORK | AD007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218472102 |  | Ground Water | YORK | AD009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218472103 |  | Ground Water | YORK | AD009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218472104 |  | Ground Water | YORK | AD012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
218472105 |  | Ground Water | YORK | AD012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
218472106 |  | Ground Water | YORK | AD015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
218472107 |  | Ground Water | YORK | AD015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
218472108 |  | Ground Water | YORK | AD018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
218472109 |  | Ground Water | YORK | AD018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
218472110 |  | Ground Water | YORK | AD007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218472111 |  | Ground Water | YORK | AD007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
218472112 |  | Ground Water | YORK | AD009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218472113 |  | Ground Water | YORK | AD009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218472114 |  | Ground Water | YORK | AD012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
218472115 |  | Ground Water | YORK | AD012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
218472116 |  | Ground Water | YORK | AD015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
218472117 |  | Ground Water | YORK | AD015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
218472118 |  | Ground Water | YORK | AD018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
218472119 |  | Ground Water | YORK | AD018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
218353637 |  | Ground Water | JOHNSON CONTROLS | DE072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218353638 |  | Ground Water | JOHNSON CONTROLS | DE072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218353639 |  | Ground Water | JOHNSON CONTROLS | DE072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218353640 |  | Ground Water | JOHNSON CONTROLS | DE096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
218353641 |  | Ground Water | JOHNSON CONTROLS | DE096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
218353642 |  | Ground Water | JOHNSON CONTROLS | DE096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
218353651 |  | Ground Water | JOHNSON CONTROLS | DQ024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353652 |  | Ground Water | JOHNSON CONTROLS | DQ024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218353653 |  | Ground Water | JOHNSON CONTROLS | DQ024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353654 |  | Ground Water | JOHNSON CONTROLS | DQ024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218353655 |  | Ground Water | JOHNSON CONTROLS | DQ024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353656 |  | Ground Water | JOHNSON CONTROLS | DQ024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218353657 |  | Ground Water | JOHNSON CONTROLS | DQ024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353658 |  | Ground Water | JOHNSON CONTROLS | DQ024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218353659 |  | Ground Water | JOHNSON CONTROLS | DQ024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353660 |  | Ground Water | JOHNSON CONTROLS | DQ024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218353661 |  | Ground Water | JOHNSON CONTROLS | DQ024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353662 |  | Ground Water | JOHNSON CONTROLS | DQ024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218353663 |  | Ground Water | JOHNSON CONTROLS | DQ024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353664 |  | Ground Water | JOHNSON CONTROLS | DQ024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218353665 |  | Ground Water | JOHNSON CONTROLS | DQ024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353666 |  | Ground Water | JOHNSON CONTROLS | DQ024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218353667 |  | Ground Water | JOHNSON CONTROLS | DQ036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218353668 |  | Ground Water | JOHNSON CONTROLS | DQ036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218353669 |  | Ground Water | JOHNSON CONTROLS | DQ036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218353670 |  | Ground Water | JOHNSON CONTROLS | DQ036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218353671 |  | Ground Water | JOHNSON CONTROLS | DQ036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218353672 |  | Ground Water | JOHNSON CONTROLS | DQ036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217642876 |  | Ground Water | GeoSmart Energy | S3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642879 |  | Ground Water | GeoSmart Energy | S3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642881 |  | Ground Water | GeoSmart Energy | S3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642883 |  | Ground Water | GeoSmart Energy | S3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642884 |  | Ground Water | GeoSmart Energy | S3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
7409789 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
7409859 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
7409937 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
7410008 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
7410095 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
7410164 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410223 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410291 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
7410355 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410435 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410522 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
7410657 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7410717 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
7410825 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7410908 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7411002 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7411100 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
215224606 |  | Ground Water | CARRIER | 50WD*009***4*(J-R)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224607 |  | Ground Water | CARRIER | 50WD*012***3*(A-H)** |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224608 |  | Ground Water | CARRIER | 50WD*012***3*(J-R)** |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224609 |  | Ground Water | CARRIER | 50WD*012***4*(A-H)** |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224610 |  | Ground Water | CARRIER | 50WD*012***4*(J-R)** |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224611 |  | Ground Water | CARRIER | 50WD*015***3*(A-H)** |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224612 |  | Ground Water | CARRIER | 50WD*015***3*(J-R)** |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224613 |  | Ground Water | CARRIER | 50WD*015***4*(A-H)** |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224614 |  | Ground Water | CARRIER | 50WD*015***4*(J-R)** |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224615 |  | Ground Water | CARRIER | 50WD*018***3*(A-H)** |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224616 |  | Ground Water | CARRIER | 50WD*018***3*(J-R)** |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224617 |  | Ground Water | CARRIER | 50WD*018***4*(A-H)** |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224618 |  | Ground Water | CARRIER | 50WD*018***4*(J-R)** |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
216801935 |  | Ground Water | CARRIER | 50PSW025***6/FB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
207348682 |  | Ground Water | WaterFurnace | URS060*0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348683 |  | Ground Water | WaterFurnace | URS060*0*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348684 |  | Ground Water | WaterFurnace | URS060*3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348685 |  | Ground Water | WaterFurnace | URS060*3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348686 |  | Ground Water | WaterFurnace | URS060*3*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348687 |  | Ground Water | WaterFurnace | URS060*4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348688 |  | Ground Water | WaterFurnace | URS060*4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348689 |  | Ground Water | WaterFurnace | URS060*4*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348707 |  | Ground Water | WaterFurnace | URD038*0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348708 |  | Ground Water | WaterFurnace | URD038*0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348709 |  | Ground Water | WaterFurnace | URD038*0*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348710 |  | Ground Water | WaterFurnace | URD038*3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348711 |  | Ground Water | WaterFurnace | URD038*3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348712 |  | Ground Water | WaterFurnace | URD038*3*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348713 |  | Ground Water | WaterFurnace | URD038*4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348714 |  | Ground Water | WaterFurnace | URD038*4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348715 |  | Ground Water | WaterFurnace | URD038*4*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348716 |  | Ground Water | WaterFurnace | URD049*0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348717 |  | Ground Water | WaterFurnace | URD049*0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348718 |  | Ground Water | WaterFurnace | URD049*0*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348719 |  | Ground Water | WaterFurnace | URD049*3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348720 |  | Ground Water | WaterFurnace | URD049*3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348721 |  | Ground Water | WaterFurnace | URD049*3*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348722 |  | Ground Water | WaterFurnace | URD049*4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348723 |  | Ground Water | WaterFurnace | URD049*4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348724 |  | Ground Water | WaterFurnace | URD049*4*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348725 |  | Ground Water | WaterFurnace | URD064*0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348726 |  | Ground Water | WaterFurnace | URD064*0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348727 |  | Ground Water | WaterFurnace | URD064*0*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348728 |  | Ground Water | WaterFurnace | URD064*3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348729 |  | Ground Water | WaterFurnace | URD064*3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348730 |  | Ground Water | WaterFurnace | URD064*3*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348731 |  | Ground Water | WaterFurnace | URD064*4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348732 |  | Ground Water | WaterFurnace | URD064*4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348733 |  | Ground Water | WaterFurnace | URD064*4*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348734 |  | Ground Water | WaterFurnace | URD072*0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348735 |  | Ground Water | WaterFurnace | URD072*0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348736 |  | Ground Water | WaterFurnace | URD072*0*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348737 |  | Ground Water | WaterFurnace | URD072*3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348738 |  | Ground Water | WaterFurnace | URD072*3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5646343 |  | Ground Water | GEOCOMFORT | GXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646344 |  | Ground Water | HYDRON MODULE | HXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646345 |  | Ground Water | TETCO | TXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646346 |  | Ground Water | GEOCOMFORT | GXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646347 |  | Ground Water | HYDRON MODULE | HXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646348 |  | Ground Water | TETCO | TXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646349 |  | Ground Water | GEOCOMFORT | GXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646350 |  | Ground Water | HYDRON MODULE | HXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646351 |  | Ground Water | TETCO | TXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646371 |  | Ground Water | GEOCOMFORT | GXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646372 |  | Ground Water | HYDRON MODULE | HXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646373 |  | Ground Water | TETCO | TXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646374 |  | Ground Water | GEOCOMFORT | GXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646375 |  | Ground Water | HYDRON MODULE | HXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646376 |  | Ground Water | TETCO | TXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646377 |  | Ground Water | GEOCOMFORT | GXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646378 |  | Ground Water | HYDRON MODULE | HXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646379 |  | Ground Water | TETCO | TXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646381 |  | Ground Water | GEOCOMFORT | GCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
5646382 |  | Ground Water | HYDRON MODULE | HCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
5646383 |  | Ground Water | TETCO | TCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
206438789 |  | Ground Water | FHP | EP030-1HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438790 |  | Ground Water | FHP | EP060-4HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438791 |  | Ground Water | FHP | EP060-3HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438792 |  | Ground Water | FHP | EP060-1HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438793 |  | Ground Water | FHP | EP070-1HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438794 |  | Ground Water | FHP | EP070-3HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438795 |  | Ground Water | FHP | EP070-4HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
207323881 |  | Ground Water | WaterFurnace | NDZ026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207323882 |  | Ground Water | WaterFurnace | NDZ026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207323883 |  | Ground Water | WaterFurnace | NDS026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207323884 |  | Ground Water | WaterFurnace | NDS026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207323885 |  | Ground Water | WaterFurnace | NDZ038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323886 |  | Ground Water | WaterFurnace | NDZ038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323887 |  | Ground Water | WaterFurnace | NDS038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323888 |  | Ground Water | WaterFurnace | NDZ049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207323889 |  | Ground Water | WaterFurnace | NDZ049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207323890 |  | Ground Water | WaterFurnace | NDS049H1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207323891 |  | Ground Water | WaterFurnace | NDS049H1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207323892 |  | Ground Water | WaterFurnace | NDZ064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207323893 |  | Ground Water | WaterFurnace | NDZ064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207323894 |  | Ground Water | WaterFurnace | NDS064H1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207323895 |  | Ground Water | WaterFurnace | NDS064H1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207323896 |  | Ground Water | WaterFurnace | NDZ072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207323897 |  | Ground Water | WaterFurnace | NDZ072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207323898 |  | Ground Water | WaterFurnace | NDS072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207323899 |  | Ground Water | WaterFurnace | NDS072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207323900 |  | Ground Water | WaterFurnace | NDS038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207323901 |  | Ground Water | WaterFurnace | NSZ022H1* | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207323902 |  | Ground Water | WaterFurnace | NSZ030H1* | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207323903 |  | Ground Water | WaterFurnace | NSZ036J1* | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207323904 |  | Ground Water | WaterFurnace | NSZ042J1* | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207323905 |  | Ground Water | WaterFurnace | NSZ048J1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207323906 |  | Ground Water | WaterFurnace | NSZ048J1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207323907 |  | Ground Water | WaterFurnace | NSZ060J1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207323908 |  | Ground Water | WaterFurnace | NSZ060J1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207323909 |  | Ground Water | WaterFurnace | NSZ070H1* | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207323910 |  | Ground Water | WaterFurnace | NSZ022H1* | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207323911 |  | Ground Water | WaterFurnace | NSZ030H1* | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207323912 |  | Ground Water | WaterFurnace | NSZ036J1* | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207323913 |  | Ground Water | WaterFurnace | NSZ042J1* | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207323914 |  | Ground Water | WaterFurnace | NSZ070H1* | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207324064 |  | Ground Water | WaterFurnace | NVV/NVH036C1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
207324066 |  | Ground Water | WaterFurnace | NVV/NVH060C1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | No
215415792 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)042A*VB |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415793 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)042A*VC |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415794 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)048A*B |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415795 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)048A*C |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415796 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)048A*VB |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415797 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)048A*VC |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415800 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)060A*VB |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415801 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)060A*VC |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415814 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)015A*B |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415815 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)015A*C |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415816 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)015A*VB |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415817 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)015A*VC |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415818 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)018A*B |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415819 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)018A*C |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415820 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)018A*VB |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415821 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)018A*VC |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415822 |  | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)024A*B |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
215415823 |  | Ground Water | SKYMARK | BY(L/R/B/P/T/K)024A*C |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
215415824 |  | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)030A*B |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
215415825 |  | Ground Water | SKYMARK | BY(L/R/B/P/T/K)030A*C |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
215415828 |  | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)042A*B |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
215415829 |  | Ground Water | SKYMARK | BY(L/R/B/P/T/K)042A*C |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
215415830 |  | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)048A*B |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
215415831 |  | Ground Water | SKYMARK | BY(L/R/B/P/T/K)048A*C |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
215415832 |  | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)060A*B |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
215415833 |  | Ground Water | SKYMARK | BY(L/R/B/P/T/K)060A*C |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
215415834 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415835 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415836 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415837 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415840 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415841 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
218353053 |  | Ground Water | SKYMARK | PE072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218353054 |  | Ground Water | SKYMARK | PE072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218353055 |  | Ground Water | SKYMARK | PE096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
218353056 |  | Ground Water | SKYMARK | PE096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
218353063 |  | Ground Water | SKYMARK | PQ024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353064 |  | Ground Water | SKYMARK | PQ024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218353065 |  | Ground Water | SKYMARK | PQ024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353066 |  | Ground Water | SKYMARK | PQ024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218353067 |  | Ground Water | SKYMARK | PQ024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353068 |  | Ground Water | SKYMARK | PQ024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218353069 |  | Ground Water | SKYMARK | PQ024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218353070 |  | Ground Water | SKYMARK | PQ024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218353071 |  | Ground Water | SKYMARK | PQ036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218353072 |  | Ground Water | SKYMARK | PQ036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218353073 |  | Ground Water | SKYMARK | PQ036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218353074 |  | Ground Water | SKYMARK | PQ036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218353075 |  | Ground Water | SKYMARK | PQ048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
218353076 |  | Ground Water | SKYMARK | PQ048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218353077 |  | Ground Water | SKYMARK | PQ048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
211594262 |  | Ground Water | TRANE | EXHG0704 |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
211594263 |  | Ground Water | TRANE | DXHG024B |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594264 |  | Ground Water | TRANE | DXHG0244 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594265 |  | Ground Water | TRANE | DXHG0247 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594266 |  | Ground Water | TRANE | DXHG036B |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594267 |  | Ground Water | TRANE | DXHG0364 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594268 |  | Ground Water | TRANE | DXHG0367 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594269 |  | Ground Water | TRANE | DXHG048B |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594270 |  | Ground Water | TRANE | DXHG0484 |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594271 |  | Ground Water | TRANE | DXHG060B |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
211594272 |  | Ground Water | TRANE | DXHG0604 |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
215748031 |  | Ground Water | NORDIC | R-55-HACW-X-1T-*-*DE** |  | 48000 | 22.2 | 47000 | 4.5 | 4 | No
217755007 |  | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755008 |  | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755009 |  | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755010 |  | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755011 |  | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755012 |  | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755019 |  | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755020 |  | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755021 |  | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
218157947 |  | Ground Water | YORK | Y5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157948 |  | Ground Water | YORK | Y5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157949 |  | Ground Water | YORK | Y5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157950 |  | Ground Water | YORK | Y5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157951 |  | Ground Water | YORK | Y5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157952 |  | Ground Water | YORK | Y5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157953 |  | Ground Water | YORK | Y5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157954 |  | Ground Water | YORK | Y5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157955 |  | Ground Water | YORK | Y5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157956 |  | Ground Water | YORK | Y5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157957 |  | Ground Water | YORK | Y5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
218157958 |  | Ground Water | YORK | Y5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
205973166 |  | Ground Water | Enertech | ERE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205973167 |  | Ground Water | Enertech | ERE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205973168 |  | Ground Water | Enertech | ERE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205973169 |  | Ground Water | Enertech | ERE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
205973771 |  | Ground Water | COMFORT-AIRE | HEV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205973772 |  | Ground Water | CENTURY | HEV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205973775 |  | Ground Water | COMFORT-AIRE | HEV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205973776 |  | Ground Water | CENTURY | HEV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205973779 |  | Ground Water | COMFORT-AIRE | HEV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
202449784 |  | Ground Water | WaterFurnace | UBV/UBH036**0*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449785 |  | Ground Water | WaterFurnace | UBV/UBH036**2*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449786 |  | Ground Water | WaterFurnace | UBV/UBH036**3*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449787 |  | Ground Water | WaterFurnace | UBV/UBH036**4*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449788 |  | Ground Water | WaterFurnace | UBV/UBH036**0*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449789 |  | Ground Water | WaterFurnace | UBV/UBH036**2*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449790 |  | Ground Water | WaterFurnace | UBV/UBH036**3*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449791 |  | Ground Water | WaterFurnace | UBV/UBH036**4*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449795 |  | Ground Water | WaterFurnace | UBV/UBH042**0*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449796 |  | Ground Water | WaterFurnace | UBV/UBH042**3*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449797 |  | Ground Water | WaterFurnace | UBV/UBH042**4*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449798 |  | Ground Water | WaterFurnace | UBV/UBH042**0*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449799 |  | Ground Water | WaterFurnace | UBV/UBH042**3*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449800 |  | Ground Water | WaterFurnace | UBV/UBH042**4*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449816 |  | Ground Water | WaterFurnace | UBV/UBH060**0*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449817 |  | Ground Water | WaterFurnace | UBV/UBH060**3*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449818 |  | Ground Water | WaterFurnace | UBV/UBH060**4*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449819 |  | Ground Water | WaterFurnace | UBV/UBH060**0*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449820 |  | Ground Water | WaterFurnace | UBV/UBH060**3*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449821 |  | Ground Water | WaterFurnace | UBV/UBH060**4*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449826 |  | Ground Water | WaterFurnace | UBV/UBH070**0*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449827 |  | Ground Water | WaterFurnace | UBV/UBH070**3*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449828 |  | Ground Water | WaterFurnace | UBV/UBH070**4*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449829 |  | Ground Water | WaterFurnace | UBV/UBH070**0*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449830 |  | Ground Water | WaterFurnace | UBV/UBH070**3*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449831 |  | Ground Water | WaterFurnace | UBV/UBH070**4*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
207216514 |  | Ground Water | GEOSTAR | GDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216515 |  | Ground Water | GEOSTAR | GDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216516 |  | Ground Water | GEOSTAR | GDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216517 |  | Ground Water | GEOSTAR | GDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
207216518 |  | Ground Water | GEOSTAR | GDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
207216519 |  | Ground Water | GEOSTAR | GDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
201907621 |  | Ground Water | WaterFurnace | URS048*0*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907622 |  | Ground Water | WaterFurnace | URS048*3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907623 |  | Ground Water | WaterFurnace | URS048*3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907624 |  | Ground Water | WaterFurnace | URS048*3*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907625 |  | Ground Water | WaterFurnace | URS048*4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907626 |  | Ground Water | WaterFurnace | URS048*4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907627 |  | Ground Water | WaterFurnace | URS048*4*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907628 |  | Ground Water | WaterFurnace | URD038*4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907629 |  | Ground Water | WaterFurnace | URD038*4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907630 |  | Ground Water | WaterFurnace | URD038*4*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907631 |  | Ground Water | WaterFurnace | URD049*4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201907632 |  | Ground Water | WaterFurnace | URD049*4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201907633 |  | Ground Water | WaterFurnace | URD049*4*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201926691 |  | Ground Water | WaterFurnace | URS060*0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926694 |  | Ground Water | WaterFurnace | URS060*0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926696 |  | Ground Water | WaterFurnace | URS060*0*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926699 |  | Ground Water | WaterFurnace | URS060*3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926702 |  | Ground Water | WaterFurnace | URS060*3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926705 |  | Ground Water | WaterFurnace | URS060*3*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926708 |  | Ground Water | WaterFurnace | URS060*4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926711 |  | Ground Water | WaterFurnace | URS060*4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926714 |  | Ground Water | WaterFurnace | URS060*4*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926717 |  | Ground Water | WaterFurnace | URS070*0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926719 |  | Ground Water | WaterFurnace | URS070*0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926724 |  | Ground Water | WaterFurnace | URS070*0*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926727 |  | Ground Water | WaterFurnace | URS070*3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926730 |  | Ground Water | WaterFurnace | URS070*3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926733 |  | Ground Water | WaterFurnace | URS070*3*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926736 |  | Ground Water | WaterFurnace | URS070*4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926738 |  | Ground Water | WaterFurnace | URS070*4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926741 |  | Ground Water | WaterFurnace | URS070*4*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926779 |  | Ground Water | WaterFurnace | URD064*4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926783 |  | Ground Water | WaterFurnace | URD064*4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926787 |  | Ground Water | WaterFurnace | URD064*4*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926799 |  | Ground Water | WaterFurnace | URD072*4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926802 |  | Ground Water | WaterFurnace | URD072*4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926804 |  | Ground Water | WaterFurnace | URD072*4*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926809 |  | Ground Water | WaterFurnace | URT096*4*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
201930362 |  | Ground Water | GEOCOMFORT | GZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
206422417 |  | Ground Water | CENTURY | HBH/V015*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
206422418 |  | Ground Water | COMFORT-AIRE | HBH/V015*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
206422419 |  | Ground Water | CENTURY | HBH/V018*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
206422420 |  | Ground Water | COMFORT-AIRE | HBH/V018*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
206422421 |  | Ground Water | CENTURY | HBH/V024*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
206422422 |  | Ground Water | COMFORT-AIRE | HBH/V024*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
206422423 |  | Ground Water | CENTURY | HBH/V030*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
206422424 |  | Ground Water | COMFORT-AIRE | HBH/V030*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
206438717 |  | Ground Water | BOSCH | EP007-1HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438718 |  | Ground Water | BOSCH | EP007-2HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438719 |  | Ground Water | BOSCH | EP009-1HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438720 |  | Ground Water | BOSCH | EP009-2HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438721 |  | Ground Water | BOSCH | EP012-0HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438722 |  | Ground Water | BOSCH | EP012-0HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438723 |  | Ground Water | BOSCH | EP012-0VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438724 |  | Ground Water | BOSCH | EP012-0VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438725 |  | Ground Water | BOSCH | EP012-1HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438726 |  | Ground Water | BOSCH | EP012-1HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438727 |  | Ground Water | BOSCH | EP012-1VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438728 |  | Ground Water | BOSCH | EP012-1VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438729 |  | Ground Water | BOSCH | EP012-2HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438730 |  | Ground Water | BOSCH | EP012-2HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438731 |  | Ground Water | BOSCH | EP012-2VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
215224293 |  | Ground Water | BOSCH-GEO | RF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224294 |  | Ground Water | BOSCH-GEO | RF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224295 |  | Ground Water | BOSCH-GEO | RF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224296 |  | Ground Water | BOSCH-GEO | RF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224297 |  | Ground Water | BOSCH-GEO | RF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | Yes
215224298 |  | Ground Water | BOSCH-GEO | RF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | Yes
215224299 |  | Ground Water | BOSCH-GEO | RF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | Yes
215224300 |  | Ground Water | BOSCH-GEO | RF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | Yes
215224301 |  | Ground Water | BOSCH-GEO | RF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224302 |  | Ground Water | BOSCH-GEO | RF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224477 |  | Ground Water | FHP | CF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
216802025 |  | Ground Water | CARRIER | 50WT*070(L/M/S/T)**5*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802026 |  | Ground Water | CARRIER | 50WT*070(L/M/S/T)**5*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802027 |  | Ground Water | CARRIER | 50WT*070(G-K;N-R)**6*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802028 |  | Ground Water | CARRIER | 50WT*070(G-K;N-R)**6*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802029 |  | Ground Water | CARRIER | 50WT*070(L/M/S/T)**6*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802030 |  | Ground Water | CARRIER | 50WT*070(L/M/S/T)**6*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216979809 |  | Ground Water | CARRIER | GCA24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979810 |  | Ground Water | BRYANT | GCA24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979811 |  | Ground Water | CARRIER | GCA24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979812 |  | Ground Water | BRYANT | GCA24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979813 |  | Ground Water | CARRIER | GCA24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979814 |  | Ground Water | BRYANT | GCA24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979815 |  | Ground Water | CARRIER | GCA24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979816 |  | Ground Water | BRYANT | GCA24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
211594118 |  | Ground Water | TRANE | GEHG006A |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
211594119 |  | Ground Water | TRANE | GEHG009A |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
211594120 |  | Ground Water | TRANE | GEHG012A |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
211594121 |  | Ground Water | TRANE | GEHG015A |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
211594122 |  | Ground Water | TRANE | GEHG018A |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
211594123 |  | Ground Water | TRANE | GEHG024A |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594124 |  | Ground Water | TRANE | GEHG030A |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594125 |  | Ground Water | TRANE | GEHG036A |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594126 |  | Ground Water | TRANE | GEHG042A |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594127 |  | Ground Water | TRANE | GEHG048A |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594128 |  | Ground Water | TRANE | GEHG060A |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
211594129 |  | Ground Water | TRANE | EXHG009A |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
211594130 |  | Ground Water | TRANE | EXHG012A |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
211594131 |  | Ground Water | TRANE | EXHG015A |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
211594132 |  | Ground Water | TRANE | EXHG018A |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
211594133 |  | Ground Water | TRANE | EXHG024A |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594134 |  | Ground Water | TRANE | EXHG030A |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594135 |  | Ground Water | TRANE | EXHG036A |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594136 |  | Ground Water | TRANE | EXHG042A |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594137 |  | Ground Water | TRANE | EXHG048A |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594138 |  | Ground Water | TRANE | EXHG060A |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594139 |  | Ground Water | TRANE | EXHG070A |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
8993504 |  | Ground Water | YORK BY JOHNSON CONTROLS | YCC/YCW/YCS/YCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
8993505 |  | Ground Water | YORK BY JOHNSON CONTROLS | YCC/YCW/YCS/YCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
9008839 |  | Ground Water | BOSCH | ES025-1CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9008840 |  | Ground Water | BOSCH | ES025-2CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9008841 |  | Ground Water | BOSCH | ES035-1CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9008842 |  | Ground Water | BOSCH | ES035-3CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9008843 |  | Ground Water | BOSCH | ES035-4CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9009353 |  | Ground Water | FHP | ES025-1CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9009366 |  | Ground Water | FHP | ES025-2CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9009369 |  | Ground Water | FHP | ES035-1CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9009382 |  | Ground Water | FHP | ES035-3CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
202921913 |  | Ground Water | BOSCH | EP036-3HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921914 |  | Ground Water | BOSCH | EP036-4HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921915 |  | Ground Water | BOSCH-GEO | BP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921952 |  | Ground Water | FHP | EP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921953 |  | Ground Water | FHP | EP036-3HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921954 |  | Ground Water | FHP | EP036-4HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921956 |  | Ground Water | BOSCH | BP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202921957 |  | Ground Water | FHP | EP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921958 |  | Ground Water | FHP | EP036-3VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921959 |  | Ground Water | FHP | EP036-4VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921960 |  | Ground Water | BOSCH | BP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922686 |  | Ground Water | CARRIER | 50PSH036***3/CA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922689 |  | Ground Water | CARRIER | 50PSH036***5/EA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922692 |  | Ground Water | CARRIER | 50PSH036***6/FA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922695 |  | Ground Water | CARRIER | GB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
207349388 |  | Ground Water | WaterFurnace | NBV/NBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349389 |  | Ground Water | WaterFurnace | NBV/NBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349390 |  | Ground Water | WaterFurnace | NBV/NBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349391 |  | Ground Water | WaterFurnace | NBV/NBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349392 |  | Ground Water | WaterFurnace | NBV/NBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349393 |  | Ground Water | WaterFurnace | NBV/NBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349394 |  | Ground Water | WaterFurnace | NBV/NBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349395 |  | Ground Water | WaterFurnace | NBV/NBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349396 |  | Ground Water | WaterFurnace | NBV/NBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349397 |  | Ground Water | WaterFurnace | NBV/NBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349398 |  | Ground Water | WaterFurnace | NBV/NBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349399 |  | Ground Water | WaterFurnace | NBV/NBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349400 |  | Ground Water | WaterFurnace | NBV/NBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349401 |  | Ground Water | WaterFurnace | NBV/NBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349402 |  | Ground Water | WaterFurnace | NBV/NBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349403 |  | Ground Water | WaterFurnace | NBV/NBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349404 |  | Ground Water | WaterFurnace | NBV/NBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349405 |  | Ground Water | WaterFurnace | NBV/NBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349406 |  | Ground Water | WaterFurnace | NBV/NBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349407 |  | Ground Water | WaterFurnace | NBV/NBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349408 |  | Ground Water | WaterFurnace | NBV/NBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349409 |  | Ground Water | WaterFurnace | NBV/NBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349410 |  | Ground Water | WaterFurnace | NBV/NBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349411 |  | Ground Water | WaterFurnace | NBV/NBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349412 |  | Ground Water | WaterFurnace | NBV/NBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207530615 |  | Ground Water | BOSCH | CA009-1*C-*****D |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
207542447 |  | Ground Water | FHP | CA009-1*C-*****D |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
207549518 |  | Ground Water | CARRIER | 50PEC09***E3/CF |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
218471794 |  | Ground Water | YORK | QD012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | Yes
218471795 |  | Ground Water | YORK | QD012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | Yes
218471796 |  | Ground Water | YORK | QD015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | Yes
218471797 |  | Ground Water | YORK | QD015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | Yes
218471798 |  | Ground Water | YORK | QD018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
218471799 |  | Ground Water | YORK | QD018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
218471830 |  | Ground Water | YORK | QQ024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
218471831 |  | Ground Water | YORK | AQ024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218471832 |  | Ground Water | YORK | AQ024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218471833 |  | Ground Water | YORK | QQ024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
218471834 |  | Ground Water | YORK | AQ024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218471835 |  | Ground Water | YORK | AQ024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218471836 |  | Ground Water | YORK | QQ024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
218471837 |  | Ground Water | YORK | AQ024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216625485 |  | Ground Water | GEOSTAR | G5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625486 |  | Ground Water | GEOSTAR | G5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625487 |  | Ground Water | GEOSTAR | G5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625488 |  | Ground Water | GEOSTAR | G5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625489 |  | Ground Water | GEOSTAR | G5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625490 |  | Ground Water | GEOSTAR | G5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625491 |  | Ground Water | GEOSTAR | G5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625492 |  | Ground Water | GEOSTAR | G5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625493 |  | Ground Water | GEOSTAR | G5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625494 |  | Ground Water | GEOSTAR | G5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625495 |  | Ground Water | GEOSTAR | G5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625496 |  | Ground Water | GEOSTAR | G5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625497 |  | Ground Water | GEOSTAR | G5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625498 |  | Ground Water | GEOSTAR | G5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625499 |  | Ground Water | GEOSTAR | G5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625500 |  | Ground Water | GEOSTAR | G5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625501 |  | Ground Water | GEOSTAR | G5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625502 |  | Ground Water | GEOSTAR | G5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625503 |  | Ground Water | GEOSTAR | G5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625504 |  | Ground Water | GEOSTAR | G5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625505 |  | Ground Water | GEOSTAR | G5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625506 |  | Ground Water | GEOSTAR | G5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625507 |  | Ground Water | GEOSTAR | G5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
3706370 |  | Ground Water | GEOSTAR | ZS018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3706371 |  | Ground Water | GEOSTAR | ZS023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706373 |  | Ground Water | GEOSTAR | ZS023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706374 |  | Ground Water | GEOSTAR | ZS023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706375 |  | Ground Water | GEOSTAR | ZS023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706376 |  | Ground Water | GEOSTAR | ZS024**0*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706377 |  | Ground Water | GEOSTAR | ZS024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706378 |  | Ground Water | GEOSTAR | ZS024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706379 |  | Ground Water | GEOSTAR | ZS024**4*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706380 |  | Ground Water | GEOSTAR | ZS030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706381 |  | Ground Water | GEOSTAR | ZS030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706382 |  | Ground Water | GEOSTAR | ZS030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706383 |  | Ground Water | GEOSTAR | ZS030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706384 |  | Ground Water | GEOSTAR | ZS036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706385 |  | Ground Water | GEOSTAR | ZS036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706387 |  | Ground Water | GEOSTAR | ZS036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706391 |  | Ground Water | GEOSTAR | ZS042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706392 |  | Ground Water | GEOSTAR | ZS042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706393 |  | Ground Water | GEOSTAR | ZS042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706394 |  | Ground Water | GEOSTAR | ZS048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3706395 |  | Ground Water | GEOSTAR | ZS048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3706396 |  | Ground Water | GEOSTAR | ZS048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3811671 |  | Ground Water | WaterFurnace | USV/USH024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3811673 |  | Ground Water | WaterFurnace | USV/USH024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4504310 |  | Ground Water | BOSCH-GEO | BP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
4509712 |  | Ground Water | BOSCH-GEO | BP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
4510474 |  | Ground Water | BOSCH-GEO | BP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
4651271 |  | Ground Water | WaterFurnace | USH023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651272 |  | Ground Water | WaterFurnace | USH023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651273 |  | Ground Water | WaterFurnace | USH023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651274 |  | Ground Water | WaterFurnace | USH023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651339 |  | Ground Water | WaterFurnace | USV/USH024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651340 |  | Ground Water | WaterFurnace | USV/USH024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651341 |  | Ground Water | WaterFurnace | USV/USH024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651342 |  | Ground Water | WaterFurnace | USV/USH024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651403 |  | Ground Water | WaterFurnace | USV/USH030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651404 |  | Ground Water | WaterFurnace | USV/USH030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
215429175 |  | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
8738042 |  | Ground Water | TETCO | TVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
8738051 |  | Ground Water | GEOCOMFORT | GVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738052 |  | Ground Water | HYDRON MODULE | HVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738053 |  | Ground Water | TETCO | TVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738054 |  | Ground Water | GEOCOMFORT | GVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738055 |  | Ground Water | HYDRON MODULE | HVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738056 |  | Ground Water | TETCO | TVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738057 |  | Ground Water | GEOCOMFORT | GVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738058 |  | Ground Water | HYDRON MODULE | HVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738059 |  | Ground Water | TETCO | TVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738060 |  | Ground Water | GEOCOMFORT | GVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738061 |  | Ground Water | HYDRON MODULE | HVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738062 |  | Ground Water | TETCO | TVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738067 |  | Ground Water | GEOCOMFORT | GVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
8738068 |  | Ground Water | HYDRON MODULE | HVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
8738069 |  | Ground Water | TETCO | TVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
8738070 |  | Ground Water | GEOCOMFORT | GVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738071 |  | Ground Water | HYDRON MODULE | HVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738072 |  | Ground Water | TETCO | TVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738073 |  | Ground Water | GEOCOMFORT | GVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
214839122 |  | Ground Water | FHP | CL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839123 |  | Ground Water | FHP | CL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839124 |  | Ground Water | FHP | CL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839125 |  | Ground Water | FHP | CL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839126 |  | Ground Water | FHP | CL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839127 |  | Ground Water | FHP | CL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
216714645 |  | Ground Water | GEOSTAR | G3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714646 |  | Ground Water | GEOSTAR | G3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714647 |  | Ground Water | GEOSTAR | G3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714648 |  | Ground Water | GEOSTAR | G3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714649 |  | Ground Water | GEOSTAR | G3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714656 |  | Ground Water | GEOSTAR | G3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714657 |  | Ground Water | GEOSTAR | G3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714658 |  | Ground Water | GEOSTAR | G3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714659 |  | Ground Water | GEOSTAR | G3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714660 |  | Ground Water | GEOSTAR | G3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714661 |  | Ground Water | GEOSTAR | G3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
207335134 |  | Ground Water | GEOSTAR | 101/102J012**1*0***** |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
207335135 |  | Ground Water | GEOSTAR | 101/102J018**1*(1,4)***** |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335136 |  | Ground Water | GEOSTAR | 101/102J030**1*(1,4)***** |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335137 |  | Ground Water | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207335138 |  | Ground Water | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335139 |  | Ground Water | GEOSTAR | 101/102K048**1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335140 |  | Ground Water | GEOSTAR | 101/102K060**1*(1,4)****** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335141 |  | Ground Water | GEOSTAR | 101/102J070**1*(1,4)***** |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335142 |  | Ground Water | GEOSTAR | 101/102J026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
215268358 |  | Ground Water | WaterFurnace | V3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268359 |  | Ground Water | WaterFurnace | V3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268365 |  | Ground Water | WaterFurnace | V3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268366 |  | Ground Water | WaterFurnace | V3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268367 |  | Ground Water | WaterFurnace | V3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268368 |  | Ground Water | WaterFurnace | V3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268369 |  | Ground Water | WaterFurnace | V3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268663 |  | Ground Water | WaterFurnace | V5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
215268664 |  | Ground Water | WaterFurnace | V5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
215268665 |  | Ground Water | WaterFurnace | V5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268666 |  | Ground Water | WaterFurnace | V5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268667 |  | Ground Water | WaterFurnace | V5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268668 |  | Ground Water | WaterFurnace | V5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268669 |  | Ground Water | WaterFurnace | V5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268670 |  | Ground Water | WaterFurnace | V5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268671 |  | Ground Water | WaterFurnace | V5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268672 |  | Ground Water | WaterFurnace | V5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268673 |  | Ground Water | WaterFurnace | V5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268674 |  | Ground Water | WaterFurnace | V5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
215268675 |  | Ground Water | WaterFurnace | V5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
215268676 |  | Ground Water | WaterFurnace | V5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268677 |  | Ground Water | WaterFurnace | V5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268678 |  | Ground Water | WaterFurnace | V5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268679 |  | Ground Water | WaterFurnace | V5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268680 |  | Ground Water | WaterFurnace | V5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268681 |  | Ground Water | WaterFurnace | V5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268682 |  | Ground Water | WaterFurnace | V5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268683 |  | Ground Water | WaterFurnace | V5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268684 |  | Ground Water | WaterFurnace | V5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268685 |  | Ground Water | WaterFurnace | V5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268686 |  | Ground Water | WaterFurnace | V5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268687 |  | Ground Water | WaterFurnace | V5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268688 |  | Ground Water | WaterFurnace | V5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268689 |  | Ground Water | WaterFurnace | V5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268690 |  | Ground Water | WaterFurnace | V5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268691 |  | Ground Water | WaterFurnace | V5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268692 |  | Ground Water | WaterFurnace | V5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268693 |  | Ground Water | WaterFurnace | V5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268694 |  | Ground Water | WaterFurnace | V5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268695 |  | Ground Water | WaterFurnace | V5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268696 |  | Ground Water | WaterFurnace | V5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268697 |  | Ground Water | WaterFurnace | V5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268698 |  | Ground Water | WaterFurnace | V5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268699 |  | Ground Water | WaterFurnace | V5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268700 |  | Ground Water | WaterFurnace | V5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268701 |  | Ground Water | WaterFurnace | V5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
217351787 |  | Ground Water | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351788 |  | Ground Water | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
202147015 |  | Ground Water | TETCO | TZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147016 |  | Ground Water | TETCO | TZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147017 |  | Ground Water | TETCO | TZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147018 |  | Ground Water | GEOCOMFORT | GZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147019 |  | Ground Water | GEOCOMFORT | GZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147020 |  | Ground Water | GEOCOMFORT | GZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147021 |  | Ground Water | GEOCOMFORT | GZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147022 |  | Ground Water | GEOCOMFORT | GZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147023 |  | Ground Water | GEOCOMFORT | GZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147024 |  | Ground Water | HYDRON MODULE | HZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147025 |  | Ground Water | HYDRON MODULE | HZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147026 |  | Ground Water | HYDRON MODULE | HZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147027 |  | Ground Water | HYDRON MODULE | HZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147028 |  | Ground Water | HYDRON MODULE | HZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147029 |  | Ground Water | HYDRON MODULE | HZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147030 |  | Ground Water | TETCO | TZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147031 |  | Ground Water | TETCO | TZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147032 |  | Ground Water | TETCO | TZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147033 |  | Ground Water | TETCO | TZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147034 |  | Ground Water | TETCO | TZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147035 |  | Ground Water | TETCO | TZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147036 |  | Ground Water | GEOCOMFORT | GZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147037 |  | Ground Water | GEOCOMFORT | GZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147038 |  | Ground Water | GEOCOMFORT | GZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147039 |  | Ground Water | GEOCOMFORT | GZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147040 |  | Ground Water | GEOCOMFORT | GZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
202147041 |  | Ground Water | GEOCOMFORT | GZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147042 |  | Ground Water | GEOCOMFORT | GZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147043 |  | Ground Water | HYDRON MODULE | HZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147044 |  | Ground Water | HYDRON MODULE | HZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147045 |  | Ground Water | HYDRON MODULE | HZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147046 |  | Ground Water | HYDRON MODULE | HZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147047 |  | Ground Water | HYDRON MODULE | HZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
202147048 |  | Ground Water | HYDRON MODULE | HZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147049 |  | Ground Water | HYDRON MODULE | HZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147050 |  | Ground Water | TETCO | TZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147051 |  | Ground Water | TETCO | TZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147052 |  | Ground Water | TETCO | TZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147053 |  | Ground Water | TETCO | TZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147054 |  | Ground Water | TETCO | TZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
202147055 |  | Ground Water | TETCO | TZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147056 |  | Ground Water | TETCO | TZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
206722530 |  | Ground Water | ClimateMaster | TRH/V006A*W/K |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
206726680 |  | Ground Water | WaterFurnace | UVV/UVH024**0*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
206726691 |  | Ground Water | WaterFurnace | UVV/UVH024**3*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
206726692 |  | Ground Water | WaterFurnace | UVV/UVH024**4*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
206726812 |  | Ground Water | GEOCOMFORT | GBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726813 |  | Ground Water | GEOCOMFORT | GBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726814 |  | Ground Water | HYDRON MODULE | HBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726815 |  | Ground Water | HYDRON MODULE | HBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726816 |  | Ground Water | TETCO | TBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726817 |  | Ground Water | TETCO | TBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726818 |  | Ground Water | GEOCOMFORT | GBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726819 |  | Ground Water | GEOCOMFORT | GBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726820 |  | Ground Water | HYDRON MODULE | HBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726821 |  | Ground Water | HYDRON MODULE | HBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726822 |  | Ground Water | TETCO | TBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726823 |  | Ground Water | TETCO | TBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726824 |  | Ground Water | GEOCOMFORT | GBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
206726825 |  | Ground Water | GEOCOMFORT | GBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726826 |  | Ground Water | HYDRON MODULE | HBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
218157883 |  | Ground Water | YORK | Y5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
218157884 |  | Ground Water | YORK | Y5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
218157885 |  | Ground Water | YORK | Y5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
218157886 |  | Ground Water | YORK | Y5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
218157887 |  | Ground Water | YORK | Y5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
218157888 |  | Ground Water | YORK | Y5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
218157889 |  | Ground Water | YORK | Y5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
218157890 |  | Ground Water | YORK | Y5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
218157891 |  | Ground Water | YORK | Y3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
218157896 |  | Ground Water | YORK | Y5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
218157897 |  | Ground Water | YORK | Y5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
218157898 |  | Ground Water | YORK | Y5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
218157899 |  | Ground Water | YORK | Y5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
218157900 |  | Ground Water | YORK | Y5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
218157901 |  | Ground Water | YORK | Y5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
218157902 |  | Ground Water | YORK | Y5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
218471584 |  | Ground Water | YORK | AE072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218471585 |  | Ground Water | YORK | AE072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218471586 |  | Ground Water | YORK | AE096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
218471587 |  | Ground Water | YORK | AE096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
201756620 |  | Ground Water | NORTHERN HEAT PUMP | RA-VE-041-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
201756621 |  | Ground Water | NORTHSTAR SERIES | RA-VE-041-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
201756622 |  | Ground Water | NORTHERN HEAT PUMP | RA-VE-053-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
201756623 |  | Ground Water | NORTHSTAR SERIES | RA-VE-053-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
201864513 |  | Ground Water | GEOCOMFORT | GZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864514 |  | Ground Water | HYDRON MODULE | HZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864515 |  | Ground Water | TETCO | TZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864519 |  | Ground Water | GEOCOMFORT | GZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864521 |  | Ground Water | HYDRON MODULE | HZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864523 |  | Ground Water | TETCO | TZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201907610 |  | Ground Water | WaterFurnace | URS036*0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907611 |  | Ground Water | WaterFurnace | URS036*0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907612 |  | Ground Water | WaterFurnace | URS036*0*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907613 |  | Ground Water | WaterFurnace | URS036*3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
217642915 |  | Ground Water | GeoSmart Energy | S3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642916 |  | Ground Water | GeoSmart Energy | S3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642917 |  | Ground Water | GeoSmart Energy | S3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642918 |  | Ground Water | GeoSmart Energy | S3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642919 |  | Ground Water | GeoSmart Energy | S3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642920 |  | Ground Water | GeoSmart Energy | S3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642921 |  | Ground Water | GeoSmart Energy | S3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642922 |  | Ground Water | GeoSmart Energy | S3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642928 |  | Ground Water | GeoSmart Energy | S3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642929 |  | Ground Water | GeoSmart Energy | S3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642930 |  | Ground Water | GeoSmart Energy | S3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642931 |  | Ground Water | GeoSmart Energy | S3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642932 |  | Ground Water | GeoSmart Energy | S3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
7414470 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414553 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414651 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414828 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414896 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415098 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415209 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7415301 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415373 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415455 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7415878 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416559 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416688 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7416782 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416889 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416979 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7417060 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417146 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417250 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7417329 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417419 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417586 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417698 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417776 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417867 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417918 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417992 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418047 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418154 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418286 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418360 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418435 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418524 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418635 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418715 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418803 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418887 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418965 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7419110 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7419218 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419321 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419403 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419473 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419527 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419618 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419681 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419733 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419797 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7420917 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7421327 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421397 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421438 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421969 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421970 |  | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
216014181 |  | Ground Water | RHEEM | RPVV/H/D036D |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
216054107 |  | Ground Water | WaterFurnace | W5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216054108 |  | Ground Water | WaterFurnace | W5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216054109 |  | Ground Water | WaterFurnace | W5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216054110 |  | Ground Water | WaterFurnace | W5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216054475 |  | Ground Water | GEOCOMFORT | GBS018* | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
216054476 |  | Ground Water | GEOCOMFORT | GBT024* | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
216054477 |  | Ground Water | GEOCOMFORT | GBT036* | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
216054478 |  | Ground Water | GEOCOMFORT | GBT048* | EAD048 | 51500 | 22.5 | 51300 | 4.5 | 4.2917 | Yes
216054479 |  | Ground Water | GEOCOMFORT | GVS009* |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
216054480 |  | Ground Water | GEOCOMFORT | GVS012* |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
216054481 |  | Ground Water | GEOCOMFORT | GVS018* |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
218353008 |  | Ground Water | SKYMARK | PA042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353012 |  | Ground Water | SKYMARK | PA042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353016 |  | Ground Water | SKYMARK | PA042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353020 |  | Ground Water | SKYMARK | PA042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218338474 |  | Ground Water | GeoSmart Energy | S5C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
218338478 |  | Ground Water | GeoSmart Energy | S5C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215268740 |  | Ground Water | WaterFurnace | V5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268741 |  | Ground Water | WaterFurnace | V5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268742 |  | Ground Water | WaterFurnace | V5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268743 |  | Ground Water | WaterFurnace | V5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268744 |  | Ground Water | WaterFurnace | V5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268745 |  | Ground Water | WaterFurnace | V5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268746 |  | Ground Water | WaterFurnace | V5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268747 |  | Ground Water | WaterFurnace | V5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268748 |  | Ground Water | WaterFurnace | V5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268749 |  | Ground Water | WaterFurnace | V5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268750 |  | Ground Water | WaterFurnace | V5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268751 |  | Ground Water | WaterFurnace | V5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268752 |  | Ground Water | WaterFurnace | V5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268753 |  | Ground Water | WaterFurnace | V5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268754 |  | Ground Water | WaterFurnace | V5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268755 |  | Ground Water | WaterFurnace | V5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268756 |  | Ground Water | WaterFurnace | V5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268757 |  | Ground Water | WaterFurnace | V5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216979888 |  | Ground Water | TEMPSTAR | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979889 |  | Ground Water | COMFORTMAKER | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979890 |  | Ground Water | DAY & NIGHT | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979891 |  | Ground Water | HEIL | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979892 |  | Ground Water | ARCOAIRE | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979893 |  | Ground Water | KEEPRITE | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979894 |  | Ground Water | TEMPSTAR | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979895 |  | Ground Water | COMFORTMAKER | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979896 |  | Ground Water | DAY & NIGHT | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
217014524 |  | Ground Water | CARRIER | GCA72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014525 |  | Ground Water | BRYANT | GCA72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014526 |  | Ground Water | CARRIER | GCA72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014527 |  | Ground Water | BRYANT | GCA72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014528 |  | Ground Water | CARRIER | GCA72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014529 |  | Ground Water | BRYANT | GCA72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014530 |  | Ground Water | CARRIER | GCA72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014531 |  | Ground Water | BRYANT | GCA72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014532 |  | Ground Water | HEIL | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014533 |  | Ground Water | ARCOAIRE | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014534 |  | Ground Water | KEEPRITE | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014535 |  | Ground Water | TEMPSTAR | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014536 |  | Ground Water | COMFORTMAKER | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014537 |  | Ground Water | DAY & NIGHT | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014538 |  | Ground Water | HEIL | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014539 |  | Ground Water | ARCOAIRE | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014540 |  | Ground Water | KEEPRITE | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014541 |  | Ground Water | TEMPSTAR | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014542 |  | Ground Water | COMFORTMAKER | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014543 |  | Ground Water | DAY & NIGHT | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014544 |  | Ground Water | HEIL | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014545 |  | Ground Water | ARCOAIRE | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014546 |  | Ground Water | KEEPRITE | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014547 |  | Ground Water | TEMPSTAR | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014548 |  | Ground Water | COMFORTMAKER | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014549 |  | Ground Water | DAY & NIGHT | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
215743134 |  | Ground Water | TRANE | GECK006 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743135 |  | Ground Water | TRANE | GECK009 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743136 |  | Ground Water | TRANE | GECK012 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
215743520 |  | Ground Water | TRANE | GECK0062 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743521 |  | Ground Water | TRANE | GECK0067 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743522 |  | Ground Water | TRANE | GECK0092 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743523 |  | Ground Water | TRANE | GECK0097 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743524 |  | Ground Water | TRANE | GECK0122 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
215743525 |  | Ground Water | TRANE | GECK0127 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
215746915 |  | Ground Water | TRANE | GSK036A3 |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746916 |  | Ground Water | TRANE | GSK048A3 |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746918 |  | Ground Water | TRANE | GSK060A3 |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746919 |  | Ground Water | TRANE | GSK072A3 |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746920 |  | Ground Water | TRANE | GSK090A3 |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
215746921 |  | Ground Water | TRANE | GSK102A3 |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
215746923 |  | Ground Water | TRANE | GSK036A4 |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746924 |  | Ground Water | TRANE | GSK036AW |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746925 |  | Ground Water | TRANE | GSK048A4 |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746926 |  | Ground Water | TRANE | GSK048AW |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746927 |  | Ground Water | TRANE | GSK060A4 |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746928 |  | Ground Water | TRANE | GSK060AW |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746929 |  | Ground Water | TRANE | GSK072A4 |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746930 |  | Ground Water | TRANE | GSK072AW |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746931 |  | Ground Water | TRANE | GSK090A4 |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
215746932 |  | Ground Water | TRANE | GSK090AW |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
215746933 |  | Ground Water | TRANE | GSK102A4 |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
215746934 |  | Ground Water | TRANE | GSK102AW |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
218471911 |  | Ground Water | YORK | AZ060-1CSC-*****A | JDE60F5XX2DS1 | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
218471912 |  | Ground Water | YORK | AZ060-1CSN-*****A | JDE60F5XX2DS1 | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
218471913 |  | Ground Water | YORK | QZ060-1CSC-*****A | JDE60F5XX2DS1 | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
218471914 |  | Ground Water | YORK | QZ060-1CSN-*****A | JDE60F5XX2DS1 | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
218471921 |  | Ground Water | YORK | AE072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
218471922 |  | Ground Water | YORK | AE096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
207177429 |  | Ground Water | TRANE | GEVG006A |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
207177430 |  | Ground Water | TRANE | GEVG0067 |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
207177431 |  | Ground Water | TRANE | GEVG009A |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
207177432 |  | Ground Water | TRANE | GEVG0097 |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
207177433 |  | Ground Water | TRANE | GEVG012A |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
207177434 |  | Ground Water | TRANE | GEVG0127 |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
207177435 |  | Ground Water | TRANE | GEVG015A |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
207177447 |  | Ground Water | TRANE | GEVG036A |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177448 |  | Ground Water | TRANE | GEVG036B |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177449 |  | Ground Water | TRANE | GEVG0364 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177450 |  | Ground Water | TRANE | GEVG0367 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177451 |  | Ground Water | TRANE | GEVG042A |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177452 |  | Ground Water | TRANE | GEVG042B |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177453 |  | Ground Water | TRANE | GEVG0424 |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177454 |  | Ground Water | TRANE | GEVG048A |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177455 |  | Ground Water | TRANE | GEVG048B |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177456 |  | Ground Water | TRANE | GEVG0484 |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177457 |  | Ground Water | TRANE | GEVG060A |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
207177458 |  | Ground Water | TRANE | GEVG060B |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
207177459 |  | Ground Water | TRANE | GEVG0604 |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
207177460 |  | Ground Water | TRANE | EXVG009A |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
207177461 |  | Ground Water | TRANE | EXVG0097 |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
207177462 |  | Ground Water | TRANE | EXVG012A |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
207177463 |  | Ground Water | TRANE | EXVG0127 |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
207177464 |  | Ground Water | TRANE | EXVG015A |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
207177465 |  | Ground Water | TRANE | EXVG0157 |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
207177466 |  | Ground Water | TRANE | EXVG018A |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
207177467 |  | Ground Water | TRANE | EXVG0187 |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
207177468 |  | Ground Water | TRANE | EXVG024A |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177469 |  | Ground Water | TRANE | EXVG024B |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177470 |  | Ground Water | TRANE | EXVG0244 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177471 |  | Ground Water | TRANE | EXVG0247 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177472 |  | Ground Water | TRANE | EXVG030A |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177473 |  | Ground Water | TRANE | EXVG030B |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177474 |  | Ground Water | TRANE | EXVG0304 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177475 |  | Ground Water | TRANE | EXVG0307 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177476 |  | Ground Water | TRANE | EXVG036A |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177477 |  | Ground Water | TRANE | EXVG036B |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177478 |  | Ground Water | TRANE | EXVG0364 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177479 |  | Ground Water | TRANE | EXVG0367 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177480 |  | Ground Water | TRANE | EXVG042A |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177481 |  | Ground Water | TRANE | EXVG042B |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177482 |  | Ground Water | TRANE | EXVG0424 |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177483 |  | Ground Water | TRANE | EXVG048A |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177484 |  | Ground Water | TRANE | EXVG048B |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177485 |  | Ground Water | TRANE | EXVG0484 |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177486 |  | Ground Water | TRANE | EXVG060A |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177487 |  | Ground Water | TRANE | EXVG060B |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177488 |  | Ground Water | TRANE | EXVG0604 |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177489 |  | Ground Water | TRANE | EXVG070A |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177490 |  | Ground Water | TRANE | EXVG070B |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177491 |  | Ground Water | TRANE | EXVG0704 |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177492 |  | Ground Water | TRANE | DXVG024A |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177493 |  | Ground Water | TRANE | DXVG024B |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177494 |  | Ground Water | TRANE | DXVG0244 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177495 |  | Ground Water | TRANE | DXVG0247 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177496 |  | Ground Water | TRANE | DXVG036A |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177497 |  | Ground Water | TRANE | DXVG036B |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177498 |  | Ground Water | TRANE | DXVG0364 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177499 |  | Ground Water | TRANE | DXVG0367 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177500 |  | Ground Water | TRANE | DXVG048A |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
207177501 |  | Ground Water | TRANE | DXVG048B |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
207177502 |  | Ground Water | TRANE | DXVG0484 |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
202146914 |  | Ground Water | GEOCOMFORT | GZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146915 |  | Ground Water | GEOCOMFORT | GZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146916 |  | Ground Water | HYDRON MODULE | HZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
202146917 |  | Ground Water | HYDRON MODULE | HZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146918 |  | Ground Water | HYDRON MODULE | HZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146919 |  | Ground Water | TETCO | TZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
202146920 |  | Ground Water | TETCO | TZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146921 |  | Ground Water | TETCO | TZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146922 |  | Ground Water | GEOCOMFORT | GZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
202146923 |  | Ground Water | GEOCOMFORT | GZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146924 |  | Ground Water | GEOCOMFORT | GZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
202146925 |  | Ground Water | GEOCOMFORT | GZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
202146926 |  | Ground Water | HYDRON MODULE | HZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
202146927 |  | Ground Water | HYDRON MODULE | HZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146928 |  | Ground Water | HYDRON MODULE | HZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
202146929 |  | Ground Water | HYDRON MODULE | HZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
202146930 |  | Ground Water | TETCO | TZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
202146931 |  | Ground Water | TETCO | TZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146932 |  | Ground Water | TETCO | TZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
202146933 |  | Ground Water | TETCO | TZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
202146936 |  | Ground Water | GEOCOMFORT | GZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146939 |  | Ground Water | HYDRON MODULE | HZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146942 |  | Ground Water | TETCO | TZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146943 |  | Ground Water | GEOCOMFORT | GZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146944 |  | Ground Water | GEOCOMFORT | GZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146945 |  | Ground Water | GEOCOMFORT | GZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146946 |  | Ground Water | GEOCOMFORT | GZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146947 |  | Ground Water | GEOCOMFORT | GZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
206438813 |  | Ground Water | FHP | EP012-1VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438814 |  | Ground Water | FHP | EP012-1HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438815 |  | Ground Water | FHP | EP012-1VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438816 |  | Ground Water | FHP | EP012-1HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438817 |  | Ground Water | FHP | EP012-0VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438818 |  | Ground Water | FHP | EP012-2VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438819 |  | Ground Water | FHP | EP012-0HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438820 |  | Ground Water | FHP | EP012-2HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438821 |  | Ground Water | FHP | EP012-0VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438822 |  | Ground Water | FHP | EP012-2VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438823 |  | Ground Water | FHP | EP012-0HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438824 |  | Ground Water | FHP | EP012-2HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438869 |  | Ground Water | CARRIER | 50PSH/V007***4/DA* |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438870 |  | Ground Water | CARRIER | 50PSH/V007***3/CA* |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438871 |  | Ground Water | CARRIER | 50PSH/V009***3/CA* |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438872 |  | Ground Water | CARRIER | 50PSH/V009***4/DA* |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438873 |  | Ground Water | CARRIER | 50PSH/V012***3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438874 |  | Ground Water | CARRIER | 50PSH/V015***3/CA* |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438875 |  | Ground Water | CARRIER | 50PSH/V015***4/DA* |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438876 |  | Ground Water | CARRIER | 50PSH/V030***4/DA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438877 |  | Ground Water | CARRIER | 50PSH/V030***6/FA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438878 |  | Ground Water | CARRIER | 50PSH/V030***5/EA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438879 |  | Ground Water | CARRIER | 50PSH/V030***3/CA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438880 |  | Ground Water | CARRIER | 50PSH/V060***6/FA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438881 |  | Ground Water | CARRIER | 50PSH/V060***5/EA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438882 |  | Ground Water | CARRIER | 50PSH/V060***3/CA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438883 |  | Ground Water | CARRIER | 50PSH/V070***3/CA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438884 |  | Ground Water | CARRIER | 50PSH/V070***5/EA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438885 |  | Ground Water | CARRIER | 50PSH/V070***6/FA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
8714940 |  | Ground Water | CARRIER | GZ024******1**1 | FE/V***F003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8714941 |  | Ground Water | BRYANT | GZ024******1*X1 | FE/V***F003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
205311951 |  | Ground Water | GEOSTAR | ZBV/ZBH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
205311952 |  | Ground Water | GEOSTAR | ZBV/ZBH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
205311983 |  | Ground Water | GEOSTAR | ZBV/ZBH030**0*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311984 |  | Ground Water | GEOSTAR | ZBV/ZBH030**2*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311985 |  | Ground Water | GEOSTAR | ZBV/ZBH030**3*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311986 |  | Ground Water | GEOSTAR | ZBV/ZBH030**4*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311987 |  | Ground Water | GEOSTAR | ZBV/ZBH030**0*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311988 |  | Ground Water | GEOSTAR | ZBV/ZBH030**2*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311989 |  | Ground Water | GEOSTAR | ZBV/ZBH030**3*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311990 |  | Ground Water | GEOSTAR | ZBV/ZBH030**4*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
214063737 |  | Ground Water | GeoSmart Energy | GBV/GBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
214063738 |  | Ground Water | GeoSmart Energy | GBV/GBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
218433695 |  | Ground Water | BOSCH-GEO | CP024-1CSC-*****A | BIVB-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
218433696 |  | Ground Water | BOSCH-GEO | CP024-1CSN-*****A | BIVB-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
218433697 |  | Ground Water | BOSCH-GEO | CP036-1CSC-*****A | BIVB-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
218433698 |  | Ground Water | BOSCH-GEO | CP036-1CSN-*****A | BIVB-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
218433699 |  | Ground Water | BOSCH-GEO | CP048-1CSC-*****A | BIVB-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
218433700 |  | Ground Water | BOSCH-GEO | CP048-1CSN-*****A | BIVB-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
218433701 |  | Ground Water | BOSCH-GEO | CP060-1CSC-*****A | BIVB-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
218433702 |  | Ground Water | BOSCH-GEO | CP060-1CSN-*****A | BIVB-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
218433703 |  | Ground Water | BOSCH-GEO | RP024-1CSC-*****A | BIVB-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
218433704 |  | Ground Water | BOSCH-GEO | RP024-1CSN-*****A | BIVB-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
218433705 |  | Ground Water | BOSCH-GEO | RP036-1CSC-*****A | BIVB-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
218433706 |  | Ground Water | BOSCH-GEO | RP036-1CSN-*****A | BIVB-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
218433707 |  | Ground Water | BOSCH-GEO | RP048-1CSC-*****A | BIVB-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
218433708 |  | Ground Water | BOSCH-GEO | RP048-1CSN-*****A | BIVB-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
218433709 |  | Ground Water | BOSCH-GEO | RP060-1CSC-*****A | BIVB-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
218433710 |  | Ground Water | BOSCH-GEO | RP060-1CSN-*****A | BIVB-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
218433932 |  | Ground Water | BOSCH | RP024-1CSC-*****A | BIVB-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
218433933 |  | Ground Water | BOSCH | RP024-1CSN-*****A | BIVB-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
218433934 |  | Ground Water | BOSCH | RP036-1CSC-*****A | BIVB-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
218433935 |  | Ground Water | BOSCH | RP036-1CSN-*****A | BIVB-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
218433936 |  | Ground Water | BOSCH | RP048-1CSC-*****A | BIVB-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
218433937 |  | Ground Water | BOSCH | RP048-1CSN-*****A | BIVB-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
218433938 |  | Ground Water | BOSCH | RP060-1CSC-*****A | BIVB-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
218433939 |  | Ground Water | BOSCH | RP060-1CSN-*****A | BIVB-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
218433940 |  | Ground Water | BOSCH | CP024-1CSC-*****A | BIVB-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
218433941 |  | Ground Water | BOSCH | CP024-1CSN-*****A | BIVB-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
218433942 |  | Ground Water | BOSCH | CP036-1CSC-*****A | BIVB-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
218433943 |  | Ground Water | BOSCH | CP036-1CSN-*****A | BIVB-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
218433944 |  | Ground Water | BOSCH | CP048-1CSC-*****A | BIVB-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
218433945 |  | Ground Water | BOSCH | CP048-1CSN-*****A | BIVB-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
218433946 |  | Ground Water | BOSCH | CP060-1CSC-*****A | BIVB-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
218433947 |  | Ground Water | BOSCH | CP060-1CSN-*****A | BIVB-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
218472068 |  | Ground Water | YORK | AA042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218472069 |  | Ground Water | YORK | QA042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218472070 |  | Ground Water | YORK | AA042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218472071 |  | Ground Water | YORK | QA042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
207200602 |  | Ground Water | GeoSmart Energy | GTZ049*1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207200603 |  | Ground Water | GeoSmart Energy | GTS064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207200604 |  | Ground Water | GeoSmart Energy | GTS064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207200605 |  | Ground Water | GeoSmart Energy | GSZ036*1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207200606 |  | Ground Water | GeoSmart Energy | GSZ042*1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207200607 |  | Ground Water | GeoSmart Energy | GTZ038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207200608 |  | Ground Water | GeoSmart Energy | GTS038*1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207200609 |  | Ground Water | GeoSmart Energy | GTS038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207200613 |  | Ground Water | GeoSmart Energy | QT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
207200614 |  | Ground Water | GeoSmart Energy | VI036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
207200616 |  | Ground Water | GeoSmart Energy | VI060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
207216511 |  | Ground Water | GEOSTAR | GDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
207216512 |  | Ground Water | GEOSTAR | GDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
207216513 |  | Ground Water | GEOSTAR | GDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206347324 |  | Ground Water | COMFORT-AIRE | HEV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206347325 |  | Ground Water | CENTURY | HEV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206347960 |  | Ground Water | HYDROTECH | WSS6006*6* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
206347961 |  | Ground Water | HYDROTECH | WSS6009*6* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
206347962 |  | Ground Water | HYDROTECH | WSS6012*6* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
206347963 |  | Ground Water | HYDROTECH | WSS6015*6* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
214839280 |  | Ground Water | BOSCH | RL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839281 |  | Ground Water | BOSCH | RL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839282 |  | Ground Water | BOSCH | RL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839283 |  | Ground Water | BOSCH | RL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839284 |  | Ground Water | BOSCH | RL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839285 |  | Ground Water | BOSCH | RL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
202211066 |  | Ground Water | WaterFurnace | URT096*3*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
202262237 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202262238 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ042J1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202272873 |  | Ground Water | BOSCH-GEO | BP018-1VT*******C |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202319683 |  | Ground Water | BOSCH-GEO | SM048-1CSC-*****A | SM048-1AV*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
202324846 |  | Ground Water | WaterFurnace | UBV/UBH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
202324847 |  | Ground Water | WaterFurnace | UBV/UBH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
202326797 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202326829 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202328433 |  | Ground Water | BOSCH | SM048-1CSC-*****A | SM048-1AV*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | Yes
202328436 |  | Ground Water | BOSCH | BP018-1VT*******C |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202330436 |  | Ground Water | AAON, Inc. | RQ-003-1-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
206900557 |  | Ground Water | GEOSTAR | GDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900558 |  | Ground Water | GEOSTAR | GDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900559 |  | Ground Water | GEOSTAR | GDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900560 |  | Ground Water | GEOSTAR | GDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900561 |  | Ground Water | GEOSTAR | GDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900571 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900572 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900573 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900574 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900575 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900576 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900577 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900578 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900579 |  | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
217351720 |  | Ground Water | FHP | WT025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351721 |  | Ground Water | FHP | WT025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351730 |  | Ground Water | CARRIER | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
207348666 |  | Ground Water | WaterFurnace | URS048*3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348667 |  | Ground Water | WaterFurnace | URS048*3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348668 |  | Ground Water | WaterFurnace | URS048*3*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348669 |  | Ground Water | WaterFurnace | URS048*4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348670 |  | Ground Water | WaterFurnace | URS048*4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348671 |  | Ground Water | WaterFurnace | URS048*4*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348672 |  | Ground Water | WaterFurnace | URS070*0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348673 |  | Ground Water | WaterFurnace | URS070*0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348674 |  | Ground Water | WaterFurnace | URS070*0*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348675 |  | Ground Water | WaterFurnace | URS070*3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348676 |  | Ground Water | WaterFurnace | URS070*3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348677 |  | Ground Water | WaterFurnace | URS070*3*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348678 |  | Ground Water | WaterFurnace | URS070*4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348679 |  | Ground Water | WaterFurnace | URS070*4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348680 |  | Ground Water | WaterFurnace | URS070*4*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348681 |  | Ground Water | WaterFurnace | URS060*0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
202132024 |  | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-038-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
202132025 |  | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-050-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
202132026 |  | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-060-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
202146863 |  | Ground Water | GEOCOMFORT | GZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
202146864 |  | Ground Water | GEOCOMFORT | GZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146865 |  | Ground Water | GEOCOMFORT | GZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146866 |  | Ground Water | HYDRON MODULE | HZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
202146867 |  | Ground Water | HYDRON MODULE | HZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146868 |  | Ground Water | HYDRON MODULE | HZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146869 |  | Ground Water | TETCO | TZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
202146870 |  | Ground Water | TETCO | TZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146871 |  | Ground Water | TETCO | TZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146872 |  | Ground Water | GEOCOMFORT | GZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
202146873 |  | Ground Water | GEOCOMFORT | GZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146874 |  | Ground Water | GEOCOMFORT | GZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146875 |  | Ground Water | GEOCOMFORT | GZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146876 |  | Ground Water | HYDRON MODULE | HZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
202146877 |  | Ground Water | HYDRON MODULE | HZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146878 |  | Ground Water | HYDRON MODULE | HZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146879 |  | Ground Water | HYDRON MODULE | HZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146880 |  | Ground Water | TETCO | TZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
202146881 |  | Ground Water | TETCO | TZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146882 |  | Ground Water | TETCO | TZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146883 |  | Ground Water | TETCO | TZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146884 |  | Ground Water | GEOCOMFORT | GZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146885 |  | Ground Water | GEOCOMFORT | GZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146886 |  | Ground Water | GEOCOMFORT | GZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146887 |  | Ground Water | HYDRON MODULE | HZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146888 |  | Ground Water | HYDRON MODULE | HZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146889 |  | Ground Water | HYDRON MODULE | HZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146890 |  | Ground Water | TETCO | TZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146891 |  | Ground Water | TETCO | TZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
206438761 |  | Ground Water | BOSCH | EP012-1HZ/VT*-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438762 |  | Ground Water | BOSCH | EP015-1HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438763 |  | Ground Water | BOSCH | EP060-1HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438764 |  | Ground Water | BOSCH | EP070-1HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438779 |  | Ground Water | FHP | EP007-2HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438780 |  | Ground Water | FHP | EP007-1HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438781 |  | Ground Water | FHP | EP009-1HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438782 |  | Ground Water | FHP | EP009-2HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438783 |  | Ground Water | FHP | EP012-1HZ/VT*-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438784 |  | Ground Water | FHP | EP015-1HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438785 |  | Ground Water | FHP | EP015-2HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438786 |  | Ground Water | FHP | EP030-2HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438787 |  | Ground Water | FHP | EP030-4HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438788 |  | Ground Water | FHP | EP030-3HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
205973780 |  | Ground Water | CENTURY | HEV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205973781 |  | Ground Water | COMFORT-AIRE | HZS048B | MWG48**-B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
205973782 |  | Ground Water | CENTURY | HZS048B | MWG48**-B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
205996637 |  | Ground Water | Johnson Controls | JCH/V024A*W/K B |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205996638 |  | Ground Water | SKYMARK | JCH/V024A*W/K C |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205996643 |  | Ground Water | Johnson Controls | JEV/H/D026B B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | No
205996644 |  | Ground Water | Johnson Controls | JEV/H/D038B B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | No
205996645 |  | Ground Water | Johnson Controls | JEV/H/D049B B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | No
205996646 |  | Ground Water | Johnson Controls | JEV/H/D064B B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | No
205996647 |  | Ground Water | Johnson Controls | JEV/H/D072B B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | No
7170606 |  | Ground Water | GEOCOMFORT | GVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170607 |  | Ground Water | HYDRON MODULE | HVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170608 |  | Ground Water | TETCO | TVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170609 |  | Ground Water | GEOCOMFORT | GVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170610 |  | Ground Water | HYDRON MODULE | HVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170611 |  | Ground Water | TETCO | TVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170612 |  | Ground Water | GEOCOMFORT | GVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
7170613 |  | Ground Water | HYDRON MODULE | HVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
7170614 |  | Ground Water | TETCO | TVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
203265288 |  | Ground Water | BOSCH-GEO | SM048-1VT/CFC-*****A |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265289 |  | Ground Water | BOSCH-GEO | SM048-1VT/CFN-*****A |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265290 |  | Ground Water | BOSCH-GEO | SM048-1HZC-*****A |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265291 |  | Ground Water | BOSCH-GEO | SM048-1HZN-*****A |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265529 |  | Ground Water | BOSCH | SM048-1HZC-*****A |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265533 |  | Ground Water | BOSCH | SM048-1HZC-*****C |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265538 |  | Ground Water | BOSCH | SM048-1HZN-*****A |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265540 |  | Ground Water | BOSCH | SM048-1HZN-*****C |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265973 |  | Ground Water | CARRIER | GC048V/C**C***1**1 |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265976 |  | Ground Water | BRYANT | GC048V/C**C***1*X1 |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265980 |  | Ground Water | CARRIER | GC048V/C**N***1**1 |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265983 |  | Ground Water | BRYANT | GC048V/C**N***1*X1 |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265987 |  | Ground Water | CARRIER | GC048H**C***1**1 |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265989 |  | Ground Water | BRYANT | GC048H**C***1*X1 |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265990 |  | Ground Water | CARRIER | GC048H**N***1**1 |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265991 |  | Ground Water | BRYANT | GC048H**N***1*X1 |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203268807 |  | Ground Water | BOSCH | SM060-1HZ*******C |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
203303750 |  | Ground Water | BOSCH-GEO | CE035-1VT/HZ/CF*-*****B |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
203303751 |  | Ground Water | BOSCH-GEO | BP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303773 |  | Ground Water | BOSCH | CE035-1VT/HZ/CF*-*****B |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303774 |  | Ground Water | BOSCH | BP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303777 |  | Ground Water | CARRIER | GB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303778 |  | Ground Water | BRYANT | GB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303779 |  | Ground Water | HEIL | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303780 |  | Ground Water | ARCOAIRE | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303781 |  | Ground Water | KEEPRITE | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303782 |  | Ground Water | TEMPSTAR | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303783 |  | Ground Water | COMFORTMAKER | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303784 |  | Ground Water | DAY & NIGHT | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303785 |  | Ground Water | CARRIER | GP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
203303786 |  | Ground Water | BRYANT | GP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303787 |  | Ground Water | HEIL | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
203303788 |  | Ground Water | ARCOAIRE | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303789 |  | Ground Water | KEEPRITE | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303790 |  | Ground Water | TEMPSTAR | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303791 |  | Ground Water | COMFORTMAKER | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303792 |  | Ground Water | DAY & NIGHT | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
215415788 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)036A*VB |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415789 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)036A*VC |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
203380971 |  | Ground Water | BOSCH | EP048-4VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203380972 |  | Ground Water | BOSCH | EP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203380973 |  | Ground Water | BOSCH | EP048-3HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203380974 |  | Ground Water | BOSCH | EP048-4HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383876 |  | Ground Water | CARRIER | 50PSV018***3/CA |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383877 |  | Ground Water | CARRIER | 50PSV018***4/DA |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383878 |  | Ground Water | CARRIER | 50PSH018***3/CA |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383879 |  | Ground Water | CARRIER | 50PSH018***4/DA |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383880 |  | Ground Water | CARRIER | 50PSV042***3/CA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383881 |  | Ground Water | CARRIER | 50PSV042***5/EA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383882 |  | Ground Water | CARRIER | 50PSV042***6/FA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383883 |  | Ground Water | CARRIER | 50PSH042***3/CA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383884 |  | Ground Water | CARRIER | 50PSH042***5/EA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383885 |  | Ground Water | CARRIER | 50PSH042***6/FA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383886 |  | Ground Water | CARRIER | 50PSV048***3/CA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383887 |  | Ground Water | CARRIER | 50PSV048***5/EA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383888 |  | Ground Water | CARRIER | 50PSV048***6/FA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383889 |  | Ground Water | CARRIER | 50PSH048***3/CA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383890 |  | Ground Water | CARRIER | 50PSH048***5/EA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383891 |  | Ground Water | CARRIER | 50PSH048***6/FA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383892 |  | Ground Water | FHP | EP018-1VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383893 |  | Ground Water | FHP | EP018-2VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383894 |  | Ground Water | FHP | EP018-1HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383895 |  | Ground Water | FHP | EP018-2HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383896 |  | Ground Water | FHP | EP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383897 |  | Ground Water | FHP | EP042-3VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383898 |  | Ground Water | FHP | EP042-4VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383899 |  | Ground Water | FHP | EP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383900 |  | Ground Water | FHP | EP042-3HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383901 |  | Ground Water | FHP | EP042-4HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383902 |  | Ground Water | FHP | EP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383903 |  | Ground Water | FHP | EP048-3VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383904 |  | Ground Water | FHP | EP048-4VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383905 |  | Ground Water | FHP | EP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383906 |  | Ground Water | FHP | EP048-3HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383907 |  | Ground Water | FHP | EP048-4HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
211594212 |  | Ground Water | TRANE | DXHG024A |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594213 |  | Ground Water | TRANE | DXHG036A |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594214 |  | Ground Water | TRANE | DXHG048A |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594215 |  | Ground Water | TRANE | DXHG060A |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
211594216 |  | Ground Water | TRANE | DXHG070A |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
211594222 |  | Ground Water | TRANE | GEHG0067 |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
211594223 |  | Ground Water | TRANE | GEHG0097 |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
211594224 |  | Ground Water | TRANE | GEHG0127 |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
211594225 |  | Ground Water | TRANE | GEHG0157 |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
211594226 |  | Ground Water | TRANE | GEHG0187 |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
211594227 |  | Ground Water | TRANE | GEHG024B |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594228 |  | Ground Water | TRANE | GEHG0244 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594229 |  | Ground Water | TRANE | GEHG0247 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594230 |  | Ground Water | TRANE | GEHG030B |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594231 |  | Ground Water | TRANE | GEHG0304 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594232 |  | Ground Water | TRANE | GEHG0307 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594233 |  | Ground Water | TRANE | GEHG036B |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594234 |  | Ground Water | TRANE | GEHG0364 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594235 |  | Ground Water | TRANE | GEHG0367 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594236 |  | Ground Water | TRANE | GEHG042B |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594237 |  | Ground Water | TRANE | GEHG0424 |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594238 |  | Ground Water | TRANE | GEHG048B |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594239 |  | Ground Water | TRANE | GEHG0484 |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594240 |  | Ground Water | TRANE | GEHG060B |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
211594241 |  | Ground Water | TRANE | GEHG0604 |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
211594242 |  | Ground Water | TRANE | EXHG0097 |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
211594243 |  | Ground Water | TRANE | EXHG0127 |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
211594244 |  | Ground Water | TRANE | EXHG0157 |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
211594245 |  | Ground Water | TRANE | EXHG0187 |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
211594246 |  | Ground Water | TRANE | EXHG024B |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594247 |  | Ground Water | TRANE | EXHG0244 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594248 |  | Ground Water | TRANE | EXHG0247 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594249 |  | Ground Water | TRANE | EXHG030B |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594250 |  | Ground Water | TRANE | EXHG0304 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594251 |  | Ground Water | TRANE | EXHG0307 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594252 |  | Ground Water | TRANE | EXHG036B |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594253 |  | Ground Water | TRANE | EXHG0364 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594254 |  | Ground Water | TRANE | EXHG0367 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594255 |  | Ground Water | TRANE | EXHG042B |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594256 |  | Ground Water | TRANE | EXHG0424 |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594257 |  | Ground Water | TRANE | EXHG048B |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594258 |  | Ground Water | TRANE | EXHG0484 |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594259 |  | Ground Water | TRANE | EXHG060B |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594260 |  | Ground Water | TRANE | EXHG0604 |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594261 |  | Ground Water | TRANE | EXHG070B |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
218472162 |  | Ground Water | YORK | AK009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
218472163 |  | Ground Water | YORK | AK009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
218472164 |  | Ground Water | YORK | AQ024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218472165 |  | Ground Water | YORK | AQ024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218472166 |  | Ground Water | YORK | AQ024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218472167 |  | Ground Water | YORK | AQ024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
218472168 |  | Ground Water | YORK | AQ024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218472169 |  | Ground Water | YORK | AQ024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
218472170 |  | Ground Water | YORK | AQ024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218472171 |  | Ground Water | YORK | AQ024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
218472172 |  | Ground Water | YORK | AQ036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218472173 |  | Ground Water | YORK | AQ036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
218472174 |  | Ground Water | YORK | AQ036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218472175 |  | Ground Water | YORK | AQ036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
218472176 |  | Ground Water | YORK | AQ048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
218472177 |  | Ground Water | YORK | AQ048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
218472178 |  | Ground Water | YORK | AQ060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
218472179 |  | Ground Water | YORK | AQ060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
5295984 |  | Ground Water | WaterFurnace | NBV/NBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295985 |  | Ground Water | WaterFurnace | NBV/NBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295986 |  | Ground Water | WaterFurnace | NBV/NBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295987 |  | Ground Water | WaterFurnace | NBV/NBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295988 |  | Ground Water | WaterFurnace | NBV/NBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295989 |  | Ground Water | WaterFurnace | NBV/NBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295990 |  | Ground Water | WaterFurnace | NBV/NBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295991 |  | Ground Water | WaterFurnace | NBV/NBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295992 |  | Ground Water | WaterFurnace | NBV/NBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295993 |  | Ground Water | WaterFurnace | NBV/NBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295994 |  | Ground Water | WaterFurnace | NBV/NBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295995 |  | Ground Water | WaterFurnace | NBV/NBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295996 |  | Ground Water | WaterFurnace | NBV/NBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5295997 |  | Ground Water | WaterFurnace | NBV/NBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5295998 |  | Ground Water | WaterFurnace | NBV/NBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5295999 |  | Ground Water | WaterFurnace | NBV/NBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296000 |  | Ground Water | WaterFurnace | NBV/NBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296001 |  | Ground Water | WaterFurnace | NBV/NBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296002 |  | Ground Water | WaterFurnace | NBV/NBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296003 |  | Ground Water | WaterFurnace | NBV/NBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296004 |  | Ground Water | WaterFurnace | NBV/NBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296005 |  | Ground Water | WaterFurnace | NBV/NBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296006 |  | Ground Water | WaterFurnace | NBV/NBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296007 |  | Ground Water | WaterFurnace | NBV/NBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296008 |  | Ground Water | WaterFurnace | NBV/NBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296009 |  | Ground Water | WaterFurnace | NBV/NBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296010 |  | Ground Water | WaterFurnace | NBV/NBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296011 |  | Ground Water | WaterFurnace | NBV/NBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296012 |  | Ground Water | WaterFurnace | NBV/NBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296013 |  | Ground Water | WaterFurnace | NBV/NBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296014 |  | Ground Water | WaterFurnace | NBV/NBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296015 |  | Ground Water | WaterFurnace | NBV/NBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296220 |  | Ground Water | WaterFurnace | NBV/NBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296221 |  | Ground Water | WaterFurnace | NBV/NBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296222 |  | Ground Water | WaterFurnace | NBV/NBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296223 |  | Ground Water | WaterFurnace | NBV/NBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296225 |  | Ground Water | WaterFurnace | NBV/NBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296226 |  | Ground Water | WaterFurnace | NBV/NBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296227 |  | Ground Water | WaterFurnace | NBV/NBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296228 |  | Ground Water | WaterFurnace | NBV/NBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296229 |  | Ground Water | WaterFurnace | NBV/NBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296230 |  | Ground Water | WaterFurnace | NBV/NBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5315753 |  | Ground Water | WaterFurnace | NBV/NBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315754 |  | Ground Water | WaterFurnace | NBV/NBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315755 |  | Ground Water | WaterFurnace | NBV/NBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315756 |  | Ground Water | WaterFurnace | NBV/NBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315758 |  | Ground Water | WaterFurnace | NBV/NBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315759 |  | Ground Water | WaterFurnace | NBV/NBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315760 |  | Ground Water | WaterFurnace | NBV/NBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315761 |  | Ground Water | WaterFurnace | NBV/NBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315762 |  | Ground Water | WaterFurnace | NBV/NBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315763 |  | Ground Water | WaterFurnace | NBV/NBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315774 |  | Ground Water | WaterFurnace | NBV/NBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315776 |  | Ground Water | WaterFurnace | NBV/NBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315777 |  | Ground Water | WaterFurnace | NBV/NBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315778 |  | Ground Water | WaterFurnace | NBV/NBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
215268313 |  | Ground Water | WaterFurnace | V3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
215268316 |  | Ground Water | WaterFurnace | V3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268318 |  | Ground Water | WaterFurnace | V3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268320 |  | Ground Water | WaterFurnace | V3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268321 |  | Ground Water | WaterFurnace | V3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268323 |  | Ground Water | WaterFurnace | V3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268325 |  | Ground Water | WaterFurnace | V3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
215268328 |  | Ground Water | WaterFurnace | V3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268329 |  | Ground Water | WaterFurnace | V3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268330 |  | Ground Water | WaterFurnace | V3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268334 |  | Ground Water | WaterFurnace | V3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268335 |  | Ground Water | WaterFurnace | V3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268336 |  | Ground Water | WaterFurnace | V3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268337 |  | Ground Water | WaterFurnace | V3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268338 |  | Ground Water | WaterFurnace | V3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268339 |  | Ground Water | WaterFurnace | V3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268340 |  | Ground Water | WaterFurnace | V3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268348 |  | Ground Water | WaterFurnace | V3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268349 |  | Ground Water | WaterFurnace | V3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268350 |  | Ground Water | WaterFurnace | V3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268351 |  | Ground Water | WaterFurnace | V3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268352 |  | Ground Water | WaterFurnace | V3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268353 |  | Ground Water | WaterFurnace | V3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268354 |  | Ground Water | WaterFurnace | V3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268355 |  | Ground Water | WaterFurnace | V3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268356 |  | Ground Water | WaterFurnace | V3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268357 |  | Ground Water | WaterFurnace | V3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
10271778 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10271926 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10271930 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10271959 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ022H1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10271961 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ022H1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10271981 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ030H1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10271985 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ030H1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10272006 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048H1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10272008 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048H1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
10272012 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060H1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10272014 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060H1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10272021 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ070H1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10272215 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10272216 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10272219 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10272220 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10272221 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10272222 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10272228 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10298936 |  | Ground Water | WaterFurnace | UVV/UVH036**0*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
10298937 |  | Ground Water | WaterFurnace | UVV/UVH036**3*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
10298938 |  | Ground Water | WaterFurnace | UVV/UVH036**4*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
10298941 |  | Ground Water | WaterFurnace | UVV/UVH048**0*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298942 |  | Ground Water | WaterFurnace | UVV/UVH048**3*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298943 |  | Ground Water | WaterFurnace | UVV/UVH048**4*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298944 |  | Ground Water | WaterFurnace | UVV/UVH060**0*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
10298946 |  | Ground Water | WaterFurnace | UVV/UVH060**3*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
10298947 |  | Ground Water | WaterFurnace | UVV/UVH060**4*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
10304639 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304640 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304641 |  | Ground Water | GeoSmart Energy | GTZ026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304642 |  | Ground Water | GEOSTAR | 103H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10304646 |  | Ground Water | GEOSTAR | 103H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304657 |  | Ground Water | GeoSmart Energy | GTZ026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10305457 |  | Ground Water | GEOSTAR | 104H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10305458 |  | Ground Water | GEOSTAR | 104H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316642 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316643 |  | Ground Water | GeoSmart Energy | GTS026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316644 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316645 |  | Ground Water | GeoSmart Energy | GTS026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316654 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316655 |  | Ground Water | GEOSTAR | 104H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316656 |  | Ground Water | GeoSmart Energy | GTS049*1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316657 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316658 |  | Ground Water | GeoSmart Energy | GTS049*1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316660 |  | Ground Water | GEOSTAR | 104H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
217351847 |  | Ground Water | DAY & NIGHT | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351849 |  | Ground Water | DAY & NIGHT | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351850 |  | Ground Water | DAY & NIGHT | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351851 |  | Ground Water | DAY & NIGHT | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351852 |  | Ground Water | DAY & NIGHT | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351853 |  | Ground Water | DAY & NIGHT | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351854 |  | Ground Water | DAY & NIGHT | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351855 |  | Ground Water | DAY & NIGHT | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351857 |  | Ground Water | DAY & NIGHT | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351858 |  | Ground Water | DAY & NIGHT | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351860 |  | Ground Water | DAY & NIGHT | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351862 |  | Ground Water | DAY & NIGHT | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351865 |  | Ground Water | HEIL | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351866 |  | Ground Water | HEIL | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351867 |  | Ground Water | HEIL | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351868 |  | Ground Water | HEIL | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351869 |  | Ground Water | HEIL | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351870 |  | Ground Water | HEIL | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351871 |  | Ground Water | HEIL | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351873 |  | Ground Water | HEIL | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351874 |  | Ground Water | HEIL | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351876 |  | Ground Water | HEIL | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351877 |  | Ground Water | HEIL | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351878 |  | Ground Water | HEIL | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351879 |  | Ground Water | HEIL | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351880 |  | Ground Water | HEIL | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351881 |  | Ground Water | HEIL | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351882 |  | Ground Water | HEIL | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351884 |  | Ground Water | HEIL | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351885 |  | Ground Water | HEIL | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351887 |  | Ground Water | HEIL | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351889 |  | Ground Water | HEIL | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351892 |  | Ground Water | KEEPRITE | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351893 |  | Ground Water | KEEPRITE | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351894 |  | Ground Water | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351895 |  | Ground Water | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351896 |  | Ground Water | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351897 |  | Ground Water | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351898 |  | Ground Water | KEEPRITE | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
218353275 |  | Ground Water | SKYMARK | PA042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
218353279 |  | Ground Water | SKYMARK | PA042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
208771547 |  | Ground Water | HYDROTECH | WSV6012B* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | Yes
208771548 |  | Ground Water | HYDROTECH | WSV6024B* |  | 24000 | 23 | 22000 | 4.1 | 2 | Yes
208771549 |  | Ground Water | HYDROTECH | WSV6030B* |  | 35500 | 22.5 | 30000 | 4.1 | 2.9583 | Yes
208816675 |  | Ground Water | HYDROTECH | WSHXE06A6* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
208816703 |  | Ground Water | HYDROTECH | WSHXE06A7* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
208856966 |  | Ground Water | HYDROTECH | WSV6060B* |  | 68000 | 23.8 | 53500 | 4.3 | 5.6667 | Yes
208856967 |  | Ground Water | HYDROTECH | WSV6072B* |  | 77500 | 22.6 | 66000 | 4.1 | 6.4583 | Yes
208856972 |  | Ground Water | AE Air | WSV6012B* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | Yes
208856973 |  | Ground Water | AE Air | WSV6024B* |  | 24000 | 23 | 22000 | 4.1 | 2 | Yes
208856974 |  | Ground Water | AE Air | WSV6030B* |  | 35500 | 22.5 | 30000 | 4.1 | 2.9583 | Yes
208856975 |  | Ground Water | AE Air | WSV6060B* |  | 68000 | 23.8 | 53500 | 4.3 | 5.6667 | Yes
208856976 |  | Ground Water | AE Air | WSV6072B* |  | 77500 | 22.6 | 66000 | 4.1 | 6.4583 | Yes
215415844 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415845 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415848 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415849 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415850 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415851 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415852 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415853 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415856 |  | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415857 |  | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
213154468 |  | Ground Water | GeoSmart Energy | GS036**1*1********L |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
213154469 |  | Ground Water | GeoSmart Energy | GS042**1*1********L |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
213154470 |  | Ground Water | GeoSmart Energy | GS048**1*1********L |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
213154471 |  | Ground Water | GeoSmart Energy | GS060**1*1********L |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
213154472 |  | Ground Water | GeoSmart Energy | GS070**1*1********L |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
213154473 |  | Ground Water | GeoSmart Energy | GT026**1*1********L |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
213154474 |  | Ground Water | GeoSmart Energy | GT038**1*1********L |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
213154475 |  | Ground Water | GeoSmart Energy | GT049**1*1********L |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
213154476 |  | Ground Water | GeoSmart Energy | GT064**1*1********L |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
213154477 |  | Ground Water | GeoSmart Energy | GT072**1*1********L |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
217903432 |  | Ground Water | WaterFurnace | V5R036*S3**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903433 |  | Ground Water | WaterFurnace | V5R036*S4**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903434 |  | Ground Water | WaterFurnace | V5R036*S4**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903435 |  | Ground Water | WaterFurnace | V5R036*S4**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903436 |  | Ground Water | WaterFurnace | V5R048*S3**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903437 |  | Ground Water | WaterFurnace | V5R048*S3**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903438 |  | Ground Water | WaterFurnace | V5R048*S3**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903439 |  | Ground Water | WaterFurnace | V5R048*S4**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903440 |  | Ground Water | WaterFurnace | V5R048*S4**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903441 |  | Ground Water | WaterFurnace | V5R048*S4**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903442 |  | Ground Water | WaterFurnace | V5R060*S3**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903443 |  | Ground Water | WaterFurnace | V5R060*S3**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903444 |  | Ground Water | WaterFurnace | V5R060*S3**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903445 |  | Ground Water | WaterFurnace | V5R060*S4**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903446 |  | Ground Water | WaterFurnace | V5R060*S4**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903447 |  | Ground Water | WaterFurnace | V5R060*S4**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903448 |  | Ground Water | WaterFurnace | V5R072*S3**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903449 |  | Ground Water | WaterFurnace | V5R072*S3**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903450 |  | Ground Water | WaterFurnace | V5R072*S3**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903451 |  | Ground Water | WaterFurnace | V5R072*S4**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
216727183 |  | Ground Water | BRYANT | GZ024*******1**1 | FE*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
216727185 |  | Ground Water | BRYANT | GZ036*******1**2 | FE*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
202147061 |  | Ground Water | GEOCOMFORT | GZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147062 |  | Ground Water | GEOCOMFORT | GZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147067 |  | Ground Water | HYDRON MODULE | HZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147068 |  | Ground Water | HYDRON MODULE | HZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147073 |  | Ground Water | TETCO | TZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147074 |  | Ground Water | TETCO | TZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147690 |  | Ground Water | GEOCOMFORT | GZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147691 |  | Ground Water | HYDRON MODULE | HZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147692 |  | Ground Water | TETCO | TZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147693 |  | Ground Water | TETCO | TZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202147694 |  | Ground Water | GEOCOMFORT | GZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147695 |  | Ground Water | HYDRON MODULE | HZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147696 |  | Ground Water | TETCO | TZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147697 |  | Ground Water | GEOCOMFORT | GZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147698 |  | Ground Water | HYDRON MODULE | HZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147699 |  | Ground Water | TETCO | TZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147700 |  | Ground Water | GEOCOMFORT | GZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147701 |  | Ground Water | HYDRON MODULE | HZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147702 |  | Ground Water | TETCO | TZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147703 |  | Ground Water | GEOCOMFORT | GZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147704 |  | Ground Water | GEOCOMFORT | GZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147705 |  | Ground Water | HYDRON MODULE | HZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147706 |  | Ground Water | HYDRON MODULE | HZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147707 |  | Ground Water | TETCO | TZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147708 |  | Ground Water | TETCO | TZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147709 |  | Ground Water | GEOCOMFORT | GZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147710 |  | Ground Water | HYDRON MODULE | HZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147711 |  | Ground Water | TETCO | TZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147712 |  | Ground Water | GEOCOMFORT | GZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147713 |  | Ground Water | HYDRON MODULE | HZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147714 |  | Ground Water | TETCO | TZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202211042 |  | Ground Water | WaterFurnace | URD038*0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211043 |  | Ground Water | WaterFurnace | URD038*0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211044 |  | Ground Water | WaterFurnace | URD038*0*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
205312027 |  | Ground Water | GEOSTAR | ZBV/ZBH060**0*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312028 |  | Ground Water | GEOSTAR | ZBV/ZBH060**3*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312029 |  | Ground Water | GEOSTAR | ZBV/ZBH060**4*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312030 |  | Ground Water | GEOSTAR | ZBV/ZBH060**0*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312031 |  | Ground Water | GEOSTAR | ZBV/ZBH060**3*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312032 |  | Ground Water | GEOSTAR | ZBV/ZBH060**4*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312037 |  | Ground Water | GEOSTAR | ZBV/ZBH070**0*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312038 |  | Ground Water | GEOSTAR | ZBV/ZBH070**3*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312039 |  | Ground Water | GEOSTAR | ZBV/ZBH070**4*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312040 |  | Ground Water | GEOSTAR | ZBV/ZBH070**0*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312041 |  | Ground Water | GEOSTAR | ZBV/ZBH070**3*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312042 |  | Ground Water | GEOSTAR | ZBV/ZBH070**4*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
214063791 |  | Ground Water | GeoSmart Energy | GBV/GBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067547 |  | Ground Water | GeoSmart Energy | GBV/GBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214067548 |  | Ground Water | GeoSmart Energy | GBV/GBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067549 |  | Ground Water | GeoSmart Energy | GBV/GBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067550 |  | Ground Water | GeoSmart Energy | GBV/GBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214067551 |  | Ground Water | GeoSmart Energy | GBV/GBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067552 |  | Ground Water | GeoSmart Energy | GBV/GBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067553 |  | Ground Water | GeoSmart Energy | GBV/GBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067554 |  | Ground Water | GeoSmart Energy | GBV/GBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067555 |  | Ground Water | GeoSmart Energy | GBV/GBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067556 |  | Ground Water | GeoSmart Energy | GBV/GBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067557 |  | Ground Water | GeoSmart Energy | GBV/GBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214067558 |  | Ground Water | GeoSmart Energy | GBV/GBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067559 |  | Ground Water | GeoSmart Energy | GBV/GBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067560 |  | Ground Water | GeoSmart Energy | GBV/GBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214067561 |  | Ground Water | GeoSmart Energy | GBV/GBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067562 |  | Ground Water | GeoSmart Energy | GBV/GBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067563 |  | Ground Water | GeoSmart Energy | GBV/GBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214067564 |  | Ground Water | GeoSmart Energy | GBV/GBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067565 |  | Ground Water | GeoSmart Energy | GBV/GBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067566 |  | Ground Water | GeoSmart Energy | GBV/GBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214067567 |  | Ground Water | GeoSmart Energy | GBV/GBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067568 |  | Ground Water | GeoSmart Energy | GBV/GBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067569 |  | Ground Water | GeoSmart Energy | GBV/GBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067570 |  | Ground Water | GeoSmart Energy | GBV/GBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067571 |  | Ground Water | GeoSmart Energy | GBV/GBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067572 |  | Ground Water | GeoSmart Energy | GBV/GBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067573 |  | Ground Water | GeoSmart Energy | GBV/GBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067574 |  | Ground Water | GeoSmart Energy | GBV/GBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067575 |  | Ground Water | GeoSmart Energy | GBV/GBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067576 |  | Ground Water | GeoSmart Energy | GBV/GBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067577 |  | Ground Water | GeoSmart Energy | GBV/GBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067578 |  | Ground Water | GeoSmart Energy | GBV/GBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067579 |  | Ground Water | GeoSmart Energy | GBV/GBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067580 |  | Ground Water | GeoSmart Energy | GBV/GBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067581 |  | Ground Water | GeoSmart Energy | GBV/GBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067582 |  | Ground Water | GeoSmart Energy | GBV/GBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067583 |  | Ground Water | GeoSmart Energy | GBV/GBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067584 |  | Ground Water | GeoSmart Energy | GBV/GBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067585 |  | Ground Water | GeoSmart Energy | GBV/GBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067586 |  | Ground Water | GeoSmart Energy | GBV/GBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067587 |  | Ground Water | GeoSmart Energy | GBV/GBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067588 |  | Ground Water | GeoSmart Energy | GBV/GBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214067589 |  | Ground Water | GeoSmart Energy | GBV/GBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067590 |  | Ground Water | GeoSmart Energy | GBV/GBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067591 |  | Ground Water | GeoSmart Energy | GBV/GBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214067592 |  | Ground Water | GeoSmart Energy | GBV/GBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207822807 |  | Ground Water | HYDROTECH | HRCX30*-6 |  | 30000 | 23.5 | 25000 | 4.1 | 2.5 | Yes
207822813 |  | Ground Water | HYDROTECH | HRCX36*-6 |  | 35500 | 21.6 | 31500 | 4.1 | 2.9583 | Yes
208106952 |  | Ground Water | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
208106953 |  | Ground Water | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
208106954 |  | Ground Water | 5 SERIES GEO-READY | NGV/NGH064*1*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
208450079 |  | Ground Water | AE Air | HRCX18*-6 |  | 20000 | 22.5 | 16000 | 4.1 | 1.6667 | Yes
208450080 |  | Ground Water | AE Air | HRCX09*-6 |  | 11500 | 26.5 | 8800 | 4.5 | 0.95833 | Yes
208450081 |  | Ground Water | AE Air | HRCX24*-6 |  | 26000 | 26.5 | 22000 | 4.4 | 2.1667 | Yes
208450082 |  | Ground Water | AE Air | HRCX12*-6 |  | 13000 | 25 | 10500 | 4.1 | 1.0833 | Yes
208450083 |  | Ground Water | AE Air | HRCX30*-6 |  | 30000 | 23.5 | 25000 | 4.1 | 2.5 | Yes
208450084 |  | Ground Water | AE Air | HRCX36*-6 |  | 35500 | 21.6 | 31500 | 4.1 | 2.9583 | Yes
218338428 |  | Ground Water | GEOSTAR | G3C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
218338429 |  | Ground Water | GEOSTAR | G3C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
218338434 |  | Ground Water | GEOSTAR | G5C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
10316661 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316662 |  | Ground Water | GEOSTAR | 104H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316663 |  | Ground Water | GeoSmart Energy | GTS064*1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316664 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316666 |  | Ground Water | GEOSTAR | 104H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316667 |  | Ground Water | GeoSmart Energy | GTS064*1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316672 |  | Ground Water | GeoSmart Energy | GTS072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316673 |  | Ground Water | GEOSTAR | 104H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316674 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316700 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316701 |  | Ground Water | GEOSTAR | 103H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316702 |  | Ground Water | GeoSmart Energy | GTZ072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10318010 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318016 |  | Ground Water | GeoSmart Energy | GSZ022*1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318017 |  | Ground Water | GEOSTAR | 103H022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10318018 |  | Ground Water | GeoSmart Energy | GSZ022*1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10318019 |  | Ground Water | GEOSTAR | 103H022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318020 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318021 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318022 |  | Ground Water | GEOSTAR | 103H030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10318023 |  | Ground Water | GeoSmart Energy | GSZ030*1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318024 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318025 |  | Ground Water | GeoSmart Energy | GSZ030*1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10318026 |  | Ground Water | GEOSTAR | 103H030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318045 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318046 |  | Ground Water | GeoSmart Energy | GSZ048*1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318047 |  | Ground Water | GEOSTAR | 103H048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
10318048 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318049 |  | Ground Water | GeoSmart Energy | GSZ048*1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318050 |  | Ground Water | GEOSTAR | 103H048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
10318051 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318052 |  | Ground Water | GeoSmart Energy | GSZ060*1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318054 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318055 |  | Ground Water | GeoSmart Energy | GSZ060*1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10318056 |  | Ground Water | GEOSTAR | 103H060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10318060 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10318061 |  | Ground Water | GEOSTAR | 103H070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10318062 |  | Ground Water | GeoSmart Energy | GSZ070*1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
214771947 |  | Ground Water | TRANE | GEHK024A |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214771948 |  | Ground Water | TRANE | GEHK030A |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214771949 |  | Ground Water | TRANE | GEHK036A |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214771950 |  | Ground Water | TRANE | GEHK042A |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214771951 |  | Ground Water | TRANE | GEHK048A |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214771952 |  | Ground Water | TRANE | GEHK060A |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214771953 |  | Ground Water | TRANE | EXHK009A |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214771954 |  | Ground Water | TRANE | EXHK012A |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214771955 |  | Ground Water | TRANE | EXHK015A |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214771956 |  | Ground Water | TRANE | EXHK018A |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214771957 |  | Ground Water | TRANE | EXHK024A |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214771958 |  | Ground Water | TRANE | EXHK030A |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214771959 |  | Ground Water | TRANE | EXHK036A |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214771960 |  | Ground Water | TRANE | EXHK042A |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214771961 |  | Ground Water | TRANE | EXHK048A |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214771962 |  | Ground Water | TRANE | EXHK060A |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214771963 |  | Ground Water | TRANE | EXHK070A |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772055 |  | Ground Water | TRANE | GEVK0097 |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214772056 |  | Ground Water | TRANE | GEVK0127 |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214772057 |  | Ground Water | TRANE | GEVK0157 |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214772058 |  | Ground Water | TRANE | GEVK0187 |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214772059 |  | Ground Water | TRANE | GEVK024B |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772060 |  | Ground Water | TRANE | GEVK0244 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772061 |  | Ground Water | TRANE | GEVK0247 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772062 |  | Ground Water | TRANE | GEVK030B |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772063 |  | Ground Water | TRANE | GEVK0304 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772064 |  | Ground Water | TRANE | GEVK0307 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772065 |  | Ground Water | TRANE | GEVK036B |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772066 |  | Ground Water | TRANE | GEVK0364 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772067 |  | Ground Water | TRANE | GEVK0367 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772068 |  | Ground Water | TRANE | GEVK042B |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772069 |  | Ground Water | TRANE | GEVK0424 |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772070 |  | Ground Water | TRANE | GEVK048B |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772071 |  | Ground Water | TRANE | GEVK0484 |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772072 |  | Ground Water | TRANE | GEVK060B |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772073 |  | Ground Water | TRANE | GEVK0604 |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772074 |  | Ground Water | TRANE | EXVK0097 |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214772075 |  | Ground Water | TRANE | EXVK0127 |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214772076 |  | Ground Water | TRANE | EXVK0157 |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214772077 |  | Ground Water | TRANE | EXVK0187 |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214772078 |  | Ground Water | TRANE | EXVK024B |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772079 |  | Ground Water | TRANE | EXVK0244 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772080 |  | Ground Water | TRANE | EXVK0247 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772081 |  | Ground Water | TRANE | EXVK030B |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772082 |  | Ground Water | TRANE | EXVK0304 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772083 |  | Ground Water | TRANE | EXVK0307 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772084 |  | Ground Water | TRANE | EXVK036B |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772085 |  | Ground Water | TRANE | EXVK0364 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
202443461 |  | Ground Water | GeoSmart Energy | GSZ036*1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202443462 |  | Ground Water | GeoSmart Energy | GSZ042*1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202443463 |  | Ground Water | GeoSmart Energy | GTZ038*1*J | SAH038* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202443470 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202443471 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202443472 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202443473 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST038**1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
202449772 |  | Ground Water | WaterFurnace | UBV/UBH030**0*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449773 |  | Ground Water | WaterFurnace | UBV/UBH030**2*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449774 |  | Ground Water | WaterFurnace | UBV/UBH030**3*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449775 |  | Ground Water | WaterFurnace | UBV/UBH030**4*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449776 |  | Ground Water | WaterFurnace | UBV/UBH030**0*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449777 |  | Ground Water | WaterFurnace | UBV/UBH030**2*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449778 |  | Ground Water | WaterFurnace | UBV/UBH030**3*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449779 |  | Ground Water | WaterFurnace | UBV/UBH030**4*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449780 |  | Ground Water | WaterFurnace | UBV/UBH036**0*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449781 |  | Ground Water | WaterFurnace | UBV/UBH036**2*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449782 |  | Ground Water | WaterFurnace | UBV/UBH036**3*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449783 |  | Ground Water | WaterFurnace | UBV/UBH036**4*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
215268763 |  | Ground Water | WaterFurnace | V5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268764 |  | Ground Water | WaterFurnace | V5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268765 |  | Ground Water | WaterFurnace | V5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268766 |  | Ground Water | WaterFurnace | V5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268767 |  | Ground Water | WaterFurnace | V5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268768 |  | Ground Water | WaterFurnace | V5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268769 |  | Ground Water | WaterFurnace | V5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268770 |  | Ground Water | WaterFurnace | V5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268771 |  | Ground Water | WaterFurnace | V5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268772 |  | Ground Water | WaterFurnace | V5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268773 |  | Ground Water | WaterFurnace | V5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268774 |  | Ground Water | WaterFurnace | V5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268775 |  | Ground Water | WaterFurnace | V5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268776 |  | Ground Water | WaterFurnace | V5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268777 |  | Ground Water | WaterFurnace | V5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268778 |  | Ground Water | WaterFurnace | V5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268779 |  | Ground Water | WaterFurnace | V5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268780 |  | Ground Water | WaterFurnace | V5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268781 |  | Ground Water | WaterFurnace | V5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268782 |  | Ground Water | WaterFurnace | V5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268783 |  | Ground Water | WaterFurnace | V5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268784 |  | Ground Water | WaterFurnace | V5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268785 |  | Ground Water | WaterFurnace | V5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268786 |  | Ground Water | WaterFurnace | V5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268787 |  | Ground Water | WaterFurnace | V5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268788 |  | Ground Water | WaterFurnace | V5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268789 |  | Ground Water | WaterFurnace | V5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268790 |  | Ground Water | WaterFurnace | V5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268791 |  | Ground Water | WaterFurnace | V5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268792 |  | Ground Water | WaterFurnace | V5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268793 |  | Ground Water | WaterFurnace | V5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268794 |  | Ground Water | WaterFurnace | V5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268795 |  | Ground Water | WaterFurnace | V5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268796 |  | Ground Water | WaterFurnace | V5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215270403 |  | Ground Water | GEO-THERMAL SPLIT | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
215270405 |  | Ground Water | GEO-THERMAL SPLIT | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
215270409 |  | Ground Water | CARRIER | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270411 |  | Ground Water | CARRIER | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215270415 |  | Ground Water | BRYANT | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270417 |  | Ground Water | BRYANT | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
217351900 |  | Ground Water | KEEPRITE | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351901 |  | Ground Water | KEEPRITE | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351903 |  | Ground Water | KEEPRITE | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351904 |  | Ground Water | KEEPRITE | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351905 |  | Ground Water | KEEPRITE | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351906 |  | Ground Water | KEEPRITE | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351907 |  | Ground Water | KEEPRITE | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351908 |  | Ground Water | KEEPRITE | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351909 |  | Ground Water | KEEPRITE | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351911 |  | Ground Water | KEEPRITE | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351912 |  | Ground Water | KEEPRITE | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351914 |  | Ground Water | KEEPRITE | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351916 |  | Ground Water | KEEPRITE | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
202350453 |  | Ground Water | AAON, Inc. | M2-007-4-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350455 |  | Ground Water | AAON, Inc. | M2-007-4-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
216801918 |  | Ground Water | BOSCH-GEO | TW025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
216801920 |  | Ground Water | BOSCH-GEO | TW049-1***-*****C |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
216801922 |  | Ground Water | BOSCH | WT025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801923 |  | Ground Water | BOSCH | WT025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801932 |  | Ground Water | CARRIER | 50PSW025***3/CB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801933 |  | Ground Water | CARRIER | 50PSW025***4/DB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801934 |  | Ground Water | CARRIER | 50PSW025***5/EB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218157987 |  | Ground Water | YORK | Y5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157988 |  | Ground Water | YORK | Y5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157989 |  | Ground Water | YORK | Y5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157990 |  | Ground Water | YORK | Y5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157991 |  | Ground Water | YORK | Y5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157992 |  | Ground Water | YORK | Y5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157993 |  | Ground Water | YORK | Y5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157994 |  | Ground Water | YORK | Y5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157995 |  | Ground Water | YORK | Y5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
218157996 |  | Ground Water | YORK | Y5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218157997 |  | Ground Water | YORK | Y5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218157998 |  | Ground Water | YORK | Y5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218157999 |  | Ground Water | YORK | Y5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218158000 |  | Ground Water | YORK | Y5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218158001 |  | Ground Water | YORK | Y5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218158002 |  | Ground Water | YORK | Y5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218158003 |  | Ground Water | YORK | Y5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218158004 |  | Ground Water | YORK | Y5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218158005 |  | Ground Water | YORK | Y5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
218158006 |  | Ground Water | YORK | Y5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
218158007 |  | Ground Water | YORK | Y5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
218158008 |  | Ground Water | YORK | Y5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
218158009 |  | Ground Water | YORK | Y5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
218158010 |  | Ground Water | YORK | Y5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
218158011 |  | Ground Water | YORK | Y5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
218158012 |  | Ground Water | YORK | Y5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
218158013 |  | Ground Water | YORK | Y5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
218158014 |  | Ground Water | YORK | Y5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215224496 |  | Ground Water | FHP | CF018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
4660771 |  | Ground Water | TRANE | GEVE0728 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4660776 |  | Ground Water | TRANE | GEVE0908 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
4947178 |  | Ground Water | TRANE | VSVE0241 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947179 |  | Ground Water | TRANE | VSVE0242 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947180 |  | Ground Water | TRANE | VSVE0244 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947183 |  | Ground Water | TRANE | VSVE0331 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947184 |  | Ground Water | TRANE | VSVE0332 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947185 |  | Ground Water | TRANE | VSVE0334 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947240 |  | Ground Water | TRANE | VSVE0501 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
4947241 |  | Ground Water | TRANE | VSVE0502 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
4947242 |  | Ground Water | TRANE | VSVE0504 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
216508982 |  | Ground Water | ClimateMaster | SJ/PN024A | SKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
216508983 |  | Ground Water | ClimateMaster | SJ/PN036A | SKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
218353153 |  | Ground Water | SKYMARK | PD012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
218353154 |  | Ground Water | SKYMARK | PD012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
218353155 |  | Ground Water | SKYMARK | PD012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
218353156 |  | Ground Water | SKYMARK | PD015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
218353157 |  | Ground Water | SKYMARK | PD015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
218353158 |  | Ground Water | SKYMARK | PD015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
218353159 |  | Ground Water | SKYMARK | PD015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
218353160 |  | Ground Water | SKYMARK | PD018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
218353161 |  | Ground Water | SKYMARK | PD018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
218353162 |  | Ground Water | SKYMARK | PD018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
218353163 |  | Ground Water | SKYMARK | PD018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
201907614 |  | Ground Water | WaterFurnace | URS036*3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907615 |  | Ground Water | WaterFurnace | URS036*3*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907616 |  | Ground Water | WaterFurnace | URS036*4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907617 |  | Ground Water | WaterFurnace | URS036*4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907618 |  | Ground Water | WaterFurnace | URS036*4*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907619 |  | Ground Water | WaterFurnace | URS048*0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907620 |  | Ground Water | WaterFurnace | URS048*0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7487669 |  | Ground Water | TETCO | TYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7499543 |  | Ground Water | FHP | LM024-1CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499546 |  | Ground Water | FHP | LM024-2CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499547 |  | Ground Water | FHP | LM024-3CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499548 |  | Ground Water | FHP | LM024-4CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499550 |  | Ground Water | FHP | LM036-1VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
203363170 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**0*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363171 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**0*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363173 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**3*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363174 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**3*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363176 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**4*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363177 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**4*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363180 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**0*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363181 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**0*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363183 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**3*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363184 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**3*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363186 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**4*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363187 |  | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**4*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203372397 |  | Ground Water | HEIL | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
203372398 |  | Ground Water | ARCOAIRE | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372399 |  | Ground Water | KEEPRITE | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372400 |  | Ground Water | TEMPSTAR | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372401 |  | Ground Water | COMFORTMAKER | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372402 |  | Ground Water | DAY & NIGHT | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372403 |  | Ground Water | HEIL | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
203372404 |  | Ground Water | ARCOAIRE | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372405 |  | Ground Water | KEEPRITE | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
211306507 |  | Ground Water | WaterFurnace | NVZ033*1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | Yes
211306508 |  | Ground Water | WaterFurnace | NVZ042*1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | Yes
6501931 |  | Ground Water | GEOSTAR | GBV/GBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501932 |  | Ground Water | GEOSTAR | GBV/GBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501933 |  | Ground Water | GEOSTAR | GBV/GBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501934 |  | Ground Water | GEOSTAR | GBV/GBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501935 |  | Ground Water | GEOSTAR | GBV/GBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501936 |  | Ground Water | GEOSTAR | GBV/GBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501937 |  | Ground Water | GEOSTAR | GBV/GBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501938 |  | Ground Water | GEOSTAR | GBV/GBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501939 |  | Ground Water | GEOSTAR | GBV/GBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501940 |  | Ground Water | GEOSTAR | GBV/GBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501941 |  | Ground Water | GEOSTAR | GBV/GBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501942 |  | Ground Water | GEOSTAR | GBV/GBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501943 |  | Ground Water | GEOSTAR | GBV/GBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501944 |  | Ground Water | GEOSTAR | GBV/GBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501945 |  | Ground Water | GEOSTAR | GBV/GBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501946 |  | Ground Water | GEOSTAR | GBV/GBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501947 |  | Ground Water | GEOSTAR | GBV/GBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501948 |  | Ground Water | GEOSTAR | GBV/GBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501949 |  | Ground Water | GEOSTAR | GBV/GBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501950 |  | Ground Water | GEOSTAR | GBV/GBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501951 |  | Ground Water | GEOSTAR | GBV/GBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501952 |  | Ground Water | GEOSTAR | GBV/GBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501953 |  | Ground Water | GEOSTAR | GBV/GBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501954 |  | Ground Water | GEOSTAR | GBV/GBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501955 |  | Ground Water | GEOSTAR | GBV/GBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501956 |  | Ground Water | GEOSTAR | GBV/GBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501957 |  | Ground Water | GEOSTAR | GBV/GBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501958 |  | Ground Water | GEOSTAR | GBV/GBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501959 |  | Ground Water | GEOSTAR | GBV/GBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501960 |  | Ground Water | GEOSTAR | GBV/GBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501961 |  | Ground Water | GEOSTAR | GBV/GBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501962 |  | Ground Water | GEOSTAR | GBV/GBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501963 |  | Ground Water | GEOSTAR | GBV/GBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501964 |  | Ground Water | GEOSTAR | GBV/GBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501965 |  | Ground Water | GEOSTAR | GBV/GBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501966 |  | Ground Water | GEOSTAR | GBV/GBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501967 |  | Ground Water | GEOSTAR | GBV/GBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
202732940 |  | Ground Water | TRANE | GWSC060H3 |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
202732941 |  | Ground Water | TRANE | GWSC060H4 |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
202732942 |  | Ground Water | TRANE | GWSC060HW |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
202833355 |  | Ground Water | BOSCH | EC096-1VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833356 |  | Ground Water | BOSCH | EC096-3VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833357 |  | Ground Water | BOSCH | EC096-4VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833829 |  | Ground Water | CARRIER | 50H/VQP096**N3B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833831 |  | Ground Water | CARRIER | 50H/VQP096**C3B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833833 |  | Ground Water | FHP | EC096-1VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833835 |  | Ground Water | CARRIER | 50H/VQP096**N5B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833836 |  | Ground Water | CARRIER | 50H/VQP096**N6B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833839 |  | Ground Water | CARRIER | 50H/VQP096**C5B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833840 |  | Ground Water | CARRIER | 50H/VQP096**C6B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833843 |  | Ground Water | FHP | EC096-3VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833844 |  | Ground Water | FHP | EC096-4VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202835053 |  | Ground Water | BOSCH | SM036-1HZ*-*****C |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
202835056 |  | Ground Water | BOSCH | SM024-1VT*-*****C |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | Yes
202835057 |  | Ground Water | BOSCH | SM060-1VT*-*****C |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | Yes
202836307 |  | Ground Water | BOSCH | SM036-1VT*-*****C |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | Yes
202836309 |  | Ground Water | BOSCH | SM048-1VT*-*****C |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | Yes
202921908 |  | Ground Water | BOSCH | EP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921909 |  | Ground Water | BOSCH | EP036-3VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921910 |  | Ground Water | BOSCH | EP036-4VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921911 |  | Ground Water | BOSCH-GEO | BP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921912 |  | Ground Water | BOSCH | EP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
216767332 |  | Ground Water | TETCO | TYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216767333 |  | Ground Water | HYDRON MODULE | HVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
216767334 |  | Ground Water | HYDRON MODULE | HVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216767335 |  | Ground Water | HYDRON MODULE | HVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216767336 |  | Ground Water | HYDRON MODULE | HVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216767337 |  | Ground Water | HYDRON MODULE | HVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216767338 |  | Ground Water | HYDRON MODULE | HYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216767339 |  | Ground Water | HYDRON MODULE | HYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216767340 |  | Ground Water | HYDRON MODULE | HYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216767341 |  | Ground Water | HYDRON MODULE | HVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216767342 |  | Ground Water | HYDRON MODULE | HYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216767344 |  | Ground Water | HYDRON MODULE | HYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216772562 |  | Ground Water | Enertech | EBS018* | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
216772563 |  | Ground Water | Enertech | EBT024* | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
216772564 |  | Ground Water | Enertech | EBT036* | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
216772565 |  | Ground Water | Enertech | EBT048* | EAD048 | 51500 | 22.5 | 51300 | 4.5 | 4.2917 | Yes
216772566 |  | Ground Water | Enertech | EVS009* |  | 11900 | 24.2 | 10150 | 4.43 | 0.99167 | Yes
216772567 |  | Ground Water | Enertech | EVS012* |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
216772568 |  | Ground Water | Enertech | EVS018* |  | 24025 | 33.6 | 19600 | 5.32 | 2.0021 | Yes
216772569 |  | Ground Water | Enertech | EVT024* |  | 27825 | 27.3 | 23900 | 4.96 | 2.3188 | Yes
216772570 |  | Ground Water | Enertech | EVT030* |  | 35000 | 25.8 | 30300 | 4.72 | 2.9167 | Yes
216772571 |  | Ground Water | Enertech | EVT036* |  | 41050 | 24.3 | 36900 | 4.7 | 3.4208 | Yes
216772572 |  | Ground Water | Enertech | EVT042* |  | 49200 | 25.3 | 41900 | 4.89 | 4.1 | Yes
216772573 |  | Ground Water | Enertech | EVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216772574 |  | Ground Water | Enertech | EYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216772575 |  | Ground Water | Enertech | EYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216772576 |  | Ground Water | Enertech | EYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216772579 |  | Ground Water | Enertech | EZT024* |  | 28200 | 25 | 23175 | 4.68 | 2.35 | Yes
216772580 |  | Ground Water | Enertech | EZT030* |  | 34550 | 23.2 | 30075 | 4.5 | 2.8792 | Yes
216772581 |  | Ground Water | Enertech | EZT036* |  | 39400 | 25.2 | 34775 | 4.6 | 3.2833 | Yes
216772582 |  | Ground Water | Enertech | EZT042* |  | 47250 | 24.6 | 40300 | 4.4 | 3.9375 | Yes
216772583 |  | Ground Water | Enertech | EZT048* |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
216772584 |  | Ground Water | Enertech | EZT060* |  | 62000 | 21.8 | 58500 | 4.25 | 5.1667 | Yes
216772585 |  | Ground Water | Enertech | EVS006* |  | 7625 | 25.9 | 6500 | 4.49 | 0.63542 | Yes
216772586 |  | Ground Water | Enertech | EVS015* |  | 18150 | 35.1 | 14400 | 5.4 | 1.5125 | Yes
216772587 |  | Ground Water | Enertech | EZS006* |  | 6900 | 22.9 | 6300 | 4.3 | 0.575 | Yes
218471790 |  | Ground Water | YORK | QD007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
218471791 |  | Ground Water | YORK | QD007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
218471792 |  | Ground Water | YORK | QD009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
218471793 |  | Ground Water | YORK | QD009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
214772149 |  | Ground Water | TRANE | DXVK0364 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772150 |  | Ground Water | TRANE | DXVK048B |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772151 |  | Ground Water | TRANE | DXVK0484 |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772152 |  | Ground Water | TRANE | DXVK060B |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772153 |  | Ground Water | TRANE | DXVK0604 |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772154 |  | Ground Water | TRANE | DXVK070B |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772155 |  | Ground Water | TRANE | DXVK0704 |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772156 |  | Ground Water | TRANE | DXHK024B |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772157 |  | Ground Water | TRANE | DXHK0244 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772158 |  | Ground Water | TRANE | DXHK036B |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772159 |  | Ground Water | TRANE | DXHK0364 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772160 |  | Ground Water | TRANE | DXHK048B |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772161 |  | Ground Water | TRANE | DXHK0484 |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772162 |  | Ground Water | TRANE | DXHK060B |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772163 |  | Ground Water | TRANE | DXHK0604 |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772164 |  | Ground Water | TRANE | DXHK070B |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772165 |  | Ground Water | TRANE | DXHK0704 |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772166 |  | Ground Water | TRANE | DXVK0247 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772167 |  | Ground Water | TRANE | DXVK0367 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772168 |  | Ground Water | TRANE | DXHK0247 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772169 |  | Ground Water | TRANE | DXHK0367 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214773311 |  | Ground Water | TRANE | GEVK072 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214773312 |  | Ground Water | TRANE | GEVK090 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776122 |  | Ground Water | TRANE | GEVK0721 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776123 |  | Ground Water | TRANE | GEVK0724 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776124 |  | Ground Water | TRANE | GEVK0728 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776125 |  | Ground Water | TRANE | GEVK0904 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776126 |  | Ground Water | TRANE | GEVK0908 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776134 |  | Ground Water | TRANE | GEVK0722 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776167 |  | Ground Water | TRANE | GETK0091-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
214776168 |  | Ground Water | TRANE | GETK0121-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776169 |  | Ground Water | TRANE | GETK0151-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776170 |  | Ground Water | TRANE | GETK0181-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
214776171 |  | Ground Water | TRANE | GETK0241-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776172 |  | Ground Water | TRANE | GETK0361-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
216621360 |  | Ground Water | GEOSTAR | G5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216621361 |  | Ground Water | GEOSTAR | G5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216621362 |  | Ground Water | GEOSTAR | G5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625455 |  | Ground Water | GEOSTAR | G5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625456 |  | Ground Water | GEOSTAR | G5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625457 |  | Ground Water | GEOSTAR | G5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625458 |  | Ground Water | GEOSTAR | G5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625459 |  | Ground Water | GEOSTAR | G5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625460 |  | Ground Water | GEOSTAR | G5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625461 |  | Ground Water | GEOSTAR | G5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625462 |  | Ground Water | GEOSTAR | G5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625463 |  | Ground Water | GEOSTAR | G5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625464 |  | Ground Water | GEOSTAR | G5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625465 |  | Ground Water | GEOSTAR | G5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625466 |  | Ground Water | GEOSTAR | G5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625467 |  | Ground Water | GEOSTAR | G5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625468 |  | Ground Water | GEOSTAR | G5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625469 |  | Ground Water | GEOSTAR | G5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625470 |  | Ground Water | GEOSTAR | G5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625471 |  | Ground Water | GEOSTAR | G5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625472 |  | Ground Water | GEOSTAR | G5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625473 |  | Ground Water | GEOSTAR | G5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625474 |  | Ground Water | GEOSTAR | G5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625475 |  | Ground Water | GEOSTAR | G5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625476 |  | Ground Water | GEOSTAR | G5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625477 |  | Ground Water | GEOSTAR | G5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625478 |  | Ground Water | GEOSTAR | G5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625479 |  | Ground Water | GEOSTAR | G5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625480 |  | Ground Water | GEOSTAR | G5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625481 |  | Ground Water | GEOSTAR | G5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625482 |  | Ground Water | GEOSTAR | G5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625483 |  | Ground Water | GEOSTAR | G5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625484 |  | Ground Water | GEOSTAR | G5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
209156996 |  | Ground Water | AE Air | WSS6015*7* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
209180330 |  | Ground Water | HYDROTECH | WSV6018B* |  | 20000 | 21.1 | 16500 | 4.1 | 1.6667 | Yes
209180331 |  | Ground Water | HYDROTECH | WSV6036B* |  | 37000 | 22 | 35000 | 4.1 | 3.0833 | Yes
209180332 |  | Ground Water | HYDROTECH | WSV6042B* |  | 44000 | 24 | 38500 | 4.4 | 3.6667 | Yes
209180334 |  | Ground Water | HYDROTECH | WSV6048B* |  | 55500 | 23 | 47000 | 4.3 | 4.625 | Yes
209180335 |  | Ground Water | AE Air | WSV6018B* |  | 20000 | 21.1 | 16500 | 4.1 | 1.6667 | Yes
209180336 |  | Ground Water | AE Air | WSV6036B* |  | 37000 | 22 | 35000 | 4.1 | 3.0833 | Yes
209180337 |  | Ground Water | AE Air | WSV6042B* |  | 44000 | 24 | 38500 | 4.4 | 3.6667 | Yes
209180338 |  | Ground Water | AE Air | WSV6048B* |  | 55500 | 23 | 47000 | 4.3 | 4.625 | Yes
209323637 |  | Ground Water | HYDROTECH | WSV6009B* |  | 11000 | 26 | 9000 | 4.3 | 0.91667 | Yes
209323638 |  | Ground Water | AE Air | WSV6009B* |  | 11000 | 26 | 9000 | 4.3 | 0.91667 | Yes
209945912 |  | Ground Water | WaterFurnace | NBV/NBH009**0*6 |  | 11000 | 23 | 10700 | 4.5 | 0.91667 | No
209945913 |  | Ground Water | WaterFurnace | NBV/NBH009**2*6 |  | 11000 | 23 | 10700 | 4.5 | 0.91667 | No
209945914 |  | Ground Water | WaterFurnace | NBV/NBH012**0*6 |  | 13400 | 23.5 | 12400 | 4.3 | 1.1167 | No
209945915 |  | Ground Water | WaterFurnace | NBV/NBH012**2*6 |  | 13400 | 23.5 | 12400 | 4.3 | 1.1167 | No
211127895 |  | Ground Water | WaterFurnace | NVV/NVH036D1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
211127897 |  | Ground Water | WaterFurnace | NVV/NVH060D1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
211127898 |  | Ground Water | GEOSTAR | 141/142D036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
211127900 |  | Ground Water | GEOSTAR | 141/142D060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
215415917 |  | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
215415918 |  | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
215415919 |  | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | No
215415920 |  | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | No
215415921 |  | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 42000 | 25 | 36000 | 4.9 | 3.5 | No
215415922 |  | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 42000 | 25 | 36000 | 4.9 | 3.5 | No
215415923 |  | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 56000 | 27 | 47300 | 4.9 | 4.6667 | No
215415924 |  | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 56000 | 27 | 47300 | 4.9 | 4.6667 | No
215415925 |  | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | No
215415926 |  | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | No
215415927 |  | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | No
215415928 |  | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | No
215426638 |  | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215426639 |  | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215426640 |  | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429151 |  | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429152 |  | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429153 |  | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429158 |  | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429159 |  | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429160 |  | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429161 |  | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429162 |  | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429163 |  | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429170 |  | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429171 |  | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429172 |  | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429173 |  | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429174 |  | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
206194160 |  | Ground Water | Johnson Controls | JCH/V006A*W/K B |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
206194161 |  | Ground Water | SKYMARK | JCH/V006A*W/K C |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
206194171 |  | Ground Water | Johnson Controls | JSH/V/D030C*K B |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
206194172 |  | Ground Water | SKYMARK | JSH/V/D030C*K C |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
206194173 |  | Ground Water | Johnson Controls | JSH/V/D048C*K B |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | No
206194174 |  | Ground Water | SKYMARK | JSH/V/D048C*K C |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | No
206194175 |  | Ground Water | Johnson Controls | JSH/V/D060C*K B |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | No
206194176 |  | Ground Water | SKYMARK | JSH/V/D060C*K C |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | No
206194177 |  | Ground Water | Johnson Controls | JSH/V/D070C*K B |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | No
206194178 |  | Ground Water | SKYMARK | JSH/V/D070C*K C |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | No
206223143 |  | Ground Water | ClimateMaster | TRT036D |  | 40000 | 22.1 | 35000 | 4.6 | 3.3333 | No
206223145 |  | Ground Water | ClimateMaster | TRT060D |  | 70000 | 23.7 | 59200 | 4.5 | 5.8333 | No
206223146 |  | Ground Water | CENTURY | HZS024B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
206223147 |  | Ground Water | COMFORT-AIRE | HZS024B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
206223148 |  | Ground Water | CENTURY | HZS024B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
206223149 |  | Ground Water | COMFORT-AIRE | HZS024B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
206223150 |  | Ground Water | CENTURY | HZS036B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
206223151 |  | Ground Water | COMFORT-AIRE | HZS036B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
206223152 |  | Ground Water | CENTURY | HZS048B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
206223153 |  | Ground Water | COMFORT-AIRE | HZS048B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
206229666 |  | Ground Water | BOSCH | EP024-1HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229667 |  | Ground Water | BOSCH | EP024-2HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229668 |  | Ground Water | BOSCH | EP024-3HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229669 |  | Ground Water | BOSCH | EP024-4HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229670 |  | Ground Water | BOSCH | EP024-1HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229671 |  | Ground Water | BOSCH | EP024-2HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229672 |  | Ground Water | BOSCH | EP024-3HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229673 |  | Ground Water | BOSCH | EP024-4HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229674 |  | Ground Water | FHP | EP024-1HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229675 |  | Ground Water | FHP | EP024-2HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229676 |  | Ground Water | FHP | EP024-3HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229677 |  | Ground Water | FHP | EP024-4HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
202330514 |  | Ground Water | AAON, Inc. | M2-003-1-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330518 |  | Ground Water | AAON, Inc. | M2-003-2-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330522 |  | Ground Water | AAON, Inc. | M2-003-3-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330526 |  | Ground Water | AAON, Inc. | M2-003-4-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330529 |  | Ground Water | AAON, Inc. | M2-004-1-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330530 |  | Ground Water | AAON, Inc. | M2-004-1-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330531 |  | Ground Water | AAON, Inc. | M2-004-1-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330532 |  | Ground Water | AAON, Inc. | M2-004-1-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330533 |  | Ground Water | AAON, Inc. | M2-004-2-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330534 |  | Ground Water | AAON, Inc. | M2-004-2-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330535 |  | Ground Water | AAON, Inc. | M2-004-2-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330536 |  | Ground Water | AAON, Inc. | M2-004-2-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330537 |  | Ground Water | AAON, Inc. | M2-004-3-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330538 |  | Ground Water | AAON, Inc. | M2-004-3-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330539 |  | Ground Water | AAON, Inc. | M2-004-3-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330540 |  | Ground Water | AAON, Inc. | M2-004-3-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330541 |  | Ground Water | AAON, Inc. | M2-004-4-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330542 |  | Ground Water | AAON, Inc. | M2-004-4-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330543 |  | Ground Water | AAON, Inc. | M2-004-4-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330544 |  | Ground Water | AAON, Inc. | M2-004-4-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330547 |  | Ground Water | AAON, Inc. | M2-005-1-H-DCAC-S0-10-000-A |  | 62100 | 21.93 | 50000 | 4.1 | 5.175 | No
202330548 |  | Ground Water | AAON, Inc. | M2-005-1-H-DCBC-S0-10-000-A |  | 65000 | 21.74 | 50400 | 4.1 | 5.4167 | No
202330551 |  | Ground Water | AAON, Inc. | M2-005-2-H-DCAC-S0-10-000-A |  | 62100 | 21.93 | 50000 | 4.1 | 5.175 | No
202330552 |  | Ground Water | AAON, Inc. | M2-005-2-H-DCBC-S0-10-000-A |  | 65000 | 21.74 | 50400 | 4.1 | 5.4167 | No
202330555 |  | Ground Water | AAON, Inc. | M2-005-3-H-DCAC-S0-10-000-A |  | 62100 | 21.93 | 50000 | 4.1 | 5.175 | No
216979867 |  | Ground Water | HEIL | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979868 |  | Ground Water | ARCOAIRE | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979869 |  | Ground Water | KEEPRITE | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979870 |  | Ground Water | TEMPSTAR | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979871 |  | Ground Water | COMFORTMAKER | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979872 |  | Ground Water | DAY & NIGHT | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979873 |  | Ground Water | HEIL | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979874 |  | Ground Water | ARCOAIRE | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979875 |  | Ground Water | KEEPRITE | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979876 |  | Ground Water | TEMPSTAR | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979877 |  | Ground Water | COMFORTMAKER | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979878 |  | Ground Water | DAY & NIGHT | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979879 |  | Ground Water | HEIL | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979880 |  | Ground Water | ARCOAIRE | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979881 |  | Ground Water | KEEPRITE | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979882 |  | Ground Water | TEMPSTAR | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979883 |  | Ground Water | COMFORTMAKER | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979884 |  | Ground Water | DAY & NIGHT | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979885 |  | Ground Water | HEIL | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216979886 |  | Ground Water | ARCOAIRE | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979887 |  | Ground Water | KEEPRITE | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216625824 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625825 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625826 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625827 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625828 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625829 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
202147004 |  | Ground Water | HYDRON MODULE | HZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147005 |  | Ground Water | HYDRON MODULE | HZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
202147006 |  | Ground Water | HYDRON MODULE | HZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147007 |  | Ground Water | HYDRON MODULE | HZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147008 |  | Ground Water | HYDRON MODULE | HZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147009 |  | Ground Water | TETCO | TZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
202147010 |  | Ground Water | TETCO | TZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147011 |  | Ground Water | TETCO | TZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147012 |  | Ground Water | TETCO | TZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147013 |  | Ground Water | TETCO | TZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147014 |  | Ground Water | TETCO | TZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
217967044 |  | Ground Water | TRANE | VSHK0504 |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967045 |  | Ground Water | TRANE | VSVK0504 |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967046 |  | Ground Water | TRANE | VSHK0604 |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967047 |  | Ground Water | TRANE | VSVK0604 |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
218002304 |  | Ground Water | Viessmann | 100-WA-AP1T027020 |  | 27300 | 26.9 | 24100 | 4.9 | 2.275 | Yes
218002305 |  | Ground Water | Viessmann | 100-WA-AP1T040029 |  | 42100 | 25.5 | 38400 | 4.7 | 3.5083 | Yes
218002306 |  | Ground Water | Viessmann | 100-WA-AP1T052038 |  | 57000 | 26.2 | 49400 | 5 | 4.75 | Yes
218002307 |  | Ground Water | Viessmann | 100-WA-AP1T066049 |  | 66800 | 22.4 | 55500 | 4.5 | 5.5667 | Yes
218002308 |  | Ground Water | Viessmann | 100-WA-AP1T077056 |  | 76700 | 21.2 | 68400 | 4.5 | 6.3917 | Yes
216743615 |  | Ground Water | BOSCH | CA009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216743616 |  | Ground Water | BOSCH | CA009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216743617 |  | Ground Water | BOSCH-GEO | RP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216743618 |  | Ground Water | BOSCH | CP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743619 |  | Ground Water | BOSCH | CP024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743620 |  | Ground Water | BOSCH | CP024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743621 |  | Ground Water | BOSCH | CP024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743622 |  | Ground Water | BOSCH-GEO | RP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216743623 |  | Ground Water | BOSCH | CP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743624 |  | Ground Water | BOSCH | CP024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743625 |  | Ground Water | BOSCH | CP024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743626 |  | Ground Water | BOSCH | CP024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743627 |  | Ground Water | BOSCH-GEO | RP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216743628 |  | Ground Water | BOSCH | CP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743629 |  | Ground Water | BOSCH | CP024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743630 |  | Ground Water | BOSCH | CP024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743631 |  | Ground Water | BOSCH | CP024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743632 |  | Ground Water | BOSCH-GEO | RP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216743633 |  | Ground Water | BOSCH | CP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743634 |  | Ground Water | BOSCH | CP024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743635 |  | Ground Water | BOSCH | CP024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743636 |  | Ground Water | BOSCH | CP024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743637 |  | Ground Water | BOSCH-GEO | RP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216743638 |  | Ground Water | BOSCH | CP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743639 |  | Ground Water | BOSCH | CP036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743640 |  | Ground Water | BOSCH | CP036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743641 |  | Ground Water | BOSCH | CP036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743642 |  | Ground Water | BOSCH-GEO | RP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216743643 |  | Ground Water | BOSCH | CP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743644 |  | Ground Water | BOSCH | CP036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743645 |  | Ground Water | BOSCH | CP036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743646 |  | Ground Water | BOSCH | CP036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743647 |  | Ground Water | BOSCH-GEO | RP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216743648 |  | Ground Water | BOSCH | CP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743649 |  | Ground Water | BOSCH | CP048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743650 |  | Ground Water | BOSCH | CP048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743651 |  | Ground Water | BOSCH-GEO | RP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216743652 |  | Ground Water | BOSCH | CP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743653 |  | Ground Water | BOSCH | CP048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743654 |  | Ground Water | BOSCH | CP048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743655 |  | Ground Water | BOSCH-GEO | RP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216743656 |  | Ground Water | BOSCH | CP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743657 |  | Ground Water | BOSCH | CP060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743658 |  | Ground Water | BOSCH | CP060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743659 |  | Ground Water | BOSCH-GEO | RP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216743660 |  | Ground Water | BOSCH | CP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216743661 |  | Ground Water | BOSCH | CP060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
4219424 |  | Ground Water | NORDIC | R45HACW-P-1T-*-SDE** |  | 38500 | 21.3 | 35700 | 4.3 | 3.2083 | Yes
4219425 |  | Ground Water | NORDIC | R55HACW-P-1T-*-SDE** |  | 50200 | 22.5 | 47200 | 4.5 | 4.1833 | Yes
217642886 |  | Ground Water | GeoSmart Energy | S3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642888 |  | Ground Water | GeoSmart Energy | S3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642891 |  | Ground Water | GeoSmart Energy | S3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642892 |  | Ground Water | GeoSmart Energy | S3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642893 |  | Ground Water | GeoSmart Energy | S3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642897 |  | Ground Water | GeoSmart Energy | S3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642898 |  | Ground Water | GeoSmart Energy | S3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642899 |  | Ground Water | GeoSmart Energy | S3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642900 |  | Ground Water | GeoSmart Energy | S3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642901 |  | Ground Water | GeoSmart Energy | S3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642902 |  | Ground Water | GeoSmart Energy | S3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642903 |  | Ground Water | GeoSmart Energy | S3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642911 |  | Ground Water | GeoSmart Energy | S3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642912 |  | Ground Water | GeoSmart Energy | S3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642913 |  | Ground Water | GeoSmart Energy | S3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642914 |  | Ground Water | GeoSmart Energy | S3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
214595658 |  | Ground Water | AAON, Inc. | RN-009-2-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595659 |  | Ground Water | AAON, Inc. | RN-009-3-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595660 |  | Ground Water | AAON, Inc. | RN-009-4-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595661 |  | Ground Water | AAON, Inc. | RN-009-2-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595662 |  | Ground Water | AAON, Inc. | RN-009-3-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595663 |  | Ground Water | AAON, Inc. | RN-009-4-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595670 |  | Ground Water | AAON, Inc. | RN-011-2-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595671 |  | Ground Water | AAON, Inc. | RN-011-3-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595672 |  | Ground Water | AAON, Inc. | RN-011-4-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595673 |  | Ground Water | AAON, Inc. | RN-011-2-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595674 |  | Ground Water | AAON, Inc. | RN-011-3-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595675 |  | Ground Water | AAON, Inc. | RN-011-4-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
205503115 |  | Ground Water | BOSCH-GEO | SM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | Yes
205503116 |  | Ground Water | BOSCH-GEO | SM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | Yes
205503117 |  | Ground Water | BOSCH-GEO | SM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205503119 |  | Ground Water | BOSCH-GEO | LM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | No
205503120 |  | Ground Water | BOSCH-GEO | LM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | No
205503121 |  | Ground Water | BOSCH-GEO | LM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205503123 |  | Ground Water | BOSCH | SM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | Yes
205503124 |  | Ground Water | BOSCH | SM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | Yes
205503125 |  | Ground Water | BOSCH | SM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205503127 |  | Ground Water | FHP | LM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | No
205503128 |  | Ground Water | FHP | LM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | No
205503129 |  | Ground Water | FHP | LM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205652453 |  | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | Yes
205652454 |  | Ground Water | BOSCH-GEO | SM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | Yes
214067603 |  | Ground Water | GeoSmart Energy | GBV/GBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067604 |  | Ground Water | GeoSmart Energy | GBV/GBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067606 |  | Ground Water | GeoSmart Energy | GBV/GBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067607 |  | Ground Water | GeoSmart Energy | GBV/GBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067608 |  | Ground Water | GeoSmart Energy | GBV/GBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067609 |  | Ground Water | GeoSmart Energy | GBV/GBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067865 |  | Ground Water | GeoSmart Energy | GBV/GBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067866 |  | Ground Water | GeoSmart Energy | GBV/GBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067867 |  | Ground Water | GeoSmart Energy | GBV/GBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067868 |  | Ground Water | GeoSmart Energy | GBV/GBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
214067869 |  | Ground Water | GeoSmart Energy | GBV/GBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067870 |  | Ground Water | GeoSmart Energy | GBV/GBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067871 |  | Ground Water | GeoSmart Energy | GBV/GBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067872 |  | Ground Water | GeoSmart Energy | GBV/GBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214595542 |  | Ground Water | AAON, Inc. | RQ-003-2-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595543 |  | Ground Water | AAON, Inc. | RQ-003-3-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595544 |  | Ground Water | AAON, Inc. | RQ-003-4-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595548 |  | Ground Water | AAON, Inc. | RQ-004-1-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595549 |  | Ground Water | AAON, Inc. | RQ-004-2-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595550 |  | Ground Water | AAON, Inc. | RQ-004-3-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595551 |  | Ground Water | AAON, Inc. | RQ-004-4-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595552 |  | Ground Water | AAON, Inc. | RQ-004-2-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595553 |  | Ground Water | AAON, Inc. | RQ-004-3-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595554 |  | Ground Water | AAON, Inc. | RQ-004-4-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595562 |  | Ground Water | AAON, Inc. | RN-006-2-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595563 |  | Ground Water | AAON, Inc. | RN-006-3-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595564 |  | Ground Water | AAON, Inc. | RN-006-4-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595565 |  | Ground Water | AAON, Inc. | RN-006-2-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595566 |  | Ground Water | AAON, Inc. | RN-006-3-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595567 |  | Ground Water | AAON, Inc. | RN-006-4-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
215268702 |  | Ground Water | WaterFurnace | V5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268703 |  | Ground Water | WaterFurnace | V5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268704 |  | Ground Water | WaterFurnace | V5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268705 |  | Ground Water | WaterFurnace | V5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268706 |  | Ground Water | WaterFurnace | V5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268707 |  | Ground Water | WaterFurnace | V5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268708 |  | Ground Water | WaterFurnace | V5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268709 |  | Ground Water | WaterFurnace | V5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268710 |  | Ground Water | WaterFurnace | V5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268711 |  | Ground Water | WaterFurnace | V5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268712 |  | Ground Water | WaterFurnace | V5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268713 |  | Ground Water | WaterFurnace | V5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268714 |  | Ground Water | WaterFurnace | V5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268715 |  | Ground Water | WaterFurnace | V5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268716 |  | Ground Water | WaterFurnace | V5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268717 |  | Ground Water | WaterFurnace | V5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268718 |  | Ground Water | WaterFurnace | V5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268719 |  | Ground Water | WaterFurnace | V5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268720 |  | Ground Water | WaterFurnace | V5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268721 |  | Ground Water | WaterFurnace | V5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268722 |  | Ground Water | WaterFurnace | V5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268723 |  | Ground Water | WaterFurnace | V5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268724 |  | Ground Water | WaterFurnace | V5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268725 |  | Ground Water | WaterFurnace | V5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268726 |  | Ground Water | WaterFurnace | V5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268727 |  | Ground Water | WaterFurnace | V5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268728 |  | Ground Water | WaterFurnace | V5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268729 |  | Ground Water | WaterFurnace | V5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268730 |  | Ground Water | WaterFurnace | V5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268731 |  | Ground Water | WaterFurnace | V5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268732 |  | Ground Water | WaterFurnace | V5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268733 |  | Ground Water | WaterFurnace | V5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268734 |  | Ground Water | WaterFurnace | V5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268735 |  | Ground Water | WaterFurnace | V5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
215268736 |  | Ground Water | WaterFurnace | V5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
215268737 |  | Ground Water | WaterFurnace | V5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268738 |  | Ground Water | WaterFurnace | V5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268739 |  | Ground Water | WaterFurnace | V5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
213307834 |  | Ground Water | GeoSmart Energy | QT038**1*(1,2)*****K |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
213307835 |  | Ground Water | GeoSmart Energy | QT049**1*(1,2)*****J |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
213348376 |  | Ground Water | ClimateMaster | TRT072D |  | 76000 | 21.3 | 72000 | 4.4 | 6.3333 | No
213351451 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLFT048**1*4*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
7519776 |  | Ground Water | HYDRON MODULE | HVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519777 |  | Ground Water | TETCO | TVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7520238 |  | Ground Water | GEOCOMFORT | GVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520239 |  | Ground Water | HYDRON MODULE | HVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520240 |  | Ground Water | TETCO | TVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520241 |  | Ground Water | GEOCOMFORT | GVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520242 |  | Ground Water | HYDRON MODULE | HVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520243 |  | Ground Water | TETCO | TVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520244 |  | Ground Water | TETCO | TVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520245 |  | Ground Water | HYDRON MODULE | HVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520246 |  | Ground Water | GEOCOMFORT | GVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520247 |  | Ground Water | HYDRON MODULE | HVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520248 |  | Ground Water | TETCO | TVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520249 |  | Ground Water | GEOCOMFORT | GVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520250 |  | Ground Water | GEOCOMFORT | GVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520251 |  | Ground Water | HYDRON MODULE | HVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520252 |  | Ground Water | TETCO | TVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520253 |  | Ground Water | GEOCOMFORT | GVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520254 |  | Ground Water | HYDRON MODULE | HVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520255 |  | Ground Water | TETCO | TVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520256 |  | Ground Water | GEOCOMFORT | GVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520257 |  | Ground Water | HYDRON MODULE | HVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520258 |  | Ground Water | TETCO | TVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520259 |  | Ground Water | GEOCOMFORT | GVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520260 |  | Ground Water | HYDRON MODULE | HVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520261 |  | Ground Water | TETCO | TVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7523956 |  | Ground Water | GEOCOMFORT | GVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
7523957 |  | Ground Water | HYDRON MODULE | HVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
7523958 |  | Ground Water | TETCO | TVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
7523959 |  | Ground Water | GEOCOMFORT | GVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
7523960 |  | Ground Water | HYDRON MODULE | HVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
7523961 |  | Ground Water | TETCO | TVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
203459712 |  | Ground Water | BOSCH-GEO | LM036-1CSC-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459713 |  | Ground Water | BOSCH-GEO | LM036-1CSN-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459714 |  | Ground Water | BOSCH-GEO | LM048-1CSC-*****A | LM048-1AV/AH*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
3706350 |  | Ground Water | GEOSTAR | ZS015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3706351 |  | Ground Water | GEOSTAR | ZS015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3706369 |  | Ground Water | GEOSTAR | ZS018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
215224782 |  | Ground Water | CARRIER | GBA18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224783 |  | Ground Water | BRYANT | GBA18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224784 |  | Ground Water | CARRIER | GBA18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224785 |  | Ground Water | BRYANT | GBA18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224810 |  | Ground Water | HEIL | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224811 |  | Ground Water | ARCOAIRE | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224812 |  | Ground Water | KEEPRITE | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224813 |  | Ground Water | TEMPSTAR | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224814 |  | Ground Water | COMFORTMAKER | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224815 |  | Ground Water | DAY & NIGHT | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224816 |  | Ground Water | HEIL | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224817 |  | Ground Water | ARCOAIRE | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224818 |  | Ground Water | KEEPRITE | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224819 |  | Ground Water | TEMPSTAR | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224820 |  | Ground Water | COMFORTMAKER | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224821 |  | Ground Water | DAY & NIGHT | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
217122387 |  | Ground Water | ClimateMaster | SWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
217193306 |  | Ground Water | WaterFurnace | V7A(V/H)024*V0**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193307 |  | Ground Water | WaterFurnace | V7A(V/H)036*V0**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193308 |  | Ground Water | WaterFurnace | V7A(V/H)048*V0**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193309 |  | Ground Water | WaterFurnace | V7A(V/H)060*V0**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217193552 |  | Ground Water | WaterFurnace | V7A(V/H)024*V3**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193553 |  | Ground Water | WaterFurnace | V7A(V/H)024*V4**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193554 |  | Ground Water | WaterFurnace | V7A(V/H)036*V3**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193555 |  | Ground Water | WaterFurnace | V7A(V/H)036*V4**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193556 |  | Ground Water | WaterFurnace | V7A(V/H)048*V3**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193557 |  | Ground Water | WaterFurnace | V7A(V/H)048*V4**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193558 |  | Ground Water | WaterFurnace | V7A(V/H)060*V3**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217193559 |  | Ground Water | WaterFurnace | V7A(V/H)060*V4**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217212043 |  | Ground Water | FHP | CP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212044 |  | Ground Water | FHP | CP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212045 |  | Ground Water | FHP | CP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212046 |  | Ground Water | FHP | CP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212048 |  | Ground Water | FHP | CP024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212049 |  | Ground Water | FHP | CP024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212050 |  | Ground Water | FHP | CP024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212051 |  | Ground Water | FHP | CP024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212052 |  | Ground Water | FHP | CP024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212054 |  | Ground Water | FHP | CP024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212055 |  | Ground Water | FHP | CP024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212056 |  | Ground Water | FHP | CP024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212057 |  | Ground Water | FHP | CP024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212059 |  | Ground Water | FHP | CP024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212060 |  | Ground Water | FHP | CP024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212061 |  | Ground Water | FHP | CP024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212062 |  | Ground Water | FHP | CP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212064 |  | Ground Water | FHP | CP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212065 |  | Ground Water | FHP | CP036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212066 |  | Ground Water | FHP | CP036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212067 |  | Ground Water | FHP | CP036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212068 |  | Ground Water | FHP | CP036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212070 |  | Ground Water | FHP | CP036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212071 |  | Ground Water | FHP | CP036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212072 |  | Ground Water | FHP | CP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
217212073 |  | Ground Water | FHP | CP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212074 |  | Ground Water | FHP | CP048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
963501 |  | Ground Water | WaterFurnace | NLH/NXH095**3 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963502 |  | Ground Water | WaterFurnace | NLH/NXH095**4 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963503 |  | Ground Water | WaterFurnace | NLH/NXH095**5 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963504 |  | Ground Water | WaterFurnace | NLH/NXH120**3 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963505 |  | Ground Water | WaterFurnace | NLH/NXH120**4 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963506 |  | Ground Water | WaterFurnace | NLH/NXH120**5 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963507 |  | Ground Water | WaterFurnace | NLV/NXV080T*3 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963508 |  | Ground Water | WaterFurnace | NLV/NXV080T*4 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963509 |  | Ground Water | WaterFurnace | NLV/NXV080T*5 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963510 |  | Ground Water | WaterFurnace | NLV/NXV095T*3 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963511 |  | Ground Water | WaterFurnace | NLV/NXV095T*4 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963512 |  | Ground Water | WaterFurnace | NLV/NXV095T*5 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963513 |  | Ground Water | WaterFurnace | NLV/NXV120T*3 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
963514 |  | Ground Water | WaterFurnace | NLV/NXV120T*4 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
963515 |  | Ground Water | WaterFurnace | NLV/NXV120T*5 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
1483426 |  | Ground Water | BOSCH | BP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
1483428 |  | Ground Water | BOSCH | BP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
1483429 |  | Ground Water | BOSCH | BP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3059231 |  | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
5315780 |  | Ground Water | WaterFurnace | NBV/NBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315781 |  | Ground Water | WaterFurnace | NBV/NBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315782 |  | Ground Water | WaterFurnace | NBV/NBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315783 |  | Ground Water | WaterFurnace | NBV/NBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315784 |  | Ground Water | WaterFurnace | NBV/NBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315785 |  | Ground Water | WaterFurnace | NBV/NBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5316500 |  | Ground Water | WaterFurnace | NBV/NBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316501 |  | Ground Water | WaterFurnace | NBV/NBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316502 |  | Ground Water | WaterFurnace | NBV/NBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316503 |  | Ground Water | WaterFurnace | NBV/NBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316504 |  | Ground Water | WaterFurnace | NBV/NBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316505 |  | Ground Water | WaterFurnace | NBV/NBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316510 |  | Ground Water | WaterFurnace | NBV/NBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316511 |  | Ground Water | WaterFurnace | NBV/NBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316512 |  | Ground Water | WaterFurnace | NBV/NBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316513 |  | Ground Water | WaterFurnace | NBV/NBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316514 |  | Ground Water | WaterFurnace | NBV/NBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316515 |  | Ground Water | WaterFurnace | NBV/NBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316516 |  | Ground Water | WaterFurnace | NBV/NBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5317193 |  | Ground Water | WaterFurnace | NBV/NBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317194 |  | Ground Water | WaterFurnace | NBV/NBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317195 |  | Ground Water | WaterFurnace | NBV/NBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317196 |  | Ground Water | WaterFurnace | NBV/NBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317197 |  | Ground Water | WaterFurnace | NBV/NBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317198 |  | Ground Water | WaterFurnace | NBV/NBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317199 |  | Ground Water | WaterFurnace | NBV/NBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317200 |  | Ground Water | WaterFurnace | NBV/NBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317201 |  | Ground Water | WaterFurnace | NBV/NBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317202 |  | Ground Water | WaterFurnace | NBV/NBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317203 |  | Ground Water | WaterFurnace | NBV/NBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317205 |  | Ground Water | WaterFurnace | NBV/NBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317206 |  | Ground Water | WaterFurnace | NBV/NBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317207 |  | Ground Water | WaterFurnace | NBV/NBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317209 |  | Ground Water | WaterFurnace | NBV/NBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317210 |  | Ground Water | WaterFurnace | NBV/NBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317211 |  | Ground Water | WaterFurnace | NBV/NBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317270 |  | Ground Water | WaterFurnace | NBV/NBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317328 |  | Ground Water | WaterFurnace | NBV/NBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317329 |  | Ground Water | WaterFurnace | NBV/NBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317330 |  | Ground Water | WaterFurnace | NBV/NBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317331 |  | Ground Water | WaterFurnace | NBV/NBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317332 |  | Ground Water | WaterFurnace | NBV/NBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317333 |  | Ground Water | WaterFurnace | NBV/NBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317334 |  | Ground Water | WaterFurnace | NBV/NBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317335 |  | Ground Water | WaterFurnace | NBV/NBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5440541 |  | Ground Water | GEOCOMFORT | GXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440542 |  | Ground Water | HYDRON MODULE | HXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440543 |  | Ground Water | TETCO | TXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440554 |  | Ground Water | GEOCOMFORT | GXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
218353355 |  | Ground Water | JOHNSON CONTROLS | DD009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218353356 |  | Ground Water | JOHNSON CONTROLS | DD009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
218353357 |  | Ground Water | JOHNSON CONTROLS | DD012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
218353358 |  | Ground Water | JOHNSON CONTROLS | DD012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
218353359 |  | Ground Water | JOHNSON CONTROLS | DD012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
218353360 |  | Ground Water | JOHNSON CONTROLS | DD012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
218353361 |  | Ground Water | JOHNSON CONTROLS | DD015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
218353362 |  | Ground Water | JOHNSON CONTROLS | DD015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
218353363 |  | Ground Water | JOHNSON CONTROLS | DD015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
218353364 |  | Ground Water | JOHNSON CONTROLS | DD015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
218353365 |  | Ground Water | JOHNSON CONTROLS | DD018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
218353366 |  | Ground Water | JOHNSON CONTROLS | DD018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
218353367 |  | Ground Water | JOHNSON CONTROLS | DD018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
218353368 |  | Ground Water | JOHNSON CONTROLS | DD018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
202146948 |  | Ground Water | GEOCOMFORT | GZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146949 |  | Ground Water | GEOCOMFORT | GZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146950 |  | Ground Water | GEOCOMFORT | GZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146951 |  | Ground Water | GEOCOMFORT | GZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146952 |  | Ground Water | HYDRON MODULE | HZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146953 |  | Ground Water | HYDRON MODULE | HZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146954 |  | Ground Water | HYDRON MODULE | HZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146955 |  | Ground Water | HYDRON MODULE | HZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146956 |  | Ground Water | HYDRON MODULE | HZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146957 |  | Ground Water | HYDRON MODULE | HZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146958 |  | Ground Water | HYDRON MODULE | HZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146959 |  | Ground Water | HYDRON MODULE | HZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146960 |  | Ground Water | HYDRON MODULE | HZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146961 |  | Ground Water | TETCO | TZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146962 |  | Ground Water | TETCO | TZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146963 |  | Ground Water | TETCO | TZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146964 |  | Ground Water | TETCO | TZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146965 |  | Ground Water | TETCO | TZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146966 |  | Ground Water | TETCO | TZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146967 |  | Ground Water | TETCO | TZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146968 |  | Ground Water | TETCO | TZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146969 |  | Ground Water | TETCO | TZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146970 |  | Ground Water | GEOCOMFORT | GZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
202146971 |  | Ground Water | GEOCOMFORT | GZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146972 |  | Ground Water | GEOCOMFORT | GZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146973 |  | Ground Water | GEOCOMFORT | GZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146974 |  | Ground Water | GEOCOMFORT | GZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146975 |  | Ground Water | GEOCOMFORT | GZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
202146976 |  | Ground Water | GEOCOMFORT | GZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146977 |  | Ground Water | HYDRON MODULE | HZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
202146978 |  | Ground Water | HYDRON MODULE | HZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146979 |  | Ground Water | HYDRON MODULE | HZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
6501887 |  | Ground Water | GEOSTAR | GBV/GBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
6501888 |  | Ground Water | GEOSTAR | GBV/GBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501889 |  | Ground Water | GEOSTAR | GBV/GBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501890 |  | Ground Water | GEOSTAR | GBV/GBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
6501891 |  | Ground Water | GEOSTAR | GBV/GBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501892 |  | Ground Water | GEOSTAR | GBV/GBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501893 |  | Ground Water | GEOSTAR | GBV/GBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
6501894 |  | Ground Water | GEOSTAR | GBV/GBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501895 |  | Ground Water | GEOSTAR | GBV/GBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501896 |  | Ground Water | GEOSTAR | GBV/GBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
6501897 |  | Ground Water | GEOSTAR | GBV/GBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501898 |  | Ground Water | GEOSTAR | GBV/GBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501899 |  | Ground Water | GEOSTAR | GBV/GBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501900 |  | Ground Water | GEOSTAR | GBV/GBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501901 |  | Ground Water | GEOSTAR | GBV/GBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501902 |  | Ground Water | GEOSTAR | GBV/GBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501903 |  | Ground Water | GEOSTAR | GBV/GBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501904 |  | Ground Water | GEOSTAR | GBV/GBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501905 |  | Ground Water | GEOSTAR | GBV/GBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501906 |  | Ground Water | GEOSTAR | GBV/GBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501907 |  | Ground Water | GEOSTAR | GBV/GBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501908 |  | Ground Water | GEOSTAR | GBV/GBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501909 |  | Ground Water | GEOSTAR | GBV/GBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501910 |  | Ground Water | GEOSTAR | GBV/GBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501911 |  | Ground Water | GEOSTAR | GBV/GBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207348739 |  | Ground Water | WaterFurnace | URD072*3*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348740 |  | Ground Water | WaterFurnace | URD072*4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348741 |  | Ground Water | WaterFurnace | URD072*4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348742 |  | Ground Water | WaterFurnace | URD072*4*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349053 |  | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
207349059 |  | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
207349379 |  | Ground Water | WaterFurnace | NBV/NBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349380 |  | Ground Water | WaterFurnace | NBV/NBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349381 |  | Ground Water | WaterFurnace | NBV/NBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349382 |  | Ground Water | WaterFurnace | NBV/NBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349383 |  | Ground Water | WaterFurnace | NBV/NBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349384 |  | Ground Water | WaterFurnace | NBV/NBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
204835632 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
204835633 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205129920 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205129921 |  | Ground Water | GEOSTAR | 103J036**1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205145424 |  | Ground Water | GEOCOMFORT | GVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145425 |  | Ground Water | GEOCOMFORT | GVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145426 |  | Ground Water | GEOCOMFORT | GVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145427 |  | Ground Water | HYDRON MODULE | HVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145428 |  | Ground Water | HYDRON MODULE | HVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145429 |  | Ground Water | HYDRON MODULE | HVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145430 |  | Ground Water | TETCO | TVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145431 |  | Ground Water | TETCO | TVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145432 |  | Ground Water | TETCO | TVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145433 |  | Ground Water | GEOCOMFORT | GVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145434 |  | Ground Water | GEOCOMFORT | GVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145435 |  | Ground Water | GEOCOMFORT | GVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145436 |  | Ground Water | HYDRON MODULE | HVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145437 |  | Ground Water | HYDRON MODULE | HVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145438 |  | Ground Water | HYDRON MODULE | HVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145439 |  | Ground Water | TETCO | TVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145527 |  | Ground Water | GEOCOMFORT | GVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145528 |  | Ground Water | HYDRON MODULE | HVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145529 |  | Ground Water | TETCO | TVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145530 |  | Ground Water | TETCO | TVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145531 |  | Ground Water | TETCO | TVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
214595607 |  | Ground Water | AAON, Inc. | M2-003-2-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595611 |  | Ground Water | AAON, Inc. | M2-003-3-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595615 |  | Ground Water | AAON, Inc. | M2-003-4-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595618 |  | Ground Water | AAON, Inc. | M2-004-1-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595619 |  | Ground Water | AAON, Inc. | M2-004-1-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
214595620 |  | Ground Water | AAON, Inc. | M2-004-2-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595621 |  | Ground Water | AAON, Inc. | M2-004-2-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595622 |  | Ground Water | AAON, Inc. | M2-004-2-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595623 |  | Ground Water | AAON, Inc. | M2-004-2-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
214595624 |  | Ground Water | AAON, Inc. | M2-004-3-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595625 |  | Ground Water | AAON, Inc. | M2-004-3-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595626 |  | Ground Water | AAON, Inc. | M2-004-3-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595627 |  | Ground Water | AAON, Inc. | M2-004-3-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
214595628 |  | Ground Water | AAON, Inc. | M2-004-4-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595629 |  | Ground Water | AAON, Inc. | M2-004-4-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595630 |  | Ground Water | AAON, Inc. | M2-004-4-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
5273062 |  | Ground Water | WaterFurnace | NBV/NBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
5273082 |  | Ground Water | WaterFurnace | NBV/NBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
5273138 |  | Ground Water | WaterFurnace | NBV/NBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
5274236 |  | Ground Water | WaterFurnace | NBV/NBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
5295936 |  | Ground Water | WaterFurnace | NBV/NBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
5295937 |  | Ground Water | WaterFurnace | NBV/NBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
5295944 |  | Ground Water | WaterFurnace | NBV/NBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295945 |  | Ground Water | WaterFurnace | NBV/NBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295947 |  | Ground Water | WaterFurnace | NBV/NBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295948 |  | Ground Water | WaterFurnace | NBV/NBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295960 |  | Ground Water | WaterFurnace | NBV/NBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
5295962 |  | Ground Water | WaterFurnace | NBV/NBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
5295964 |  | Ground Water | WaterFurnace | NBV/NBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295966 |  | Ground Water | WaterFurnace | NBV/NBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295968 |  | Ground Water | WaterFurnace | NBV/NBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295969 |  | Ground Water | WaterFurnace | NBV/NBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295980 |  | Ground Water | WaterFurnace | NBV/NBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295981 |  | Ground Water | WaterFurnace | NBV/NBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295982 |  | Ground Water | WaterFurnace | NBV/NBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295983 |  | Ground Water | WaterFurnace | NBV/NBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
205767605 |  | Ground Water | ClimateMaster | VEV/H/D1860 |  | 48000 | 35.5 | 60000 | 4.3 | 4 | Yes
205767606 |  | Ground Water | ClimateMaster | VEV/H/D0930 |  | 24000 | 42 | 30000 | 4.8 | 2 | Yes
205767607 |  | Ground Water | ClimateMaster | TZV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
205767608 |  | Ground Water | ClimateMaster | TZV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205767610 |  | Ground Water | ClimateMaster | TZV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205767612 |  | Ground Water | ClimateMaster | TZV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205767615 |  | Ground Water | ClimateMaster | QEV/H/D0930 |  | 24000 | 42 | 30000 | 4.8 | 2 | Yes
205767616 |  | Ground Water | ClimateMaster | TYV/H060B |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | No
205767623 |  | Ground Water | ClimateMaster | TCH/V015A*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205767624 |  | Ground Water | ClimateMaster | TRH/V015A*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205767626 |  | Ground Water | ClimateMaster | TES/P038B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
205767627 |  | Ground Water | ClimateMaster | TES/P049B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
205780261 |  | Ground Water | GEOSTAR | 111J038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205782086 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ042J1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
205782087 |  | Ground Water | GEOSTAR | 103J042**1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
205782239 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205782240 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
205782241 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782242 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAST038**1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782243 |  | Ground Water | GeoSmart Energy | GSZ036*1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205782244 |  | Ground Water | GeoSmart Energy | GSZ042*1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
205782245 |  | Ground Water | GeoSmart Energy | GTZ038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782246 |  | Ground Water | GeoSmart Energy | GTS038*1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
205782247 |  | Ground Water | GeoSmart Energy | GTS038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782567 |  | Ground Water | YORK BY JOHNSON CONTROLS | YACT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205782571 |  | Ground Water | GeoSmart Energy | QT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205788273 |  | Ground Water | Johnson Controls | JSH/V/D018B B |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
205788274 |  | Ground Water | SKYMARK | JSH/V/D018B C |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
205788275 |  | Ground Water | Johnson Controls | JSH/V/D018B*K B |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205788276 |  | Ground Water | SKYMARK | JSH/V/D018B*K C |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205788277 |  | Ground Water | Johnson Controls | JSH/V/D024C B |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | No
205788278 |  | Ground Water | SKYMARK | JSH/V/D024C C |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | No
205788279 |  | Ground Water | Johnson Controls | JSH/V/D024C*K B |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | No
205788280 |  | Ground Water | SKYMARK | JSH/V/D024C*K C |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | No
205788281 |  | Ground Water | Johnson Controls | JSH/V/D030C B |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | No
205788282 |  | Ground Water | SKYMARK | JSH/V/D030C C |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | No
205788283 |  | Ground Water | Johnson Controls | JSH/V/D036C B |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | No
205788284 |  | Ground Water | SKYMARK | JSH/V/D036C C |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | No
214772086 |  | Ground Water | TRANE | EXVK0367 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772087 |  | Ground Water | TRANE | EXVK042B |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772088 |  | Ground Water | TRANE | EXVK0424 |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772089 |  | Ground Water | TRANE | EXVK048B |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772090 |  | Ground Water | TRANE | EXVK0484 |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772091 |  | Ground Water | TRANE | EXVK060B |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772092 |  | Ground Water | TRANE | EXVK0604 |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772093 |  | Ground Water | TRANE | EXVK070B |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772094 |  | Ground Water | TRANE | EXVK0704 |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772095 |  | Ground Water | TRANE | DXVK024A |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772096 |  | Ground Water | TRANE | DXVK036A |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772097 |  | Ground Water | TRANE | DXVK048A |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772098 |  | Ground Water | TRANE | DXVK060A |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772099 |  | Ground Water | TRANE | DXVK070A |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
207177503 |  | Ground Water | TRANE | DXVG060A |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177504 |  | Ground Water | TRANE | DXVG060B |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177505 |  | Ground Water | TRANE | DXVG0604 |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177506 |  | Ground Water | TRANE | DXVG070A |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207177507 |  | Ground Water | TRANE | DXVG070B |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207177508 |  | Ground Water | TRANE | DXVG0704 |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207178484 |  | Ground Water | GEOSTAR | 163H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178485 |  | Ground Water | GEOSTAR | 164H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178486 |  | Ground Water | GEOSTAR | 164H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178487 |  | Ground Water | GEOSTAR | 163H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207178492 |  | Ground Water | GEOSTAR | 163J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178493 |  | Ground Water | GEOSTAR | 164J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178495 |  | Ground Water | GEOSTAR | 163J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178496 |  | Ground Water | GEOSTAR | 163J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178497 |  | Ground Water | GEOSTAR | 163J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178498 |  | Ground Water | GEOSTAR | 163J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178499 |  | Ground Water | GEOSTAR | 164J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178500 |  | Ground Water | GEOSTAR | 163J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178519 |  | Ground Water | GEOSTAR | 164H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178520 |  | Ground Water | GEOSTAR | 164H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178521 |  | Ground Water | GEOSTAR | 164H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178522 |  | Ground Water | GEOSTAR | 164H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178523 |  | Ground Water | GEOSTAR | 164H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207178524 |  | Ground Water | GEOSTAR | 164H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207178525 |  | Ground Water | GEOSTAR | 161/162J064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207178536 |  | Ground Water | GEOSTAR | 163H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178537 |  | Ground Water | GEOSTAR | 163H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
217897447 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
217897448 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
217897449 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
217897450 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
217897451 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
217897452 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
217897453 |  | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
217897454 |  | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
217897455 |  | Ground Water | CENTURY | MJN024A | MKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
217897456 |  | Ground Water | COMFORT-AIRE | MJN024A | MKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
217897457 |  | Ground Water | CENTURY | MJN036A | MKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
217897458 |  | Ground Water | COMFORT-AIRE | MJN036A | MKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
217897463 |  | Ground Water | CENTURY | MJN024A | MAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
217897464 |  | Ground Water | COMFORT-AIRE | MJN024A | MAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
217897465 |  | Ground Water | CENTURY | MJN036A | MAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
217897466 |  | Ground Water | COMFORT-AIRE | MJN036A | MAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
217897467 |  | Ground Water | CENTURY | MJN048A | MAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
217897468 |  | Ground Water | COMFORT-AIRE | MJN048A | MAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
217897469 |  | Ground Water | CENTURY | MJN060A | MAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
217897470 |  | Ground Water | COMFORT-AIRE | MJN060A | MAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
217897473 |  | Ground Water | CENTURY | MWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
217897474 |  | Ground Water | COMFORT-AIRE | MWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
217902632 |  | Ground Water | Johnson Controls | BWM060A*B |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | No
217902633 |  | Ground Water | SKYMARK | BWM060A*C |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | No
217903418 |  | Ground Water | WaterFurnace | V5R036*S0**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903419 |  | Ground Water | WaterFurnace | V5R036*S0**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903420 |  | Ground Water | WaterFurnace | V5R036*S0**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903421 |  | Ground Water | WaterFurnace | V5R048*S0**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903422 |  | Ground Water | WaterFurnace | V5R048*S0**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903423 |  | Ground Water | WaterFurnace | V5R048*S0**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903424 |  | Ground Water | WaterFurnace | V5R060*S0**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903425 |  | Ground Water | WaterFurnace | V5R060*S0**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903426 |  | Ground Water | WaterFurnace | V5R060*S0**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903427 |  | Ground Water | WaterFurnace | V5R072*S0**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903428 |  | Ground Water | WaterFurnace | V5R072*S0**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903429 |  | Ground Water | WaterFurnace | V5R072*S0**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903430 |  | Ground Water | WaterFurnace | V5R036*S3**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903431 |  | Ground Water | WaterFurnace | V5R036*S3**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
207348654 |  | Ground Water | WaterFurnace | URS036*0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348655 |  | Ground Water | WaterFurnace | URS036*0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348656 |  | Ground Water | WaterFurnace | URS036*0*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348657 |  | Ground Water | WaterFurnace | URS036*3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348658 |  | Ground Water | WaterFurnace | URS036*3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348659 |  | Ground Water | WaterFurnace | URS036*3*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348660 |  | Ground Water | WaterFurnace | URS036*4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348661 |  | Ground Water | WaterFurnace | URS036*4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348662 |  | Ground Water | WaterFurnace | URS036*4*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348663 |  | Ground Water | WaterFurnace | URS048*0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348664 |  | Ground Water | WaterFurnace | URS048*0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348665 |  | Ground Water | WaterFurnace | URS048*0*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5440555 |  | Ground Water | HYDRON MODULE | HXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
5440557 |  | Ground Water | TETCO | TXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
5440573 |  | Ground Water | GEOCOMFORT | GXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440574 |  | Ground Water | HYDRON MODULE | HXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440575 |  | Ground Water | TETCO | TXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440576 |  | Ground Water | GEOCOMFORT | GXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440577 |  | Ground Water | HYDRON MODULE | HXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440578 |  | Ground Water | TETCO | TXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440703 |  | Ground Water | GEOCOMFORT | GXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440704 |  | Ground Water | HYDRON MODULE | HXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440705 |  | Ground Water | TETCO | TXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440708 |  | Ground Water | GEOCOMFORT | GXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440709 |  | Ground Water | HYDRON MODULE | HXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440710 |  | Ground Water | TETCO | TXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5599272 |  | Ground Water | BOSCH-GEO | SM036-1CF/HZ/VT |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
5599275 |  | Ground Water | BOSCH-GEO | SM060-1CF/HZ/VT |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
5599276 |  | Ground Water | BOSCH-GEO | SM070-1CF/HZ/VT |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
207335143 |  | Ground Water | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335144 |  | Ground Water | GEOSTAR | 101/102K049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335145 |  | Ground Water | GEOSTAR | 101/102K064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335146 |  | Ground Water | GEOSTAR | 101/102J072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335147 |  | Ground Water | GEOSTAR | 161/162K064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335247 |  | Ground Water | GEOSTAR | 101/102J022**1*(1,4)***** |  | 21900 | 27.5 | 21900 | 5 | 1.825 | Yes
207335249 |  | Ground Water | GEOSTAR | 161/162J026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335251 |  | Ground Water | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335253 |  | Ground Water | GEOSTAR | 161/162K049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335255 |  | Ground Water | GEOSTAR | 161/162J072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335335 |  | Ground Water | GEOSTAR | 111J049**1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
207335338 |  | Ground Water | GEOSTAR | 111K038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
207335397 |  | Ground Water | GeoSmart Energy | GT026**1*(1,4)*J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335398 |  | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335399 |  | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335400 |  | Ground Water | GeoSmart Energy | GT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335401 |  | Ground Water | GeoSmart Energy | GT072**1*(1,4)*J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335402 |  | Ground Water | GeoSmart Energy | GS012**1*0*J |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207335403 |  | Ground Water | GeoSmart Energy | GS018**1*(1,4)*J |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335404 |  | Ground Water | GeoSmart Energy | GS018**1*0*J |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | Yes
207335406 |  | Ground Water | GeoSmart Energy | GS022**1*(1,4)*J |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
207335407 |  | Ground Water | GeoSmart Energy | GS030**1*(0,3)*J |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | Yes
207335408 |  | Ground Water | GeoSmart Energy | GS030**1*(1,4)*J |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335409 |  | Ground Water | GeoSmart Energy | GS036**1*(0,3)*K |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207335410 |  | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*K |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207335411 |  | Ground Water | GeoSmart Energy | GS042**1*(0,3)*K |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | Yes
207335412 |  | Ground Water | GeoSmart Energy | GS048**1*(0,3)*K |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | Yes
207335413 |  | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*K |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335414 |  | Ground Water | GeoSmart Energy | GS060**1*(1,4)*K |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335415 |  | Ground Water | GeoSmart Energy | GS060**1*0*K |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | Yes
207335416 |  | Ground Water | GeoSmart Energy | GS070**1*(1,4)*J |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335514 |  | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335570 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS012**1*0****J |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207335571 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****J |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335572 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(1,4)****J |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
207335573 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335574 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*K |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207335575 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335576 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*K |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335577 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****K |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335578 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****J |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335579 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335580 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335581 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335582 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335583 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335584 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335585 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335586 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335587 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335588 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335589 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335590 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
7519769 |  | Ground Water | GEOCOMFORT | GVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519770 |  | Ground Water | HYDRON MODULE | HVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519771 |  | Ground Water | TETCO | TVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519772 |  | Ground Water | GEOCOMFORT | GVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519773 |  | Ground Water | HYDRON MODULE | HVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519774 |  | Ground Water | TETCO | TVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519775 |  | Ground Water | GEOCOMFORT | GVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
204100658 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204100659 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204100660 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204100661 |  | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204101161 |  | Ground Water | 5 SERIES | NDV/NDH064J1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204117015 |  | Ground Water | GEOSTAR | 101/102J064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204117016 |  | Ground Water | GEOSTAR | 103J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204117017 |  | Ground Water | GEOSTAR | 103J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204140569 |  | Ground Water | GEO-THERMAL SPLIT | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140570 |  | Ground Water | CARRIER | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | No
204140571 |  | Ground Water | BRYANT | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140572 |  | Ground Water | HEIL | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | No
204140573 |  | Ground Water | ARCOAIRE | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140574 |  | Ground Water | KEEPRITE | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140575 |  | Ground Water | TEMPSTAR | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140576 |  | Ground Water | COMFORTMAKER | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140577 |  | Ground Water | DAY & NIGHT | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204272856 |  | Ground Water | GeoSmart Energy | GT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204272857 |  | Ground Water | GeoSmart Energy | GTS064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204272858 |  | Ground Water | GeoSmart Energy | GTS064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204272859 |  | Ground Water | GeoSmart Energy | GTZ064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272860 |  | Ground Water | GeoSmart Energy | GTZ064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272890 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204272892 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272893 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204276830 |  | Ground Water | GEOSTAR | 104J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
214067593 |  | Ground Water | GeoSmart Energy | GBV/GBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067594 |  | Ground Water | GeoSmart Energy | GBV/GBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214067595 |  | Ground Water | GeoSmart Energy | GBV/GBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067596 |  | Ground Water | GeoSmart Energy | GBV/GBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067597 |  | Ground Water | GeoSmart Energy | GBV/GBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067598 |  | Ground Water | GeoSmart Energy | GBV/GBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067600 |  | Ground Water | GeoSmart Energy | GBV/GBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067601 |  | Ground Water | GeoSmart Energy | GBV/GBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
218158127 |  | Ground Water | YORK | Y3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
218338422 |  | Ground Water | GEOSTAR | G5C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
218158015 |  | Ground Water | YORK | Y5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
218158016 |  | Ground Water | YORK | Y5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
218158017 |  | Ground Water | YORK | Y5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
218158018 |  | Ground Water | YORK | Y5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
218158019 |  | Ground Water | YORK | Y5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
218158020 |  | Ground Water | YORK | Y5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
218158021 |  | Ground Water | YORK | Y5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215224679 |  | Ground Water | BOSCH | RF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224680 |  | Ground Water | BOSCH | RF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224681 |  | Ground Water | BOSCH | RF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224682 |  | Ground Water | BOSCH | RF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224683 |  | Ground Water | BOSCH | RF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | Yes
215224684 |  | Ground Water | BOSCH | RF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | Yes
215224685 |  | Ground Water | BOSCH | RF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | Yes
215224686 |  | Ground Water | BOSCH | RF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | Yes
215224687 |  | Ground Water | BOSCH | RF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224688 |  | Ground Water | BOSCH | RF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
217212076 |  | Ground Water | FHP | CP048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212077 |  | Ground Water | FHP | CP048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
217212078 |  | Ground Water | FHP | CP048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212079 |  | Ground Water | FHP | CP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212080 |  | Ground Water | FHP | CP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212082 |  | Ground Water | FHP | CP060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212083 |  | Ground Water | FHP | CP060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212084 |  | Ground Water | FHP | CP060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212085 |  | Ground Water | FHP | CP060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212086 |  | Ground Water | FHP | CP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212088 |  | Ground Water | FHP | CP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212089 |  | Ground Water | FHP | CP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212090 |  | Ground Water | FHP | CP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212091 |  | Ground Water | FHP | CP070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212093 |  | Ground Water | FHP | CP070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212094 |  | Ground Water | FHP | CP070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212095 |  | Ground Water | FHP | CP070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
214772101 |  | Ground Water | TRANE | GEHK0097 |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214772102 |  | Ground Water | TRANE | GEHK0127 |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214772103 |  | Ground Water | TRANE | GEHK0157 |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214772104 |  | Ground Water | TRANE | GEHK0187 |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214772105 |  | Ground Water | TRANE | GEHK024B |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772106 |  | Ground Water | TRANE | GEHK0244 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772107 |  | Ground Water | TRANE | GEHK0247 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772108 |  | Ground Water | TRANE | GEHK030B |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772109 |  | Ground Water | TRANE | GEHK0304 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772110 |  | Ground Water | TRANE | GEHK0307 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772111 |  | Ground Water | TRANE | GEHK036B |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772112 |  | Ground Water | TRANE | GEHK0364 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772113 |  | Ground Water | TRANE | GEHK0367 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772114 |  | Ground Water | TRANE | GEHK042B |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772115 |  | Ground Water | TRANE | GEHK0424 |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772116 |  | Ground Water | TRANE | GEHK048B |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772117 |  | Ground Water | TRANE | GEHK0484 |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772118 |  | Ground Water | TRANE | GEHK060B |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772119 |  | Ground Water | TRANE | GEHK0604 |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772120 |  | Ground Water | TRANE | EXHK0097 |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214772121 |  | Ground Water | TRANE | EXHK0127 |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214772122 |  | Ground Water | TRANE | EXHK0157 |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214772123 |  | Ground Water | TRANE | EXHK0187 |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214772124 |  | Ground Water | TRANE | EXHK024B |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772125 |  | Ground Water | TRANE | EXHK0244 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772126 |  | Ground Water | TRANE | EXHK0247 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772127 |  | Ground Water | TRANE | EXHK030B |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772128 |  | Ground Water | TRANE | EXHK0304 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772129 |  | Ground Water | TRANE | EXHK0307 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772130 |  | Ground Water | TRANE | EXHK036B |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772131 |  | Ground Water | TRANE | EXHK0364 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772132 |  | Ground Water | TRANE | EXHK0367 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772133 |  | Ground Water | TRANE | EXHK042B |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772134 |  | Ground Water | TRANE | EXHK0424 |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772135 |  | Ground Water | TRANE | EXHK048B |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772136 |  | Ground Water | TRANE | EXHK0484 |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772137 |  | Ground Water | TRANE | EXHK060B |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772138 |  | Ground Water | TRANE | EXHK0604 |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772139 |  | Ground Water | TRANE | EXHK070B |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772140 |  | Ground Water | TRANE | EXHK0704 |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772141 |  | Ground Water | TRANE | DXHK024A |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214776185 |  | Ground Water | TRANE | GETK0092-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
214776186 |  | Ground Water | TRANE | GETK0097-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
214776187 |  | Ground Water | TRANE | GETK0122-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776188 |  | Ground Water | TRANE | GETK0127-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776189 |  | Ground Water | TRANE | GETK0152-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776190 |  | Ground Water | TRANE | GETK0157-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776191 |  | Ground Water | TRANE | GETK0182-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
214776192 |  | Ground Water | TRANE | GETK0187-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
214776193 |  | Ground Water | TRANE | GETK0242-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776194 |  | Ground Water | TRANE | GETK0247-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776195 |  | Ground Water | TRANE | GETK0362-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
214776196 |  | Ground Water | TRANE | GETK0367-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
214796343 |  | Ground Water | WaterFurnace | W5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214796344 |  | Ground Water | WaterFurnace | W5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214796345 |  | Ground Water | WaterFurnace | W5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214796346 |  | Ground Water | WaterFurnace | W5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214796347 |  | Ground Water | WaterFurnace | W5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214796667 |  | Ground Water | WaterFurnace | W5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214796668 |  | Ground Water | WaterFurnace | W5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214796669 |  | Ground Water | WaterFurnace | W5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214810491 |  | Ground Water | GEOSTAR | G5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214810492 |  | Ground Water | GEOSTAR | G5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214810493 |  | Ground Water | GEOSTAR | G5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214810494 |  | Ground Water | GEOSTAR | G5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214810495 |  | Ground Water | GEOSTAR | G5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214810496 |  | Ground Water | GEOSTAR | G5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214810497 |  | Ground Water | GEOSTAR | G5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214810498 |  | Ground Water | GEOSTAR | G5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214823444 |  | Ground Water | GeoSmart Energy | S5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214823445 |  | Ground Water | GeoSmart Energy | S5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214823446 |  | Ground Water | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214823447 |  | Ground Water | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214823448 |  | Ground Water | GeoSmart Energy | S5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214823449 |  | Ground Water | GeoSmart Energy | S5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214823450 |  | Ground Water | GeoSmart Energy | S5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214823451 |  | Ground Water | GeoSmart Energy | S5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214837733 |  | Ground Water | BOSCH | EC072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837734 |  | Ground Water | BOSCH | EC072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837735 |  | Ground Water | BOSCH | EC072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837736 |  | Ground Water | BOSCH | EC096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837737 |  | Ground Water | BOSCH | EC096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837738 |  | Ground Water | BOSCH | EC096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
217351731 |  | Ground Water | CARRIER | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351732 |  | Ground Water | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351733 |  | Ground Water | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351734 |  | Ground Water | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351735 |  | Ground Water | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351736 |  | Ground Water | CARRIER | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351738 |  | Ground Water | CARRIER | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351739 |  | Ground Water | CARRIER | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351741 |  | Ground Water | CARRIER | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351742 |  | Ground Water | CARRIER | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351743 |  | Ground Water | CARRIER | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351744 |  | Ground Water | CARRIER | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351745 |  | Ground Water | CARRIER | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351746 |  | Ground Water | CARRIER | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351747 |  | Ground Water | CARRIER | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351749 |  | Ground Water | CARRIER | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351750 |  | Ground Water | CARRIER | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351752 |  | Ground Water | CARRIER | GW024WA********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351754 |  | Ground Water | CARRIER | GW048WA********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351757 |  | Ground Water | BRYANT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351758 |  | Ground Water | BRYANT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351759 |  | Ground Water | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351760 |  | Ground Water | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351761 |  | Ground Water | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351762 |  | Ground Water | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351763 |  | Ground Water | BRYANT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351765 |  | Ground Water | BRYANT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351766 |  | Ground Water | BRYANT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351768 |  | Ground Water | BRYANT | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351769 |  | Ground Water | BRYANT | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351770 |  | Ground Water | BRYANT | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351771 |  | Ground Water | BRYANT | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351772 |  | Ground Water | BRYANT | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351773 |  | Ground Water | BRYANT | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351774 |  | Ground Water | BRYANT | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351776 |  | Ground Water | BRYANT | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351777 |  | Ground Water | BRYANT | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351779 |  | Ground Water | BRYANT | GW024WA********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351781 |  | Ground Water | BRYANT | GW048WA********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351784 |  | Ground Water | ARCOAIRE | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351785 |  | Ground Water | ARCOAIRE | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351786 |  | Ground Water | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
9100310 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100311 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100313 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100314 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100316 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100317 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100319 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100320 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100325 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
9100326 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
205767490 |  | Ground Water | ClimateMaster | TSH/V/D018B*K |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205767496 |  | Ground Water | ClimateMaster | TCH/V015A |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205767497 |  | Ground Water | ClimateMaster | TCH/V018A |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205767508 |  | Ground Water | ClimateMaster | TRH/V015A |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205767509 |  | Ground Water | ClimateMaster | TRH/V018A |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205767513 |  | Ground Water | ClimateMaster | TSH/V/D024C |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | Yes
205767514 |  | Ground Water | ClimateMaster | TSH/V/D024C*K |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | Yes
205767515 |  | Ground Water | ClimateMaster | TSH/V/D030C |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | Yes
205767516 |  | Ground Water | ClimateMaster | TSH/V/D030C*K |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
205767517 |  | Ground Water | ClimateMaster | TSH/V/D036C |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | Yes
205767518 |  | Ground Water | ClimateMaster | TSH/V/D036C*K |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | Yes
205767519 |  | Ground Water | ClimateMaster | TSH/V/D042C |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | Yes
205767520 |  | Ground Water | ClimateMaster | TSH/V/D042C*K |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205767521 |  | Ground Water | ClimateMaster | TSH/V/D048C*K |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | Yes
205767522 |  | Ground Water | ClimateMaster | TSH/V/D060C |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | Yes
205767523 |  | Ground Water | ClimateMaster | TSH/V/D060C*K |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | Yes
205767525 |  | Ground Water | ClimateMaster | TSH/V/D070C*K |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | Yes
205767526 |  | Ground Water | ClimateMaster | TSH/V009A |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
216054489 |  | Ground Water | GEOCOMFORT | GYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216054492 |  | Ground Water | GEOCOMFORT | GZT024* |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
216054493 |  | Ground Water | GEOCOMFORT | GZT030* |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
216054494 |  | Ground Water | GEOCOMFORT | GZT036* |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
216054495 |  | Ground Water | GEOCOMFORT | GZT042* |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
216054496 |  | Ground Water | GEOCOMFORT | GZT048* |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
216054497 |  | Ground Water | GEOCOMFORT | GZT060* |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
216054498 |  | Ground Water | GEOCOMFORT | GVS006* |  | 7600 | 25.9 | 6500 | 4.4 | 0.63333 | Yes
216054499 |  | Ground Water | GEOCOMFORT | GVS015* |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
216054500 |  | Ground Water | GEOCOMFORT | GZS006* |  | 6900 | 22.9 | 6300 | 4.3 | 0.575 | Yes
216057509 |  | Ground Water | GEOCOMFORT | GBT060* | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
216057511 |  | Ground Water | GEOCOMFORT | GVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216057512 |  | Ground Water | GEOCOMFORT | GYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216057513 |  | Ground Water | GEOCOMFORT | GZS015* |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
216057514 |  | Ground Water | GEOCOMFORT | GZS017* |  | 18000 | 21.9 | 15800 | 4.1 | 1.5 | Yes
216057515 |  | Ground Water | GEOCOMFORT | GZS018* |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
216057517 |  | Ground Water | GEOCOMFORT | GYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216065302 |  | Ground Water | GEOCOMFORT | GWS036* |  | 35600 | 22.9 | 38300 | 4.1 | 2.9667 | Yes
216065303 |  | Ground Water | GEOCOMFORT | GWS048* |  | 52500 | 22.9 | 58700 | 4.2 | 4.375 | Yes
216065306 |  | Ground Water | GEOCOMFORT | GWT048* |  | 52700 | 21.2 | 61100 | 4.2 | 4.3917 | Yes
216128491 |  | Ground Water | GEOSTAR | G5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216128493 |  | Ground Water | GEOSTAR | G5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216128495 |  | Ground Water | GEOSTAR | G5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216128497 |  | Ground Water | GEOSTAR | G5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216411469 |  | Ground Water | ClimateMaster | SJ/PN024A | SAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
216411470 |  | Ground Water | ClimateMaster | SJ/PN036A | SAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
216411471 |  | Ground Water | ClimateMaster | SJ/PN048A | SAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
216411472 |  | Ground Water | ClimateMaster | SJ/PN060A | SAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
216419856 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
216419857 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
216419860 |  | Ground Water | Whalen | WC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415734 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)024A*B |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415735 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)024A*C |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415736 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)024A*VB |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415737 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)024A*VC |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415740 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)030A*VB |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415741 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)030A*VC |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415744 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)036A*VB |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415745 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)036A*VC |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415748 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)042A*VB |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415749 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)042A*VC |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415750 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)048A*B |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415751 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)048A*C |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415752 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)048A*VB |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415753 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)048A*VC |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415756 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)060A*VB |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415757 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)060A*VC |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415770 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)015A*B |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415771 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)015A*C |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415772 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)015A*VB |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415773 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)015A*VC |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415774 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)018A*B |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415775 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)018A*C |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415776 |  | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)018A*VB |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415777 |  | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)018A*VC |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415778 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)024A*B |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415779 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)024A*C |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415780 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)024A*VB |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415781 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)024A*VC |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415784 |  | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)030A*VB |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415785 |  | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)030A*VC |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
217754991 |  | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217754992 |  | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217754993 |  | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755000 |  | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755001 |  | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755002 |  | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
8740369 |  | Ground Water | HYDRON MODULE | HVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
8740370 |  | Ground Water | TETCO | TVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
8740371 |  | Ground Water | GEOCOMFORT | GVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740372 |  | Ground Water | HYDRON MODULE | HVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740373 |  | Ground Water | TETCO | TVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740374 |  | Ground Water | GEOCOMFORT | GVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740375 |  | Ground Water | HYDRON MODULE | HVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740376 |  | Ground Water | TETCO | TVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8791878 |  | Ground Water | GEOSTAR | 101/102H060**1*(1,4)***** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791879 |  | Ground Water | GeoSmart Energy | GS060**1*(1,4)********H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791880 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791883 |  | Ground Water | GEOSTAR | 101/102H060**1*0***** |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8791884 |  | Ground Water | GeoSmart Energy | GS060**1*0********H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8791885 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*0****H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8963989 |  | Ground Water | HEIL | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | No
8963990 |  | Ground Water | ARCOAIRE | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963991 |  | Ground Water | COMFORTMAKER | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963992 |  | Ground Water | DAY & NIGHT | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963993 |  | Ground Water | TEMPSTAR | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963994 |  | Ground Water | KEEPRITE | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8964157 |  | Ground Water | BRYANT | GC036C/H/V******1*X1 + UI |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
8964158 |  | Ground Water | CARRIER | GC036C/H/V******1**1 + UI |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
8964161 |  | Ground Water | BRYANT | GC060C/H/V******1*X1 + UI |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
8964162 |  | Ground Water | CARRIER | GC060C/H/V******1**1 + UI |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
8964163 |  | Ground Water | BRYANT | GC072C/H/V******1*X1 + UI |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
8964164 |  | Ground Water | CARRIER | GC072C/H/V******1**1 + UI |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
204276831 |  | Ground Water | GEOSTAR | 103J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
204278291 |  | Ground Water | WaterFurnace | SDV038J1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
204283848 |  | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | SM048-1AH*******A | 52800 | 21.15 | 46600 | 4.4 | 4.4 | Yes
204283849 |  | Ground Water | BOSCH | SM048-1CS*-*****A | SM048-1AH*******A | 52800 | 21.15 | 46600 | 4.4 | 4.4 | Yes
204346746 |  | Ground Water | GeoCool | GCHPV/H/D024T**A*** |  | 29000 | 27.4 | 25700 | 5.4 | 2.4167 | No
204346873 |  | Ground Water | GeoCool | GCHPV/H/D036T**A*** |  | 43000 | 27.2 | 38000 | 5.3 | 3.5833 | No
204346874 |  | Ground Water | GeoCool | GCHPV/H/D048T**A*** |  | 56000 | 26 | 50000 | 4.9 | 4.6667 | No
204370721 |  | Ground Water | GeoCool | GCHPV/H/D060T**A*** |  | 72500 | 24 | 64500 | 4.9 | 6.0417 | No
218157903 |  | Ground Water | YORK | Y5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
218157904 |  | Ground Water | YORK | Y5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
218157905 |  | Ground Water | YORK | Y5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
218157906 |  | Ground Water | YORK | Y5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
218157907 |  | Ground Water | YORK | Y5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
218157908 |  | Ground Water | YORK | Y5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
218157909 |  | Ground Water | YORK | Y5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
218157910 |  | Ground Water | YORK | Y5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
218157911 |  | Ground Water | YORK | Y5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
218157912 |  | Ground Water | YORK | Y5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
218157913 |  | Ground Water | YORK | Y5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
218157914 |  | Ground Water | YORK | Y5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
218157915 |  | Ground Water | YORK | Y5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
218157916 |  | Ground Water | YORK | Y5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
218157917 |  | Ground Water | YORK | Y5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
218157918 |  | Ground Water | YORK | Y5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218157919 |  | Ground Water | YORK | Y5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218157920 |  | Ground Water | YORK | Y5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218157921 |  | Ground Water | YORK | Y5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218157922 |  | Ground Water | YORK | Y5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218157923 |  | Ground Water | YORK | Y5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218157924 |  | Ground Water | YORK | Y5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218157925 |  | Ground Water | YORK | Y5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
218157926 |  | Ground Water | YORK | Y5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
218157927 |  | Ground Water | YORK | Y5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
218157928 |  | Ground Water | YORK | Y5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
218157929 |  | Ground Water | YORK | Y5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
218157930 |  | Ground Water | YORK | Y5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
218157931 |  | Ground Water | YORK | Y5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
218157932 |  | Ground Water | YORK | Y5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
218157933 |  | Ground Water | YORK | Y5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
218157934 |  | Ground Water | YORK | Y5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
218157935 |  | Ground Water | YORK | Y5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
218157936 |  | Ground Water | YORK | Y5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
218157937 |  | Ground Water | YORK | Y5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
218157938 |  | Ground Water | YORK | Y5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
218157939 |  | Ground Water | YORK | Y5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
218157940 |  | Ground Water | YORK | Y5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
218157941 |  | Ground Water | YORK | Y5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
218157942 |  | Ground Water | YORK | Y5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157943 |  | Ground Water | YORK | Y5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157944 |  | Ground Water | YORK | Y5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157945 |  | Ground Water | YORK | Y5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
218157946 |  | Ground Water | YORK | Y5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215832281 |  | Ground Water | HYDROTECH | WSH6009D* |  | 10000 | 23 | 8000 | 4.2 | 0.83333 | No
215832282 |  | Ground Water | HYDROTECH | WSH6012D* |  | 13000 | 23 | 11000 | 4.6 | 1.0833 | No
215832283 |  | Ground Water | HYDROTECH | WSH6018D* |  | 20400 | 25 | 16000 | 4.3 | 1.7 | No
215832284 |  | Ground Water | HYDROTECH | WSH6024D* |  | 28000 | 25 | 21400 | 4.3 | 2.3333 | No
215832285 |  | Ground Water | HYDROTECH | WSH6030D* |  | 32400 | 24 | 26000 | 4.2 | 2.7 | No
215832286 |  | Ground Water | HYDROTECH | WSH6036D* |  | 39000 | 23.2 | 35000 | 4.1 | 3.25 | No
215832287 |  | Ground Water | HYDROTECH | WSH6042D* |  | 45500 | 23.3 | 38000 | 4.3 | 3.7917 | No
215832288 |  | Ground Water | HYDROTECH | WSH6048D* |  | 52500 | 23.6 | 45500 | 4.2 | 4.375 | No
215832289 |  | Ground Water | HYDROTECH | WSH6060D* |  | 64000 | 23.5 | 51000 | 4.3 | 5.3333 | No
215832290 |  | Ground Water | HYDROTECH | WSH6072D* |  | 78000 | 21.8 | 68000 | 4.1 | 6.5 | No
215832291 |  | Ground Water | AE Air | WSH6009D* |  | 10000 | 23 | 8000 | 4.2 | 0.83333 | No
215832292 |  | Ground Water | AE Air | WSH6012D* |  | 13000 | 23 | 11000 | 4.6 | 1.0833 | No
215832293 |  | Ground Water | AE Air | WSH6018D* |  | 20400 | 25 | 16000 | 4.3 | 1.7 | No
215832294 |  | Ground Water | AE Air | WSH6024D* |  | 28000 | 25 | 21400 | 4.3 | 2.3333 | No
215832295 |  | Ground Water | AE Air | WSH6030D* |  | 32400 | 24 | 26000 | 4.2 | 2.7 | No
215832296 |  | Ground Water | AE Air | WSH6036D* |  | 39000 | 23.2 | 35000 | 4.1 | 3.25 | No
215832297 |  | Ground Water | AE Air | WSH6042D* |  | 45500 | 23.3 | 38000 | 4.3 | 3.7917 | No
215832298 |  | Ground Water | AE Air | WSH6048D* |  | 52500 | 23.6 | 45500 | 4.2 | 4.375 | No
215832299 |  | Ground Water | AE Air | WSH6060D* |  | 64000 | 23.5 | 51000 | 4.3 | 5.3333 | No
215832300 |  | Ground Water | AE Air | WSH6072D* |  | 78000 | 21.8 | 68000 | 4.1 | 6.5 | No
217903488 |  | Ground Water | WaterFurnace | V5R072*D0**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903489 |  | Ground Water | WaterFurnace | V5R072*D3**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903490 |  | Ground Water | WaterFurnace | V5R072*D3**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903491 |  | Ground Water | WaterFurnace | V5R072*D3**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903492 |  | Ground Water | WaterFurnace | V5R096*T3**5* |  | 96600 | 24.9 | 85800 | 4.5 | 8.05 | No
217903493 |  | Ground Water | WaterFurnace | V5R120*T3**5* |  | 128500 | 23.3 | 113700 | 4.5 | 10.7083 | No
217967018 |  | Ground Water | TRANE | VSHK024A |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
203459725 |  | Ground Water | FHP | LM036-1CSC-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459726 |  | Ground Water | FHP | LM036-1CSN-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459727 |  | Ground Water | FHP | LM048-1CSC-*****A | LM048-1AV/AH*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
203459750 |  | Ground Water | BOSCH | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | No
203459757 |  | Ground Water | FHP | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | No
203466717 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
203471325 |  | Ground Water | 5 SERIES INDOOR SPLITS | NDZ049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
203490411 |  | Ground Water | GeoSmart Energy | GTZ049*1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
203490420 |  | Ground Water | GeoSmart Energy | GTZ049*1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
203495469 |  | Ground Water | GEOSTAR | 101/102J049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203495470 |  | Ground Water | GEOSTAR | 103J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
203495474 |  | Ground Water | GEOSTAR | 103J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
203817319 |  | Ground Water | BOSCH-GEO | CE061-1HZC-*****B |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818209 |  | Ground Water | CARRIER | GP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818210 |  | Ground Water | BRYANT | GP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818211 |  | Ground Water | HEIL | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818212 |  | Ground Water | ARCOAIRE | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818214 |  | Ground Water | KEEPRITE | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818215 |  | Ground Water | TEMPSTAR | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818216 |  | Ground Water | COMFORTMAKER | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818217 |  | Ground Water | DAY & NIGHT | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818278 |  | Ground Water | BOSCH | CE061-1HZC-*****B |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203993050 |  | Ground Water | GEOSTAR | 111H049**1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
211594273 |  | Ground Water | TRANE | DXHG070B |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
211594274 |  | Ground Water | TRANE | DXHG0704 |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
212428693 |  | Ground Water | HYDROTECH | WSH6009A6* |  | 10000 | 23 | 8500 | 4.2 | 0.83333 | Yes
212428694 |  | Ground Water | HYDROTECH | WSH6012A6* |  | 12500 | 23.1 | 11000 | 4.6 | 1.0417 | Yes
212428695 |  | Ground Water | HYDROTECH | WSH6018A6* |  | 20500 | 26 | 16000 | 4.3 | 1.7083 | Yes
212428696 |  | Ground Water | HYDROTECH | WSH6024A6* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | Yes
212428697 |  | Ground Water | HYDROTECH | WSH6030A6* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | Yes
212428698 |  | Ground Water | HYDROTECH | WSH6036A6* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | Yes
212428699 |  | Ground Water | HYDROTECH | WSH6042A6* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | Yes
212428700 |  | Ground Water | HYDROTECH | WSH6048A6* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | Yes
212428701 |  | Ground Water | AE Air | WSH6009A6* |  | 10000 | 23 | 8500 | 4.2 | 0.83333 | Yes
212428702 |  | Ground Water | AE Air | WSH6012A6* |  | 12500 | 23.1 | 11000 | 4.6 | 1.0417 | Yes
212428703 |  | Ground Water | AE Air | WSH6018A6* |  | 20500 | 26 | 16000 | 4.3 | 1.7083 | Yes
212428704 |  | Ground Water | AE Air | WSH6024A6* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | Yes
212428705 |  | Ground Water | AE Air | WSH6030A6* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | Yes
212428706 |  | Ground Water | AE Air | WSH6036A6* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | Yes
212428707 |  | Ground Water | AE Air | WSH6042A6* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | Yes
212428708 |  | Ground Water | AE Air | WSH6048A6* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | Yes
212505502 |  | Ground Water | HYDROTECH | WSH6060A6* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | Yes
212505503 |  | Ground Water | HYDROTECH | WSH6072A6* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | Yes
212505505 |  | Ground Water | AE Air | WSH6060A6* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | Yes
212505506 |  | Ground Water | AE Air | WSH6072A6* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | Yes
212505509 |  | Ground Water | HYDROTECH | WSH6036AM* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212505510 |  | Ground Water | HYDROTECH | WSH6042AM* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
217351073 |  | Ground Water | BOSCH | CP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
217351074 |  | Ground Water | BOSCH | CP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
217351075 |  | Ground Water | BOSCH | CP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
217351076 |  | Ground Water | BOSCH | CP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
217351077 |  | Ground Water | BOSCH | CP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
217351078 |  | Ground Water | BOSCH | CP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
217351079 |  | Ground Water | BOSCH | CP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | No
217351080 |  | Ground Water | BOSCH | CP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | No
217351081 |  | Ground Water | BOSCH | CP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | No
217351082 |  | Ground Water | BOSCH | CP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | No
217351083 |  | Ground Water | BOSCH | CP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | No
217351084 |  | Ground Water | BOSCH | CP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | No
217351086 |  | Ground Water | BOSCH | CP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | No
217351087 |  | Ground Water | BOSCH-GEO | RP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
217351088 |  | Ground Water | BOSCH-GEO | RP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
217351089 |  | Ground Water | BOSCH-GEO | RP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
217351090 |  | Ground Water | BOSCH-GEO | RP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
217351091 |  | Ground Water | BOSCH-GEO | RP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
217351092 |  | Ground Water | BOSCH-GEO | RP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
217351093 |  | Ground Water | BOSCH-GEO | RP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
217351094 |  | Ground Water | BOSCH-GEO | RP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
217351095 |  | Ground Water | BOSCH-GEO | RP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | Yes
217351096 |  | Ground Water | BOSCH-GEO | RP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | Yes
217351097 |  | Ground Water | BOSCH-GEO | RP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | Yes
217351098 |  | Ground Water | BOSCH-GEO | RP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | Yes
217351099 |  | Ground Water | BOSCH-GEO | RP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | Yes
217351100 |  | Ground Water | BOSCH-GEO | RP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | Yes
217351102 |  | Ground Water | BOSCH-GEO | RP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | Yes
217351103 |  | Ground Water | GEO-THERMAL SPLIT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351104 |  | Ground Water | GEO-THERMAL SPLIT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351105 |  | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351106 |  | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351107 |  | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351108 |  | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351109 |  | Ground Water | GEO-THERMAL SPLIT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351111 |  | Ground Water | GEO-THERMAL SPLIT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351112 |  | Ground Water | GEO-THERMAL SPLIT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351114 |  | Ground Water | GEO-THERMAL SPLIT | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351115 |  | Ground Water | GEO-THERMAL SPLIT | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351116 |  | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351117 |  | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351118 |  | Ground Water | GEO-THERMAL SPLIT | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351119 |  | Ground Water | GEO-THERMAL SPLIT | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351120 |  | Ground Water | GEO-THERMAL SPLIT | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351122 |  | Ground Water | GEO-THERMAL SPLIT | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351123 |  | Ground Water | GEO-THERMAL SPLIT | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351671 |  | Ground Water | BOSCH | RP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
217351672 |  | Ground Water | BOSCH | RP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
217351673 |  | Ground Water | BOSCH | RP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
217351674 |  | Ground Water | BOSCH | RP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
202547467 |  | Ground Water | FHP | EC096-1VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547468 |  | Ground Water | FHP | EC096-3VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547469 |  | Ground Water | FHP | EC096-4VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
8735477 |  | Ground Water | GEOCOMFORT | GVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735495 |  | Ground Water | HYDRON MODULE | HVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735512 |  | Ground Water | TETCO | TVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735538 |  | Ground Water | GEOCOMFORT | GVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735552 |  | Ground Water | HYDRON MODULE | HVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735567 |  | Ground Water | TETCO | TVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735607 |  | Ground Water | GEOCOMFORT | GVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735711 |  | Ground Water | HYDRON MODULE | HVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735721 |  | Ground Water | TETCO | TVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735754 |  | Ground Water | GEOCOMFORT | GVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735767 |  | Ground Water | HYDRON MODULE | HVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735778 |  | Ground Water | TETCO | TVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735903 |  | Ground Water | GEOCOMFORT | GVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735904 |  | Ground Water | HYDRON MODULE | HVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735905 |  | Ground Water | TETCO | TVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735906 |  | Ground Water | GEOCOMFORT | GVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735907 |  | Ground Water | HYDRON MODULE | HVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735908 |  | Ground Water | TETCO | TVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735909 |  | Ground Water | GEOCOMFORT | GVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735910 |  | Ground Water | HYDRON MODULE | HVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735911 |  | Ground Water | TETCO | TVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8737970 |  | Ground Water | GEOCOMFORT | GVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737971 |  | Ground Water | HYDRON MODULE | HVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737972 |  | Ground Water | TETCO | TVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737973 |  | Ground Water | GEOCOMFORT | GVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737974 |  | Ground Water | HYDRON MODULE | HVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737975 |  | Ground Water | TETCO | TVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737976 |  | Ground Water | GEOCOMFORT | GVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737977 |  | Ground Water | HYDRON MODULE | HVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737978 |  | Ground Water | TETCO | TVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737982 |  | Ground Water | GEOCOMFORT | GVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737983 |  | Ground Water | HYDRON MODULE | HVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737984 |  | Ground Water | TETCO | TVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737985 |  | Ground Water | GEOCOMFORT | GVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737986 |  | Ground Water | HYDRON MODULE | HVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737987 |  | Ground Water | TETCO | TVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737988 |  | Ground Water | GEOCOMFORT | GVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737989 |  | Ground Water | HYDRON MODULE | HVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737990 |  | Ground Water | TETCO | TVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737991 |  | Ground Water | GEOCOMFORT | GVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737992 |  | Ground Water | HYDRON MODULE | HVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737993 |  | Ground Water | TETCO | TVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8738031 |  | Ground Water | GEOCOMFORT | GVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738032 |  | Ground Water | HYDRON MODULE | HVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738033 |  | Ground Water | TETCO | TVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738034 |  | Ground Water | GEOCOMFORT | GVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738035 |  | Ground Water | HYDRON MODULE | HVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738036 |  | Ground Water | TETCO | TVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738037 |  | Ground Water | GEOCOMFORT | GVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738038 |  | Ground Water | HYDRON MODULE | HVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738039 |  | Ground Water | TETCO | TVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738040 |  | Ground Water | GEOCOMFORT | GVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
8738041 |  | Ground Water | HYDRON MODULE | HVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
205311991 |  | Ground Water | GEOSTAR | ZBV/ZBH036**0*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311992 |  | Ground Water | GEOSTAR | ZBV/ZBH036**2*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311993 |  | Ground Water | GEOSTAR | ZBV/ZBH036**3*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311994 |  | Ground Water | GEOSTAR | ZBV/ZBH036**4*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311995 |  | Ground Water | GEOSTAR | ZBV/ZBH036**0*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311996 |  | Ground Water | GEOSTAR | ZBV/ZBH036**2*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311997 |  | Ground Water | GEOSTAR | ZBV/ZBH036**3*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311998 |  | Ground Water | GEOSTAR | ZBV/ZBH036**4*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311999 |  | Ground Water | GEOSTAR | ZBV/ZBH036**0*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312000 |  | Ground Water | GEOSTAR | ZBV/ZBH036**2*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312001 |  | Ground Water | GEOSTAR | ZBV/ZBH036**3*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312002 |  | Ground Water | GEOSTAR | ZBV/ZBH036**4*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312006 |  | Ground Water | GEOSTAR | ZBV/ZBH042**0*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312007 |  | Ground Water | GEOSTAR | ZBV/ZBH042**3*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312008 |  | Ground Water | GEOSTAR | ZBV/ZBH042**4*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312009 |  | Ground Water | GEOSTAR | ZBV/ZBH042**0*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312010 |  | Ground Water | GEOSTAR | ZBV/ZBH042**3*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312011 |  | Ground Water | GEOSTAR | ZBV/ZBH042**4*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202541572 |  | Ground Water | BOSCH-GEO | BP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202541573 |  | Ground Water | BOSCH | BP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202541574 |  | Ground Water | CARRIER | GB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202541575 |  | Ground Water | BRYANT | GB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202543170 |  | Ground Water | CARRIER | GB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202543171 |  | Ground Water | BRYANT | GB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202547425 |  | Ground Water | BOSCH | EC096-1VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547426 |  | Ground Water | BOSCH | EC096-3VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547427 |  | Ground Water | BOSCH | EC096-4VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
207335591 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335592 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335593 |  | Ground Water | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207337449 |  | Ground Water | GEOSTAR | 12(1,2)A048 |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
207337469 |  | Ground Water | GEOSTAR | 103H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337470 |  | Ground Water | GEOSTAR | 103H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337471 |  | Ground Water | GEOSTAR | 163H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337472 |  | Ground Water | GEOSTAR | 163H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337473 |  | Ground Water | GEOSTAR | 104H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337474 |  | Ground Water | GEOSTAR | 104H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337475 |  | Ground Water | GEOSTAR | 164H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337476 |  | Ground Water | GEOSTAR | 164H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337477 |  | Ground Water | GEOSTAR | 103J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337478 |  | Ground Water | GEOSTAR | 103J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337479 |  | Ground Water | GEOSTAR | 163J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337480 |  | Ground Water | GEOSTAR | 163J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202146980 |  | Ground Water | HYDRON MODULE | HZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146981 |  | Ground Water | HYDRON MODULE | HZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146982 |  | Ground Water | HYDRON MODULE | HZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
202146983 |  | Ground Water | HYDRON MODULE | HZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146984 |  | Ground Water | TETCO | TZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
202146985 |  | Ground Water | TETCO | TZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146986 |  | Ground Water | TETCO | TZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146987 |  | Ground Water | TETCO | TZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146988 |  | Ground Water | TETCO | TZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146989 |  | Ground Water | TETCO | TZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
202146990 |  | Ground Water | TETCO | TZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146991 |  | Ground Water | GEOCOMFORT | GZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
202146992 |  | Ground Water | GEOCOMFORT | GZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146993 |  | Ground Water | GEOCOMFORT | GZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146994 |  | Ground Water | GEOCOMFORT | GZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146995 |  | Ground Water | GEOCOMFORT | GZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146996 |  | Ground Water | GEOCOMFORT | GZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
202146997 |  | Ground Water | GEOCOMFORT | GZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202146998 |  | Ground Water | GEOCOMFORT | GZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202146999 |  | Ground Water | GEOCOMFORT | GZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147000 |  | Ground Water | HYDRON MODULE | HZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
202147001 |  | Ground Water | HYDRON MODULE | HZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147002 |  | Ground Water | HYDRON MODULE | HZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147003 |  | Ground Water | HYDRON MODULE | HZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
206438903 |  | Ground Water | CARRIER | 50PSV012**C3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438904 |  | Ground Water | CARRIER | 50PSH012**C3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438905 |  | Ground Water | CARRIER | 50PSV012**N3/CA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438906 |  | Ground Water | CARRIER | 50PSH012**N3/CA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438907 |  | Ground Water | CARRIER | 50PSV012**C0/BA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438908 |  | Ground Water | CARRIER | 50PSV012**C4/DA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438909 |  | Ground Water | CARRIER | 50PSH012**C0/BA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438910 |  | Ground Water | CARRIER | 50PSH012**C4/DA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438911 |  | Ground Water | CARRIER | 50PSV012**N0/BA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438912 |  | Ground Water | CARRIER | 50PSV012**N4/DA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438913 |  | Ground Water | CARRIER | 50PSH012**N0/BA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438914 |  | Ground Water | CARRIER | 50PSH012**N4/DA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206570649 |  | Ground Water | 7 SERIES | NVV/NVH036C1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206570651 |  | Ground Water | 7 SERIES | NVV/NVH060C1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206570652 |  | Ground Water | GEOSTAR | 141/142C036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206570654 |  | Ground Water | GEOSTAR | 141/142C060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206598629 |  | Ground Water | GeoSmart Energy | VI036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206598631 |  | Ground Water | GeoSmart Energy | VI060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206598632 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206598634 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFV060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206608717 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048J1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608718 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048J1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608719 |  | Ground Water | GEOSTAR | 103J048**1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608720 |  | Ground Water | GEOSTAR | 103J048**1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608721 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060J1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608722 |  | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060J1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608723 |  | Ground Water | GEOSTAR | 103J060**1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608724 |  | Ground Water | GEOSTAR | 103J060**1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206611110 |  | Ground Water | COMFORT-AIRE | HEH/V024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
206611111 |  | Ground Water | CENTURY | HEH/V024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
206611114 |  | Ground Water | COMFORT-AIRE | HEH/V036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206611115 |  | Ground Water | CENTURY | HEH/V036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206611116 |  | Ground Water | COMFORT-AIRE | HEH/V042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
206611117 |  | Ground Water | CENTURY | HEH/V042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
206611120 |  | Ground Water | COMFORT-AIRE | HEH/V060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
206611121 |  | Ground Water | CENTURY | HEH/V060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
207349385 |  | Ground Water | WaterFurnace | NBV/NBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349386 |  | Ground Water | WaterFurnace | NBV/NBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349387 |  | Ground Water | WaterFurnace | NBV/NBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202350503 |  | Ground Water | AAON, Inc. | M2-014-4-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
215224599 |  | Ground Water | CARRIER | 50WD*007***3*(A-H)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224600 |  | Ground Water | CARRIER | 50WD*007***3*(J-R)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224601 |  | Ground Water | CARRIER | 50WD*007***4*(A-H)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224602 |  | Ground Water | CARRIER | 50WD*007***4*(J-R)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224603 |  | Ground Water | CARRIER | 50WD*009***3*(A-H)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224604 |  | Ground Water | CARRIER | 50WD*009***3*(J-R)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224605 |  | Ground Water | CARRIER | 50WD*009***4*(A-H)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
217351919 |  | Ground Water | TEMPSTAR | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351920 |  | Ground Water | TEMPSTAR | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351921 |  | Ground Water | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351922 |  | Ground Water | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351923 |  | Ground Water | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351924 |  | Ground Water | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351925 |  | Ground Water | TEMPSTAR | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351927 |  | Ground Water | TEMPSTAR | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351928 |  | Ground Water | TEMPSTAR | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351930 |  | Ground Water | TEMPSTAR | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351931 |  | Ground Water | TEMPSTAR | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351932 |  | Ground Water | TEMPSTAR | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351933 |  | Ground Water | TEMPSTAR | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351934 |  | Ground Water | TEMPSTAR | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351935 |  | Ground Water | TEMPSTAR | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351936 |  | Ground Water | TEMPSTAR | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351938 |  | Ground Water | TEMPSTAR | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351939 |  | Ground Water | TEMPSTAR | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351941 |  | Ground Water | TEMPSTAR | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351943 |  | Ground Water | TEMPSTAR | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
6677754 |  | Ground Water | BOSCH | LM048-4VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
6677875 |  | Ground Water | BOSCH | LM060-1VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677876 |  | Ground Water | BOSCH | LM060-3VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677878 |  | Ground Water | BOSCH | LM060-4VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677886 |  | Ground Water | BOSCH | LM070-1VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
6677887 |  | Ground Water | BOSCH | LM070-3VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
6677889 |  | Ground Water | BOSCH | LM070-4VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
217014550 |  | Ground Water | HEIL | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014551 |  | Ground Water | ARCOAIRE | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014552 |  | Ground Water | KEEPRITE | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014553 |  | Ground Water | TEMPSTAR | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014554 |  | Ground Water | COMFORTMAKER | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014555 |  | Ground Water | DAY & NIGHT | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217037811 |  | Ground Water | GeoSmart Energy | S5SS024BD1 | S5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037812 |  | Ground Water | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037813 |  | Ground Water | GeoSmart Energy | S5SS048BD1 | S5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037814 |  | Ground Water | GeoSmart Energy | S5SS060BD1 | S5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037815 |  | Ground Water | GeoSmart Energy | S5SS066BD1 | S5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037816 |  | Ground Water | GeoSmart Energy | S5SZ024BD1 | S5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037817 |  | Ground Water | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037818 |  | Ground Water | GeoSmart Energy | S5SZ048BD1 | S5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037819 |  | Ground Water | GeoSmart Energy | S5SZ060BD1 | S5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037820 |  | Ground Water | GeoSmart Energy | S5SZ066BD1 | S5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037821 |  | Ground Water | GeoSmart Energy | S5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037822 |  | Ground Water | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037823 |  | Ground Water | GeoSmart Energy | S5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037824 |  | Ground Water | GeoSmart Energy | S5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037825 |  | Ground Water | GeoSmart Energy | S5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037826 |  | Ground Water | GeoSmart Energy | S5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037827 |  | Ground Water | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037828 |  | Ground Water | GeoSmart Energy | S5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037829 |  | Ground Water | GeoSmart Energy | S5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037830 |  | Ground Water | GeoSmart Energy | S5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217903452 |  | Ground Water | WaterFurnace | V5R072*S4**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903453 |  | Ground Water | WaterFurnace | V5R072*S4**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903454 |  | Ground Water | WaterFurnace | V5R036*D4**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903455 |  | Ground Water | WaterFurnace | V5R036*D4**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903456 |  | Ground Water | WaterFurnace | V5R036*D4**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903457 |  | Ground Water | WaterFurnace | V5R048*D4**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903458 |  | Ground Water | WaterFurnace | V5R048*D4**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903459 |  | Ground Water | WaterFurnace | V5R048*D4**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903460 |  | Ground Water | WaterFurnace | V5R060*D4**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903461 |  | Ground Water | WaterFurnace | V5R060*D4**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903462 |  | Ground Water | WaterFurnace | V5R060*D4**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903463 |  | Ground Water | WaterFurnace | V5R072*D4**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903464 |  | Ground Water | WaterFurnace | V5R072*D4**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903465 |  | Ground Water | WaterFurnace | V5R072*D4**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903466 |  | Ground Water | WaterFurnace | V5R096*T4**5* |  | 96600 | 24.9 | 85800 | 4.5 | 8.05 | No
217903467 |  | Ground Water | WaterFurnace | V5R120*T4**5* |  | 128500 | 23.3 | 113700 | 4.5 | 10.7083 | No
217903468 |  | Ground Water | WaterFurnace | V5R036*D0**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903469 |  | Ground Water | WaterFurnace | V5R036*D0**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903470 |  | Ground Water | WaterFurnace | V5R036*D0**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903471 |  | Ground Water | WaterFurnace | V5R036*D3**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903472 |  | Ground Water | WaterFurnace | V5R036*D3**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903473 |  | Ground Water | WaterFurnace | V5R036*D3**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903474 |  | Ground Water | WaterFurnace | V5R048*D0**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903475 |  | Ground Water | WaterFurnace | V5R048*D0**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903476 |  | Ground Water | WaterFurnace | V5R048*D0**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903477 |  | Ground Water | WaterFurnace | V5R048*D3**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903478 |  | Ground Water | WaterFurnace | V5R048*D3**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903479 |  | Ground Water | WaterFurnace | V5R048*D3**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903480 |  | Ground Water | WaterFurnace | V5R060*D0**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903481 |  | Ground Water | WaterFurnace | V5R060*D0**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903482 |  | Ground Water | WaterFurnace | V5R060*D0**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903483 |  | Ground Water | WaterFurnace | V5R060*D3**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903484 |  | Ground Water | WaterFurnace | V5R060*D3**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903485 |  | Ground Water | WaterFurnace | V5R060*D3**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903486 |  | Ground Water | WaterFurnace | V5R072*D0**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903487 |  | Ground Water | WaterFurnace | V5R072*D0**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
9100327 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
9100328 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
9100330 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
9100332 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
9100335 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100337 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100338 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100340 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100341 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100343 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100345 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100346 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100348 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100349 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100351 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100352 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100354 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100355 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100357 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100358 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100359 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100361 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100362 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100364 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100365 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100367 |  | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
6501968 |  | Ground Water | GEOSTAR | GBV/GBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501969 |  | Ground Water | GEOSTAR | GBV/GBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501970 |  | Ground Water | GEOSTAR | GBV/GBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501971 |  | Ground Water | GEOSTAR | GBV/GBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501972 |  | Ground Water | GEOSTAR | GBV/GBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501973 |  | Ground Water | GEOSTAR | GBV/GBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501974 |  | Ground Water | GEOSTAR | GBV/GBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501975 |  | Ground Water | GEOSTAR | GBV/GBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501976 |  | Ground Water | GEOSTAR | GBV/GBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501977 |  | Ground Water | GEOSTAR | GBV/GBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501978 |  | Ground Water | GEOSTAR | GBV/GBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501979 |  | Ground Water | GEOSTAR | GBV/GBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501980 |  | Ground Water | GEOSTAR | GBV/GBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501981 |  | Ground Water | GEOSTAR | GBV/GBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501982 |  | Ground Water | GEOSTAR | GBV/GBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501983 |  | Ground Water | GEOSTAR | GBV/GBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501984 |  | Ground Water | GEOSTAR | GBV/GBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501985 |  | Ground Water | GEOSTAR | GBV/GBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501986 |  | Ground Water | GEOSTAR | GBV/GBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501987 |  | Ground Water | GEOSTAR | GBV/GBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501988 |  | Ground Water | GEOSTAR | GBV/GBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501989 |  | Ground Water | GEOSTAR | GBV/GBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501990 |  | Ground Water | GEOSTAR | GBV/GBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501991 |  | Ground Water | GEOSTAR | GBV/GBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501993 |  | Ground Water | GEOSTAR | GBV/GBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501994 |  | Ground Water | GEOSTAR | GBV/GBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501996 |  | Ground Water | GEOSTAR | GBV/GBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501997 |  | Ground Water | GEOSTAR | GBV/GBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501999 |  | Ground Water | GEOSTAR | GBV/GBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6502000 |  | Ground Water | GEOSTAR | GBV/GBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6502002 |  | Ground Water | GEOSTAR | GBV/GBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502003 |  | Ground Water | GEOSTAR | GBV/GBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502004 |  | Ground Water | GEOSTAR | GBV/GBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502005 |  | Ground Water | GEOSTAR | GBV/GBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502006 |  | Ground Water | GEOSTAR | GBV/GBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502007 |  | Ground Water | GEOSTAR | GBV/GBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6674620 |  | Ground Water | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674621 |  | Ground Water | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674622 |  | Ground Water | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674623 |  | Ground Water | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6676515 |  | Ground Water | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676516 |  | Ground Water | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676518 |  | Ground Water | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676519 |  | Ground Water | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6677645 |  | Ground Water | BOSCH | LM048-1VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
6677682 |  | Ground Water | BOSCH | LM048-3VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
202922697 |  | Ground Water | BRYANT | GB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922700 |  | Ground Water | HEIL | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922703 |  | Ground Water | ARCOAIRE | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922706 |  | Ground Water | KEEPRITE | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922708 |  | Ground Water | TEMPSTAR | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922711 |  | Ground Water | COMFORTMAKER | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922714 |  | Ground Water | DAY & NIGHT | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922716 |  | Ground Water | CARRIER | 50PSV036***3/CA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922719 |  | Ground Water | CARRIER | 50PSV036***5/EA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922722 |  | Ground Water | CARRIER | 50PSV036***6/FA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922725 |  | Ground Water | CARRIER | GB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922728 |  | Ground Water | BRYANT | GB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922731 |  | Ground Water | HEIL | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922734 |  | Ground Water | ARCOAIRE | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922737 |  | Ground Water | KEEPRITE | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922740 |  | Ground Water | TEMPSTAR | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922742 |  | Ground Water | COMFORTMAKER | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922745 |  | Ground Water | DAY & NIGHT | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
218353686 |  | Ground Water | JOHNSON CONTROLS | DQ060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
218353687 |  | Ground Water | JOHNSON CONTROLS | DQ070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353688 |  | Ground Water | JOHNSON CONTROLS | DQ070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353689 |  | Ground Water | JOHNSON CONTROLS | DQ070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353690 |  | Ground Water | JOHNSON CONTROLS | DQ070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353691 |  | Ground Water | JOHNSON CONTROLS | DQ070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353692 |  | Ground Water | JOHNSON CONTROLS | DQ070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353693 |  | Ground Water | JOHNSON CONTROLS | DQ070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353694 |  | Ground Water | JOHNSON CONTROLS | DQ070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353695 |  | Ground Water | JOHNSON CONTROLS | DQ070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353696 |  | Ground Water | JOHNSON CONTROLS | DQ070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218353697 |  | Ground Water | JOHNSON CONTROLS | DQ070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
218353698 |  | Ground Water | JOHNSON CONTROLS | DQ070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
218378550 |  | Ground Water | WaterFurnace | W5SZ030BD1 | W5BM030BN1**2 | 29800 | 22.7 | 28900 | 4.5 | 2.4833 | No
218378551 |  | Ground Water | WaterFurnace | W5SZ042BD1 | W5BM042BN1**2 | 43300 | 24.1 | 38300 | 4.6 | 3.6083 | No
218389121 |  | Ground Water | GEOSTAR | G5SZ030BD1 | G5BM030BN1**2 | 29800 | 22.7 | 28900 | 4.5 | 2.4833 | No
218389122 |  | Ground Water | GEOSTAR | G5SZ042BD1 | G5BM042BN1**2 | 43300 | 24.1 | 38300 | 4.6 | 3.6083 | No
218389123 |  | Ground Water | GeoSmart Energy | S5SZ030BD1 | S5BM030BN1**2 | 29800 | 22.7 | 28900 | 4.5 | 2.4833 | No
218389124 |  | Ground Water | GeoSmart Energy | S5SZ042BD1 | S5BM042BN1**2 | 43300 | 24.1 | 38300 | 4.6 | 3.6083 | No
218389125 |  | Ground Water | YORK | Y5SZ030BD1 | Y5BM030BN1**2 | 29800 | 22.7 | 28900 | 4.5 | 2.4833 | No
218389126 |  | Ground Water | YORK | Y5SZ042BD1 | Y5BM042BN1**2 | 43300 | 24.1 | 38300 | 4.6 | 3.6083 | No
218396700 |  | Ground Water | JOHNSON CONTROLS | DH025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
218396701 |  | Ground Water | JOHNSON CONTROLS | DH025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
202211045 |  | Ground Water | WaterFurnace | URD038*3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211046 |  | Ground Water | WaterFurnace | URD038*3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211047 |  | Ground Water | WaterFurnace | URD038*3*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211048 |  | Ground Water | WaterFurnace | URD049*0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
206726850 |  | Ground Water | TETCO | TBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
206726851 |  | Ground Water | GEOCOMFORT | GBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726852 |  | Ground Water | HYDRON MODULE | HBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726853 |  | Ground Water | TETCO | TBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726854 |  | Ground Water | GEOCOMFORT | GBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726855 |  | Ground Water | GEOCOMFORT | GBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726856 |  | Ground Water | HYDRON MODULE | HBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726857 |  | Ground Water | HYDRON MODULE | HBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726858 |  | Ground Water | TETCO | TBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726859 |  | Ground Water | TETCO | TBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726860 |  | Ground Water | GEOCOMFORT | GBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
206726861 |  | Ground Water | GEOCOMFORT | GBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
206726862 |  | Ground Water | HYDRON MODULE | HBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
206726863 |  | Ground Water | HYDRON MODULE | HBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
206726864 |  | Ground Water | TETCO | TBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
206726865 |  | Ground Water | TETCO | TBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
206726878 |  | Ground Water | GEOCOMFORT | GBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726879 |  | Ground Water | HYDRON MODULE | HBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726880 |  | Ground Water | TETCO | TBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726881 |  | Ground Water | GEOCOMFORT | GBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
206726882 |  | Ground Water | HYDRON MODULE | HBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
206726883 |  | Ground Water | TETCO | TBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
206900466 |  | Ground Water | WaterFurnace | UDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900467 |  | Ground Water | WaterFurnace | UDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900469 |  | Ground Water | WaterFurnace | UDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900470 |  | Ground Water | WaterFurnace | UDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900471 |  | Ground Water | WaterFurnace | UDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900472 |  | Ground Water | WaterFurnace | UDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900473 |  | Ground Water | WaterFurnace | UDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900474 |  | Ground Water | WaterFurnace | UDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900475 |  | Ground Water | WaterFurnace | UDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900553 |  | Ground Water | GEOSTAR | GDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900554 |  | Ground Water | GEOSTAR | GDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900555 |  | Ground Water | GEOSTAR | GDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900556 |  | Ground Water | GEOSTAR | GDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
215224027 |  | Ground Water | BOSCH | CF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224028 |  | Ground Water | BOSCH | CF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224029 |  | Ground Water | BOSCH | CF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224030 |  | Ground Water | BOSCH | CF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224031 |  | Ground Water | BOSCH | CF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224032 |  | Ground Water | BOSCH | CF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224033 |  | Ground Water | BOSCH | CF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
7785665 |  | Ground Water | DAIKIN | WVHW3021*J (W/ECM MOTOR) |  | 24100 | 23.2 | 19900 | 4.2 | 2.0083 | No
7795914 |  | Ground Water | GEOCOMFORT | GVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795915 |  | Ground Water | HYDRON MODULE | HVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795916 |  | Ground Water | TETCO | TVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795918 |  | Ground Water | GEOCOMFORT | GVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795919 |  | Ground Water | HYDRON MODULE | HVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795920 |  | Ground Water | TETCO | TVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795921 |  | Ground Water | GEOCOMFORT | GVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795922 |  | Ground Water | HYDRON MODULE | HVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795923 |  | Ground Water | TETCO | TVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795924 |  | Ground Water | GEOCOMFORT | GVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795925 |  | Ground Water | HYDRON MODULE | HVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795926 |  | Ground Water | TETCO | TVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795943 |  | Ground Water | GEOCOMFORT | GVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
7795944 |  | Ground Water | HYDRON MODULE | HVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
7795945 |  | Ground Water | TETCO | TVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
7795946 |  | Ground Water | GEOCOMFORT | GVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795947 |  | Ground Water | HYDRON MODULE | HVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795948 |  | Ground Water | TETCO | TVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795949 |  | Ground Water | GEOCOMFORT | GVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795950 |  | Ground Water | HYDRON MODULE | HVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795951 |  | Ground Water | TETCO | TVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795952 |  | Ground Water | GEOCOMFORT | GVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795953 |  | Ground Water | HYDRON MODULE | HVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795954 |  | Ground Water | TETCO | TVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
8077723 |  | Ground Water | GEOCOMFORT | GYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077724 |  | Ground Water | HYDRON MODULE | HYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077725 |  | Ground Water | TETCO | TYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077726 |  | Ground Water | GEOCOMFORT | GYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
204031803 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
214838955 |  | Ground Water | BOSCH | CL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838956 |  | Ground Water | BOSCH | CL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838957 |  | Ground Water | BOSCH | CL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838958 |  | Ground Water | BOSCH | CL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838959 |  | Ground Water | BOSCH | CL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838960 |  | Ground Water | BOSCH | CL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
216625830 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625831 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625832 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625833 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625834 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625835 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625836 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625837 |  | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
202923075 |  | Ground Water | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
10268198 |  | Ground Water | GEOCOMFORT | GBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268199 |  | Ground Water | HYDRON MODULE | HBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268200 |  | Ground Water | TETCO | TBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
202391369 |  | Ground Water | AQUARIUS | EP012-1VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391370 |  | Ground Water | AQUARIUS | EP012-1HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391371 |  | Ground Water | AQUARIUS | EP012-1VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391372 |  | Ground Water | AQUARIUS | EP012-1HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
205448524 |  | Ground Water | 7 SERIES INDOOR SPLITS | NVZ033A1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | No
7499466 |  | Ground Water | FHP | EP030-2HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499467 |  | Ground Water | FHP | EP030-3HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499468 |  | Ground Water | FHP | EP030-4HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499480 |  | Ground Water | FHP | EP060-1HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499482 |  | Ground Water | FHP | EP060-3HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499483 |  | Ground Water | FHP | EP060-4HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499484 |  | Ground Water | FHP | EP070-1HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7492839 |  | Ground Water | 3 SERIES | LD(V,H)048A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
202330379 |  | Ground Water | AAON, Inc. | WV-030-1-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330380 |  | Ground Water | AAON, Inc. | WV-030-A-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330383 |  | Ground Water | AAON, Inc. | WV-030-2-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330384 |  | Ground Water | AAON, Inc. | WV-030-3-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330350 |  | Ground Water | AAON, Inc. | WV-012-B-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
202330351 |  | Ground Water | AAON, Inc. | WV-012-1-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
202330352 |  | Ground Water | AAON, Inc. | WV-012-A-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
202330355 |  | Ground Water | AAON, Inc. | WV-015-1-H-ACAC-C0-10-200-A |  | 16600 | 25.7 | 14700 | 4.2 | 1.3833 | No
202330356 |  | Ground Water | AAON, Inc. | WV-015-A-H-ACAC-C0-10-200-A |  | 16600 | 25.7 | 14700 | 4.2 | 1.3833 | No
10581116 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAPT064**1*1******H |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
10581117 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAPT072**1*1******H |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
10581118 |  | Ground Water | GEOSTAR | 107H026**1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
10581119 |  | Ground Water | GEOSTAR | 107H038**1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581120 |  | Ground Water | GEOSTAR | 107H049**1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
10581122 |  | Ground Water | GEOSTAR | 107H072**1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
8849312 |  | Ground Water | 5 SERIES | NDV/NDH026H1*(1,4) |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214855065 |  | Ground Water | WHALEN | CASV*030AJ**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855066 |  | Ground Water | WHALEN | CASV*030AM**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855067 |  | Ground Water | WHALEN | CASH*036AB**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855068 |  | Ground Water | WHALEN | CASH*036AD**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855069 |  | Ground Water | WHALEN | CASH*036AJ**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855070 |  | Ground Water | WHALEN | CASH*036AM**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855071 |  | Ground Water | WHALEN | CASV*036AB**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330777 |  | Ground Water | WHALEN | CASH*042AM**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330778 |  | Ground Water | WHALEN | CASV*042AM**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330779 |  | Ground Water | WHALEN | CASH*048AJ**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330780 |  | Ground Water | WHALEN | CASV*048AJ**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330781 |  | Ground Water | WHALEN | CASH*048AM**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330782 |  | Ground Water | WHALEN | CASV*048AM**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330783 |  | Ground Water | WHALEN | CASH*060AJ**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214776173 |  | Ground Water | TRANE | GETK0092 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
214776174 |  | Ground Water | TRANE | GETK0097 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
204031802 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
204031806 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
204031808 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
209156925 |  | Ground Water | AE Air | HRCC09*-2 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
207200622 |  | Ground Water | GeoSmart Energy | QT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
207200624 |  | Ground Water | GeoSmart Energy | VI048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
207200625 |  | Ground Water | GeoSmart Energy | VI060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
207213249 |  | Ground Water | GeoSmart Energy | YT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
202391373 |  | Ground Water | AQUARIUS | EP012-0VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391374 |  | Ground Water | AQUARIUS | EP012-2VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391375 |  | Ground Water | AQUARIUS | EP012-0HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391376 |  | Ground Water | AQUARIUS | EP012-2HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391377 |  | Ground Water | AQUARIUS | EP012-0VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391378 |  | Ground Water | AQUARIUS | EP012-2VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391379 |  | Ground Water | AQUARIUS | EP012-0HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
214855100 |  | Ground Water | WHALEN | CASV*054AD**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855101 |  | Ground Water | WHALEN | CASV*054AJ**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855102 |  | Ground Water | WHALEN | CASV*054AM**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855103 |  | Ground Water | WHALEN | CASV*060AB**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855104 |  | Ground Water | WHALEN | CASV*060AD**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855105 |  | Ground Water | WHALEN | CASV*060AJ**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855106 |  | Ground Water | WHALEN | CASV*060AM**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
7493299 |  | Ground Water | GeoSmart Energy | YT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
7493316 |  | Ground Water | GEOSTAR | 12(1,2)A048 |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
7493326 |  | Ground Water | YORK BY JOHNSON CONTROLS | YLFT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
202330367 |  | Ground Water | AAON, Inc. | WV-019-1-H-ACAC-C0-10-200-A |  | 21400 | 27 | 17000 | 4.1 | 1.7833 | No
202330368 |  | Ground Water | AAON, Inc. | WV-019-A-H-ACAC-C0-10-200-A |  | 21400 | 27 | 17000 | 4.1 | 1.7833 | No
202330336 |  | Ground Water | AAON, Inc. | WH-060-3-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330339 |  | Ground Water | AAON, Inc. | WH-036-A-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202330340 |  | Ground Water | AAON, Inc. | WH-036-3-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
10268238 |  | Ground Water | TETCO | TBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268244 |  | Ground Water | GEOCOMFORT | GBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268245 |  | Ground Water | HYDRON MODULE | HBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268246 |  | Ground Water | TETCO | TBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268247 |  | Ground Water | GEOCOMFORT | GBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268248 |  | Ground Water | HYDRON MODULE | HBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268249 |  | Ground Water | TETCO | TBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
207334459 |  | Ground Water | WaterFurnace | NDP038H1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
207334460 |  | Ground Water | WaterFurnace | NDP049H1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
207334461 |  | Ground Water | WaterFurnace | NDP072H1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
207334462 |  | Ground Water | WaterFurnace | NDP064H1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
207335405 |  | Ground Water | GeoSmart Energy | GS022**1*(0,3)*J |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
207337519 |  | Ground Water | GEOSTAR | 103H060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
202391453 |  | Ground Water | CARRIER | 50PSV012**N0/BA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391454 |  | Ground Water | CARRIER | 50PSV012**N4/DA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391455 |  | Ground Water | CARRIER | 50PSH012**N0/BA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391456 |  | Ground Water | CARRIER | 50PSH012**N4/DA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202443455 |  | Ground Water | GeoSmart Energy | GS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202443457 |  | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
204344184 |  | Ground Water | 7 SERIES | NVV/NVH036B1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
204452547 |  | Ground Water | GeoSmart Energy | VI036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
204457696 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
6965857 |  | Ground Water | TRANE | EXHF0121 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
6965858 |  | Ground Water | TRANE | EXHF0122 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
6965859 |  | Ground Water | TRANE | EXHF0127 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
5708463 |  | Ground Water | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708493 |  | Ground Water | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708550 |  | Ground Water | GEOSTAR | 101/102A022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708623 |  | Ground Water | GeoSmart Energy | GS022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5731224 |  | Ground Water | BARD | GTC36S2-A | GTA3600UD1AA+GTB1-A | 41000 | 21.6 | 37500 | 4.8 | 3.4167 | No
5296263 |  | Ground Water | TRANE | EXVF0488 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296264 |  | Ground Water | TRANE | EXVF0428 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296265 |  | Ground Water | TRANE | EXVF0481 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296259 |  | Ground Water | TRANE | EXVF0421 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296260 |  | Ground Water | TRANE | EXVF0422 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296261 |  | Ground Water | TRANE | EXVF0423 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296262 |  | Ground Water | TRANE | EXVF0424 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
209156963 |  | Ground Water | AE Air | WSV6036A |  | 41500 | 24 | 35500 | 4.1 | 3.4583 | No
209156964 |  | Ground Water | AE Air | WSV6042A |  | 46500 | 24 | 39000 | 4.2 | 3.875 | No
209156970 |  | Ground Water | AE Air | WSV6060A |  | 65000 | 23 | 53500 | 4.1 | 5.4167 | No
214855093 |  | Ground Water | WHALEN | CASH*054AJ**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855094 |  | Ground Water | WHALEN | CASH*054AM**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855095 |  | Ground Water | WHALEN | CASH*060AB**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855096 |  | Ground Water | WHALEN | CASH*060AD**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855097 |  | Ground Water | WHALEN | CASH*060AJ**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855098 |  | Ground Water | WHALEN | CASH*060AM**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855099 |  | Ground Water | WHALEN | CASV*054AB**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202330407 |  | Ground Water | AAON, Inc. | WV-048-2-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330408 |  | Ground Water | AAON, Inc. | WV-048-3-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330411 |  | Ground Water | AAON, Inc. | WV-060-1-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330412 |  | Ground Water | AAON, Inc. | WV-060-A-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
5295956 |  | Ground Water | TRANE | EXHF0363 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295957 |  | Ground Water | TRANE | EXHF0368 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295958 |  | Ground Water | TRANE | EXHF0364 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295959 |  | Ground Water | TRANE | EXHF0421 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295961 |  | Ground Water | TRANE | EXHF0422 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295963 |  | Ground Water | TRANE | EXHF0423 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295965 |  | Ground Water | TRANE | EXHF0424 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
10443502 |  | Ground Water | GEOCOMFORT | GBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443503 |  | Ground Water | HYDRON MODULE | HBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443504 |  | Ground Water | TETCO | TBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443509 |  | Ground Water | GEOCOMFORT | GBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443510 |  | Ground Water | HYDRON MODULE | HBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443511 |  | Ground Water | TETCO | TBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443512 |  | Ground Water | GEOCOMFORT | GBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10268261 |  | Ground Water | HYDRON MODULE | HBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268262 |  | Ground Water | TETCO | TBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268263 |  | Ground Water | GEOCOMFORT | GBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268264 |  | Ground Water | HYDRON MODULE | HBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268265 |  | Ground Water | TETCO | TBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268268 |  | Ground Water | GEOCOMFORT | GBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268269 |  | Ground Water | HYDRON MODULE | HBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
3919854 |  | Ground Water | AQUARIUS | EP015-1HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
3919855 |  | Ground Water | AQUARIUS | EP015-2HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
3919884 |  | Ground Water | AQUARIUS | EP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
3919931 |  | Ground Water | AQUARIUS | EP024-2HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
3920297 |  | Ground Water | AQUARIUS | EP030-2HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920298 |  | Ground Water | AQUARIUS | EP030-4HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920299 |  | Ground Water | AQUARIUS | EP030-3HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
8560542 |  | Ground Water | 5 SERIES | NSV/NSH012H1*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8560785 |  | Ground Water | 5 SERIES | NSV/NSH018H1*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8560786 |  | Ground Water | 5 SERIES | NSV/NSH022H1*(0,3) |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8560787 |  | Ground Water | 5 SERIES | NSV/NSH030H1*(0,3) |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8103479 |  | Ground Water | TRANE | DXHF0241 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105907 |  | Ground Water | TRANE | DXHF0242 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105909 |  | Ground Water | TRANE | DXHF0243 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
207178547 |  | Ground Water | GEOSTAR | 161/162H072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207200554 |  | Ground Water | GeoSmart Energy | GT026**1*(1,4)*H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207200555 |  | Ground Water | GeoSmart Energy | GT072**1*(1,4)*H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207200556 |  | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207200557 |  | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207200559 |  | Ground Water | GeoSmart Energy | GS012**1*0*H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
207200560 |  | Ground Water | GeoSmart Energy | GS018**1*(1,4)*H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214855051 |  | Ground Water | WHALEN | CASH*024AB**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855052 |  | Ground Water | WHALEN | CASH*024AD**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855053 |  | Ground Water | WHALEN | CASH*024AJ**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855054 |  | Ground Water | WHALEN | CASH*024AM**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855055 |  | Ground Water | WHALEN | CASV*024AB**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855056 |  | Ground Water | WHALEN | CASV*024AD**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855057 |  | Ground Water | WHALEN | CASV*024AJ**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330331 |  | Ground Water | AAON, Inc. | WH-060-1-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330332 |  | Ground Water | AAON, Inc. | WH-060-A-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330335 |  | Ground Water | AAON, Inc. | WH-060-2-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
5296247 |  | Ground Water | TRANE | EXVF0241 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
5296248 |  | Ground Water | TRANE | EXVF0242 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
10443495 |  | Ground Water | TETCO | TBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443496 |  | Ground Water | GEOCOMFORT | GBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443497 |  | Ground Water | HYDRON MODULE | HBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443498 |  | Ground Water | TETCO | TBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443499 |  | Ground Water | GEOCOMFORT | GBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443500 |  | Ground Water | HYDRON MODULE | HBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443501 |  | Ground Water | TETCO | TBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
8786549 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8786552 |  | Ground Water | GEOSTAR | 101/102H012**1*0***** |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786553 |  | Ground Water | GeoSmart Energy | GS012**1*0********H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786554 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS012**1*0****H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786557 |  | Ground Water | GEOSTAR | 101/102H018**1*(1,4)***** |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8786558 |  | Ground Water | GeoSmart Energy | GS018**1*(1,4)********H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8786559 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8105931 |  | Ground Water | TRANE | DXHF0701 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105932 |  | Ground Water | TRANE | DXHF0702 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105933 |  | Ground Water | TRANE | DXHF0703 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105934 |  | Ground Water | TRANE | DXHF0704 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105935 |  | Ground Water | TRANE | DXHF0708 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105950 |  | Ground Water | TRANE | DXVF0241 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105955 |  | Ground Water | TRANE | DXVF0242 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
207200561 |  | Ground Water | GeoSmart Energy | GS018**1*0*H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
207200562 |  | Ground Water | GeoSmart Energy | GS022**1*(0,3)*H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
207200563 |  | Ground Water | GeoSmart Energy | GS030**1*(0,3)*H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
207200564 |  | Ground Water | GeoSmart Energy | GS030**1*(1,4)*H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
207200567 |  | Ground Water | GeoSmart Energy | GS070**1*(1,4)*H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207200569 |  | Ground Water | GeoSmart Energy | GS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202330748 |  | Ground Water | WHALEN | CASH*036AD**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330749 |  | Ground Water | WHALEN | CASV*036AD**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330750 |  | Ground Water | WHALEN | CASH*042AB**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330751 |  | Ground Water | WHALEN | CASV*042AB**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330752 |  | Ground Water | WHALEN | CASH*042AD**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330753 |  | Ground Water | WHALEN | CASV*042AD**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330754 |  | Ground Water | WHALEN | CASH*048AB**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
10443513 |  | Ground Water | HYDRON MODULE | HBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443514 |  | Ground Water | TETCO | TBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443577 |  | Ground Water | GEOCOMFORT | GBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443578 |  | Ground Water | HYDRON MODULE | HBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443579 |  | Ground Water | TETCO | TBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443580 |  | Ground Water | GEOCOMFORT | GBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443581 |  | Ground Water | HYDRON MODULE | HBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
202443458 |  | Ground Water | GeoSmart Energy | GS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202443459 |  | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202443460 |  | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
202443465 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202443466 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202443467 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
4231098 |  | Ground Water | DAIKIN | WCCW4024*K*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
9951968 |  | Ground Water | BARD | GV27S3AA |  | 26600 | 22.8 | 26200 | 5 | 2.2167 | No
9951969 |  | Ground Water | BARD | GV38S3AA |  | 41400 | 22 | 38600 | 4.7 | 3.45 | No
9951970 |  | Ground Water | BARD | GV51S3AA |  | 53500 | 21.7 | 49500 | 4.45 | 4.4583 | No
8791889 |  | Ground Water | GeoSmart Energy | GS070**1*(1,4)********H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8791890 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8105984 |  | Ground Water | TRANE | DXVF0702 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8105985 |  | Ground Water | TRANE | DXVF0703 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8106144 |  | Ground Water | TRANE | DXVF0704 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8106145 |  | Ground Water | TRANE | DXVF0708 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
202330770 |  | Ground Water | WHALEN | CASV*030AM**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330771 |  | Ground Water | WHALEN | CASH*036AJ**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330772 |  | Ground Water | WHALEN | CASV*036AJ**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330773 |  | Ground Water | WHALEN | CASH*036AM**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330774 |  | Ground Water | WHALEN | CASV*036AM**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330775 |  | Ground Water | WHALEN | CASH*042AJ**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330776 |  | Ground Water | WHALEN | CASV*042AJ**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
204474784 |  | Ground Water | GEOSTAR | 141/142B036**1*(1,2) |  | 38000 | 31.5 | 41000 | 4.6 | 3.1667 | No
6936993 |  | Ground Water | BARD | GTC60S2-A | HE49948D210B2705AW | 67500 | 21.56 | 61500 | 4.3 | 5.625 | No
6945298 |  | Ground Water | BARD | GTC48S2-A | HE49948D210B2705AW | 54500 | 23.5 | 48000 | 4.55 | 4.5417 | No
202330308 |  | Ground Water | AAON, Inc. | WH-036-A-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330309 |  | Ground Water | AAON, Inc. | WH-036-2-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330310 |  | Ground Water | AAON, Inc. | WH-036-3-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330311 |  | Ground Water | AAON, Inc. | WH-036-2-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330312 |  | Ground Water | AAON, Inc. | WH-036-3-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
10443593 |  | Ground Water | GEOCOMFORT | GBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443594 |  | Ground Water | HYDRON MODULE | HBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443595 |  | Ground Water | TETCO | TBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443596 |  | Ground Water | GEOCOMFORT | GBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443597 |  | Ground Water | HYDRON MODULE | HBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443598 |  | Ground Water | TETCO | TBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10445242 |  | Ground Water | WaterFurnace | SDV049H1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
10268270 |  | Ground Water | TETCO | TBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268271 |  | Ground Water | GEOCOMFORT | GBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268272 |  | Ground Water | HYDRON MODULE | HBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268273 |  | Ground Water | TETCO | TBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268274 |  | Ground Water | GEOCOMFORT | GBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268275 |  | Ground Water | HYDRON MODULE | HBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268276 |  | Ground Water | TETCO | TBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
8105924 |  | Ground Water | TRANE | DXHF0367 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105925 |  | Ground Water | TRANE | DXHF0368 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105926 |  | Ground Water | TRANE | DXHF0481 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105927 |  | Ground Water | TRANE | DXHF0482 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105928 |  | Ground Water | TRANE | DXHF0483 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105929 |  | Ground Water | TRANE | DXHF0484 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105930 |  | Ground Water | TRANE | DXHF0488 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
207178494 |  | Ground Water | GEOSTAR | 161/162J049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207178526 |  | Ground Water | GEOSTAR | 161/162H026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207178527 |  | Ground Water | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214855043 |  | Ground Water | WHALEN | CASH*015AB**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
7167357 |  | Ground Water | CARRIER | 50PSH/V060***6/FA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7167358 |  | Ground Water | CARRIER | 50PSH/V060***5/EA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7167359 |  | Ground Water | CARRIER | 50PSH/V060***3/CA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7167360 |  | Ground Water | CARRIER | 50PSH/V070***3/CA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7167361 |  | Ground Water | CARRIER | 50PSH/V070***5/EA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7167362 |  | Ground Water | CARRIER | 50PSH/V070***6/FA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7076986 |  | Ground Water | AQUARIUS | EP024-3HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7076987 |  | Ground Water | AQUARIUS | EP024-4HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
202330322 |  | Ground Water | AAON, Inc. | WH-048-A-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330323 |  | Ground Water | AAON, Inc. | WH-048-1-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
202330324 |  | Ground Water | AAON, Inc. | WH-048-A-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
202330325 |  | Ground Water | AAON, Inc. | WH-048-2-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330326 |  | Ground Water | AAON, Inc. | WH-048-3-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330327 |  | Ground Water | AAON, Inc. | WH-048-2-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
202330328 |  | Ground Water | AAON, Inc. | WH-048-3-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
5360714 |  | Ground Water | BARD | GTC36S2-A | GTADP-3642-* | 42000 | 23.9 | 38000 | 5 | 3.5 | No
5360715 |  | Ground Water | BARD | GTC48S2-A | GTADP-4860-C | 54500 | 23.5 | 48000 | 4.55 | 4.5417 | No
5360791 |  | Ground Water | BARD | GTC60S2-A | GTADP-4860-C | 67500 | 21.56 | 61500 | 4.3 | 5.625 | No
202330297 |  | Ground Water | AAON, Inc. | WH-030-1-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
202330298 |  | Ground Water | AAON, Inc. | WH-030-A-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
201846902 |  | Ground Water | GEOSTAR | 111H038**1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
5295967 |  | Ground Water | TRANE | EXHF0428 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295970 |  | Ground Water | TRANE | EXHF0481 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295971 |  | Ground Water | TRANE | EXHF0482 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295972 |  | Ground Water | TRANE | EXHF0483 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295973 |  | Ground Water | TRANE | EXHF0484 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295974 |  | Ground Water | TRANE | EXHF0488 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
10443582 |  | Ground Water | TETCO | TBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443583 |  | Ground Water | GEOCOMFORT | GBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443584 |  | Ground Water | HYDRON MODULE | HBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443585 |  | Ground Water | TETCO | TBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443586 |  | Ground Water | GEOCOMFORT | GBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443587 |  | Ground Water | HYDRON MODULE | HBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443588 |  | Ground Water | TETCO | TBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
202607201 |  | Ground Water | WHALEN | CASH*054AD**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607202 |  | Ground Water | WHALEN | CASV*054AD**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607203 |  | Ground Water | WHALEN | CASH*054AJ**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607204 |  | Ground Water | WHALEN | CASV*054AJ**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607205 |  | Ground Water | WHALEN | CASH*054AM**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607206 |  | Ground Water | WHALEN | CASV*054AM**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
4219428 |  | Ground Water | NORDIC | RH25HACW-P-1T-*-SDE** |  | 26200 | 22 | 22500 | 4.2 | 2.1833 | No
4219442 |  | Ground Water | NORDIC | RS25HACW-P-1T-* | AH-25-P-1-***** | 26800 | 23.1 | 23100 | 4.4 | 2.2333 | No
3919846 |  | Ground Water | AQUARIUS | EP007-2HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
3919847 |  | Ground Water | AQUARIUS | EP007-1HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
3919848 |  | Ground Water | AQUARIUS | EP009-1HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
3919850 |  | Ground Water | AQUARIUS | EP009-2HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
3919853 |  | Ground Water | AQUARIUS | EP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
8786527 |  | Ground Water | GEOSTAR | 101/102H026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
8786528 |  | Ground Water | GeoSmart Energy | GT026**1*(1,4)********H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
8786529 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
8786547 |  | Ground Water | GEOSTAR | 101/102H072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8786548 |  | Ground Water | GeoSmart Energy | GT072**1*(1,4)********H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8105956 |  | Ground Water | TRANE | DXVF0243 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105960 |  | Ground Water | TRANE | DXVF0244 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105965 |  | Ground Water | TRANE | DXVF0247 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105966 |  | Ground Water | TRANE | DXVF0248 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105967 |  | Ground Water | TRANE | DXVF0361 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105968 |  | Ground Water | TRANE | DXVF0362 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105969 |  | Ground Water | TRANE | DXVF0363 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
202350416 |  | Ground Water | AAON, Inc. | RN-009-4-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
202350426 |  | Ground Water | AAON, Inc. | RN-011-2-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
202350427 |  | Ground Water | AAON, Inc. | RN-011-3-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
202350428 |  | Ground Water | AAON, Inc. | RN-011-4-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
7499485 |  | Ground Water | FHP | EP070-3HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7499487 |  | Ground Water | FHP | EP070-4HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
202330763 |  | Ground Water | WHALEN | CASH*024AJ**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330764 |  | Ground Water | WHALEN | CASV*024AJ**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330765 |  | Ground Water | WHALEN | CASH*024AM**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330766 |  | Ground Water | WHALEN | CASV*024AM**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330767 |  | Ground Water | WHALEN | CASH*030AJ**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330768 |  | Ground Water | WHALEN | CASV*030AJ**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330769 |  | Ground Water | WHALEN | CASH*030AM**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
5696567 |  | Ground Water | 5 SERIES | NSV/NSH022G1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5296256 |  | Ground Water | TRANE | EXVF0364 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296257 |  | Ground Water | TRANE | EXVF0367 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296258 |  | Ground Water | TRANE | EXVF0368 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
10447649 |  | Ground Water | RHEEM | RPVS/EC025 | RCFL-HM2417 | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
10447650 |  | Ground Water | RHEEM | RPVS/EC025 | RCFL-HM2621 | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
10447662 |  | Ground Water | RHEEM | RPVS/EC036 | RCFL-HM38** | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
10447665 |  | Ground Water | RHEEM | RPVS/EC048 | RCFL-HM48** | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
10581108 |  | Ground Water | 5 SERIES | NDP026H1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
10268277 |  | Ground Water | GEOCOMFORT | GBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268278 |  | Ground Water | HYDRON MODULE | HBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268279 |  | Ground Water | TETCO | TBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10318053 |  | Ground Water | GEOSTAR | 103H060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10443493 |  | Ground Water | GEOCOMFORT | GBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443494 |  | Ground Water | HYDRON MODULE | HBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
3920300 |  | Ground Water | AQUARIUS | EP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920500 |  | Ground Water | AQUARIUS | EP060-4HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
3920501 |  | Ground Water | AQUARIUS | EP060-3HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
3920502 |  | Ground Water | AQUARIUS | EP060-1HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
3920503 |  | Ground Water | AQUARIUS | EP070-1HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
3920504 |  | Ground Water | AQUARIUS | EP070-3HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
3920505 |  | Ground Water | AQUARIUS | EP070-4HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
9032337 |  | Ground Water | HYDROTECH | HRCC09*-2 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
8560799 |  | Ground Water | 5 SERIES | NSV/NSH018H1*(1,4) |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8560800 |  | Ground Water | 5 SERIES | NSV/NSH022H1*(1,4) |  | 21900 | 27.5 | 19500 | 5 | 1.825 | No
8560801 |  | Ground Water | 5 SERIES | NSV/NSH030H1*(1,4) |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8560806 |  | Ground Water | 5 SERIES | NSV/NSH070H1*(1,4) |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8570181 |  | Ground Water | 5 SERIES | NDV/NDH072H1*(1,4) |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8105911 |  | Ground Water | TRANE | DXHF0244 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105912 |  | Ground Water | TRANE | DXHF0247 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105913 |  | Ground Water | TRANE | DXHF0248 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105914 |  | Ground Water | TRANE | DXHF0361 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105916 |  | Ground Water | TRANE | DXHF0362 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105922 |  | Ground Water | TRANE | DXHF0363 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105923 |  | Ground Water | TRANE | DXHF0364 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
202350098 |  | Ground Water | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202350414 |  | Ground Water | AAON, Inc. | RN-009-2-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
202350415 |  | Ground Water | AAON, Inc. | RN-009-3-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
214855058 |  | Ground Water | WHALEN | CASV*024AM**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855059 |  | Ground Water | WHALEN | CASH*030AB**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855060 |  | Ground Water | WHALEN | CASH*030AD**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855061 |  | Ground Water | WHALEN | CASH*030AJ**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855062 |  | Ground Water | WHALEN | CASH*030AM**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855063 |  | Ground Water | WHALEN | CASV*030AB**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855064 |  | Ground Water | WHALEN | CASV*030AD**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
7167339 |  | Ground Water | CARRIER | 50PSH/V015***4/DA |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7167342 |  | Ground Water | CARRIER | 50PSH/V024***3/CA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7167343 |  | Ground Water | CARRIER | 50PSH/V024***4/DA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7167344 |  | Ground Water | CARRIER | 50PSH/V030***4/DA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167345 |  | Ground Water | CARRIER | 50PSH/V030***6/FA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167346 |  | Ground Water | CARRIER | 50PSH/V030***5/EA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167347 |  | Ground Water | CARRIER | 50PSH/V030***3/CA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
202330315 |  | Ground Water | AAON, Inc. | WH-042-1-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330316 |  | Ground Water | AAON, Inc. | WH-042-A-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330319 |  | Ground Water | AAON, Inc. | WH-042-2-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330320 |  | Ground Water | AAON, Inc. | WH-042-3-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330321 |  | Ground Water | AAON, Inc. | WH-048-1-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
5612208 |  | Ground Water | GeoSmart Energy | VI060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
5613676 |  | Ground Water | GEOSTAR | 141/142A048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
5613677 |  | Ground Water | GEOSTAR | 141/142A060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
214776161 |  | Ground Water | TRANE | GETK009 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
202330280 |  | Ground Water | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 17100 | 29.9 | 14400 | 5.2 | 1.425 | No
202330281 |  | Ground Water | AAON, Inc. | WH-018-1-H-ACAC-C0-10-100-A |  | 19600 | 23.5 | 17600 | 4.6 | 1.6333 | No
202330282 |  | Ground Water | AAON, Inc. | WH-018-A-H-ACAC-C0-10-100-A |  | 19600 | 23.5 | 17600 | 4.6 | 1.6333 | No
202330283 |  | Ground Water | AAON, Inc. | WH-018-1-H-ACAC-C0-10-200-A |  | 19500 | 26.5 | 16100 | 4.8 | 1.625 | No
202330284 |  | Ground Water | AAON, Inc. | WH-018-A-H-ACAC-C0-10-200-A |  | 19500 | 26.5 | 16100 | 4.8 | 1.625 | No
5440741 |  | Ground Water | 7 SERIES | NVV/NVH048A1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
5440778 |  | Ground Water | 7 SERIES | NVV/NVH060A1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
5505441 |  | Ground Water | BARD | GTC36S2-A | HE37942D175B2505AW/HE37942D210B2505AW | 40500 | 24 | 34000 | 4.85 | 3.375 | No
5612204 |  | Ground Water | GeoSmart Energy | VI048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
10268250 |  | Ground Water | GEOCOMFORT | GBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268251 |  | Ground Water | HYDRON MODULE | HBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268252 |  | Ground Water | TETCO | TBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268253 |  | Ground Water | GEOCOMFORT | GBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268254 |  | Ground Water | HYDRON MODULE | HBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268255 |  | Ground Water | TETCO | TBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268260 |  | Ground Water | GEOCOMFORT | GBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
212508380 |  | Ground Water | HYDROTECH | WSH6030AN* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212508395 |  | Ground Water | AE Air | WSH6024AN* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212508397 |  | Ground Water | AE Air | WSH6030AN* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
202391380 |  | Ground Water | AQUARIUS | EP012-2HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391433 |  | Ground Water | FHP | EP012-2HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391434 |  | Ground Water | FHP | EP012-0HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391435 |  | Ground Water | FHP | EP012-2VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391436 |  | Ground Water | FHP | EP012-0VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391437 |  | Ground Water | FHP | EP012-2HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391438 |  | Ground Water | FHP | EP012-0HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
7499447 |  | Ground Water | FHP | EP007-1HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7499448 |  | Ground Water | FHP | EP007-2HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7499450 |  | Ground Water | FHP | EP009-1HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7499451 |  | Ground Water | FHP | EP009-2HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7499453 |  | Ground Water | FHP | EP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
7167555 |  | Ground Water | CARRIER | 50PSH/V024***5/EA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7167556 |  | Ground Water | CARRIER | 50PSH/V024***6/FA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
202330371 |  | Ground Water | AAON, Inc. | WV-024-1-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330372 |  | Ground Water | AAON, Inc. | WV-024-A-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330375 |  | Ground Water | AAON, Inc. | WV-024-2-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330376 |  | Ground Water | AAON, Inc. | WV-024-3-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330343 |  | Ground Water | AAON, Inc. | WH-048-A-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202330344 |  | Ground Water | AAON, Inc. | WH-048-3-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202330345 |  | Ground Water | AAON, Inc. | WH-060-A-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202330346 |  | Ground Water | AAON, Inc. | WH-060-3-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202330347 |  | Ground Water | AAON, Inc. | WV-009-B-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
202330348 |  | Ground Water | AAON, Inc. | WV-009-1-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
202330349 |  | Ground Water | AAON, Inc. | WV-009-A-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
202330273 |  | Ground Water | AAON, Inc. | WH-009-A-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
202330277 |  | Ground Water | AAON, Inc. | WH-015-1-H-ACAC-C0-10-100-A |  | 16500 | 26.1 | 14600 | 4.9 | 1.375 | No
5295949 |  | Ground Water | TRANE | EXHF0247 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
5295950 |  | Ground Water | TRANE | EXHF0301 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295951 |  | Ground Water | TRANE | EXHF0302 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295952 |  | Ground Water | TRANE | EXHF0307 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295953 |  | Ground Water | TRANE | EXHF0361 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295954 |  | Ground Water | TRANE | EXHF0362 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295955 |  | Ground Water | TRANE | EXHF0367 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
202330278 |  | Ground Water | AAON, Inc. | WH-015-A-H-ACAC-C0-10-100-A |  | 16500 | 26.1 | 14600 | 4.9 | 1.375 | No
202330279 |  | Ground Water | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 17100 | 29.9 | 14400 | 5.2 | 1.425 | No
8789591 |  | Ground Water | GEOSTAR | 101/102H030**1*(0,3)***** |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789592 |  | Ground Water | GeoSmart Energy | GS030**1*(0,3)********H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789593 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789596 |  | Ground Water | GEOSTAR | 101/102H030**1*(1,4)***** |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8789597 |  | Ground Water | GeoSmart Energy | GS030**1*(1,4)********H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8789598 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8791888 |  | Ground Water | GEOSTAR | 101/102H070**1*(1,4)***** |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8105970 |  | Ground Water | TRANE | DXVF0364 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105971 |  | Ground Water | TRANE | DXVF0367 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105972 |  | Ground Water | TRANE | DXVF0368 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105973 |  | Ground Water | TRANE | DXVF0481 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105974 |  | Ground Water | TRANE | DXVF0482 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105975 |  | Ground Water | TRANE | DXVF0483 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105976 |  | Ground Water | TRANE | DXVF0484 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
202330784 |  | Ground Water | WHALEN | CASV*060AJ**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330785 |  | Ground Water | WHALEN | CASH*060AM**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330786 |  | Ground Water | WHALEN | CASV*060AM**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202350093 |  | Ground Water | 5 SERIES | NSV/NSH036J1*(0,3) |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202350094 |  | Ground Water | 5 SERIES | NSV/NSH042J1*(0,3) |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202350095 |  | Ground Water | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202350096 |  | Ground Water | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214855044 |  | Ground Water | WHALEN | CASH*015AD**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855045 |  | Ground Water | WHALEN | CASV*015AB**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855046 |  | Ground Water | WHALEN | CASV*015AD**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855047 |  | Ground Water | WHALEN | CASH*018AB**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855048 |  | Ground Water | WHALEN | CASH*018AD**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855049 |  | Ground Water | WHALEN | CASV*018AB**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855050 |  | Ground Water | WHALEN | CASV*018AD**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
205148067 |  | Ground Water | HYDROTECH | WSV6060A |  | 65000 | 23 | 53500 | 4.1 | 5.4167 | No
6580833 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
6580857 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFV060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
6581203 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
10581109 |  | Ground Water | 5 SERIES | NDP038H1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581110 |  | Ground Water | 5 SERIES | NDP049H1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
10581111 |  | Ground Water | 5 SERIES | NDP064H1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
10581112 |  | Ground Water | 5 SERIES | NDP072H1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
10581113 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAPT026**1*1******H |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
10581114 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581115 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAPT049**1*1******H |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
209156961 |  | Ground Water | AE Air | WSV6024A |  | 25400 | 24 | 22000 | 4.1 | 2.1167 | No
214855072 |  | Ground Water | WHALEN | CASV*036AD**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855073 |  | Ground Water | WHALEN | CASV*036AJ**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855074 |  | Ground Water | WHALEN | CASV*036AM**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855075 |  | Ground Water | WHALEN | CASH*042AB**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855076 |  | Ground Water | WHALEN | CASH*042AD**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855077 |  | Ground Water | WHALEN | CASH*042AJ**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855078 |  | Ground Water | WHALEN | CASH*042AM**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202350506 |  | Ground Water | AAON, Inc. | WH-036-1-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202350507 |  | Ground Water | AAON, Inc. | WH-036-2-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202350510 |  | Ground Water | AAON, Inc. | WH-048-1-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
7499455 |  | Ground Water | FHP | EP015-1HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7499456 |  | Ground Water | FHP | EP015-2HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7499460 |  | Ground Water | FHP | EP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499461 |  | Ground Water | FHP | EP024-2HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499463 |  | Ground Water | FHP | EP024-3HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499464 |  | Ground Water | FHP | EP024-4HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499465 |  | Ground Water | FHP | EP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
202330420 |  | Ground Water | AAON, Inc. | WV-030-A-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202330421 |  | Ground Water | AAON, Inc. | WV-030-3-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202330422 |  | Ground Water | AAON, Inc. | WV-036-A-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202330424 |  | Ground Water | AAON, Inc. | WV-036-3-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202330425 |  | Ground Water | AAON, Inc. | WV-042-A-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202330426 |  | Ground Water | AAON, Inc. | WV-042-3-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202330392 |  | Ground Water | AAON, Inc. | WV-036-3-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330395 |  | Ground Water | AAON, Inc. | WV-042-1-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330396 |  | Ground Water | AAON, Inc. | WV-042-A-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330303 |  | Ground Water | AAON, Inc. | WH-030-2-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
202330304 |  | Ground Water | AAON, Inc. | WH-030-3-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
202330305 |  | Ground Water | AAON, Inc. | WH-036-1-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330306 |  | Ground Water | AAON, Inc. | WH-036-A-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330307 |  | Ground Water | AAON, Inc. | WH-036-1-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
203113881 |  | Ground Water | GEOSTAR | 101/102J036**1*(0,3)***** |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
203113882 |  | Ground Water | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
203113884 |  | Ground Water | GEOSTAR | 101/102J042**1*(0,3)***** |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202391446 |  | Ground Water | CARRIER | 50PSH012**C3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391447 |  | Ground Water | CARRIER | 50PSV012**N3/CA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391448 |  | Ground Water | CARRIER | 50PSH012**N3/CA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391449 |  | Ground Water | CARRIER | 50PSV012**C0/BA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391450 |  | Ground Water | CARRIER | 50PSV012**C4/DA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391451 |  | Ground Water | CARRIER | 50PSH012**C0/BA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391452 |  | Ground Water | CARRIER | 50PSH012**C4/DA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206599757 |  | Ground Water | 5 SERIES | NSV/NSH060J1*0* |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
206599760 |  | Ground Water | 5 SERIES | NSV/NSH060J1*(1,4)* |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
206599762 |  | Ground Water | GEOSTAR | 101/102J060**1*0****** |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
206599765 |  | Ground Water | GEOSTAR | 101/102J060**1*(1,4)****** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
205782572 |  | Ground Water | GeoSmart Energy | QT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
205993815 |  | Ground Water | Denise | NLH/NXH080**3 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206199262 |  | Ground Water | RHEEM | RPVV/H/D026D |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | No
206199264 |  | Ground Water | RHEEM | RPVV/H/D049D |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | No
206199265 |  | Ground Water | RHEEM | RPVV/H/D064D |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | No
206199266 |  | Ground Water | RHEEM | RPVV/H/D072D |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | No
203696349 |  | Ground Water | HYDROTECH | WSV6024A |  | 25400 | 24 | 22000 | 4.1 | 2.1167 | No
203696351 |  | Ground Water | HYDROTECH | WSV6036A |  | 41500 | 24 | 35500 | 4.1 | 3.4583 | No
203995293 |  | Ground Water | HYDROTECH | WSV6042A |  | 46500 | 24 | 39000 | 4.2 | 3.875 | No
202330755 |  | Ground Water | WHALEN | CASV*048AB**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330756 |  | Ground Water | WHALEN | CASH*048AD**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330757 |  | Ground Water | WHALEN | CASV*048AD**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330758 |  | Ground Water | WHALEN | CASH*060AB**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330759 |  | Ground Water | WHALEN | CASV*060AB**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330760 |  | Ground Water | WHALEN | CASH*060AD**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330761 |  | Ground Water | WHALEN | CASV*060AD**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
4230750 |  | Ground Water | DAIKIN | WCCW4024*E*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
4230752 |  | Ground Water | DAIKIN | WCCW4024*F*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
4230754 |  | Ground Water | DAIKIN | WCCW4024*J*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
8786562 |  | Ground Water | GEOSTAR | 101/102H018**1*0***** |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8786563 |  | Ground Water | GeoSmart Energy | GS018**1*0********H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8786564 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*0****H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8789580 |  | Ground Water | GEOSTAR | 101/102H022**1*(0,3)***** |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8789581 |  | Ground Water | GeoSmart Energy | GS022**1*(0,3)********H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8789582 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3)****H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8789586 |  | Ground Water | GEOSTAR | 101/102H022**1*(1,4)***** |  | 21900 | 27.5 | 19500 | 5 | 1.825 | No
8105977 |  | Ground Water | TRANE | DXVF0488 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105978 |  | Ground Water | TRANE | DXVF0601 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105979 |  | Ground Water | TRANE | DXVF0602 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105980 |  | Ground Water | TRANE | DXVF0603 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105981 |  | Ground Water | TRANE | DXVF0604 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105982 |  | Ground Water | TRANE | DXVF0608 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105983 |  | Ground Water | TRANE | DXVF0701 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
207200570 |  | Ground Water | GeoSmart Energy | GS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
207200571 |  | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207200572 |  | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
207200573 |  | Ground Water | GeoSmart Energy | GS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
207200574 |  | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207200617 |  | Ground Water | GeoSmart Energy | VI036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
7167332 |  | Ground Water | CARRIER | 50PSH/V007***4/DA |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7167333 |  | Ground Water | CARRIER | 50PSH/V007***3/CA |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7167334 |  | Ground Water | CARRIER | 50PSH/V009***3/CA |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7167335 |  | Ground Water | CARRIER | 50PSH/V009***4/DA |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7167337 |  | Ground Water | CARRIER | 50PSH/V012***3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
7167338 |  | Ground Water | CARRIER | 50PSH/V015***3/CA |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
6966727 |  | Ground Water | TRANE | EXVF0121 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
6966753 |  | Ground Water | TRANE | EXVF0122 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
6966789 |  | Ground Water | TRANE | EXVF0127 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
6966837 |  | Ground Water | TRANE | EXVF0151 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
6966860 |  | Ground Water | TRANE | EXVF0152 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
6966875 |  | Ground Water | TRANE | EXVF0157 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
203466716 |  | Ground Water | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203470605 |  | Ground Water | 5 SERIES | NSV/NSH048J1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
203470607 |  | Ground Water | 5 SERIES | NSV/NSH048J1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5295943 |  | Ground Water | TRANE | EXHF0241 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
5295946 |  | Ground Water | TRANE | EXHF0242 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
202443468 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202443469 |  | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
202607199 |  | Ground Water | WHALEN | CASH*054AB**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607200 |  | Ground Water | WHALEN | CASV*054AB**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
207337520 |  | Ground Water | GEOSTAR | 103H060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
207348743 |  | Ground Water | WaterFurnace | URT096*3*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
207348744 |  | Ground Water | WaterFurnace | URT096*4*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
214855086 |  | Ground Water | WHALEN | CASH*048AM**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855087 |  | Ground Water | WHALEN | CASV*048AB**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855088 |  | Ground Water | WHALEN | CASV*048AD**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855089 |  | Ground Water | WHALEN | CASV*048AJ**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855090 |  | Ground Water | WHALEN | CASV*048AM**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855091 |  | Ground Water | WHALEN | CASH*054AB**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855092 |  | Ground Water | WHALEN | CASH*054AD**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202350518 |  | Ground Water | AAON, Inc. | WV-030-2-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202350519 |  | Ground Water | AAON, Inc. | WV-036-1-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202350521 |  | Ground Water | AAON, Inc. | WV-036-2-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202350522 |  | Ground Water | AAON, Inc. | WV-042-1-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202350523 |  | Ground Water | AAON, Inc. | WV-042-2-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202350524 |  | Ground Water | AAON, Inc. | WV-048-1-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202330575 |  | Ground Water | AAON, Inc. | WH-006-A-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330576 |  | Ground Water | AAON, Inc. | WV-006-B-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330577 |  | Ground Water | AAON, Inc. | WV-006-1-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330578 |  | Ground Water | AAON, Inc. | WV-006-A-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330738 |  | Ground Water | WHALEN | CASH*024AB**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330739 |  | Ground Water | WHALEN | CASV*024AB**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330740 |  | Ground Water | WHALEN | CASH*024AD**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330399 |  | Ground Water | AAON, Inc. | WV-042-2-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330400 |  | Ground Water | AAON, Inc. | WV-042-3-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330403 |  | Ground Water | AAON, Inc. | WV-048-1-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330404 |  | Ground Water | AAON, Inc. | WV-048-A-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330359 |  | Ground Water | AAON, Inc. | WV-016-1-H-ACAC-C0-10-200-A |  | 17200 | 27.1 | 14800 | 4.2 | 1.4333 | No
202330360 |  | Ground Water | AAON, Inc. | WV-016-A-H-ACAC-C0-10-200-A |  | 17200 | 27.1 | 14800 | 4.2 | 1.4333 | No
10268201 |  | Ground Water | GEOCOMFORT | GBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268202 |  | Ground Water | HYDRON MODULE | HBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268203 |  | Ground Water | TETCO | TBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268204 |  | Ground Water | GEOCOMFORT | GBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268205 |  | Ground Water | HYDRON MODULE | HBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268206 |  | Ground Water | TETCO | TBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268207 |  | Ground Water | GEOCOMFORT | GBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
212505504 |  | Ground Water | AE Air | WSH6030AM* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212505507 |  | Ground Water | HYDROTECH | WSH6024AM* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212505508 |  | Ground Water | HYDROTECH | WSH6030AM* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212505512 |  | Ground Water | AE Air | WSH6024AM* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212508378 |  | Ground Water | HYDROTECH | WSH6024AN* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
214855079 |  | Ground Water | WHALEN | CASV*042AB**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855080 |  | Ground Water | WHALEN | CASV*042AD**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855081 |  | Ground Water | WHALEN | CASV*042AJ**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855082 |  | Ground Water | WHALEN | CASV*042AM**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855083 |  | Ground Water | WHALEN | CASH*048AB**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855084 |  | Ground Water | WHALEN | CASH*048AD**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855085 |  | Ground Water | WHALEN | CASH*048AJ**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202350511 |  | Ground Water | AAON, Inc. | WH-048-2-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202350512 |  | Ground Water | AAON, Inc. | WH-060-1-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202350513 |  | Ground Water | AAON, Inc. | WH-060-2-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202350514 |  | Ground Water | AAON, Inc. | WV-024-1-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202350515 |  | Ground Water | AAON, Inc. | WV-024-1-H-DCAC-C0-10-D00-A |  | 29000 | 22.7 | 21800 | 4.4 | 2.4167 | No
202350516 |  | Ground Water | AAON, Inc. | WV-024-2-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202350517 |  | Ground Water | AAON, Inc. | WV-030-1-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202330741 |  | Ground Water | WHALEN | CASV*024AD**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330742 |  | Ground Water | WHALEN | CASH*030AB**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330743 |  | Ground Water | WHALEN | CASV*030AB**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330744 |  | Ground Water | WHALEN | CASH*030AD**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330745 |  | Ground Water | WHALEN | CASV*030AD**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330746 |  | Ground Water | WHALEN | CASH*036AB**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330747 |  | Ground Water | WHALEN | CASV*036AB**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
5296266 |  | Ground Water | TRANE | EXVF0482 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296267 |  | Ground Water | TRANE | EXVF0483 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296268 |  | Ground Water | TRANE | EXVF0484 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
203113887 |  | Ground Water | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
10206404 |  | Ground Water | BARD | GTC36S2-A | HE37942D210B2505AW | 42000 | 23.9 | 38000 | 5 | 3.5 | No
10206405 |  | Ground Water | BARD | GTC36S2-A | HE37942D175B2505AW | 42000 | 23.9 | 38000 | 5 | 3.5 | No
202350526 |  | Ground Water | AAON, Inc. | WV-048-2-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
206315251 |  | Ground Water | WHALEN | CASH*015AD**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315252 |  | Ground Water | WHALEN | CASV*015AD**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315253 |  | Ground Water | WHALEN | CASH*018AB**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206315254 |  | Ground Water | WHALEN | CASV*018AB**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206315255 |  | Ground Water | WHALEN | CASH*018AD**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206315256 |  | Ground Water | WHALEN | CASV*018AD**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
205448525 |  | Ground Water | 7 SERIES INDOOR SPLITS | NVZ042A1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | No
205536324 |  | Ground Water | AAON, Inc. | WH-072-2-H-DCAC-C0-10-200-A |  | 91000 | 24 | 75800 | 4.3 | 7.5833 | No
205536327 |  | Ground Water | AAON, Inc. | WH-072-3-H-DCAC-C0-10-200-A |  | 91000 | 24 | 75800 | 4.3 | 7.5833 | No
205536344 |  | Ground Water | AAON, Inc. | WV-072-2-0-DCAC-C0-10-200-A |  | 90800 | 25 | 79800 | 4.9 | 7.5667 | No
202330467 |  | Ground Water | AAON, Inc. | RN-006-3-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
202330468 |  | Ground Water | AAON, Inc. | RN-006-4-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
202330472 |  | Ground Water | AAON, Inc. | RN-007-2-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330473 |  | Ground Water | AAON, Inc. | RN-007-3-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330474 |  | Ground Water | AAON, Inc. | RN-007-4-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330573 |  | Ground Water | AAON, Inc. | WH-006-B-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330574 |  | Ground Water | AAON, Inc. | WH-006-1-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330387 |  | Ground Water | AAON, Inc. | WV-036-1-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330388 |  | Ground Water | AAON, Inc. | WV-036-A-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330391 |  | Ground Water | AAON, Inc. | WV-036-2-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
10268208 |  | Ground Water | HYDRON MODULE | HBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268209 |  | Ground Water | TETCO | TBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268233 |  | Ground Water | GEOCOMFORT | GBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268234 |  | Ground Water | HYDRON MODULE | HBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268235 |  | Ground Water | TETCO | TBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268236 |  | Ground Water | GEOCOMFORT | GBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268237 |  | Ground Water | HYDRON MODULE | HBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
207312264 |  | Ground Water | WaterFurnace | NSV/NSH022J1*(0,3) |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
207324061 |  | Ground Water | WaterFurnace | NVZ033A1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | No
207324062 |  | Ground Water | WaterFurnace | NVZ042A1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | No
207334458 |  | Ground Water | WaterFurnace | NDP026H1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
202391439 |  | Ground Water | FHP | EP012-2VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391440 |  | Ground Water | FHP | EP012-0VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391441 |  | Ground Water | FHP | EP012-1HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391442 |  | Ground Water | FHP | EP012-1VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391443 |  | Ground Water | FHP | EP012-1HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391444 |  | Ground Water | FHP | EP012-1VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391445 |  | Ground Water | CARRIER | 50PSV012**C3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206315249 |  | Ground Water | WHALEN | CASH*015AB**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315250 |  | Ground Water | WHALEN | CASV*015AB**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
205536348 |  | Ground Water | AAON, Inc. | WV-072-3-0-DCAC-C0-10-200-A |  | 90800 | 25 | 79800 | 4.9 | 7.5667 | No
205536354 |  | Ground Water | AAON, Inc. | WV-096-2-0-DCAC-C0-10-200-A |  | 108200 | 23.2 | 99200 | 4.5 | 9.0167 | No
205536369 |  | Ground Water | AAON, Inc. | WV-096-3-0-DCAC-C0-10-200-A |  | 108200 | 23.2 | 99200 | 4.5 | 9.0167 | No
205782568 |  | Ground Water | YORK BY JOHNSON CONTROLS | YACT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
203490410 |  | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203490414 |  | Ground Water | GeoSmart Energy | GS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
203490416 |  | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
203494005 |  | Ground Water | GEOSTAR | 101/102J048**1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
203495471 |  | Ground Water | GEOSTAR | 101/102J048**1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
202330427 |  | Ground Water | AAON, Inc. | WV-048-A-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202330428 |  | Ground Water | AAON, Inc. | WV-048-A-H-DCAC-C0-10-D00-A |  | 54500 | 22 | 54200 | 4.8 | 4.5417 | No
202330429 |  | Ground Water | AAON, Inc. | WV-048-3-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202330431 |  | Ground Water | AAON, Inc. | WV-060-A-H-DCAC-C0-10-D00-A |  | 64000 | 21.7 | 65000 | 4.9 | 5.3333 | No
202330466 |  | Ground Water | AAON, Inc. | RN-006-2-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
202330415 |  | Ground Water | AAON, Inc. | WV-060-2-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330416 |  | Ground Water | AAON, Inc. | WV-060-3-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330417 |  | Ground Water | AAON, Inc. | WV-024-A-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202330418 |  | Ground Water | AAON, Inc. | WV-024-A-H-DCAC-C0-10-D00-A |  | 29000 | 22.7 | 21800 | 4.4 | 2.4167 | No
202330419 |  | Ground Water | AAON, Inc. | WV-024-3-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202330271 |  | Ground Water | AAON, Inc. | WH-009-B-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
202330272 |  | Ground Water | AAON, Inc. | WH-009-1-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
5296249 |  | Ground Water | TRANE | EXVF0247 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
5296250 |  | Ground Water | TRANE | EXVF0301 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296251 |  | Ground Water | TRANE | EXVF0302 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296252 |  | Ground Water | TRANE | EXVF0307 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296253 |  | Ground Water | TRANE | EXVF0361 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296254 |  | Ground Water | TRANE | EXVF0362 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296255 |  | Ground Water | TRANE | EXVF0363 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No

## Commercial Ground Loop HP
AHRI Certified Reference Number | Date No Longer Eligible | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage | Tax Credit (IRA) Eligibility
216714642 |  | Ground Loop | GEOSTAR | G3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714643 |  | Ground Loop | GEOSTAR | G3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714644 |  | Ground Loop | GEOSTAR | G3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
202211049 |  | Ground Loop | WaterFurnace | URD049*0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211050 |  | Ground Loop | WaterFurnace | URD049*0*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211051 |  | Ground Loop | WaterFurnace | URD049*3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211052 |  | Ground Loop | WaterFurnace | URD049*3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211053 |  | Ground Loop | WaterFurnace | URD049*3*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
202211054 |  | Ground Loop | WaterFurnace | URD064*0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211055 |  | Ground Loop | WaterFurnace | URD064*0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211056 |  | Ground Loop | WaterFurnace | URD064*0*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211057 |  | Ground Loop | WaterFurnace | URD064*3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211058 |  | Ground Loop | WaterFurnace | URD064*3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211059 |  | Ground Loop | WaterFurnace | URD064*3*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
202211060 |  | Ground Loop | WaterFurnace | URD072*0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211061 |  | Ground Loop | WaterFurnace | URD072*0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211062 |  | Ground Loop | WaterFurnace | URD072*0*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211063 |  | Ground Loop | WaterFurnace | URD072*3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211064 |  | Ground Loop | WaterFurnace | URD072*3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
202211065 |  | Ground Loop | WaterFurnace | URD072*3*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
217351675 |  | Ground Loop | BOSCH | RP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | Yes
217351676 |  | Ground Loop | BOSCH | RP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | Yes
217351677 |  | Ground Loop | BOSCH | RP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | Yes
217351678 |  | Ground Loop | BOSCH | RP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | Yes
217351679 |  | Ground Loop | BOSCH | RP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | Yes
217351680 |  | Ground Loop | BOSCH | RP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | Yes
217351682 |  | Ground Loop | BOSCH | RP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | Yes
217351683 |  | Ground Loop | BOSCH | RP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | Yes
217351684 |  | Ground Loop | BOSCH | RP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3 | Yes
217351692 |  | Ground Loop | FHP | CP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | No
217351693 |  | Ground Loop | FHP | CP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | No
217351694 |  | Ground Loop | FHP | CP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | No
217351695 |  | Ground Loop | FHP | CP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | No
217351696 |  | Ground Loop | FHP | CP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | No
217351697 |  | Ground Loop | FHP | CP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | No
217351698 |  | Ground Loop | FHP | CP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | No
217351699 |  | Ground Loop | FHP | CP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | No
217351700 |  | Ground Loop | FHP | CP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | No
217351701 |  | Ground Loop | FHP | CP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | No
217351703 |  | Ground Loop | FHP | CP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | No
217351704 |  | Ground Loop | FHP | CP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | No
217351705 |  | Ground Loop | FHP | CP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3 | No
216621350 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621351 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621352 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621353 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621354 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216621355 |  | Ground Loop | GEOSTAR | G5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216621356 |  | Ground Loop | GEOSTAR | G5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216621357 |  | Ground Loop | GEOSTAR | G5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216621358 |  | Ground Loop | GEOSTAR | G5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216621359 |  | Ground Loop | GEOSTAR | G5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
202084059 |  | Ground Loop | GEOCOMFORT | GZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
202084060 |  | Ground Loop | HYDRON MODULE | HZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | Yes
202084061 |  | Ground Loop | HYDRON MODULE | HZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
202084062 |  | Ground Loop | TETCO | TZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | Yes
202084063 |  | Ground Loop | TETCO | TZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
3628355 |  | Ground Loop | WaterFurnace | USV/USH070**0*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
3628356 |  | Ground Loop | WaterFurnace | USV/USH070**3*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
3628357 |  | Ground Loop | WaterFurnace | USV/USH070**4*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
3628359 |  | Ground Loop | WaterFurnace | USV/USH060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3628360 |  | Ground Loop | WaterFurnace | USV/USH060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3628361 |  | Ground Loop | WaterFurnace | USV/USH060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3628363 |  | Ground Loop | WaterFurnace | USV/USH048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3628364 |  | Ground Loop | WaterFurnace | USV/USH048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3628365 |  | Ground Loop | WaterFurnace | USV/USH048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3628367 |  | Ground Loop | WaterFurnace | USV/USH042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3628368 |  | Ground Loop | WaterFurnace | USV/USH042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3628369 |  | Ground Loop | WaterFurnace | USV/USH042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3628403 |  | Ground Loop | WaterFurnace | USV/USH030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3628404 |  | Ground Loop | WaterFurnace | USV/USH030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3628405 |  | Ground Loop | WaterFurnace | USV/USH030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3628406 |  | Ground Loop | WaterFurnace | USV/USH030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3628407 |  | Ground Loop | WaterFurnace | USH023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3628408 |  | Ground Loop | WaterFurnace | USV/USH036**3*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
3628409 |  | Ground Loop | WaterFurnace | USV/USH036**0*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
3628410 |  | Ground Loop | WaterFurnace | USV/USH036**4*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
3628411 |  | Ground Loop | WaterFurnace | USH023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3628412 |  | Ground Loop | WaterFurnace | USH023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3628413 |  | Ground Loop | WaterFurnace | USH023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
7022707 |  | Ground Loop | GeoSmart Energy | ZS060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
7022708 |  | Ground Loop | GEOSTAR | ZS060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
7167375 |  | Ground Loop | BRYANT | GB024H/V******1*X1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
7167376 |  | Ground Loop | CARRIER | GB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
7167377 |  | Ground Loop | BRYANT | GB030H/V******1*X1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
7167378 |  | Ground Loop | CARRIER | GB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
7167538 |  | Ground Loop | CARRIER | 50PTD/H/V024***3/CA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7167539 |  | Ground Loop | CARRIER | 50PTD/H/V024***5/EA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7167540 |  | Ground Loop | CARRIER | 50PTD/H/V024***4/DA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7167541 |  | Ground Loop | CARRIER | 50PTD/H/V024***6/FA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7167542 |  | Ground Loop | CARRIER | 50PTD/H/V036***3/CA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7167543 |  | Ground Loop | CARRIER | 50PTD/H/V036***5/EA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7167544 |  | Ground Loop | CARRIER | 50PTD/H/V036***4/DA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7167545 |  | Ground Loop | CARRIER | 50PTD/H/V036***6/FA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7167546 |  | Ground Loop | CARRIER | 50PTD/H/V048***3/CA |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7167547 |  | Ground Loop | CARRIER | 50PTD/H/V048***5/EA |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7167548 |  | Ground Loop | CARRIER | 50PTD/H/V048***6/FA |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7167549 |  | Ground Loop | CARRIER | 50PTD/H/V060***3/CA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7167550 |  | Ground Loop | CARRIER | 50PTD/H/V060***5/EA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7167551 |  | Ground Loop | CARRIER | 50PTD/H/V060***6/FA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7170602 |  | Ground Loop | GEOCOMFORT | GVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | Yes
7170603 |  | Ground Loop | HYDRON MODULE | HVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | Yes
7170604 |  | Ground Loop | TETCO | TVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | Yes
217752681 |  | Ground Loop | DAIKIN | WSSH030J1*H*T |  | 30600 | 21.15 | 21200 | 3.95 | 2.55 | No
217752683 |  | Ground Loop | DAIKIN | WSSH030J1*H*C |  | 30600 | 21.15 | 21200 | 3.95 | 2.55 | No
217752685 |  | Ground Loop | DAIKIN | WSSH036J1*H*T |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583 | No
217752687 |  | Ground Loop | DAIKIN | WSSH036J1*H*C |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583 | No
7499552 |  | Ground Loop | FHP | LM036-2VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7499553 |  | Ground Loop | FHP | LM036-3VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7499554 |  | Ground Loop | FHP | LM036-4VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
7499556 |  | Ground Loop | FHP | LM048-1VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7499559 |  | Ground Loop | FHP | LM048-3VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7499560 |  | Ground Loop | FHP | LM048-4VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
7499562 |  | Ground Loop | FHP | LM060-1VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7499565 |  | Ground Loop | FHP | LM060-3VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7499566 |  | Ground Loop | FHP | LM060-4VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425 | No
7499702 |  | Ground Loop | BOSCH | SM036-1CF/HZ/VT |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | Yes
7519546 |  | Ground Loop | GEOCOMFORT | GVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | No
7519547 |  | Ground Loop | HYDRON MODULE | HVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | No
7519548 |  | Ground Loop | TETCO | TVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833 | No
7519549 |  | Ground Loop | GEOCOMFORT | GVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519550 |  | Ground Loop | HYDRON MODULE | HVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519551 |  | Ground Loop | TETCO | TVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519552 |  | Ground Loop | GEOCOMFORT | GVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519553 |  | Ground Loop | HYDRON MODULE | HVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519554 |  | Ground Loop | TETCO | TVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519555 |  | Ground Loop | GEOCOMFORT | GVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519556 |  | Ground Loop | HYDRON MODULE | HVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519557 |  | Ground Loop | TETCO | TVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519558 |  | Ground Loop | GEOCOMFORT | GVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519559 |  | Ground Loop | HYDRON MODULE | HVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519560 |  | Ground Loop | TETCO | TVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | No
7519561 |  | Ground Loop | GEOCOMFORT | GVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519562 |  | Ground Loop | HYDRON MODULE | HVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519563 |  | Ground Loop | TETCO | TVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519564 |  | Ground Loop | GEOCOMFORT | GVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519565 |  | Ground Loop | HYDRON MODULE | HVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519566 |  | Ground Loop | TETCO | TVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519567 |  | Ground Loop | GEOCOMFORT | GVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519568 |  | Ground Loop | HYDRON MODULE | HVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519569 |  | Ground Loop | TETCO | TVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519570 |  | Ground Loop | GEOCOMFORT | GVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519571 |  | Ground Loop | HYDRON MODULE | HVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519572 |  | Ground Loop | TETCO | TVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | No
7519573 |  | Ground Loop | GEOCOMFORT | GVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519574 |  | Ground Loop | HYDRON MODULE | HVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519575 |  | Ground Loop | TETCO | TVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519576 |  | Ground Loop | GEOCOMFORT | GVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519577 |  | Ground Loop | HYDRON MODULE | HVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519578 |  | Ground Loop | TETCO | TVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519579 |  | Ground Loop | GEOCOMFORT | GVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519580 |  | Ground Loop | HYDRON MODULE | HVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519581 |  | Ground Loop | TETCO | TVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519582 |  | Ground Loop | GEOCOMFORT | GVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519583 |  | Ground Loop | HYDRON MODULE | HVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519584 |  | Ground Loop | TETCO | TVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | No
7519727 |  | Ground Loop | GEOCOMFORT | GVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | Yes
7519748 |  | Ground Loop | HYDRON MODULE | HVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | Yes
7519756 |  | Ground Loop | TETCO | TVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | Yes
203372406 |  | Ground Loop | TEMPSTAR | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372407 |  | Ground Loop | COMFORTMAKER | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372408 |  | Ground Loop | DAY & NIGHT | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372993 |  | Ground Loop | BOSCH | SM060-1HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
203380957 |  | Ground Loop | BOSCH | EP018-1VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203380958 |  | Ground Loop | BOSCH | EP018-2VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203380959 |  | Ground Loop | BOSCH | EP018-1HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203380960 |  | Ground Loop | BOSCH | EP018-2HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203380963 |  | Ground Loop | BOSCH | EP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203380964 |  | Ground Loop | BOSCH | EP042-3VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203380965 |  | Ground Loop | BOSCH | EP042-4VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203380966 |  | Ground Loop | BOSCH | EP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203380967 |  | Ground Loop | BOSCH | EP042-3HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203380968 |  | Ground Loop | BOSCH | EP042-4HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203380969 |  | Ground Loop | BOSCH | EP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203380970 |  | Ground Loop | BOSCH | EP048-3VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
202434398 |  | Ground Loop | FHP | LV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434399 |  | Ground Loop | FHP | LV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434436 |  | Ground Loop | FHP | LV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434437 |  | Ground Loop | FHP | LV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
215837874 |  | Ground Loop | DAIKIN | WSSH042J1*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837876 |  | Ground Loop | DAIKIN | WSSH042K3*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837882 |  | Ground Loop | DAIKIN | WSSH048F3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837883 |  | Ground Loop | DAIKIN | WSSH048K3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837884 |  | Ground Loop | DAIKIN | WSSH048L3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837891 |  | Ground Loop | DAIKIN | WSSH048F3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837892 |  | Ground Loop | DAIKIN | WSSH048K3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
215837893 |  | Ground Loop | DAIKIN | WSSH048L3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
218158076 |  | Ground Loop | YORK | Y3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
218158078 |  | Ground Loop | YORK | Y3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
218158079 |  | Ground Loop | YORK | Y3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
218158081 |  | Ground Loop | YORK | Y3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
218158092 |  | Ground Loop | YORK | Y3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
218158093 |  | Ground Loop | YORK | Y3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
218158094 |  | Ground Loop | YORK | Y3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
218158095 |  | Ground Loop | YORK | Y3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
218158096 |  | Ground Loop | YORK | Y3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
218158097 |  | Ground Loop | YORK | Y3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
218158098 |  | Ground Loop | YORK | Y3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
218158106 |  | Ground Loop | YORK | Y3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
218158107 |  | Ground Loop | YORK | Y3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
218158108 |  | Ground Loop | YORK | Y3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
218158109 |  | Ground Loop | YORK | Y3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
218158110 |  | Ground Loop | YORK | Y3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
218158111 |  | Ground Loop | YORK | Y3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
218158112 |  | Ground Loop | YORK | Y3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
218158113 |  | Ground Loop | YORK | Y3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
218158114 |  | Ground Loop | YORK | Y3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
218158115 |  | Ground Loop | YORK | Y3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
218158116 |  | Ground Loop | YORK | Y3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
218158117 |  | Ground Loop | YORK | Y3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
218158123 |  | Ground Loop | YORK | Y3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
218158124 |  | Ground Loop | YORK | Y3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
218158125 |  | Ground Loop | YORK | Y3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
218158126 |  | Ground Loop | YORK | Y3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
10259059 |  | Ground Loop | TETCO | TZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | No
10259062 |  | Ground Loop | GEOCOMFORT | GZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | Yes
218353673 |  | Ground Loop | JOHNSON CONTROLS | DQ036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218353674 |  | Ground Loop | JOHNSON CONTROLS | DQ036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218353675 |  | Ground Loop | JOHNSON CONTROLS | DQ048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
218353676 |  | Ground Loop | JOHNSON CONTROLS | DQ048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218353677 |  | Ground Loop | JOHNSON CONTROLS | DQ048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
218353678 |  | Ground Loop | JOHNSON CONTROLS | DQ048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218353679 |  | Ground Loop | JOHNSON CONTROLS | DQ048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
218353680 |  | Ground Loop | JOHNSON CONTROLS | DQ048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218353681 |  | Ground Loop | JOHNSON CONTROLS | DQ060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218353682 |  | Ground Loop | JOHNSON CONTROLS | DQ060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
218353683 |  | Ground Loop | JOHNSON CONTROLS | DQ060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218353684 |  | Ground Loop | JOHNSON CONTROLS | DQ060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
218353685 |  | Ground Loop | JOHNSON CONTROLS | DQ060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218471838 |  | Ground Loop | YORK | AQ024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218471839 |  | Ground Loop | YORK | QQ024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
218471840 |  | Ground Loop | YORK | AQ024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218471841 |  | Ground Loop | YORK | AQ024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218471842 |  | Ground Loop | YORK | QQ036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
218471843 |  | Ground Loop | YORK | AQ036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218471844 |  | Ground Loop | YORK | AQ036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218471845 |  | Ground Loop | YORK | QQ036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
218471846 |  | Ground Loop | YORK | AQ036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218471847 |  | Ground Loop | YORK | AQ036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218471848 |  | Ground Loop | YORK | QQ048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
218471849 |  | Ground Loop | YORK | AQ048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
218471850 |  | Ground Loop | YORK | AQ048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
218471851 |  | Ground Loop | YORK | QQ048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
218471852 |  | Ground Loop | YORK | AQ048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218471853 |  | Ground Loop | YORK | AQ048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218471854 |  | Ground Loop | YORK | QQ060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
218471855 |  | Ground Loop | YORK | AQ060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218471856 |  | Ground Loop | YORK | AQ060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218471857 |  | Ground Loop | YORK | QQ060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
218471858 |  | Ground Loop | YORK | AQ060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
218471859 |  | Ground Loop | YORK | AQ060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
218471860 |  | Ground Loop | YORK | QQ070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
218471861 |  | Ground Loop | YORK | AQ070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218471862 |  | Ground Loop | YORK | AQ070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218471866 |  | Ground Loop | YORK | QQ070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
218471867 |  | Ground Loop | YORK | AQ070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218471868 |  | Ground Loop | YORK | AQ070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218471891 |  | Ground Loop | YORK | QZ024-1CSC-*****A | CDM24B5XXS1A | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | Yes
218471892 |  | Ground Loop | YORK | QZ024-1CSN-*****A | CDM24B5XXS1A | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | Yes
217351843 |  | Ground Loop | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351844 |  | Ground Loop | DAY & NIGHT | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351846 |  | Ground Loop | DAY & NIGHT | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
7411231 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7411301 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
7411380 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7411778 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7411875 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
7411949 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7412057 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7412158 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
7412253 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7412381 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
7412626 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7412712 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7412777 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7412856 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7412926 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7413034 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7413487 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7414142 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
7414232 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7414335 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
203337768 |  | Ground Loop | BOSCH-GEO | CE025-1VT/HZ/CF*-*****B |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
203337769 |  | Ground Loop | BOSCH | CE025-1VT/HZ/CF*-*****B |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337770 |  | Ground Loop | CARRIER | GP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
203337771 |  | Ground Loop | BRYANT | GP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337772 |  | Ground Loop | HEIL | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
203337773 |  | Ground Loop | ARCOAIRE | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337774 |  | Ground Loop | KEEPRITE | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337775 |  | Ground Loop | TEMPSTAR | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337776 |  | Ground Loop | COMFORTMAKER | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203337777 |  | Ground Loop | DAY & NIGHT | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | Yes
203343532 |  | Ground Loop | BOSCH-GEO | SM024-1CS*******A | SM024-1AV/AH*-*****A | 26200 | 17 | 17700 | 3.75 | 2.1833 | Yes
203343535 |  | Ground Loop | BOSCH | SM024-1CS*******A | SM024-1AV/AH*-*****A | 26200 | 17 | 17700 | 3.75 | 2.1833 | Yes
4651405 |  | Ground Loop | WaterFurnace | USV/USH030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651407 |  | Ground Loop | WaterFurnace | USV/USH030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651417 |  | Ground Loop | WaterFurnace | USV/USH036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651418 |  | Ground Loop | WaterFurnace | USV/USH036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651419 |  | Ground Loop | WaterFurnace | USV/USH036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651420 |  | Ground Loop | WaterFurnace | USV/USH036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651530 |  | Ground Loop | WaterFurnace | USV/USH042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651532 |  | Ground Loop | WaterFurnace | USV/USH042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651533 |  | Ground Loop | WaterFurnace | USV/USH042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651546 |  | Ground Loop | WaterFurnace | USV/USH048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651547 |  | Ground Loop | WaterFurnace | USV/USH048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651548 |  | Ground Loop | WaterFurnace | USV/USH048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651574 |  | Ground Loop | WaterFurnace | USV/USH060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651575 |  | Ground Loop | WaterFurnace | USV/USH060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651576 |  | Ground Loop | WaterFurnace | USV/USH060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651577 |  | Ground Loop | WaterFurnace | USV/USH070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651578 |  | Ground Loop | WaterFurnace | USV/USH070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651579 |  | Ground Loop | WaterFurnace | USV/USH070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651610 |  | Ground Loop | GEOSTAR | ZS023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651611 |  | Ground Loop | GeoSmart Energy | ZS023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651614 |  | Ground Loop | GEOSTAR | ZS024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651615 |  | Ground Loop | GeoSmart Energy | ZS024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651618 |  | Ground Loop | GEOSTAR | ZS024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651619 |  | Ground Loop | GeoSmart Energy | ZS024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651622 |  | Ground Loop | GEOSTAR | ZS024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651623 |  | Ground Loop | GeoSmart Energy | ZS024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651626 |  | Ground Loop | GEOSTAR | ZS024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651627 |  | Ground Loop | GeoSmart Energy | ZS024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651630 |  | Ground Loop | GEOSTAR | ZS030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651631 |  | Ground Loop | GeoSmart Energy | ZS030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651634 |  | Ground Loop | GEOSTAR | ZS030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651635 |  | Ground Loop | GeoSmart Energy | ZS030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651639 |  | Ground Loop | GEOSTAR | ZS030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651640 |  | Ground Loop | GeoSmart Energy | ZS030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651644 |  | Ground Loop | GEOSTAR | ZS030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651645 |  | Ground Loop | GeoSmart Energy | ZS030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651657 |  | Ground Loop | GEOSTAR | ZS036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651658 |  | Ground Loop | GeoSmart Energy | ZS036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651665 |  | Ground Loop | GEOSTAR | ZS036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651666 |  | Ground Loop | GeoSmart Energy | ZS036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651726 |  | Ground Loop | GEOSTAR | ZS036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651727 |  | Ground Loop | GeoSmart Energy | ZS036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651732 |  | Ground Loop | GEOSTAR | ZS036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651733 |  | Ground Loop | GeoSmart Energy | ZS036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
4651865 |  | Ground Loop | GEOSTAR | ZS023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651866 |  | Ground Loop | GeoSmart Energy | ZS023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651869 |  | Ground Loop | GEOSTAR | ZS023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
202434678 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434679 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
216801983 |  | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**3*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801984 |  | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**3*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801985 |  | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**3*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801986 |  | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**3*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801987 |  | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**4*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801988 |  | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**4*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801989 |  | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**4*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801990 |  | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**4*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801991 |  | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**5*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801992 |  | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**5*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801993 |  | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**5*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801994 |  | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**5*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801995 |  | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**6*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801996 |  | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**6*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801997 |  | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**6*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216801998 |  | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**6*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216801999 |  | Ground Loop | CARRIER | 50WT*036***3*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216802000 |  | Ground Loop | CARRIER | 50WT*036***3*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216802001 |  | Ground Loop | CARRIER | 50WT*036***4*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216802002 |  | Ground Loop | CARRIER | 50WT*036***4*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216802003 |  | Ground Loop | CARRIER | 50WT*036***5*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216802004 |  | Ground Loop | CARRIER | 50WT*036***5*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216802005 |  | Ground Loop | CARRIER | 50WT*036***6*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216802006 |  | Ground Loop | CARRIER | 50WT*036***6*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216802007 |  | Ground Loop | CARRIER | 50WT*048***3*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216802008 |  | Ground Loop | CARRIER | 50WT*048***3*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216802009 |  | Ground Loop | CARRIER | 50WT*048***5*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216802010 |  | Ground Loop | CARRIER | 50WT*048***5*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216802011 |  | Ground Loop | CARRIER | 50WT*048***6*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216802012 |  | Ground Loop | CARRIER | 50WT*048***6*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216802013 |  | Ground Loop | CARRIER | 50WT*060***3*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216802014 |  | Ground Loop | CARRIER | 50WT*060***3*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216802015 |  | Ground Loop | CARRIER | 50WT*060***5*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216802016 |  | Ground Loop | CARRIER | 50WT*060***5*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216802017 |  | Ground Loop | CARRIER | 50WT*060***6*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216802018 |  | Ground Loop | CARRIER | 50WT*060***6*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216802019 |  | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**3*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216802021 |  | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**3*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216802023 |  | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**5*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218471894 |  | Ground Loop | YORK | QZ036-1CSN-*****A | CDM30B5XXS1A | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | Yes
218471895 |  | Ground Loop | YORK | QZ048-1CSC-*****A | CDM48C5XXS1A | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | Yes
218471896 |  | Ground Loop | YORK | QZ048-1CSN-*****A | CDM48C5XXS1A | 51600 | 17.8 | 38200 | 4.1 | 4.3 | Yes
218471899 |  | Ground Loop | YORK | AZ024-1CSC-*****A | JDE24E5XX2DS1 | 26000 | 18.3 | 18400 | 4 | 2.1667 | No
218471900 |  | Ground Loop | YORK | AZ024-1CSN-*****A | JDE24E5XX2DS1 | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | No
218471901 |  | Ground Loop | YORK | QZ024-1CSC-*****A | JDE24E5XX2DS1 | 26000 | 18.3 | 18400 | 4 | 2.1667 | Yes
218471902 |  | Ground Loop | YORK | QZ024-1CSN-*****A | JDE24E5XX2DS1 | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | Yes
218471903 |  | Ground Loop | YORK | AZ036-1CSC-*****A | JDE36E5XX2DS1 | 38200 | 17.6 | 29200 | 4 | 3.1833 | No
218471904 |  | Ground Loop | YORK | AZ036-1CSN-*****A | JDE36E5XX2DS1 | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | No
218471905 |  | Ground Loop | YORK | QZ036-1CSC-*****A | JDE36E5XX2DS1 | 38200 | 17.6 | 29200 | 4 | 3.1833 | Yes
218471906 |  | Ground Loop | YORK | QZ036-1CSN-*****A | JDE36E5XX2DS1 | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | Yes
218471907 |  | Ground Loop | YORK | AZ048-1CSC-*****A | JDE48F5XX2DS1 | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | No
218471908 |  | Ground Loop | YORK | AZ048-1CSN-*****A | JDE48F5XX2DS1 | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | No
218471909 |  | Ground Loop | YORK | QZ048-1CSC-*****A | JDE48F5XX2DS1 | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | Yes
218471910 |  | Ground Loop | YORK | QZ048-1CSN-*****A | JDE48F5XX2DS1 | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | Yes
5646384 |  | Ground Loop | GEOCOMFORT | GCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646385 |  | Ground Loop | HYDRON MODULE | HCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646386 |  | Ground Loop | TETCO | TCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646387 |  | Ground Loop | GEOCOMFORT | GCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646388 |  | Ground Loop | HYDRON MODULE | HCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646389 |  | Ground Loop | TETCO | TCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | No
5646391 |  | Ground Loop | GEOCOMFORT | GXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | Yes
5646392 |  | Ground Loop | HYDRON MODULE | HXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | Yes
5646393 |  | Ground Loop | TETCO | TXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | Yes
5646394 |  | Ground Loop | GEOCOMFORT | GXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646395 |  | Ground Loop | HYDRON MODULE | HXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646396 |  | Ground Loop | TETCO | TXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646397 |  | Ground Loop | GEOCOMFORT | GXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646398 |  | Ground Loop | HYDRON MODULE | HXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646399 |  | Ground Loop | TETCO | TXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833 | No
5646765 |  | Ground Loop | GEOCOMFORT | GCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | Yes
5646766 |  | Ground Loop | HYDRON MODULE | HCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | Yes
5646767 |  | Ground Loop | TETCO | TCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | Yes
215400079 |  | Ground Loop | DAIKIN | WSMV015E1*G/J*P |  | 16100 | 20.21 | 11200 | 3.65 | 1.3417 | No
215400081 |  | Ground Loop | DAIKIN | WSMV015E1*G/J*T |  | 16300 | 21.12 | 11100 | 3.74 | 1.3583 | No
215400083 |  | Ground Loop | DAIKIN | WSMV015E1*G/J*C |  | 16300 | 21.12 | 11100 | 3.74 | 1.3583 | No
215400087 |  | Ground Loop | DAIKIN | WSMV019E1*G/J*T |  | 20600 | 20.26 | 15100 | 3.69 | 1.7167 | No
215400089 |  | Ground Loop | DAIKIN | WSMV019E1*G/J*C |  | 20600 | 20.26 | 15100 | 3.69 | 1.7167 | No
215400092 |  | Ground Loop | DAIKIN | WSMV024E1*G/J*P |  | 25500 | 19.55 | 18900 | 3.72 | 2.125 | No
215400093 |  | Ground Loop | DAIKIN | WSMV024F3*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
215400096 |  | Ground Loop | DAIKIN | WSMV024E1*G/J*T |  | 25600 | 20.91 | 18600 | 3.87 | 2.1333 | No
215400097 |  | Ground Loop | DAIKIN | WSMV024F3*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215400100 |  | Ground Loop | DAIKIN | WSMV024E1*G/J*C |  | 25600 | 20.91 | 18600 | 3.87 | 2.1333 | No
215400101 |  | Ground Loop | DAIKIN | WSMV024F3*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215400104 |  | Ground Loop | DAIKIN | WSMV030E1*G/J*P |  | 29500 | 19.36 | 21300 | 3.62 | 2.4583 | No
215400108 |  | Ground Loop | DAIKIN | WSMV030E1*G/J*T |  | 29800 | 19.77 | 21500 | 3.65 | 2.4833 | No
215400112 |  | Ground Loop | DAIKIN | WSMV030E1*G/J*C |  | 29800 | 19.77 | 21500 | 3.65 | 2.4833 | No
215400116 |  | Ground Loop | DAIKIN | WSMV036E1*G/J*P |  | 37600 | 19.36 | 28000 | 3.69 | 3.1333 | No
215400120 |  | Ground Loop | DAIKIN | WSMV036E1*G/J*T |  | 37500 | 19.9 | 28000 | 3.82 | 3.125 | No
215400121 |  | Ground Loop | DAIKIN | WSMV036F3*G/J*T |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917 | No
215400124 |  | Ground Loop | DAIKIN | WSMV036E1*G/J*C |  | 37500 | 19.9 | 28000 | 3.82 | 3.125 | No
217754418 |  | Ground Loop | DAIKIN | WSSH070F1*H*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
217754419 |  | Ground Loop | DAIKIN | WSSH070K1*H*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
217754422 |  | Ground Loop | DAIKIN | WSSH070F1*H*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
217754423 |  | Ground Loop | DAIKIN | WSSH070K1*H*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
217754426 |  | Ground Loop | DAIKIN | WSSV024F1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
202434372 |  | Ground Loop | FHP | LV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434373 |  | Ground Loop | FHP | LV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434374 |  | Ground Loop | FHP | LV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202146892 |  | Ground Loop | TETCO | TZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146893 |  | Ground Loop | GEOCOMFORT | GZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | Yes
202146894 |  | Ground Loop | GEOCOMFORT | GZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146895 |  | Ground Loop | GEOCOMFORT | GZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146896 |  | Ground Loop | GEOCOMFORT | GZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146897 |  | Ground Loop | HYDRON MODULE | HZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | Yes
202146898 |  | Ground Loop | HYDRON MODULE | HZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146899 |  | Ground Loop | HYDRON MODULE | HZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146900 |  | Ground Loop | HYDRON MODULE | HZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146901 |  | Ground Loop | TETCO | TZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | Yes
202146902 |  | Ground Loop | TETCO | TZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146903 |  | Ground Loop | TETCO | TZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202146913 |  | Ground Loop | GEOCOMFORT | GZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | Yes
217754698 |  | Ground Loop | DAIKIN | WSMV060K1*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
217754701 |  | Ground Loop | DAIKIN | WSMV060F1*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
217754702 |  | Ground Loop | DAIKIN | WSMV060K1*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
218353078 |  | Ground Loop | SKYMARK | PQ048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218353079 |  | Ground Loop | SKYMARK | PQ060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218353080 |  | Ground Loop | SKYMARK | PQ060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
218353081 |  | Ground Loop | SKYMARK | PQ060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218353082 |  | Ground Loop | SKYMARK | PQ060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
218353083 |  | Ground Loop | SKYMARK | PQ070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353085 |  | Ground Loop | SKYMARK | PQ070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353087 |  | Ground Loop | SKYMARK | PQ070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353089 |  | Ground Loop | SKYMARK | PQ070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353144 |  | Ground Loop | SKYMARK | PD007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218353145 |  | Ground Loop | SKYMARK | PD007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218353146 |  | Ground Loop | SKYMARK | PD007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218353147 |  | Ground Loop | SKYMARK | PD007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218353148 |  | Ground Loop | SKYMARK | PD009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218353149 |  | Ground Loop | SKYMARK | PD009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218353150 |  | Ground Loop | SKYMARK | PD009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218353151 |  | Ground Loop | SKYMARK | PD009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218353152 |  | Ground Loop | SKYMARK | PD012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
216739885 |  | Ground Loop | DAIKIN | WSDV036E1*G/J*C |  | 37100 | 19 | 27300 | 3.8 | 3.0917 | No
216739886 |  | Ground Loop | DAIKIN | WSDV036F3*G/J*C |  | 37100 | 18.6 | 27300 | 3.7 | 3.0917 | No
216739887 |  | Ground Loop | DAIKIN | WSDV036J1*G/J*C |  | 37100 | 18.6 | 27300 | 3.7 | 3.0917 | No
216739888 |  | Ground Loop | DAIKIN | WSDV036K3*G/J*C |  | 37100 | 18.4 | 27300 | 3.7 | 3.0917 | No
216739901 |  | Ground Loop | DAIKIN | WSDV060E1*G/J*C |  | 62000 | 17.3 | 46100 | 3.7 | 5.1667 | No
216739902 |  | Ground Loop | DAIKIN | WSDV060F3*G/J*C |  | 62000 | 17 | 46100 | 3.6 | 5.1667 | No
216739903 |  | Ground Loop | DAIKIN | WSDV060K3*G/J*C |  | 62000 | 17 | 46100 | 3.6 | 5.1667 | No
216739914 |  | Ground Loop | DAIKIN | WSNH024E1*G/J*C |  | 25300 | 18.5 | 17900 | 3.6 | 2.1083 | No
216739922 |  | Ground Loop | DAIKIN | WSNH030E1*G/J*C |  | 32100 | 18.3 | 23800 | 3.6 | 2.675 | No
216739930 |  | Ground Loop | DAIKIN | WSNH036E1*G/J*C |  | 35700 | 19.6 | 25500 | 3.6 | 2.975 | No
217897411 |  | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
217897412 |  | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
217897413 |  | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
217897414 |  | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
217897417 |  | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
217897418 |  | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
217897421 |  | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
217897422 |  | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
207200558 |  | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207200565 |  | Ground Loop | GeoSmart Energy | GS060**1*(1,4)*H |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207200566 |  | Ground Loop | GeoSmart Energy | GS060**1*0*H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
207200576 |  | Ground Loop | GeoSmart Energy | GTZ026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207200577 |  | Ground Loop | GeoSmart Energy | GTZ026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
207200578 |  | Ground Loop | GeoSmart Energy | GTS026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207200579 |  | Ground Loop | GeoSmart Energy | GTS026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207200580 |  | Ground Loop | GeoSmart Energy | GTS049*1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207200581 |  | Ground Loop | GeoSmart Energy | GTS049*1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207200582 |  | Ground Loop | GeoSmart Energy | GTS064*1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207200583 |  | Ground Loop | GeoSmart Energy | GTS064*1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207200586 |  | Ground Loop | GeoSmart Energy | GSZ022*1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
207200587 |  | Ground Loop | GeoSmart Energy | GSZ022*1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
207200588 |  | Ground Loop | GeoSmart Energy | GSZ030*1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
207200589 |  | Ground Loop | GeoSmart Energy | GSZ030*1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
207200590 |  | Ground Loop | GeoSmart Energy | GSZ048*1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
207200591 |  | Ground Loop | GeoSmart Energy | GSZ048*1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
207200592 |  | Ground Loop | GeoSmart Energy | GSZ060*1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
207200593 |  | Ground Loop | GeoSmart Energy | GSZ060*1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
207200594 |  | Ground Loop | GeoSmart Energy | GSZ070*1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207200596 |  | Ground Loop | GeoSmart Energy | GSZ070*1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | Yes
207200598 |  | Ground Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
207200599 |  | Ground Loop | GeoSmart Energy | GSZ042*1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
207200600 |  | Ground Loop | GeoSmart Energy | GTZ038*1*J | SAH038* | 36000 | 19 | 27900 | 4 | 3 | No
207200601 |  | Ground Loop | GeoSmart Energy | GTZ049*1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
217967019 |  | Ground Loop | TRANE | VSVK024A |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917 | No
217967020 |  | Ground Loop | TRANE | VSHK033A |  | 33300 | 18.1 | 27700 | 4.1 | 2.775 | No
217967021 |  | Ground Loop | TRANE | VSVK033A |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417 | No
217967022 |  | Ground Loop | TRANE | VSHK042A |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167 | No
217967023 |  | Ground Loop | TRANE | VSVK042A |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417 | No
217967024 |  | Ground Loop | TRANE | VSHK050A |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417 | No
217967025 |  | Ground Loop | TRANE | VSVK050A |  | 50400 | 19.3 | 40400 | 4.3 | 4.2 | No
217967026 |  | Ground Loop | TRANE | VSHK060A |  | 61900 | 17 | 51400 | 3.9 | 5.1583 | No
217967027 |  | Ground Loop | TRANE | VSVK060A |  | 61200 | 17.9 | 49500 | 4.1 | 5.1 | No
217967028 |  | Ground Loop | TRANE | VSHK024B |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167 | No
217967029 |  | Ground Loop | TRANE | VSVK024B |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917 | No
217967030 |  | Ground Loop | TRANE | VSHK033B |  | 33300 | 18.1 | 27700 | 4.1 | 2.775 | No
217967031 |  | Ground Loop | TRANE | VSVK033B |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417 | No
217967032 |  | Ground Loop | TRANE | VSHK042B |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167 | No
217967033 |  | Ground Loop | TRANE | VSVK042B |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417 | No
217967034 |  | Ground Loop | TRANE | VSHK050B |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417 | No
217967035 |  | Ground Loop | TRANE | VSVK050B |  | 50400 | 19.3 | 40400 | 4.3 | 4.2 | No
217967036 |  | Ground Loop | TRANE | VSHK060B |  | 61900 | 17 | 51400 | 3.9 | 5.1583 | No
217967037 |  | Ground Loop | TRANE | VSVK060B |  | 61200 | 17.9 | 49500 | 4.1 | 5.1 | No
217967038 |  | Ground Loop | TRANE | VSHK0244 |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167 | No
217967039 |  | Ground Loop | TRANE | VSVK0244 |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917 | No
217967040 |  | Ground Loop | TRANE | VSHK0334 |  | 33300 | 18.1 | 27700 | 4.1 | 2.775 | No
217967041 |  | Ground Loop | TRANE | VSVK0334 |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417 | No
217967042 |  | Ground Loop | TRANE | VSHK0424 |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167 | No
217967043 |  | Ground Loop | TRANE | VSVK0424 |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417 | No
9100383 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100384 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100390 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100391 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100393 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100394 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100396 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100397 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
9100400 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100401 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100403 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100404 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100417 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9100431 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
9105364 |  | Ground Loop | GEOCOMFORT | GVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6 | Yes
9105366 |  | Ground Loop | HYDRON MODULE | HVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6 | Yes
9105367 |  | Ground Loop | TETCO | TVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6 | Yes
9111997 |  | Ground Loop | BOSCH | SM024-1VT/CF*-*****B |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417 | No
9111998 |  | Ground Loop | BOSCH | SM036-1VT/CF*-*****B |  | 40200 | 21 | 28200 | 4.3 | 3.35 | No
9113111 |  | Ground Loop | BOSCH | SM048-1VT/CF*-*****B* |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167 | No
9113180 |  | Ground Loop | BOSCH | SM060-1VT/CF*-*****B |  | 63900 | 18.6 | 48600 | 4 | 5.325 | No
9113181 |  | Ground Loop | BOSCH | SM070-1VT/CF*-*****B |  | 71500 | 17.3 | 56000 | 3.8 | 5.9583 | No
9113182 |  | Ground Loop | BOSCH | SM024-1VT/CF*-*****B |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417 | Yes
9113183 |  | Ground Loop | BOSCH | SM036-1VT/CF*-*****B |  | 40200 | 21 | 28200 | 4.3 | 3.35 | Yes
9113184 |  | Ground Loop | BOSCH | SM048-1VT/CF*-*****B* |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167 | Yes
9113185 |  | Ground Loop | BOSCH | SM060-1VT/CF*-*****B |  | 63900 | 18.6 | 48600 | 4 | 5.325 | Yes
9113186 |  | Ground Loop | BOSCH | SM070-1VT/CF*-*****B |  | 71500 | 17.3 | 56000 | 3.8 | 5.9583 | Yes
213614585 |  | Ground Loop | DAIKIN | WSCH015E1*G/J*T |  | 15600 | 19 | 11900 | 3.6 | 1.3 | No
213614586 |  | Ground Loop | DAIKIN | WSCH015E1*G/J*C |  | 15600 | 19 | 11900 | 3.6 | 1.3 | No
212505511 |  | Ground Loop | HYDROTECH | WSH6048AM* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | No
212505513 |  | Ground Loop | AE Air | WSH6036AM* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | No
212505514 |  | Ground Loop | AE Air | WSH6042AM* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | No
212505515 |  | Ground Loop | AE Air | WSH6048AM* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | No
212508382 |  | Ground Loop | HYDROTECH | WSH6036AN* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | No
212508384 |  | Ground Loop | HYDROTECH | WSH6042AN* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | No
212508386 |  | Ground Loop | HYDROTECH | WSH6048AN* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | No
212508387 |  | Ground Loop | HYDROTECH | WSH6060AM* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | No
212508388 |  | Ground Loop | HYDROTECH | WSH6060AN* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | No
212508389 |  | Ground Loop | HYDROTECH | WSH6072AM* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | No
212508390 |  | Ground Loop | HYDROTECH | WSH6072AN* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | No
212508399 |  | Ground Loop | AE Air | WSH6036AN* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | No
212508401 |  | Ground Loop | AE Air | WSH6042AN* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | No
212508403 |  | Ground Loop | AE Air | WSH6048AN* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | No
212508404 |  | Ground Loop | AE Air | WSH6072AM* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | No
212508405 |  | Ground Loop | AE Air | WSH6072AN* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | No
212509300 |  | Ground Loop | AE Air | WSH6060AM* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | No
212509301 |  | Ground Loop | AE Air | WSH6060AN* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | No
215811946 |  | Ground Loop | HYDROTECH | WSV6009D* |  | 9800 | 19 | 6800 | 3.7 | 0.81667 | No
215811947 |  | Ground Loop | AE Air | WSV6009D* |  | 9800 | 19 | 6800 | 3.7 | 0.81667 | No
215811948 |  | Ground Loop | HYDROTECH | WSV6012D* |  | 12500 | 19 | 9000 | 3.6 | 1.0417 | No
215811950 |  | Ground Loop | AE Air | WSV6012D* |  | 12500 | 19 | 9000 | 3.6 | 1.0417 | No
215811951 |  | Ground Loop | HYDROTECH | WSV6018D* |  | 18000 | 17.2 | 13000 | 3.6 | 1.5 | No
215811952 |  | Ground Loop | AE Air | WSV6018D* |  | 18000 | 17.2 | 13000 | 3.6 | 1.5 | No
215811953 |  | Ground Loop | HYDROTECH | WSV6024D* |  | 23000 | 18 | 17500 | 3.6 | 1.9167 | No
215811954 |  | Ground Loop | AE Air | WSV6024D* |  | 23000 | 18 | 17500 | 3.6 | 1.9167 | No
215811955 |  | Ground Loop | HYDROTECH | WSV6030D* |  | 28000 | 17.5 | 19900 | 3.6 | 2.3333 | No
215811957 |  | Ground Loop | AE Air | WSV6030D* |  | 28000 | 17.5 | 19900 | 3.6 | 2.3333 | No
215811958 |  | Ground Loop | HYDROTECH | WSV6036D* |  | 37000 | 18 | 28000 | 3.6 | 3.0833 | No
215811959 |  | Ground Loop | AE Air | WSV6036D* |  | 37000 | 18 | 28000 | 3.6 | 3.0833 | No
215811960 |  | Ground Loop | HYDROTECH | WSV6042D* |  | 42000 | 18 | 30000 | 3.6 | 3.5 | No
215811961 |  | Ground Loop | AE Air | WSV6042D* |  | 42000 | 18 | 30000 | 3.6 | 3.5 | No
215815841 |  | Ground Loop | HYDROTECH | WSV6060D* |  | 63000 | 18 | 42500 | 3.6 | 5.25 | No
215815842 |  | Ground Loop | AE Air | WSV6060D* |  | 63000 | 18 | 42500 | 3.6 | 5.25 | No
215815843 |  | Ground Loop | HYDROTECH | WSV6072D* |  | 73000 | 17.9 | 52000 | 3.6 | 6.0833 | No
215815844 |  | Ground Loop | AE Air | WSV6072D* |  | 73000 | 17.9 | 52000 | 3.6 | 6.0833 | No
207337509 |  | Ground Loop | GEOSTAR | 103H022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
207337510 |  | Ground Loop | GEOSTAR | 103H022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
207337511 |  | Ground Loop | GEOSTAR | 103H030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
207337512 |  | Ground Loop | GEOSTAR | 103H030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
207337513 |  | Ground Loop | GEOSTAR | 103J036**1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | No
207337514 |  | Ground Loop | GEOSTAR | 103J036**1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | No
207337515 |  | Ground Loop | GEOSTAR | 103J042**1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
207337516 |  | Ground Loop | GEOSTAR | 103J042**1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
207337517 |  | Ground Loop | GEOSTAR | 103H048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
207337518 |  | Ground Loop | GEOSTAR | 103H048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
207337521 |  | Ground Loop | GEOSTAR | 103H070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207337522 |  | Ground Loop | GEOSTAR | 103H070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207337481 |  | Ground Loop | GEOSTAR | 104J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207337482 |  | Ground Loop | GEOSTAR | 104J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207337483 |  | Ground Loop | GEOSTAR | 164J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207337484 |  | Ground Loop | GEOSTAR | 164J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207337485 |  | Ground Loop | GEOSTAR | 103J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337486 |  | Ground Loop | GEOSTAR | 103J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337487 |  | Ground Loop | GEOSTAR | 163J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337488 |  | Ground Loop | GEOSTAR | 163J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337489 |  | Ground Loop | GEOSTAR | 104H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337490 |  | Ground Loop | GEOSTAR | 104H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337491 |  | Ground Loop | GEOSTAR | 164H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337492 |  | Ground Loop | GEOSTAR | 164H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207337493 |  | Ground Loop | GEOSTAR | 103J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337494 |  | Ground Loop | GEOSTAR | 103J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337495 |  | Ground Loop | GEOSTAR | 163J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337496 |  | Ground Loop | GEOSTAR | 163J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337497 |  | Ground Loop | GEOSTAR | 104H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337498 |  | Ground Loop | GEOSTAR | 104H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337499 |  | Ground Loop | GEOSTAR | 164H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207337500 |  | Ground Loop | GEOSTAR | 164H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
215399878 |  | Ground Loop | DAIKIN | WSSV048K3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215399879 |  | Ground Loop | DAIKIN | WSSV048L3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215399882 |  | Ground Loop | DAIKIN | WSSV048K3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215399883 |  | Ground Loop | DAIKIN | WSSV048L3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217752689 |  | Ground Loop | DAIKIN | WSSH042J1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217752691 |  | Ground Loop | DAIKIN | WSSH042J1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
214841657 |  | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
214841658 |  | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
214841660 |  | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
214841662 |  | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
214841676 |  | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
214841678 |  | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
214841679 |  | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
214841680 |  | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
214841682 |  | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
214841684 |  | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
218471730 |  | Ground Loop | YORK | AD024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218471731 |  | Ground Loop | YORK | AD024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
217754499 |  | Ground Loop | DAIKIN | WSTH070E1*H*C |  | 75600 | 19.03 | 52200 | 3.66 | 6.3 | No
217754503 |  | Ground Loop | DAIKIN | WSTV024E1*H*C |  | 22400 | 17.99 | 17200 | 3.98 | 1.8667 | No
217754504 |  | Ground Loop | DAIKIN | WSTV024F1*H*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667 | No
217754507 |  | Ground Loop | DAIKIN | WSTV030E1*H*C |  | 32200 | 19.48 | 20800 | 3.78 | 2.6833 | No
217754508 |  | Ground Loop | DAIKIN | WSTV030F1*H*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833 | No
217754511 |  | Ground Loop | DAIKIN | WSTV036E1*H*C |  | 39100 | 21.12 | 25600 | 3.68 | 3.2583 | No
217754512 |  | Ground Loop | DAIKIN | WSTV036F1*H*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583 | No
217754515 |  | Ground Loop | DAIKIN | WSTV042E1*H*C |  | 44800 | 19.54 | 27600 | 3.74 | 3.7333 | No
217754516 |  | Ground Loop | DAIKIN | WSTV042F1*H*C |  | 44800 | 19.15 | 27600 | 3.66 | 3.7333 | No
217754519 |  | Ground Loop | DAIKIN | WSTV048E1*H*C |  | 52400 | 20.17 | 35200 | 3.9 | 4.3667 | No
217754520 |  | Ground Loop | DAIKIN | WSTV048F1*H*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667 | No
217754523 |  | Ground Loop | DAIKIN | WSTV060E1*H*C |  | 63100 | 19.6 | 46800 | 4.1 | 5.2583 | No
217754524 |  | Ground Loop | DAIKIN | WSTV060F1*H*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583 | No
8560916 |  | Ground Loop | GEOCOMFORT | GVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560917 |  | Ground Loop | HYDRON MODULE | HVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560918 |  | Ground Loop | TETCO | TVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560919 |  | Ground Loop | GEOCOMFORT | GVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560920 |  | Ground Loop | HYDRON MODULE | HVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560921 |  | Ground Loop | TETCO | TVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | No
8560930 |  | Ground Loop | GEOCOMFORT | GVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167 | Yes
8560931 |  | Ground Loop | HYDRON MODULE | HVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167 | Yes
8560932 |  | Ground Loop | TETCO | TVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167 | Yes
8560938 |  | Ground Loop | GEOCOMFORT | GVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | Yes
8560939 |  | Ground Loop | HYDRON MODULE | HVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | Yes
8560940 |  | Ground Loop | TETCO | TVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | Yes
8560941 |  | Ground Loop | GEOCOMFORT | GVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | No
8560942 |  | Ground Loop | HYDRON MODULE | HVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | No
8560943 |  | Ground Loop | TETCO | TVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333 | No
8560946 |  | Ground Loop | GEOCOMFORT | GVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | Yes
8560947 |  | Ground Loop | HYDRON MODULE | HVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | Yes
8560948 |  | Ground Loop | TETCO | TVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | Yes
8560949 |  | Ground Loop | GEOCOMFORT | GVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | No
8560950 |  | Ground Loop | HYDRON MODULE | HVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | No
8560951 |  | Ground Loop | TETCO | TVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | No
8077727 |  | Ground Loop | HYDRON MODULE | HYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077728 |  | Ground Loop | TETCO | TYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077729 |  | Ground Loop | GEOCOMFORT | GYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077730 |  | Ground Loop | HYDRON MODULE | HYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077731 |  | Ground Loop | TETCO | TYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
8077735 |  | Ground Loop | GEOCOMFORT | GYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | Yes
8077736 |  | Ground Loop | HYDRON MODULE | HYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | Yes
8077737 |  | Ground Loop | TETCO | TYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | Yes
8077738 |  | Ground Loop | GEOCOMFORT | GYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077739 |  | Ground Loop | HYDRON MODULE | HYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077740 |  | Ground Loop | TETCO | TYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077741 |  | Ground Loop | GEOCOMFORT | GYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077742 |  | Ground Loop | HYDRON MODULE | HYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8077743 |  | Ground Loop | TETCO | TYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917 | No
8233354 |  | Ground Loop | DAIKIN | W.CCW.2.072*F |  | 80100 | 17.1 | 58700 | 3.75 | 6.675 | No
8233365 |  | Ground Loop | DAIKIN | W.CCW.2.072*K |  | 80100 | 17.1 | 58700 | 3.75 | 6.675 | No
8332268 |  | Ground Loop | GEOCOMFORT | GYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
8332358 |  | Ground Loop | HYDRON MODULE | HYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
8332380 |  | Ground Loop | TETCO | TYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
8332431 |  | Ground Loop | GEOCOMFORT | GYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332452 |  | Ground Loop | HYDRON MODULE | HYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332472 |  | Ground Loop | TETCO | TYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332525 |  | Ground Loop | GEOCOMFORT | GYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332545 |  | Ground Loop | HYDRON MODULE | HYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8332563 |  | Ground Loop | TETCO | TYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | No
8560797 |  | Ground Loop | 5 SERIES | NSV/NSH060H1*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
8560805 |  | Ground Loop | 5 SERIES | NSV/NSH060H1*(1,4) |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
8560913 |  | Ground Loop | GEOCOMFORT | GVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | Yes
8560914 |  | Ground Loop | HYDRON MODULE | HVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | Yes
8560915 |  | Ground Loop | TETCO | TVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | Yes
203113888 |  | Ground Loop | GEOSTAR | 103J036**1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
203113890 |  | Ground Loop | GEOSTAR | 103J042**1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
203113892 |  | Ground Loop | GEOSTAR | 103J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
203113894 |  | Ground Loop | GEOSTAR | 104J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
203143108 |  | Ground Loop | GEOCOMFORT | GVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | Yes
203143111 |  | Ground Loop | GEOCOMFORT | GVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143114 |  | Ground Loop | GEOCOMFORT | GVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143119 |  | Ground Loop | GEOCOMFORT | GVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143124 |  | Ground Loop | HYDRON MODULE | HVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | Yes
203143129 |  | Ground Loop | HYDRON MODULE | HVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143133 |  | Ground Loop | HYDRON MODULE | HVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143138 |  | Ground Loop | HYDRON MODULE | HVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143143 |  | Ground Loop | TETCO | TVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | Yes
203143148 |  | Ground Loop | TETCO | TVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143153 |  | Ground Loop | TETCO | TVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143157 |  | Ground Loop | TETCO | TVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225 | No
203143746 |  | Ground Loop | GEOCOMFORT | GVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | Yes
203143749 |  | Ground Loop | GEOCOMFORT | GVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143752 |  | Ground Loop | GEOCOMFORT | GVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143764 |  | Ground Loop | HYDRON MODULE | HVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | Yes
203143767 |  | Ground Loop | HYDRON MODULE | HVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143770 |  | Ground Loop | HYDRON MODULE | HVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143781 |  | Ground Loop | TETCO | TVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | Yes
207657653 |  | Ground Loop | ClimateMaster | TSM30 D |  | 29000 | 17.6 | 22200 | 3.6 | 2.4167 | No
207657660 |  | Ground Loop | ClimateMaster | TSL15 A/C |  | 15400 | 17.7 | 11500 | 3.6 | 1.2833 | No
207657661 |  | Ground Loop | ClimateMaster | TSL15 D |  | 15400 | 19.2 | 11000 | 3.7 | 1.2833 | No
207657665 |  | Ground Loop | ClimateMaster | TSL24 D |  | 26500 | 19.4 | 18500 | 3.6 | 2.2083 | No
207657667 |  | Ground Loop | ClimateMaster | TSL30 D |  | 29500 | 18.4 | 21000 | 3.7 | 2.4583 | No
218158022 |  | Ground Loop | YORK | Y5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
218158023 |  | Ground Loop | YORK | Y5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
218158024 |  | Ground Loop | YORK | Y5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
218158025 |  | Ground Loop | YORK | Y5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
218158026 |  | Ground Loop | YORK | Y5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
218158027 |  | Ground Loop | YORK | Y5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
218158028 |  | Ground Loop | YORK | Y5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
218158029 |  | Ground Loop | YORK | Y5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
218158030 |  | Ground Loop | YORK | Y5SS024BD1 | Y5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
218158031 |  | Ground Loop | YORK | Y5SS036BD1 | Y5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
218158032 |  | Ground Loop | YORK | Y5SS048BD1 | Y5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
218158033 |  | Ground Loop | YORK | Y5SS060BD1 | Y5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
218158035 |  | Ground Loop | YORK | Y5SZ024BD1 | Y5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
218158036 |  | Ground Loop | YORK | Y5SZ036BD1 | Y5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
218158037 |  | Ground Loop | YORK | Y5SZ048BD1 | Y5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
218158038 |  | Ground Loop | YORK | Y5SZ060BD1 | Y5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
218158040 |  | Ground Loop | YORK | Y5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
218158041 |  | Ground Loop | YORK | Y5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
218158042 |  | Ground Loop | YORK | Y5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
218158043 |  | Ground Loop | YORK | Y5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
218158045 |  | Ground Loop | YORK | Y5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
218158046 |  | Ground Loop | YORK | Y5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
218158047 |  | Ground Loop | YORK | Y5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
218158048 |  | Ground Loop | YORK | Y5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
9910757 |  | Ground Loop | TETCO | TZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910758 |  | Ground Loop | GEOCOMFORT | GZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910759 |  | Ground Loop | HYDRON MODULE | HZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910760 |  | Ground Loop | TETCO | TZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
9910764 |  | Ground Loop | GEOCOMFORT | GZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | Yes
9910765 |  | Ground Loop | HYDRON MODULE | HZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | Yes
9910766 |  | Ground Loop | TETCO | TZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | Yes
9910767 |  | Ground Loop | GEOCOMFORT | GZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910768 |  | Ground Loop | HYDRON MODULE | HZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910769 |  | Ground Loop | TETCO | TZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910770 |  | Ground Loop | GEOCOMFORT | GZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910771 |  | Ground Loop | HYDRON MODULE | HZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910772 |  | Ground Loop | TETCO | TZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910773 |  | Ground Loop | GEOCOMFORT | GZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910774 |  | Ground Loop | HYDRON MODULE | HZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910775 |  | Ground Loop | TETCO | TZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417 | No
9910780 |  | Ground Loop | GEOCOMFORT | GZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | Yes
9910781 |  | Ground Loop | HYDRON MODULE | HZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | Yes
9910782 |  | Ground Loop | TETCO | TZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | Yes
9910783 |  | Ground Loop | GEOCOMFORT | GZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910784 |  | Ground Loop | HYDRON MODULE | HZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910785 |  | Ground Loop | TETCO | TZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910786 |  | Ground Loop | GEOCOMFORT | GZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910787 |  | Ground Loop | HYDRON MODULE | HZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
9910788 |  | Ground Loop | TETCO | TZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083 | No
10581121 |  | Ground Loop | GEOSTAR | 107H064**1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083 | No
3628414 |  | Ground Loop | WaterFurnace | USV/USH018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
3628415 |  | Ground Loop | WaterFurnace | USV/USH018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
3628416 |  | Ground Loop | WaterFurnace | USV/USH015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
3628417 |  | Ground Loop | WaterFurnace | USV/USH015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
217212097 |  | Ground Loop | FHP | CP070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212099 |  | Ground Loop | FHP | CP070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212102 |  | Ground Loop | BOSCH | RP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
217212103 |  | Ground Loop | BOSCH | RP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
217212105 |  | Ground Loop | BOSCH | RP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
217212106 |  | Ground Loop | BOSCH | RP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
217212107 |  | Ground Loop | BOSCH | RP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
217212108 |  | Ground Loop | BOSCH | RP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
217212109 |  | Ground Loop | BOSCH | RP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
217212111 |  | Ground Loop | BOSCH | RP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
217212112 |  | Ground Loop | BOSCH | RP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
217212113 |  | Ground Loop | BOSCH | RP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
217212114 |  | Ground Loop | BOSCH | RP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217212116 |  | Ground Loop | BOSCH | RP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217351071 |  | Ground Loop | BOSCH | CP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | No
217351072 |  | Ground Loop | BOSCH | CP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | No
218472180 |  | Ground Loop | YORK | AQ070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218472182 |  | Ground Loop | YORK | AQ070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218472198 |  | Ground Loop | YORK | AZ024-1CSC-*****A | CDM24B5XXS1A | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | No
218472199 |  | Ground Loop | YORK | AZ024-1CSN-*****A | CDM24B5XXS1A | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | No
218472201 |  | Ground Loop | YORK | AZ036-1CSN-*****A | CDM30B5XXS1A | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | No
218472202 |  | Ground Loop | YORK | AZ048-1CSC-*****A | CDM48C5XXS1A | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | No
218472203 |  | Ground Loop | YORK | AZ048-1CSN-*****A | CDM48C5XXS1A | 51600 | 17.8 | 38200 | 4.1 | 4.3 | No
218494303 |  | Ground Loop | ClimateMaster | SMS(S,M)15A*L |  | 14800 | 17.5 | 11000 | 3.6 | 1.2333 | No
218494304 |  | Ground Loop | ClimateMaster | SMT(S,M)15A*L |  | 15400 | 18.8 | 11000 | 3.7 | 1.2833 | No
214837742 |  | Ground Loop | CARRIER | 50H/VQP072***3C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837743 |  | Ground Loop | CARRIER | 50H/VQP072***5C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837744 |  | Ground Loop | CARRIER | 50H/VQP072***6C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837745 |  | Ground Loop | CARRIER | 50H/VQP096***3C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837746 |  | Ground Loop | CARRIER | 50H/VQP096***5C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837747 |  | Ground Loop | CARRIER | 50H/VQP096***6C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
216625508 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625509 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625510 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625511 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625512 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625513 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625514 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625515 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625516 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625517 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625518 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625519 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625520 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625521 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625522 |  | Ground Loop | GEOSTAR | G5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625523 |  | Ground Loop | GEOSTAR | G5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625524 |  | Ground Loop | GEOSTAR | G5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625525 |  | Ground Loop | GEOSTAR | G5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625526 |  | Ground Loop | GEOSTAR | G5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625527 |  | Ground Loop | GEOSTAR | G5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625528 |  | Ground Loop | GEOSTAR | G5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625529 |  | Ground Loop | GEOSTAR | G5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625530 |  | Ground Loop | GEOSTAR | G5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625531 |  | Ground Loop | GEOSTAR | G5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625532 |  | Ground Loop | GEOSTAR | G5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625533 |  | Ground Loop | GEOSTAR | G5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625534 |  | Ground Loop | GEOSTAR | G5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625535 |  | Ground Loop | GEOSTAR | G5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625542 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625543 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625750 |  | Ground Loop | GeoSmart Energy | S5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216625751 |  | Ground Loop | GeoSmart Energy | S5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216625752 |  | Ground Loop | GeoSmart Energy | S5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625753 |  | Ground Loop | GeoSmart Energy | S5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625754 |  | Ground Loop | GeoSmart Energy | S5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625755 |  | Ground Loop | GeoSmart Energy | S5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625756 |  | Ground Loop | GeoSmart Energy | S5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216625757 |  | Ground Loop | GeoSmart Energy | S5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216625758 |  | Ground Loop | GeoSmart Energy | S5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625759 |  | Ground Loop | GeoSmart Energy | S5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625760 |  | Ground Loop | GeoSmart Energy | S5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625761 |  | Ground Loop | GeoSmart Energy | S5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625762 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625763 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625764 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625765 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625766 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625767 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625768 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625769 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216625770 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625771 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625772 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625773 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218353322 |  | Ground Loop | SKYMARK | PQ070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353324 |  | Ground Loop | SKYMARK | PQ070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353349 |  | Ground Loop | JOHNSON CONTROLS | DD007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218353350 |  | Ground Loop | JOHNSON CONTROLS | DD007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218353351 |  | Ground Loop | JOHNSON CONTROLS | DD007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218353352 |  | Ground Loop | JOHNSON CONTROLS | DD007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218353353 |  | Ground Loop | JOHNSON CONTROLS | DD009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218353354 |  | Ground Loop | JOHNSON CONTROLS | DD009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
202667081 |  | Ground Loop | BOSCH-GEO | BP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
202679205 |  | Ground Loop | BOSCH-GEO | SM036-1CSC-*****B | SM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583 | Yes
202679208 |  | Ground Loop | BOSCH | SM036-1CSC-*****B | SM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583 | Yes
202729320 |  | Ground Loop | HEIL | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
202729321 |  | Ground Loop | ARCOAIRE | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729322 |  | Ground Loop | KEEPRITE | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729323 |  | Ground Loop | TEMPSTAR | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729324 |  | Ground Loop | COMFORTMAKER | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729325 |  | Ground Loop | DAY & NIGHT | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202729332 |  | Ground Loop | HEIL | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
202729333 |  | Ground Loop | ARCOAIRE | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202729334 |  | Ground Loop | KEEPRITE | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202729335 |  | Ground Loop | TEMPSTAR | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202729336 |  | Ground Loop | COMFORTMAKER | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202729337 |  | Ground Loop | DAY & NIGHT | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
202732300 |  | Ground Loop | BOSCH | BP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732301 |  | Ground Loop | CARRIER | GB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
202732302 |  | Ground Loop | BRYANT | GB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732303 |  | Ground Loop | ARCOAIRE | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
202732304 |  | Ground Loop | HEIL | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732305 |  | Ground Loop | KEEPRITE | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732306 |  | Ground Loop | TEMPSTAR | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732307 |  | Ground Loop | COMFORTMAKER | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732308 |  | Ground Loop | DAY & NIGHT | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | Yes
202732914 |  | Ground Loop | BOSCH-GEO | BP018-1HZ*******C |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
202732916 |  | Ground Loop | BOSCH | BP018-1HZ*******C |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732917 |  | Ground Loop | CARRIER | GB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
202732918 |  | Ground Loop | BRYANT | GB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732919 |  | Ground Loop | HEIL | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
202732920 |  | Ground Loop | ARCOAIRE | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732921 |  | Ground Loop | KEEPRITE | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732922 |  | Ground Loop | TEMPSTAR | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732923 |  | Ground Loop | COMFORTMAKER | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732924 |  | Ground Loop | DAY & NIGHT | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | Yes
202732937 |  | Ground Loop | TRANE | GWSC048H3 |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917 | No
202732938 |  | Ground Loop | TRANE | GWSC048H4 |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917 | No
202732939 |  | Ground Loop | TRANE | GWSC048HW |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917 | No
5646768 |  | Ground Loop | GEOCOMFORT | GCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646769 |  | Ground Loop | HYDRON MODULE | HCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646770 |  | Ground Loop | TETCO | TCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646771 |  | Ground Loop | GEOCOMFORT | GCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646772 |  | Ground Loop | HYDRON MODULE | HCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5646773 |  | Ground Loop | TETCO | TCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833 | No
5699505 |  | Ground Loop | TRANE | VSVE0421 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85 | No
5699525 |  | Ground Loop | TRANE | VSVE0422 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85 | No
5699526 |  | Ground Loop | TRANE | VSVE0424 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85 | No
5699527 |  | Ground Loop | TRANE | VSVE0601 |  | 64600 | 18.3 | 50000 | 4 | 5.3833 | No
5699534 |  | Ground Loop | TRANE | VSVE0602 |  | 64600 | 18.3 | 50000 | 4 | 5.3833 | No
5699535 |  | Ground Loop | TRANE | VSVE0604 |  | 64600 | 18.3 | 50000 | 4 | 5.3833 | No
5699628 |  | Ground Loop | TRANE | VSHE0241 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833 | No
5699631 |  | Ground Loop | TRANE | VSHE0242 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833 | No
5699633 |  | Ground Loop | TRANE | VSHE0244 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833 | No
5699634 |  | Ground Loop | TRANE | VSHE0331 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417 | No
5699635 |  | Ground Loop | TRANE | VSHE0332 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417 | No
5699637 |  | Ground Loop | TRANE | VSHE0334 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417 | No
5699639 |  | Ground Loop | TRANE | VSHE0421 |  | 44600 | 22 | 31500 | 4.5 | 3.7167 | No
5699644 |  | Ground Loop | TRANE | VSHE0422 |  | 44600 | 22 | 31500 | 4.5 | 3.7167 | No
5699650 |  | Ground Loop | TRANE | VSHE0424 |  | 44600 | 22 | 31500 | 4.5 | 3.7167 | No
5699652 |  | Ground Loop | TRANE | VSHE0501 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667 | No
5699653 |  | Ground Loop | TRANE | VSHE0502 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667 | No
5699654 |  | Ground Loop | TRANE | VSHE0504 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667 | No
5699655 |  | Ground Loop | TRANE | VSHE0601 |  | 63200 | 17 | 50400 | 3.8 | 5.2667 | No
5699656 |  | Ground Loop | TRANE | VSHE0602 |  | 63200 | 17 | 50400 | 3.8 | 5.2667 | No
5699657 |  | Ground Loop | TRANE | VSHE0604 |  | 63200 | 17 | 50400 | 3.8 | 5.2667 | No
205767538 |  | Ground Loop | ClimateMaster | TSM30 B |  | 29000 | 17.6 | 22200 | 3.6 | 2.4167 | No
205767541 |  | Ground Loop | ClimateMaster | TCH/V018A*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
214595688 |  | Ground Loop | AAON, Inc. | M2-007-2-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417 | No
214595689 |  | Ground Loop | AAON, Inc. | M2-007-2-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5 | No
214595690 |  | Ground Loop | AAON, Inc. | M2-007-3-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417 | No
214595691 |  | Ground Loop | AAON, Inc. | M2-007-3-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5 | No
214595692 |  | Ground Loop | AAON, Inc. | M2-007-4-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417 | No
214595693 |  | Ground Loop | AAON, Inc. | M2-007-4-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5 | No
214606639 |  | Ground Loop | Dandelion Geo | DP1G072V3A1000S |  | 70000 | 17.5 | 61000 | 4.3 | 5.8333 | Yes
214771921 |  | Ground Loop | TRANE | GEVK009A |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333 | No
214771923 |  | Ground Loop | TRANE | GEVK015A |  | 15900 | 18.2 | 12500 | 3.85 | 1.325 | No
214771924 |  | Ground Loop | TRANE | GEVK018A |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417 | No
214771925 |  | Ground Loop | TRANE | GEVK024A |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214771926 |  | Ground Loop | TRANE | GEVK030A |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214771929 |  | Ground Loop | TRANE | GEVK048A |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214771930 |  | Ground Loop | TRANE | GEVK060A |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214771931 |  | Ground Loop | TRANE | EXVK009A |  | 9000 | 21.2 | 6100 | 3.91 | 0.75 | No
214771932 |  | Ground Loop | TRANE | EXVK012A |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167 | No
214771933 |  | Ground Loop | TRANE | EXVK015A |  | 16200 | 18.7 | 11800 | 3.73 | 1.35 | No
214771934 |  | Ground Loop | TRANE | EXVK018A |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417 | No
214771935 |  | Ground Loop | TRANE | EXVK024A |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214771936 |  | Ground Loop | TRANE | EXVK030A |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214771937 |  | Ground Loop | TRANE | EXVK036A |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214771938 |  | Ground Loop | TRANE | EXVK042A |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214771939 |  | Ground Loop | TRANE | EXVK048A |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
216054482 |  | Ground Loop | GEOCOMFORT | GVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
216054483 |  | Ground Loop | GEOCOMFORT | GVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
216054484 |  | Ground Loop | GEOCOMFORT | GVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
216054485 |  | Ground Loop | GEOCOMFORT | GVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
216054486 |  | Ground Loop | GEOCOMFORT | GVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917 | Yes
216054487 |  | Ground Loop | GEOCOMFORT | GYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
216054488 |  | Ground Loop | GEOCOMFORT | GYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083 | Yes
216419863 |  | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
217754527 |  | Ground Loop | DAIKIN | WSTV070E1*H*C |  | 74600 | 19 | 56000 | 4 | 6.2167 | No
217754528 |  | Ground Loop | DAIKIN | WSTV070F1*H*C |  | 74600 | 18.62 | 56000 | 3.92 | 6.2167 | No
217754535 |  | Ground Loop | DAIKIN | WSMH024F1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
217754536 |  | Ground Loop | DAIKIN | WSMH024K1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
217754539 |  | Ground Loop | DAIKIN | WSMH024F1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
217754540 |  | Ground Loop | DAIKIN | WSMH024K1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
217754543 |  | Ground Loop | DAIKIN | WSMH024F1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
217754544 |  | Ground Loop | DAIKIN | WSMH024K1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
217754547 |  | Ground Loop | DAIKIN | WSMH030F1*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333 | No
217754548 |  | Ground Loop | DAIKIN | WSMH030K1*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333 | No
217754551 |  | Ground Loop | DAIKIN | WSMH030F1*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
217754552 |  | Ground Loop | DAIKIN | WSMH030K1*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
217754555 |  | Ground Loop | DAIKIN | WSMH030F1*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
217754556 |  | Ground Loop | DAIKIN | WSMH030K1*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
217754559 |  | Ground Loop | DAIKIN | WSMH036F1*G/J*P |  | 37800 | 18.18 | 30700 | 3.79 | 3.15 | No
217754560 |  | Ground Loop | DAIKIN | WSMH036K1*G/J*P |  | 37800 | 18.1 | 30700 | 3.79 | 3.15 | No
217754563 |  | Ground Loop | DAIKIN | WSMH036F1*G/J*T |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667 | No
217754564 |  | Ground Loop | DAIKIN | WSMH036K1*G/J*T |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667 | No
217754567 |  | Ground Loop | DAIKIN | WSMH036F1*G/J*C |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667 | No
217754568 |  | Ground Loop | DAIKIN | WSMH036K1*G/J*C |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667 | No
217754572 |  | Ground Loop | DAIKIN | WSMH042E1*G/J*P |  | 39900 | 17.5 | 32500 | 3.7 | 3.325 | No
217754573 |  | Ground Loop | DAIKIN | WSMH042F1*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325 | No
217754574 |  | Ground Loop | DAIKIN | WSMH042K1*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325 | No
217754578 |  | Ground Loop | DAIKIN | WSMH042E1*G/J*T |  | 40800 | 19.4 | 31600 | 3.8 | 3.4 | No
217754579 |  | Ground Loop | DAIKIN | WSMH042F1*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
217754580 |  | Ground Loop | DAIKIN | WSMH042K1*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
217754584 |  | Ground Loop | DAIKIN | WSMH042E1*G/J*C |  | 40800 | 19.4 | 31600 | 3.8 | 3.4 | No
217754585 |  | Ground Loop | DAIKIN | WSMH042F1*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
217754674 |  | Ground Loop | DAIKIN | WSMV042K1*G/J*C |  | 42600 | 19.67 | 29700 | 3.63 | 3.55 | No
217754678 |  | Ground Loop | DAIKIN | WSMV048F1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
217754679 |  | Ground Loop | DAIKIN | WSMV048K1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
217754680 |  | Ground Loop | DAIKIN | WSMV048L1*G/J*P |  | 49700 | 18.61 | 36700 | 3.64 | 4.1417 | No
217754683 |  | Ground Loop | DAIKIN | WSMV048F1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
217754684 |  | Ground Loop | DAIKIN | WSMV048K1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
217754687 |  | Ground Loop | DAIKIN | WSMV048F1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
217754688 |  | Ground Loop | DAIKIN | WSMV048K1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
217754697 |  | Ground Loop | DAIKIN | WSMV060F1*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
205652455 |  | Ground Loop | BOSCH-GEO | SM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917 | Yes
205652457 |  | Ground Loop | BOSCH-GEO | LM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083 | No
205652458 |  | Ground Loop | BOSCH-GEO | LM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417 | No
205652459 |  | Ground Loop | BOSCH-GEO | LM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917 | No
205652461 |  | Ground Loop | BOSCH | SM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083 | Yes
205652462 |  | Ground Loop | BOSCH | SM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417 | Yes
205652463 |  | Ground Loop | BOSCH | SM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917 | Yes
205652465 |  | Ground Loop | FHP | LM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083 | No
205652466 |  | Ground Loop | FHP | LM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417 | No
205652467 |  | Ground Loop | FHP | LM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917 | No
205737516 |  | Ground Loop | ICE AIR LLC | 8VSHPGE15** |  | 15000 | 17.5 | 10500 | 3.7 | 1.25 | No
205746250 |  | Ground Loop | ICE AIR LLC | 8VSHPGE09** |  | 11000 | 21.3 | 6500 | 3.64 | 0.91667 | No
205746251 |  | Ground Loop | ICE AIR LLC | 8VSHPGE12** |  | 13800 | 20.1 | 9000 | 3.7 | 1.15 | No
205746252 |  | Ground Loop | ICE AIR LLC | 8VSHPGE18** |  | 19500 | 18.7 | 13400 | 3.63 | 1.625 | No
205746253 |  | Ground Loop | ICE AIR LLC | 8VSHPGE24** |  | 24800 | 18.4 | 17000 | 3.66 | 2.0667 | No
205754414 |  | Ground Loop | ICE AIR LLC | 8VSHPGE30** |  | 30000 | 17.3 | 21900 | 3.6 | 2.5 | No
205754885 |  | Ground Loop | Johnson Controls | JCH/V015A*W/K B |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
205754886 |  | Ground Loop | SKYMARK | JCH/V015A*W/K C |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
205754889 |  | Ground Loop | Johnson Controls | JCH/V018A*W/K B |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
205754890 |  | Ground Loop | SKYMARK | JCH/V018A*W/K C |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
4651870 |  | Ground Loop | GeoSmart Energy | ZS023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651873 |  | Ground Loop | GEOSTAR | ZS023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651874 |  | Ground Loop | GeoSmart Energy | ZS023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651882 |  | Ground Loop | GEOSTAR | ZS042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651883 |  | Ground Loop | GeoSmart Energy | ZS042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651888 |  | Ground Loop | GEOSTAR | ZS042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651889 |  | Ground Loop | GeoSmart Energy | ZS042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651894 |  | Ground Loop | GEOSTAR | ZS042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651895 |  | Ground Loop | GeoSmart Energy | ZS042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
4651936 |  | Ground Loop | GEOSTAR | ZS048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651937 |  | Ground Loop | GeoSmart Energy | ZS048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651942 |  | Ground Loop | GeoSmart Energy | ZS048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651943 |  | Ground Loop | GEOSTAR | ZS048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651948 |  | Ground Loop | GEOSTAR | ZS048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651949 |  | Ground Loop | GeoSmart Energy | ZS048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
4651954 |  | Ground Loop | GEOSTAR | ZS060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651955 |  | Ground Loop | GeoSmart Energy | ZS060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651966 |  | Ground Loop | GEOSTAR | ZS060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651967 |  | Ground Loop | GeoSmart Energy | ZS060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
4651972 |  | Ground Loop | GEOSTAR | ZS070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651973 |  | Ground Loop | GeoSmart Energy | ZS070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651978 |  | Ground Loop | GEOSTAR | ZS070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651979 |  | Ground Loop | GeoSmart Energy | ZS070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651984 |  | Ground Loop | GEOSTAR | ZS070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
4651985 |  | Ground Loop | GeoSmart Energy | ZS070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083 | No
202434653 |  | Ground Loop | CARRIER | 50PCV024J/K*C5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434654 |  | Ground Loop | CARRIER | 50PCV024J/K*C6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434655 |  | Ground Loop | CARRIER | 50PCV024J/K*C4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434660 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434661 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434662 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434663 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434668 |  | Ground Loop | CARRIER | 50PCV024J/K*N3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434669 |  | Ground Loop | CARRIER | 50PCV024J/K*N5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434670 |  | Ground Loop | CARRIER | 50PCV024J/K*N6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434671 |  | Ground Loop | CARRIER | 50PCV024J/K*N4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434676 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434677 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207198729 |  | Ground Loop | FHP | QV024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198730 |  | Ground Loop | FHP | QV024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198733 |  | Ground Loop | FHP | QV024-2HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198734 |  | Ground Loop | FHP | QV024-2HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198737 |  | Ground Loop | FHP | QV024-3HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198738 |  | Ground Loop | FHP | QV024-3HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198741 |  | Ground Loop | FHP | QV024-4HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198742 |  | Ground Loop | FHP | QV024-4HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198745 |  | Ground Loop | FHP | QV030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198746 |  | Ground Loop | FHP | QV030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198747 |  | Ground Loop | FHP | QV030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198748 |  | Ground Loop | FHP | QV030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198749 |  | Ground Loop | FHP | QV030-2HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198750 |  | Ground Loop | FHP | QV030-2HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198751 |  | Ground Loop | FHP | QV030-2VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198752 |  | Ground Loop | FHP | QV030-2VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198753 |  | Ground Loop | FHP | QV030-3HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198754 |  | Ground Loop | FHP | QV030-3HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198755 |  | Ground Loop | FHP | QV030-3VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198756 |  | Ground Loop | FHP | QV030-3VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198757 |  | Ground Loop | FHP | QV030-4HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198758 |  | Ground Loop | FHP | QV030-4HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198759 |  | Ground Loop | FHP | QV030-4VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198760 |  | Ground Loop | FHP | QV030-4VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198761 |  | Ground Loop | FHP | QV036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198763 |  | Ground Loop | FHP | QV036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198764 |  | Ground Loop | FHP | QV036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198765 |  | Ground Loop | FHP | QV036-2HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198767 |  | Ground Loop | FHP | QV036-2VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198768 |  | Ground Loop | FHP | QV036-2VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198769 |  | Ground Loop | FHP | QV036-3HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198771 |  | Ground Loop | FHP | QV036-3VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198772 |  | Ground Loop | FHP | QV036-3VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198773 |  | Ground Loop | FHP | QV036-4HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198775 |  | Ground Loop | FHP | QV036-4VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198776 |  | Ground Loop | FHP | QV036-4VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
215268758 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268759 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268760 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268761 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268762 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
202330562 |  | Ground Loop | AAON, Inc. | M2-006-2-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7 | No
202330564 |  | Ground Loop | AAON, Inc. | M2-006-2-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725 | No
202330566 |  | Ground Loop | AAON, Inc. | M2-006-3-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7 | No
202330568 |  | Ground Loop | AAON, Inc. | M2-006-3-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725 | No
202330570 |  | Ground Loop | AAON, Inc. | M2-006-4-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7 | No
202330572 |  | Ground Loop | AAON, Inc. | M2-006-4-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725 | No
202350417 |  | Ground Loop | AAON, Inc. | RN-009-2-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425 | No
202350418 |  | Ground Loop | AAON, Inc. | RN-009-3-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425 | No
202350419 |  | Ground Loop | AAON, Inc. | RN-009-4-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425 | No
202350429 |  | Ground Loop | AAON, Inc. | RN-011-2-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417 | No
202350430 |  | Ground Loop | AAON, Inc. | RN-011-3-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417 | No
202350431 |  | Ground Loop | AAON, Inc. | RN-011-4-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417 | No
202350444 |  | Ground Loop | AAON, Inc. | M2-007-2-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7 | No
202350445 |  | Ground Loop | AAON, Inc. | M2-007-2-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583 | No
202350446 |  | Ground Loop | AAON, Inc. | M2-007-2-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417 | No
202350447 |  | Ground Loop | AAON, Inc. | M2-007-2-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5 | No
202350448 |  | Ground Loop | AAON, Inc. | M2-007-3-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7 | No
202350449 |  | Ground Loop | AAON, Inc. | M2-007-3-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583 | No
202350450 |  | Ground Loop | AAON, Inc. | M2-007-3-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417 | No
202350451 |  | Ground Loop | AAON, Inc. | M2-007-3-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5 | No
215224034 |  | Ground Loop | BOSCH | CF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224035 |  | Ground Loop | BOSCH | CF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224036 |  | Ground Loop | BOSCH | CF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224037 |  | Ground Loop | BOSCH | CF007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224038 |  | Ground Loop | BOSCH | CF007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224039 |  | Ground Loop | BOSCH | CF009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224040 |  | Ground Loop | BOSCH | CF009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224041 |  | Ground Loop | BOSCH | CF012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224042 |  | Ground Loop | BOSCH | CF012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224043 |  | Ground Loop | BOSCH | CF015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224044 |  | Ground Loop | BOSCH | CF015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224045 |  | Ground Loop | BOSCH | CF018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224046 |  | Ground Loop | BOSCH | CF018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224047 |  | Ground Loop | BOSCH | CF024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224048 |  | Ground Loop | BOSCH | CF024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224049 |  | Ground Loop | BOSCH | CF024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224050 |  | Ground Loop | BOSCH | CF024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
216772588 |  | Ground Loop | Enertech | EBT060* | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
216772590 |  | Ground Loop | Enertech | EVT060* |  | 60900 | 17.6 | 46700 | 3.8 | 5.075 | Yes
216772591 |  | Ground Loop | Enertech | EYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583 | Yes
216772592 |  | Ground Loop | Enertech | EZS015* |  | 14525 | 18.6 | 11200 | 3.9 | 1.2104 | Yes
216772593 |  | Ground Loop | Enertech | EZS017* |  | 17300 | 17 | 12825 | 3.61 | 1.4417 | Yes
216772594 |  | Ground Loop | Enertech | EZS018* |  | 20400 | 21.5 | 14100 | 3.86 | 1.7 | Yes
216772596 |  | Ground Loop | Enertech | EYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583 | Yes
204031812 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
213087558 |  | Ground Loop | WaterFurnace | NDS049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
213087559 |  | Ground Loop | WaterFurnace | NDS049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
213087562 |  | Ground Loop | WaterFurnace | NDS064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
213087563 |  | Ground Loop | WaterFurnace | NDS064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
213154439 |  | Ground Loop | GeoSmart Energy | GTS026*1******K | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
213154440 |  | Ground Loop | GeoSmart Energy | GTS026*1******K | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
213154441 |  | Ground Loop | GeoSmart Energy | GTS049*1******K | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
213154442 |  | Ground Loop | GeoSmart Energy | GTS049*1******K | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
213154445 |  | Ground Loop | GeoSmart Energy | GTS064*1******K | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
213154446 |  | Ground Loop | GeoSmart Energy | GTS064*1******K | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
213154447 |  | Ground Loop | GeoSmart Energy | GTS038*1******K | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
213154448 |  | Ground Loop | GeoSmart Energy | GTS038*1******K | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
213154454 |  | Ground Loop | GeoSmart Energy | GTZ026*1******K | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
213154455 |  | Ground Loop | GeoSmart Energy | GTZ026*1******K | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
213154456 |  | Ground Loop | GeoSmart Energy | GTZ038*1******K | SAH036* | 36000 | 19 | 27900 | 4 | 3 | Yes
213154457 |  | Ground Loop | GeoSmart Energy | GTZ038*1******K | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
213154458 |  | Ground Loop | GeoSmart Energy | GTZ049*1******K | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
213154459 |  | Ground Loop | GeoSmart Energy | GTZ049*1******K | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
213154460 |  | Ground Loop | GeoSmart Energy | GTZ064*1******K | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
213154461 |  | Ground Loop | GeoSmart Energy | GTZ064*1******K | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
213154465 |  | Ground Loop | GeoSmart Energy | GS018**1*1********L |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
213154466 |  | Ground Loop | GeoSmart Energy | GS022**1*1********L |  | 19200 | 18.7 | 15000 | 4 | 1.6 | Yes
213154467 |  | Ground Loop | GeoSmart Energy | GS030**1*1********L |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
206229682 |  | Ground Loop | CARRIER | 50PSH/V024**C3/CA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229683 |  | Ground Loop | CARRIER | 50PSH/V024**C4/DA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229684 |  | Ground Loop | CARRIER | 50PSH/V024**C5/EA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229685 |  | Ground Loop | CARRIER | 50PSH/V024**C6/FA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206342117 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*3 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
206342118 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*4 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
206342119 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*5 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
206342120 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
206342121 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
206342122 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
206342123 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*3 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
206342124 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*5 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
206342125 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*4 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
216625838 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625839 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625840 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625841 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625842 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625843 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625844 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625845 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625846 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625847 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
216625848 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625849 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625850 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625851 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625852 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625853 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625854 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625855 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625856 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625857 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216625858 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625859 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625860 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625861 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625862 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625863 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
216625864 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625865 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625866 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625867 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625868 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625869 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216625870 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625871 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625872 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625873 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625874 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625875 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625876 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625877 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625878 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625879 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625880 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216625881 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216687113 |  | Ground Loop | WaterFurnace | W5SS024BD1 | W5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216687114 |  | Ground Loop | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216687115 |  | Ground Loop | WaterFurnace | W5SS048BD1 | W5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216687116 |  | Ground Loop | WaterFurnace | W5SS060BD1 | W5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
203143785 |  | Ground Loop | TETCO | TVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203143790 |  | Ground Loop | TETCO | TVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167 | No
203238019 |  | Ground Loop | BOSCH-GEO | BP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203238919 |  | Ground Loop | BOSCH-GEO | SM024-1VT/CFN-*****A |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167 | Yes
203238923 |  | Ground Loop | BOSCH-GEO | SM024-1HZC-*****A |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | No
203238926 |  | Ground Loop | BOSCH-GEO | SM024-1HZN-*****A |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | No
203253412 |  | Ground Loop | BOSCH | BP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203253413 |  | Ground Loop | BOSCH | SM024-1HZC-*****A |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | Yes
203253414 |  | Ground Loop | BOSCH | SM024-1HZC-*****C |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | Yes
203253415 |  | Ground Loop | BOSCH | SM024-1HZN-*****A |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | Yes
203253416 |  | Ground Loop | BOSCH | SM024-1HZN-*****C |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | Yes
203254061 |  | Ground Loop | BOSCH-GEO | SM070-1VT*-*****C |  | 71500 | 17.3 | 56000 | 3.7 | 5.9583 | Yes
203254465 |  | Ground Loop | BOSCH | SM070-1VT*******C |  | 71500 | 17.3 | 56000 | 3.7 | 5.9583 | Yes
203254606 |  | Ground Loop | CARRIER | GB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203254607 |  | Ground Loop | BRYANT | GB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254608 |  | Ground Loop | ARCOAIRE | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203254609 |  | Ground Loop | HEIL | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254610 |  | Ground Loop | KEEPRITE | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254611 |  | Ground Loop | TEMPSTAR | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254612 |  | Ground Loop | COMFORTMAKER | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254614 |  | Ground Loop | DAY & NIGHT | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | Yes
203254620 |  | Ground Loop | BRYANT | GC024V/C**N***1*X1 |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167 | Yes
203254624 |  | Ground Loop | BRYANT | GC024H**C***1*X1 |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | Yes
203254626 |  | Ground Loop | BRYANT | GC024H**N***1*X1 |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | Yes
203254744 |  | Ground Loop | CARRIER | GC024V/C**N***1**1 |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167 | Yes
203254748 |  | Ground Loop | CARRIER | GC024H**C***1**1 |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167 | Yes
203254752 |  | Ground Loop | CARRIER | GC024H**N***1**1 |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167 | Yes
203260718 |  | Ground Loop | BOSCH-GEO | SM024-1VT/CFC******A |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167 | Yes
203260866 |  | Ground Loop | CARRIER | GC024V/C**C***1**1 + UI |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167 | Yes
203260867 |  | Ground Loop | BRYANT | GC024V/C**C***1*X1 + UI |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167 | Yes
216979817 |  | Ground Loop | CARRIER | GCA36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979818 |  | Ground Loop | BRYANT | GCA36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979819 |  | Ground Loop | CARRIER | GCA36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216979820 |  | Ground Loop | BRYANT | GCA36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979821 |  | Ground Loop | CARRIER | GCA48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979822 |  | Ground Loop | BRYANT | GCA48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979823 |  | Ground Loop | CARRIER | GCA48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979824 |  | Ground Loop | BRYANT | GCA48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979825 |  | Ground Loop | CARRIER | GCA60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979826 |  | Ground Loop | BRYANT | GCA60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979827 |  | Ground Loop | CARRIER | GCA60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979828 |  | Ground Loop | BRYANT | GCA60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979837 |  | Ground Loop | HEIL | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979838 |  | Ground Loop | ARCOAIRE | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979839 |  | Ground Loop | KEEPRITE | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979840 |  | Ground Loop | TEMPSTAR | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979841 |  | Ground Loop | COMFORTMAKER | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979842 |  | Ground Loop | DAY & NIGHT | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979843 |  | Ground Loop | HEIL | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979844 |  | Ground Loop | ARCOAIRE | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979845 |  | Ground Loop | KEEPRITE | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979846 |  | Ground Loop | TEMPSTAR | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979847 |  | Ground Loop | COMFORTMAKER | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979848 |  | Ground Loop | DAY & NIGHT | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979849 |  | Ground Loop | HEIL | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979850 |  | Ground Loop | ARCOAIRE | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979851 |  | Ground Loop | KEEPRITE | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979852 |  | Ground Loop | TEMPSTAR | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979853 |  | Ground Loop | COMFORTMAKER | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979854 |  | Ground Loop | DAY & NIGHT | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979855 |  | Ground Loop | HEIL | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979856 |  | Ground Loop | ARCOAIRE | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979857 |  | Ground Loop | KEEPRITE | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979858 |  | Ground Loop | TEMPSTAR | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979859 |  | Ground Loop | COMFORTMAKER | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979860 |  | Ground Loop | DAY & NIGHT | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979861 |  | Ground Loop | HEIL | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979862 |  | Ground Loop | ARCOAIRE | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979863 |  | Ground Loop | KEEPRITE | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979864 |  | Ground Loop | TEMPSTAR | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979865 |  | Ground Loop | COMFORTMAKER | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216979866 |  | Ground Loop | DAY & NIGHT | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
9100368 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100370 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100371 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100373 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100374 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
9100377 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100378 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100380 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
9100381 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
205767548 |  | Ground Loop | ClimateMaster | TRH/V018A*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
205767559 |  | Ground Loop | ClimateMaster | TZV/H060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
205767566 |  | Ground Loop | ClimateMaster | TSL15 A |  | 15400 | 17.7 | 11500 | 3.6 | 1.2833 | No
205767567 |  | Ground Loop | ClimateMaster | TSL15 B |  | 15400 | 19.2 | 11000 | 3.7 | 1.2833 | No
205767571 |  | Ground Loop | ClimateMaster | TSL24 B |  | 26500 | 19.4 | 18500 | 3.6 | 2.2083 | No
205767573 |  | Ground Loop | ClimateMaster | TSL30 B |  | 29500 | 18.4 | 21000 | 3.7 | 2.4583 | No
205767582 |  | Ground Loop | ClimateMaster | TES/P038B | TAH038C | 37700 | 17.8 | 26200 | 3.8 | 3.1417 | Yes
205767586 |  | Ground Loop | ClimateMaster | TES/P026B | TAH026C***A* | 24700 | 17.7 | 18800 | 3.6 | 2.0583 | Yes
205767587 |  | Ground Loop | ClimateMaster | TES/P026B | TAH026C***B* | 25800 | 18.3 | 18700 | 3.8 | 2.15 | Yes
205767588 |  | Ground Loop | ClimateMaster | TES/P026B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
205767589 |  | Ground Loop | ClimateMaster | TES/P026B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
205767592 |  | Ground Loop | ClimateMaster | TRE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175 | No
214771940 |  | Ground Loop | TRANE | EXVK060A |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214771941 |  | Ground Loop | TRANE | EXVK070A |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214771943 |  | Ground Loop | TRANE | GEHK009A |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333 | No
214771945 |  | Ground Loop | TRANE | GEHK015A |  | 15900 | 18.2 | 12500 | 3.85 | 1.325 | No
214771946 |  | Ground Loop | TRANE | GEHK018A |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417 | No
217735435 |  | Ground Loop | DAIKIN | WSTH024J1*H*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917 | No
217735437 |  | Ground Loop | DAIKIN | WSTH030J1*H*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725 | No
217735439 |  | Ground Loop | DAIKIN | WSTH036J1*H*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225 | No
217735441 |  | Ground Loop | DAIKIN | WSTV024J1*H*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667 | No
217735443 |  | Ground Loop | DAIKIN | WSTV030J1*H*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833 | No
217735445 |  | Ground Loop | DAIKIN | WSTV036J1*H*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583 | No
7421973 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421974 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
7421975 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421976 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421977 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
7421980 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421989 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
7421999 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
7422020 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422043 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422058 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422072 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422083 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422093 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
7422134 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422147 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422187 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422202 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422225 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422234 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
7422268 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422280 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422290 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422299 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422309 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7422322 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
7423168 |  | Ground Loop | WaterFurnace | NBV/NBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7423169 |  | Ground Loop | GEOSTAR | GBV/GBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7423171 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
7487652 |  | Ground Loop | GEOCOMFORT | GYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | Yes
7487653 |  | Ground Loop | HYDRON MODULE | HYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | Yes
7487654 |  | Ground Loop | TETCO | TYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | Yes
7487655 |  | Ground Loop | TETCO | TYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487656 |  | Ground Loop | GEOCOMFORT | GYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487657 |  | Ground Loop | HYDRON MODULE | HYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487658 |  | Ground Loop | HYDRON MODULE | HYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487659 |  | Ground Loop | GEOCOMFORT | GYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487660 |  | Ground Loop | TETCO | TYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333 | No
7487661 |  | Ground Loop | GEOCOMFORT | GYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | Yes
7487662 |  | Ground Loop | HYDRON MODULE | HYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | Yes
7487663 |  | Ground Loop | TETCO | TYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | Yes
7487664 |  | Ground Loop | TETCO | TYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487665 |  | Ground Loop | HYDRON MODULE | HYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487666 |  | Ground Loop | GEOCOMFORT | GYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487667 |  | Ground Loop | GEOCOMFORT | GYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7487668 |  | Ground Loop | HYDRON MODULE | HYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
217351789 |  | Ground Loop | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351790 |  | Ground Loop | ARCOAIRE | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351792 |  | Ground Loop | ARCOAIRE | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351793 |  | Ground Loop | ARCOAIRE | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351795 |  | Ground Loop | ARCOAIRE | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351796 |  | Ground Loop | ARCOAIRE | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351797 |  | Ground Loop | ARCOAIRE | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351798 |  | Ground Loop | ARCOAIRE | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351799 |  | Ground Loop | ARCOAIRE | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351801 |  | Ground Loop | ARCOAIRE | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351802 |  | Ground Loop | ARCOAIRE | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351803 |  | Ground Loop | ARCOAIRE | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351811 |  | Ground Loop | COMFORTMAKER | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351812 |  | Ground Loop | COMFORTMAKER | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351815 |  | Ground Loop | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351816 |  | Ground Loop | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351817 |  | Ground Loop | COMFORTMAKER | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351819 |  | Ground Loop | COMFORTMAKER | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351820 |  | Ground Loop | COMFORTMAKER | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351822 |  | Ground Loop | COMFORTMAKER | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351823 |  | Ground Loop | COMFORTMAKER | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351824 |  | Ground Loop | COMFORTMAKER | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351825 |  | Ground Loop | COMFORTMAKER | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351826 |  | Ground Loop | COMFORTMAKER | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351828 |  | Ground Loop | COMFORTMAKER | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351829 |  | Ground Loop | COMFORTMAKER | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351830 |  | Ground Loop | COMFORTMAKER | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351838 |  | Ground Loop | DAY & NIGHT | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351839 |  | Ground Loop | DAY & NIGHT | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351842 |  | Ground Loop | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
6501912 |  | Ground Loop | GEOSTAR | GBV/GBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501913 |  | Ground Loop | GEOSTAR | GBV/GBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501914 |  | Ground Loop | GEOSTAR | GBV/GBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501915 |  | Ground Loop | GEOSTAR | GBV/GBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501916 |  | Ground Loop | GEOSTAR | GBV/GBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501917 |  | Ground Loop | GEOSTAR | GBV/GBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
6501918 |  | Ground Loop | GEOSTAR | GBV/GBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
6501919 |  | Ground Loop | GEOSTAR | GBV/GBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501920 |  | Ground Loop | GEOSTAR | GBV/GBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501921 |  | Ground Loop | GEOSTAR | GBV/GBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
6501922 |  | Ground Loop | GEOSTAR | GBV/GBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501923 |  | Ground Loop | GEOSTAR | GBV/GBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501924 |  | Ground Loop | GEOSTAR | GBV/GBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
6501925 |  | Ground Loop | GEOSTAR | GBV/GBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501926 |  | Ground Loop | GEOSTAR | GBV/GBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501927 |  | Ground Loop | GEOSTAR | GBV/GBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
6501928 |  | Ground Loop | GEOSTAR | GBV/GBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501929 |  | Ground Loop | GEOSTAR | GBV/GBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
6501930 |  | Ground Loop | GEOSTAR | GBV/GBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
206726827 |  | Ground Loop | HYDRON MODULE | HBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
206726828 |  | Ground Loop | TETCO | TBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | Yes
206726829 |  | Ground Loop | TETCO | TBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
206726830 |  | Ground Loop | GEOCOMFORT | GBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
206726831 |  | Ground Loop | GEOCOMFORT | GBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | No
206726832 |  | Ground Loop | HYDRON MODULE | HBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
206726833 |  | Ground Loop | HYDRON MODULE | HBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | No
206726834 |  | Ground Loop | TETCO | TBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | No
206726835 |  | Ground Loop | TETCO | TBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | No
206726836 |  | Ground Loop | GEOCOMFORT | GBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | Yes
206726837 |  | Ground Loop | GEOCOMFORT | GBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | Yes
206726838 |  | Ground Loop | HYDRON MODULE | HBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | Yes
206726839 |  | Ground Loop | HYDRON MODULE | HBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | Yes
206726840 |  | Ground Loop | TETCO | TBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | Yes
206726841 |  | Ground Loop | TETCO | TBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | Yes
206726842 |  | Ground Loop | GEOCOMFORT | GBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
206726843 |  | Ground Loop | GEOCOMFORT | GBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | No
206726844 |  | Ground Loop | HYDRON MODULE | HBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
206726845 |  | Ground Loop | HYDRON MODULE | HBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | No
206726846 |  | Ground Loop | TETCO | TBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275 | No
206726847 |  | Ground Loop | TETCO | TBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917 | No
206726848 |  | Ground Loop | GEOCOMFORT | GBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | Yes
206726849 |  | Ground Loop | HYDRON MODULE | HBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | Yes
214841698 |  | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
214841700 |  | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
214841701 |  | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | Yes
214841705 |  | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | Yes
214841706 |  | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | Yes
214841707 |  | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | No
214841711 |  | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | No
214841712 |  | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | No
214844588 |  | Ground Loop | WaterFurnace | W7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083 | Yes
214844645 |  | Ground Loop | WaterFurnace | W7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833 | Yes
214844646 |  | Ground Loop | WaterFurnace | W7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75 | Yes
215223494 |  | Ground Loop | WaterFurnace | V5AV084*D4**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
9910545 |  | Ground Loop | TETCO | TZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | No
9910548 |  | Ground Loop | GEOCOMFORT | GZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | Yes
9910549 |  | Ground Loop | HYDRON MODULE | HZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | Yes
9910550 |  | Ground Loop | TETCO | TZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | Yes
9910551 |  | Ground Loop | GEOCOMFORT | GZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910552 |  | Ground Loop | HYDRON MODULE | HZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910553 |  | Ground Loop | TETCO | TZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910554 |  | Ground Loop | GEOCOMFORT | GZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910555 |  | Ground Loop | HYDRON MODULE | HZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910556 |  | Ground Loop | TETCO | TZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910557 |  | Ground Loop | GEOCOMFORT | GZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910558 |  | Ground Loop | HYDRON MODULE | HZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910559 |  | Ground Loop | TETCO | TZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175 | No
9910564 |  | Ground Loop | GEOCOMFORT | GZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | Yes
9910565 |  | Ground Loop | HYDRON MODULE | HZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | Yes
9910566 |  | Ground Loop | TETCO | TZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | Yes
9910567 |  | Ground Loop | GEOCOMFORT | GZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
205788285 |  | Ground Loop | Johnson Controls | JSH/V/D036C*K B |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833 | No
205788286 |  | Ground Loop | SKYMARK | JSH/V/D036C*K C |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833 | No
205788287 |  | Ground Loop | Johnson Controls | JSH/V/D042C B |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417 | No
205788288 |  | Ground Loop | SKYMARK | JSH/V/D042C C |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417 | No
205788289 |  | Ground Loop | Johnson Controls | JSH/V/D042C*K B |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917 | Yes
205788290 |  | Ground Loop | SKYMARK | JSH/V/D042C*K C |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917 | Yes
205788293 |  | Ground Loop | Johnson Controls | JSH/V/D060C B |  | 63900 | 17.2 | 46900 | 3.7 | 5.325 | No
205788294 |  | Ground Loop | SKYMARK | JSH/V/D060C C |  | 63900 | 17.2 | 46900 | 3.7 | 5.325 | No
205823049 |  | Ground Loop | OMEGA HEAT PUMP | VSHP050G |  | 15000 | 18.5 | 10600 | 3.7 | 1.25 | No
205823050 |  | Ground Loop | OMEGA HEAT PUMP | VSHP060G |  | 18200 | 17.3 | 14000 | 3.6 | 1.5167 | No
205901397 |  | Ground Loop | DUAL AIR | CFX049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833 | Yes
205901398 |  | Ground Loop | MIAMI HEAT PUMP | HPX049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833 | Yes
205961529 |  | Ground Loop | Johnson Controls | JRE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175 | No
214772142 |  | Ground Loop | TRANE | DXHK036A |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772143 |  | Ground Loop | TRANE | DXHK048A |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772144 |  | Ground Loop | TRANE | DXHK060A |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772145 |  | Ground Loop | TRANE | DXHK070A |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772146 |  | Ground Loop | TRANE | DXVK024B |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772147 |  | Ground Loop | TRANE | DXVK0244 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772148 |  | Ground Loop | TRANE | DXVK036B |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
213502579 |  | Ground Loop | DAIKIN | WSCH048E1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
213502580 |  | Ground Loop | DAIKIN | WSCH048E1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
213502581 |  | Ground Loop | DAIKIN | WSCH048E1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
213614501 |  | Ground Loop | DAIKIN | WSCH015A1*G/J*T |  | 15600 | 19 | 11900 | 3.6 | 1.3 | No
213614502 |  | Ground Loop | DAIKIN | WSCH015A1*G/J*C |  | 15600 | 19 | 11900 | 3.6 | 1.3 | No
213614506 |  | Ground Loop | DAIKIN | WSCH015J1*G/J*P |  | 15500 | 18 | 11900 | 3.6 | 1.2917 | No
213614507 |  | Ground Loop | DAIKIN | WSCH015J1*G/J*T |  | 15500 | 18.7 | 12000 | 3.8 | 1.2917 | No
213614508 |  | Ground Loop | DAIKIN | WSCH015J1*G/J*C |  | 15500 | 18.7 | 12000 | 3.8 | 1.2917 | No
215837601 |  | Ground Loop | DAIKIN | WSCH048F3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837603 |  | Ground Loop | DAIKIN | WSCH048K3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837604 |  | Ground Loop | DAIKIN | WSCH048L3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837610 |  | Ground Loop | DAIKIN | WSCH048F3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837611 |  | Ground Loop | DAIKIN | WSCH048K3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215837613 |  | Ground Loop | DAIKIN | WSCH048L3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
7421971 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
7421972 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
200083642 |  | Ground Loop | COMFORT-AIRE | HZV/H/D036B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | Yes
200083643 |  | Ground Loop | CENTURY | HZV/H/D036B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | Yes
200083644 |  | Ground Loop | COMFORT-AIRE | HZV/H/D024B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | Yes
200083645 |  | Ground Loop | CENTURY | HZV/H/D024B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | Yes
200083646 |  | Ground Loop | COMFORT-AIRE | HZV/H/D048B |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | Yes
200083647 |  | Ground Loop | CENTURY | HZV/H/D048B |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | Yes
200083648 |  | Ground Loop | COMFORT-AIRE | HZV/H/D060B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | Yes
200083649 |  | Ground Loop | CENTURY | HZV/H/D060B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | Yes
200083684 |  | Ground Loop | COMFORT-AIRE | HZS024B | WDG024**A-*B | 24700 | 17.7 | 18800 | 3.6 | 2.0583 | Yes
200083685 |  | Ground Loop | CENTURY | HZS024B | WDG024**A-*B | 24700 | 17.7 | 18800 | 3.6 | 2.0583 | Yes
200083686 |  | Ground Loop | COMFORT-AIRE | HZS024B | WDG024**B-*B | 25800 | 18.3 | 18700 | 3.8 | 2.15 | Yes
200083687 |  | Ground Loop | CENTURY | HZS024B | WDG024**B-*B | 25800 | 18.3 | 18700 | 3.8 | 2.15 | Yes
200083688 |  | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*A-B | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
200083689 |  | Ground Loop | CENTURY | HZS024B | MWG24*A-B | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
200083690 |  | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*C-B | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
200083691 |  | Ground Loop | CENTURY | HZS024B | MWG24*C-B | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
200083692 |  | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*B-B | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
200083693 |  | Ground Loop | CENTURY | HZS024B | MWG24*B-B | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
200083694 |  | Ground Loop | COMFORT-AIRE | HZS036B | MWG36**-B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | No
200083695 |  | Ground Loop | CENTURY | HZS036B | MWG36**-B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
200083696 |  | Ground Loop | COMFORT-AIRE | HZS036B | WDG036***-*B | 37700 | 17.8 | 26200 | 3.8 | 3.1417 | Yes
200083697 |  | Ground Loop | CENTURY | HZS036B | WDG036***-*B | 37700 | 17.8 | 26200 | 3.8 | 3.1417 | Yes
200083804 |  | Ground Loop | NORTHERN HEAT PUMP | RA-VE-061-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15 | No
200083805 |  | Ground Loop | NORTHSTAR SERIES | RA-VE-061-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15 | No
206346929 |  | Ground Loop | DAIKIN | WVFW*024*K***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
206346930 |  | Ground Loop | DAIKIN | WVFW*030*K***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
206346937 |  | Ground Loop | DAIKIN | WCCW*019*E***14* |  | 20600 | 19 | 14000 | 3.7 | 1.7167 | No
206346938 |  | Ground Loop | DAIKIN | WCCW*019*J***14* |  | 20600 | 19 | 14000 | 3.7 | 1.7167 | No
206346939 |  | Ground Loop | DAIKIN | WCCW*024*E***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
206346940 |  | Ground Loop | DAIKIN | WCCW*024*F***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
206346941 |  | Ground Loop | DAIKIN | WCCW*024*J***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
206346942 |  | Ground Loop | DAIKIN | WCCW*024*K***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
206346943 |  | Ground Loop | DAIKIN | WVFW*019*E***14 |  | 19700 | 19 | 13400 | 3.7 | 1.6417 | No
206346944 |  | Ground Loop | DAIKIN | WVFW*019*J***14 |  | 19700 | 19 | 13400 | 3.7 | 1.6417 | No
218338487 |  | Ground Loop | YORK | Y5AV084*D5**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
218352925 |  | Ground Loop | SKYMARK | PD024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218352926 |  | Ground Loop | SKYMARK | PD024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
10346259 |  | Ground Loop | GEOCOMFORT | GZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346260 |  | Ground Loop | HYDRON MODULE | HZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346261 |  | Ground Loop | TETCO | TZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10384616 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ070H1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | Yes
10435614 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10435615 |  | Ground Loop | GEOSTAR | 103H070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | Yes
10435616 |  | Ground Loop | GeoSmart Energy | GSZ070*1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | Yes
216625774 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625775 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625776 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625777 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625778 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625779 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625780 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625781 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625782 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625783 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625784 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625785 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625786 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625787 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625788 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625789 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625790 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625791 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625792 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625793 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625794 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625795 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625796 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625797 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625798 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625799 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625800 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625801 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625802 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625803 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625804 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625805 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625806 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625807 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625808 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625809 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625810 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625811 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625812 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625813 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625814 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625815 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625816 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625817 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625818 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625819 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625820 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625821 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625822 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625823 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
207312016 |  | Ground Loop | WaterFurnace | SDV049J1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | Yes
207312018 |  | Ground Loop | WaterFurnace | SDV072J1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | Yes
207312019 |  | Ground Loop | WaterFurnace | SDV038K1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3 | Yes
207312171 |  | Ground Loop | WaterFurnace | NDV/NDH026J1*(1,4) |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207312172 |  | Ground Loop | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207312173 |  | Ground Loop | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207312174 |  | Ground Loop | WaterFurnace | NDV/NDH072J1*(1,4) |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207312176 |  | Ground Loop | WaterFurnace | NDV/NDH064K1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207312224 |  | Ground Loop | WaterFurnace | NSV/NSH018J1*(1,4) |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
207312225 |  | Ground Loop | WaterFurnace | NSV/NSH030J1*(1,4) |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
207312226 |  | Ground Loop | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | Yes
207312227 |  | Ground Loop | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
207312228 |  | Ground Loop | WaterFurnace | NSV/NSH048K1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
207312229 |  | Ground Loop | WaterFurnace | NSV/NSH060K1*(1,4)* |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
207312230 |  | Ground Loop | WaterFurnace | NSV/NSH070J1*(1,4) |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
207312265 |  | Ground Loop | WaterFurnace | NSV/NSH030J1*(0,3) |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | Yes
207312266 |  | Ground Loop | WaterFurnace | NSV/NSH036K1*(0,3) |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | Yes
207312269 |  | Ground Loop | WaterFurnace | NSV/NSH060K1*0* |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | Yes
207312271 |  | Ground Loop | WaterFurnace | NSV/NSH022J1*(1,4) |  | 19200 | 18.7 | 15000 | 4 | 1.6 | Yes
213502525 |  | Ground Loop | DAIKIN | WSMH015A1*G/J*P |  | 16000 | 20.1 | 12100 | 4 | 1.3333 | No
213502526 |  | Ground Loop | DAIKIN | WSMH015A1*G/J*T |  | 16300 | 21.1 | 11800 | 4.1 | 1.3583 | No
213502527 |  | Ground Loop | DAIKIN | WSMH015A1*G/J*C |  | 16300 | 21.1 | 11800 | 4.1 | 1.3583 | No
213502531 |  | Ground Loop | DAIKIN | WSMH015E1*G/J*P |  | 16000 | 20.1 | 12300 | 4 | 1.3333 | No
213502532 |  | Ground Loop | DAIKIN | WSMH015E1*G/J*T |  | 16300 | 21.1 | 12000 | 4.1 | 1.3583 | No
213502533 |  | Ground Loop | DAIKIN | WSMH015E1*G/J*C |  | 16300 | 21.1 | 12000 | 4.1 | 1.3583 | No
213502537 |  | Ground Loop | DAIKIN | WSMH015J1*G/J*P |  | 16000 | 18.9 | 12300 | 3.9 | 1.3333 | No
213502538 |  | Ground Loop | DAIKIN | WSMH015J1*G/J*T |  | 16300 | 19.9 | 12000 | 4 | 1.3583 | No
213502539 |  | Ground Loop | DAIKIN | WSMH015J1*G/J*C |  | 16300 | 19.9 | 12000 | 4 | 1.3583 | No
213502543 |  | Ground Loop | DAIKIN | WSMH019E1*G/J*P |  | 20500 | 18.8 | 15600 | 3.8 | 1.7083 | No
213502544 |  | Ground Loop | DAIKIN | WSMH019E1*G/J*T |  | 20700 | 19.5 | 15300 | 3.9 | 1.725 | No
213502545 |  | Ground Loop | DAIKIN | WSMH019E1*G/J*C |  | 20700 | 19.5 | 15300 | 3.9 | 1.725 | No
213502549 |  | Ground Loop | DAIKIN | WSMH019J1*G/J*P |  | 20500 | 18.8 | 15600 | 3.7 | 1.7083 | No
213502550 |  | Ground Loop | DAIKIN | WSMH019J1*G/J*T |  | 20700 | 19.5 | 15300 | 3.8 | 1.725 | No
213502551 |  | Ground Loop | DAIKIN | WSMH019J1*G/J*C |  | 20700 | 19.5 | 15300 | 3.8 | 1.725 | No
213502555 |  | Ground Loop | DAIKIN | WSMH024E1*G/J*P |  | 25600 | 19.2 | 18400 | 3.9 | 2.1333 | No
213502556 |  | Ground Loop | DAIKIN | WSMH024E1*G/J*T |  | 25800 | 20.5 | 18200 | 3.9 | 2.15 | No
213502557 |  | Ground Loop | DAIKIN | WSMH024E1*G/J*C |  | 25800 | 20.5 | 18200 | 3.9 | 2.15 | No
213502561 |  | Ground Loop | DAIKIN | WSMH030E1*G/J*P |  | 29200 | 19 | 22200 | 3.8 | 2.4333 | No
206438733 |  | Ground Loop | BOSCH | EP015-2HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438734 |  | Ground Loop | BOSCH | EP030-1HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438735 |  | Ground Loop | BOSCH | EP030-2HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438736 |  | Ground Loop | BOSCH | EP030-3HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438737 |  | Ground Loop | BOSCH | EP030-4HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438738 |  | Ground Loop | BOSCH | EP060-3HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438739 |  | Ground Loop | BOSCH | EP060-4HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438740 |  | Ground Loop | BOSCH | EP070-3HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438741 |  | Ground Loop | BOSCH | EP070-4HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
9011292 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
9032648 |  | Ground Loop | HYDROTECH | HRCX18*-6 |  | 18000 | 17.1 | 13000 | 3.6 | 1.5 | Yes
9033424 |  | Ground Loop | HYDROTECH | HRCX09*-6 |  | 10000 | 19 | 6800 | 3.6 | 0.83333 | Yes
9033758 |  | Ground Loop | HYDROTECH | HRCX24*-6 |  | 24000 | 19 | 17000 | 3.6 | 2 | Yes
9033759 |  | Ground Loop | HYDROTECH | HRCX12*-6 |  | 11800 | 18 | 8000 | 3.6 | 0.98333 | Yes
9035993 |  | Ground Loop | GEOCOMFORT | GZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | Yes
9035994 |  | Ground Loop | HYDRON MODULE | HZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | Yes
205767473 |  | Ground Loop | ClimateMaster | TEV/H/D026B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | Yes
205767474 |  | Ground Loop | ClimateMaster | TEV/H/D038B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | Yes
205767475 |  | Ground Loop | ClimateMaster | TEV/H/D049B |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | Yes
205767476 |  | Ground Loop | ClimateMaster | TEV/H/D064B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | Yes
205767489 |  | Ground Loop | ClimateMaster | TSH/V/D018B |  | 19500 | 18.4 | 14500 | 3.6 | 1.625 | No
215400191 |  | Ground Loop | DAIKIN | WSSV030K3*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
215400194 |  | Ground Loop | DAIKIN | WSSV030J1*H*C |  | 30200 | 20.49 | 20700 | 3.83 | 2.5167 | No
215400195 |  | Ground Loop | DAIKIN | WSSV030K3*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
215400198 |  | Ground Loop | DAIKIN | WSSV036J1*H*T |  | 40500 | 20.65 | 27600 | 3.84 | 3.375 | No
215400199 |  | Ground Loop | DAIKIN | WSSV036K3*H*T |  | 40500 | 21.09 | 27600 | 3.83 | 3.375 | No
215400202 |  | Ground Loop | DAIKIN | WSSV036J1*H*C |  | 40500 | 20.65 | 27600 | 3.84 | 3.375 | No
215400203 |  | Ground Loop | DAIKIN | WSSV036K3*H*C |  | 40500 | 21.09 | 27600 | 3.83 | 3.375 | No
215400206 |  | Ground Loop | DAIKIN | WSSV042E1*H*T |  | 44800 | 21.3 | 29000 | 3.92 | 3.7333 | No
215400207 |  | Ground Loop | DAIKIN | WSSV042F3*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
215400210 |  | Ground Loop | DAIKIN | WSSV042E1*H*C |  | 44800 | 21.3 | 29000 | 3.92 | 3.7333 | No
215400211 |  | Ground Loop | DAIKIN | WSSV042F3*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
215400214 |  | Ground Loop | DAIKIN | WSSV048E1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215400215 |  | Ground Loop | DAIKIN | WSSV048F3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215400218 |  | Ground Loop | DAIKIN | WSSV048E1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215400219 |  | Ground Loop | DAIKIN | WSSV048F3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
215402552 |  | Ground Loop | DAIKIN | WSSV024E1*H*T |  | 25400 | 21.11 | 15700 | 3.7 | 2.1167 | No
215402553 |  | Ground Loop | DAIKIN | WSSV024F3*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215402556 |  | Ground Loop | DAIKIN | WSSV024E1*H*C |  | 25400 | 21.11 | 15700 | 3.7 | 2.1167 | No
215402557 |  | Ground Loop | DAIKIN | WSSV024F3*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215402560 |  | Ground Loop | DAIKIN | WSSV030E1*H*T |  | 30200 | 21.8 | 20700 | 3.83 | 2.5167 | No
215402561 |  | Ground Loop | DAIKIN | WSSV030F3*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
202434548 |  | Ground Loop | BOSCH | SV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434549 |  | Ground Loop | BOSCH | SV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434550 |  | Ground Loop | BOSCH | SV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434551 |  | Ground Loop | BOSCH | SV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434556 |  | Ground Loop | BOSCH | SV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434557 |  | Ground Loop | BOSCH | SV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434558 |  | Ground Loop | BOSCH | SV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434559 |  | Ground Loop | BOSCH | SV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
4219430 |  | Ground Loop | NORDIC | RH55HACW-P-1T-*-SDE** |  | 44400 | 17 | 34700 | 3.6 | 3.7 | No
4219434 |  | Ground Loop | NORDIC | TF55HACW-P-1T-*-SDE** |  | 45400 | 17.1 | 35400 | 3.8 | 3.7833 | Yes
4219444 |  | Ground Loop | NORDIC | RS55HACW-P-1T-* | AH-55-P-1-***** | 45400 | 17 | 35600 | 3.8 | 3.7833 | Yes
4230311 |  | Ground Loop | DAIKIN | WCCW4015*E*01* |  | 16700 | 18.7 | 11400 | 3.7 | 1.3917 | No
4230745 |  | Ground Loop | DAIKIN | WCCW4019*E*01* |  | 22600 | 17.3 | 14700 | 3.6 | 1.8833 | No
4230747 |  | Ground Loop | DAIKIN | WCCW4019*J*01* |  | 22600 | 17.3 | 14700 | 3.6 | 1.8833 | No
4233405 |  | Ground Loop | DAIKIN | WVFW1042*E***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833 | No
4233406 |  | Ground Loop | DAIKIN | WVFW1042*F***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833 | No
4233407 |  | Ground Loop | DAIKIN | WVFW1042*K***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833 | No
4233408 |  | Ground Loop | DAIKIN | WVFW1042*L***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833 | No
207198421 |  | Ground Loop | BOSCH | QV030-2HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198422 |  | Ground Loop | BOSCH | QV030-2HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198424 |  | Ground Loop | BOSCH | QV030-2VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198425 |  | Ground Loop | BOSCH | QV030-2VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198426 |  | Ground Loop | BOSCH | QV030-3HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198428 |  | Ground Loop | BOSCH | QV030-3HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198429 |  | Ground Loop | BOSCH | QV030-3VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198430 |  | Ground Loop | BOSCH | QV030-3VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198432 |  | Ground Loop | BOSCH | QV030-4HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198433 |  | Ground Loop | BOSCH | QV030-4HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198434 |  | Ground Loop | BOSCH | QV030-4VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
215837677 |  | Ground Loop | DAIKIN | WSMH024F3*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837679 |  | Ground Loop | DAIKIN | WSMH024J1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837680 |  | Ground Loop | DAIKIN | WSMH024K3*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837686 |  | Ground Loop | DAIKIN | WSMH024F3*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837687 |  | Ground Loop | DAIKIN | WSMH024J1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837689 |  | Ground Loop | DAIKIN | WSMH024K3*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15 | No
215837694 |  | Ground Loop | DAIKIN | WSMH030F3*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333 | No
215837697 |  | Ground Loop | DAIKIN | WSMH030K3*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333 | No
215837703 |  | Ground Loop | DAIKIN | WSMH030F3*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
215837704 |  | Ground Loop | DAIKIN | WSMH030J1*G/J*T |  | 29500 | 19.36 | 21900 | 3.76 | 2.4583 | No
215837705 |  | Ground Loop | DAIKIN | WSMH030K3*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
215837711 |  | Ground Loop | DAIKIN | WSMH030F3*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
215837712 |  | Ground Loop | DAIKIN | WSMH030J1*G/J*C |  | 29500 | 19.36 | 21900 | 3.76 | 2.4583 | No
215837714 |  | Ground Loop | DAIKIN | WSMH030K3*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583 | No
215837719 |  | Ground Loop | DAIKIN | WSMH036F3*G/J*P |  | 37800 | 18.18 | 30700 | 3.79 | 3.15 | No
215837721 |  | Ground Loop | DAIKIN | WSMH036J1*G/J*P |  | 37800 | 17.73 | 30700 | 3.8 | 3.15 | No
215837722 |  | Ground Loop | DAIKIN | WSMH036K3*G/J*P |  | 37800 | 18.1 | 30700 | 3.79 | 3.15 | No
215837728 |  | Ground Loop | DAIKIN | WSMH036F3*G/J*T |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667 | No
215837730 |  | Ground Loop | DAIKIN | WSMH036J1*G/J*T |  | 38000 | 18.77 | 30000 | 3.9 | 3.1667 | No
215837731 |  | Ground Loop | DAIKIN | WSMH036K3*G/J*T |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667 | No
215837737 |  | Ground Loop | DAIKIN | WSMH036F3*G/J*C |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667 | No
215837739 |  | Ground Loop | DAIKIN | WSMH036J1*G/J*C |  | 38000 | 18.77 | 30000 | 3.9 | 3.1667 | No
215837740 |  | Ground Loop | DAIKIN | WSMH036K3*G/J*C |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667 | No
215837744 |  | Ground Loop | DAIKIN | WSMH042F3*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325 | No
215837746 |  | Ground Loop | DAIKIN | WSMH042K3*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325 | No
215837750 |  | Ground Loop | DAIKIN | WSMH042F3*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
215837751 |  | Ground Loop | DAIKIN | WSMH042K3*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
218157959 |  | Ground Loop | YORK | Y5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157960 |  | Ground Loop | YORK | Y5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157961 |  | Ground Loop | YORK | Y5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157962 |  | Ground Loop | YORK | Y5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157963 |  | Ground Loop | YORK | Y5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157964 |  | Ground Loop | YORK | Y5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157965 |  | Ground Loop | YORK | Y5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157966 |  | Ground Loop | YORK | Y5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157967 |  | Ground Loop | YORK | Y5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157968 |  | Ground Loop | YORK | Y5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157969 |  | Ground Loop | YORK | Y5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157970 |  | Ground Loop | YORK | Y5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157971 |  | Ground Loop | YORK | Y5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157972 |  | Ground Loop | YORK | Y5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157973 |  | Ground Loop | YORK | Y5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157974 |  | Ground Loop | YORK | Y5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157975 |  | Ground Loop | YORK | Y5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
218157976 |  | Ground Loop | YORK | Y5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157977 |  | Ground Loop | YORK | Y5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157978 |  | Ground Loop | YORK | Y5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157979 |  | Ground Loop | YORK | Y5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157980 |  | Ground Loop | YORK | Y5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157981 |  | Ground Loop | YORK | Y5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157982 |  | Ground Loop | YORK | Y5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157983 |  | Ground Loop | YORK | Y5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157984 |  | Ground Loop | YORK | Y5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157985 |  | Ground Loop | YORK | Y5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
218157986 |  | Ground Loop | YORK | Y5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
207083897 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083899 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083901 |  | Ground Loop | CARRIER | 50PCV024J/K*C/A3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083903 |  | Ground Loop | CARRIER | 50PCV024J/K*N/J3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
215224478 |  | Ground Loop | FHP | CF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224479 |  | Ground Loop | FHP | CF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224480 |  | Ground Loop | FHP | CF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224481 |  | Ground Loop | FHP | CF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224482 |  | Ground Loop | FHP | CF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224483 |  | Ground Loop | FHP | CF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224484 |  | Ground Loop | FHP | CF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224485 |  | Ground Loop | FHP | CF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224486 |  | Ground Loop | FHP | CF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224487 |  | Ground Loop | FHP | CF007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224488 |  | Ground Loop | FHP | CF007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224489 |  | Ground Loop | FHP | CF009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224490 |  | Ground Loop | FHP | CF009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224491 |  | Ground Loop | FHP | CF012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224492 |  | Ground Loop | FHP | CF012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224493 |  | Ground Loop | FHP | CF015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224494 |  | Ground Loop | FHP | CF015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224495 |  | Ground Loop | FHP | CF018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
8738074 |  | Ground Loop | HYDRON MODULE | HVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738075 |  | Ground Loop | TETCO | TVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738076 |  | Ground Loop | GEOCOMFORT | GVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738077 |  | Ground Loop | HYDRON MODULE | HVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738078 |  | Ground Loop | TETCO | TVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8740368 |  | Ground Loop | GEOCOMFORT | GVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | Yes
216419880 |  | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
216419883 |  | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
216419898 |  | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
216419899 |  | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
216419902 |  | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
216419904 |  | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
216419921 |  | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
216419924 |  | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
216419941 |  | Ground Loop | Whalen | WZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | Yes
216419946 |  | Ground Loop | Whalen | WZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | Yes
216419947 |  | Ground Loop | Whalen | WZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | Yes
216439574 |  | Ground Loop | GeoSmart Energy | S5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667 | Yes
216439575 |  | Ground Loop | GeoSmart Energy | S5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917 | Yes
216439576 |  | Ground Loop | GeoSmart Energy | S5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083 | Yes
216439577 |  | Ground Loop | GeoSmart Energy | S5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583 | Yes
216726189 |  | Ground Loop | DAIKIN | WSRC007*E*G/J |  | 7100 | 19.4 | 4700 | 3.6 | 0.59167 | No
216726191 |  | Ground Loop | DAIKIN | WSRC009*E*G/J |  | 9100 | 18.1 | 6500 | 3.6 | 0.75833 | No
216726195 |  | Ground Loop | DAIKIN | WSRC015*E*G/J |  | 15400 | 18.9 | 11200 | 3.6 | 1.2833 | No
214839009 |  | Ground Loop | FHP | EC072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214839010 |  | Ground Loop | FHP | EC072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214839011 |  | Ground Loop | FHP | EC072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214839012 |  | Ground Loop | FHP | EC096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214839013 |  | Ground Loop | FHP | EC096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214839014 |  | Ground Loop | FHP | EC096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
216687118 |  | Ground Loop | WaterFurnace | W5SZ024BD1 | W5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216687119 |  | Ground Loop | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216687120 |  | Ground Loop | WaterFurnace | W5SZ048BD1 | W5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216687121 |  | Ground Loop | WaterFurnace | W5SZ060BD1 | W5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216687731 |  | Ground Loop | GEOSTAR | G5SS024BD1 | G5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216687732 |  | Ground Loop | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216687733 |  | Ground Loop | GEOSTAR | G5SS048BD1 | G5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216687734 |  | Ground Loop | GEOSTAR | G5SS060BD1 | G5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216687736 |  | Ground Loop | GEOSTAR | G5SZ024BD1 | G5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216687737 |  | Ground Loop | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216687738 |  | Ground Loop | GEOSTAR | G5SZ048BD1 | G5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216687739 |  | Ground Loop | GEOSTAR | G5SZ060BD1 | G5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216714620 |  | Ground Loop | GEOSTAR | G3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714621 |  | Ground Loop | GEOSTAR | G3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714622 |  | Ground Loop | GEOSTAR | G3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714623 |  | Ground Loop | GEOSTAR | G3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714624 |  | Ground Loop | GEOSTAR | G3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714625 |  | Ground Loop | GEOSTAR | G3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714626 |  | Ground Loop | GEOSTAR | G3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714627 |  | Ground Loop | GEOSTAR | G3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
216714636 |  | Ground Loop | GEOSTAR | G3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714637 |  | Ground Loop | GEOSTAR | G3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714638 |  | Ground Loop | GEOSTAR | G3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714639 |  | Ground Loop | GEOSTAR | G3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714640 |  | Ground Loop | GEOSTAR | G3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
216714641 |  | Ground Loop | GEOSTAR | G3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215224827 |  | Ground Loop | DAY & NIGHT | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224828 |  | Ground Loop | HEIL | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224829 |  | Ground Loop | ARCOAIRE | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224830 |  | Ground Loop | KEEPRITE | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224831 |  | Ground Loop | TEMPSTAR | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224832 |  | Ground Loop | COMFORTMAKER | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224833 |  | Ground Loop | DAY & NIGHT | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
216569713 |  | Ground Loop | GeoCool | GCHPV/H/D024BT**A*** |  | 26400 | 17.95 | 19000 | 4.2 | 2.2 | No
216569714 |  | Ground Loop | GeoCool | GCHPV/H/D036BT**A*** |  | 39000 | 17.86 | 28500 | 4.2 | 3.25 | No
216621310 |  | Ground Loop | GEOSTAR | G5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216621311 |  | Ground Loop | GEOSTAR | G5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216621312 |  | Ground Loop | GEOSTAR | G5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216621313 |  | Ground Loop | GEOSTAR | G5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216621314 |  | Ground Loop | GEOSTAR | G5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216621315 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216621316 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216621317 |  | Ground Loop | GEOSTAR | G5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
216621318 |  | Ground Loop | GEOSTAR | G5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
216621319 |  | Ground Loop | GEOSTAR | G5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
216621323 |  | Ground Loop | GEOSTAR | G5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216621324 |  | Ground Loop | GEOSTAR | G5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
216621325 |  | Ground Loop | GEOSTAR | G5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621326 |  | Ground Loop | GEOSTAR | G5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621327 |  | Ground Loop | GEOSTAR | G5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621328 |  | Ground Loop | GEOSTAR | G5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621329 |  | Ground Loop | GEOSTAR | G5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621330 |  | Ground Loop | GEOSTAR | G5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621331 |  | Ground Loop | GEOSTAR | G5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621332 |  | Ground Loop | GEOSTAR | G5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
216621333 |  | Ground Loop | GEOSTAR | G5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216621334 |  | Ground Loop | GEOSTAR | G5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216621335 |  | Ground Loop | GEOSTAR | G5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216621336 |  | Ground Loop | GEOSTAR | G5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216621337 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621338 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621339 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621340 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621341 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621342 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216621343 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621344 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621345 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621346 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621347 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621348 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216621349 |  | Ground Loop | GEOSTAR | G5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218353294 |  | Ground Loop | SKYMARK | PE072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218353295 |  | Ground Loop | SKYMARK | PE096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
218353306 |  | Ground Loop | SKYMARK | PQ024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353307 |  | Ground Loop | SKYMARK | PQ024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353308 |  | Ground Loop | SKYMARK | PQ024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353309 |  | Ground Loop | SKYMARK | PQ024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353310 |  | Ground Loop | SKYMARK | PQ024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353311 |  | Ground Loop | SKYMARK | PQ024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353312 |  | Ground Loop | SKYMARK | PQ024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353313 |  | Ground Loop | SKYMARK | PQ024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353314 |  | Ground Loop | SKYMARK | PQ036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218353315 |  | Ground Loop | SKYMARK | PQ036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218353316 |  | Ground Loop | SKYMARK | PQ036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218353317 |  | Ground Loop | SKYMARK | PQ036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218353318 |  | Ground Loop | SKYMARK | PQ048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
218353319 |  | Ground Loop | SKYMARK | PQ048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218353320 |  | Ground Loop | SKYMARK | PQ060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218353321 |  | Ground Loop | SKYMARK | PQ060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
215415872 |  | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415873 |  | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415876 |  | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415877 |  | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415878 |  | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | Yes
215415879 |  | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | Yes
215415886 |  | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | Yes
215415887 |  | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | Yes
215415888 |  | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | Yes
215415889 |  | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | Yes
215415909 |  | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | Yes
215415910 |  | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | Yes
215415911 |  | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 39200 | 19.5 | 28400 | 4.2 | 3.2667 | Yes
215415912 |  | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 39200 | 19.5 | 28400 | 4.2 | 3.2667 | Yes
215415913 |  | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 52000 | 20.2 | 37600 | 4.1 | 4.3333 | Yes
215415914 |  | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 52000 | 20.2 | 37600 | 4.1 | 4.3333 | Yes
215415915 |  | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | Yes
215415916 |  | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | Yes
217754758 |  | Ground Loop | DAIKIN | WSCH048F1*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
217754759 |  | Ground Loop | DAIKIN | WSCH048K1*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
217754762 |  | Ground Loop | DAIKIN | WSCH048F1*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
217754763 |  | Ground Loop | DAIKIN | WSCH048K1*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1 | No
215285739 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | Yes
215285740 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 39200 | 19.5 | 28400 | 4.2 | 3.2667 | Yes
215285741 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 52000 | 20.2 | 37600 | 4.1 | 4.3333 | Yes
215285742 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | Yes
215285743 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | Yes
215310891 |  | Ground Loop | GEOSTAR | G7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083 | Yes
215310892 |  | Ground Loop | GEOSTAR | G7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833 | Yes
215310893 |  | Ground Loop | GEOSTAR | G7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75 | Yes
215310990 |  | Ground Loop | GeoSmart Energy | S7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083 | Yes
215310991 |  | Ground Loop | GeoSmart Energy | S7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833 | Yes
215310992 |  | Ground Loop | GeoSmart Energy | S7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75 | Yes
217531660 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)006A |  | 6700 | 20 | 4600 | 3.6 | 0.55833 | Yes
217531661 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)009A |  | 9700 | 19 | 7000 | 3.7 | 0.80833 | Yes
217531662 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)012A |  | 12400 | 18.9 | 9200 | 3.6 | 1.0333 | Yes
217531663 |  | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)018A |  | 20100 | 19.5 | 14500 | 4.1 | 1.675 | Yes
215399846 |  | Ground Loop | DAIKIN | WSMV060K3*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
215399850 |  | Ground Loop | DAIKIN | WSMV060K3*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
215399858 |  | Ground Loop | DAIKIN | WSSV015A1*H*T |  | 17000 | 23.75 | 10400 | 3.77 | 1.4167 | No
215399859 |  | Ground Loop | DAIKIN | WSSV015J1*H*T |  | 17000 | 22.25 | 10500 | 3.77 | 1.4167 | No
215399862 |  | Ground Loop | DAIKIN | WSSV015A1*H*C |  | 17000 | 23.75 | 10400 | 3.77 | 1.4167 | No
215399863 |  | Ground Loop | DAIKIN | WSSV015J1*H*C |  | 17000 | 22.25 | 10500 | 3.77 | 1.4167 | No
215399865 |  | Ground Loop | DAIKIN | WSSV019J1*H*T |  | 20600 | 20.96 | 14100 | 3.63 | 1.7167 | No
215399867 |  | Ground Loop | DAIKIN | WSSV019J1*H*C |  | 20600 | 20.96 | 14100 | 3.63 | 1.7167 | No
215399870 |  | Ground Loop | DAIKIN | WSSV042J1*H*T |  | 44352 | 21.08 | 28710 | 3.88 | 3.696 | No
215399871 |  | Ground Loop | DAIKIN | WSSV042K3*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
215399874 |  | Ground Loop | DAIKIN | WSSV042J1*H*C |  | 44352 | 21.08 | 28710 | 3.88 | 3.696 | No
215399875 |  | Ground Loop | DAIKIN | WSSV042K3*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217752403 |  | Ground Loop | ClimateMaster | SL(A/*)*06A |  | 6300 | 20.5 | 4600 | 3.6 | 0.525 | No
217752677 |  | Ground Loop | DAIKIN | WSSH024J1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217752679 |  | Ground Loop | DAIKIN | WSSH024J1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
207177436 |  | Ground Loop | TRANE | GEVG0157 |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917 | No
207177437 |  | Ground Loop | TRANE | GEVG018A |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083 | No
207177438 |  | Ground Loop | TRANE | GEVG0187 |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083 | No
207177439 |  | Ground Loop | TRANE | GEVG024A |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
207177440 |  | Ground Loop | TRANE | GEVG024B |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
207177441 |  | Ground Loop | TRANE | GEVG0244 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
207177442 |  | Ground Loop | TRANE | GEVG0247 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
207177443 |  | Ground Loop | TRANE | GEVG030A |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
207177444 |  | Ground Loop | TRANE | GEVG030B |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
207177445 |  | Ground Loop | TRANE | GEVG0304 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
207177446 |  | Ground Loop | TRANE | GEVG0307 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
202350498 |  | Ground Loop | AAON, Inc. | M2-014-2-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083 | No
202350499 |  | Ground Loop | AAON, Inc. | M2-014-2-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725 | No
202350500 |  | Ground Loop | AAON, Inc. | M2-014-3-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083 | No
202350501 |  | Ground Loop | AAON, Inc. | M2-014-3-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725 | No
202350502 |  | Ground Loop | AAON, Inc. | M2-014-4-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083 | No
216743662 |  | Ground Loop | BOSCH | CP060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216743663 |  | Ground Loop | BOSCH-GEO | RP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
216743664 |  | Ground Loop | BOSCH | CP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743665 |  | Ground Loop | BOSCH | CP070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743666 |  | Ground Loop | BOSCH | CP070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743671 |  | Ground Loop | BOSCH-GEO | RP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
216743672 |  | Ground Loop | BOSCH | CP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743673 |  | Ground Loop | BOSCH | CP070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216743674 |  | Ground Loop | BOSCH | CP070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216759674 |  | Ground Loop | WaterFurnace | W7SZ042BV1**F | W7BM042BN1**2 | 41600 | 19.3 | 41400 | 3.8 | 3.4667 | Yes
216759816 |  | Ground Loop | WaterFurnace | W5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216759817 |  | Ground Loop | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216759818 |  | Ground Loop | WaterFurnace | W5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216759819 |  | Ground Loop | WaterFurnace | W5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216759821 |  | Ground Loop | GEOSTAR | G5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216759822 |  | Ground Loop | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216759823 |  | Ground Loop | GEOSTAR | G5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216759824 |  | Ground Loop | GEOSTAR | G5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216759826 |  | Ground Loop | WaterFurnace | W5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216759827 |  | Ground Loop | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216759828 |  | Ground Loop | WaterFurnace | W5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216759829 |  | Ground Loop | WaterFurnace | W5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216759831 |  | Ground Loop | GEOSTAR | G5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
216759832 |  | Ground Loop | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
216759833 |  | Ground Loop | GEOSTAR | G5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
216759834 |  | Ground Loop | GEOSTAR | G5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
216767321 |  | Ground Loop | TETCO | TVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
216767322 |  | Ground Loop | TETCO | TVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
216767323 |  | Ground Loop | TETCO | TVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
216767324 |  | Ground Loop | TETCO | TVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
216767325 |  | Ground Loop | TETCO | TVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917 | Yes
216767326 |  | Ground Loop | TETCO | TYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
216767327 |  | Ground Loop | TETCO | TYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083 | Yes
216767328 |  | Ground Loop | TETCO | TYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325 | Yes
216767329 |  | Ground Loop | TETCO | TVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
216767330 |  | Ground Loop | TETCO | TYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583 | Yes
214063740 |  | Ground Loop | GeoSmart Energy | GBV/GBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
214063741 |  | Ground Loop | GeoSmart Energy | GBV/GBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
214063742 |  | Ground Loop | GeoSmart Energy | GBV/GBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
214063743 |  | Ground Loop | GeoSmart Energy | GBV/GBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
214063744 |  | Ground Loop | GeoSmart Energy | GBV/GBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
214063745 |  | Ground Loop | GeoSmart Energy | GBV/GBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
214063747 |  | Ground Loop | GeoSmart Energy | GBV/GBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214063748 |  | Ground Loop | GeoSmart Energy | GBV/GBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214063750 |  | Ground Loop | GeoSmart Energy | GBV/GBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214063751 |  | Ground Loop | GeoSmart Energy | GBV/GBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214063752 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
214063753 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214063754 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214063755 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
214063756 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214063757 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214063758 |  | Ground Loop | GeoSmart Energy | GBV/GBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214063759 |  | Ground Loop | GeoSmart Energy | GBV/GBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214063760 |  | Ground Loop | GeoSmart Energy | GBV/GBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214063761 |  | Ground Loop | GeoSmart Energy | GBV/GBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214063762 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
214063763 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214063764 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214063765 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
214063766 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214063767 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214063768 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
214063769 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214063770 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214063771 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
214063772 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214063773 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214063774 |  | Ground Loop | GeoSmart Energy | GBV/GBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063775 |  | Ground Loop | GeoSmart Energy | GBV/GBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063776 |  | Ground Loop | GeoSmart Energy | GBV/GBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063777 |  | Ground Loop | GeoSmart Energy | GBV/GBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063778 |  | Ground Loop | GeoSmart Energy | GBV/GBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214063779 |  | Ground Loop | GeoSmart Energy | GBV/GBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214063780 |  | Ground Loop | GeoSmart Energy | GBV/GBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214063781 |  | Ground Loop | GeoSmart Energy | GBV/GBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214063782 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
214063783 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214063784 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214063785 |  | Ground Loop | GeoSmart Energy | GBV/GBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214063786 |  | Ground Loop | GeoSmart Energy | GBV/GBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214063788 |  | Ground Loop | GeoSmart Energy | GBV/GBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214063789 |  | Ground Loop | GeoSmart Energy | GBV/GBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214063790 |  | Ground Loop | GeoSmart Energy | GBV/GBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
215837832 |  | Ground Loop | DAIKIN | WSSH030J1*G/J*T |  | 30600 | 21.15 | 21200 | 3.95 | 2.55 | No
215837833 |  | Ground Loop | DAIKIN | WSSH030K3*G/J*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
215837839 |  | Ground Loop | DAIKIN | WSSH030F3*G/J*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
215837840 |  | Ground Loop | DAIKIN | WSSH030J1*G/J*C |  | 30600 | 21.15 | 21200 | 3.95 | 2.55 | No
215837841 |  | Ground Loop | DAIKIN | WSSH030K3*G/J*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
215837847 |  | Ground Loop | DAIKIN | WSSH036F3*G/J*T |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583 | No
215837848 |  | Ground Loop | DAIKIN | WSSH036J1*G/J*T |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583 | No
215837850 |  | Ground Loop | DAIKIN | WSSH036K3*G/J*T |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583 | No
215837855 |  | Ground Loop | DAIKIN | WSSH036F3*G/J*C |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583 | No
215837856 |  | Ground Loop | DAIKIN | WSSH036J1*G/J*C |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583 | No
215837857 |  | Ground Loop | DAIKIN | WSSH036K3*G/J*C |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583 | No
215837863 |  | Ground Loop | DAIKIN | WSSH042F3*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837865 |  | Ground Loop | DAIKIN | WSSH042J1*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837866 |  | Ground Loop | DAIKIN | WSSH042K3*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
215837873 |  | Ground Loop | DAIKIN | WSSH042F3*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
218472100 |  | Ground Loop | YORK | AD007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218472101 |  | Ground Loop | YORK | AD007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218472102 |  | Ground Loop | YORK | AD009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218472103 |  | Ground Loop | YORK | AD009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218472104 |  | Ground Loop | YORK | AD012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218472105 |  | Ground Loop | YORK | AD012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218472106 |  | Ground Loop | YORK | AD015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
218472107 |  | Ground Loop | YORK | AD015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
218472108 |  | Ground Loop | YORK | AD018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
218472109 |  | Ground Loop | YORK | AD018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
218472110 |  | Ground Loop | YORK | AD007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218472111 |  | Ground Loop | YORK | AD007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
218472112 |  | Ground Loop | YORK | AD009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218472113 |  | Ground Loop | YORK | AD009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218472114 |  | Ground Loop | YORK | AD012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218472115 |  | Ground Loop | YORK | AD012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218472116 |  | Ground Loop | YORK | AD015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
218472117 |  | Ground Loop | YORK | AD015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
218472118 |  | Ground Loop | YORK | AD018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
218472119 |  | Ground Loop | YORK | AD018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
218472120 |  | Ground Loop | YORK | AD024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218472121 |  | Ground Loop | YORK | AD024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353637 |  | Ground Loop | JOHNSON CONTROLS | DE072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218353638 |  | Ground Loop | JOHNSON CONTROLS | DE072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218353639 |  | Ground Loop | JOHNSON CONTROLS | DE072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218353640 |  | Ground Loop | JOHNSON CONTROLS | DE096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
218353641 |  | Ground Loop | JOHNSON CONTROLS | DE096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
218353642 |  | Ground Loop | JOHNSON CONTROLS | DE096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
218353651 |  | Ground Loop | JOHNSON CONTROLS | DQ024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353652 |  | Ground Loop | JOHNSON CONTROLS | DQ024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353653 |  | Ground Loop | JOHNSON CONTROLS | DQ024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353654 |  | Ground Loop | JOHNSON CONTROLS | DQ024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353655 |  | Ground Loop | JOHNSON CONTROLS | DQ024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353656 |  | Ground Loop | JOHNSON CONTROLS | DQ024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353657 |  | Ground Loop | JOHNSON CONTROLS | DQ024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353658 |  | Ground Loop | JOHNSON CONTROLS | DQ024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353659 |  | Ground Loop | JOHNSON CONTROLS | DQ024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353660 |  | Ground Loop | JOHNSON CONTROLS | DQ024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353661 |  | Ground Loop | JOHNSON CONTROLS | DQ024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353662 |  | Ground Loop | JOHNSON CONTROLS | DQ024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353663 |  | Ground Loop | JOHNSON CONTROLS | DQ024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353664 |  | Ground Loop | JOHNSON CONTROLS | DQ024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353665 |  | Ground Loop | JOHNSON CONTROLS | DQ024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353666 |  | Ground Loop | JOHNSON CONTROLS | DQ024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353667 |  | Ground Loop | JOHNSON CONTROLS | DQ036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218353668 |  | Ground Loop | JOHNSON CONTROLS | DQ036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218353669 |  | Ground Loop | JOHNSON CONTROLS | DQ036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218353670 |  | Ground Loop | JOHNSON CONTROLS | DQ036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218353671 |  | Ground Loop | JOHNSON CONTROLS | DQ036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218353672 |  | Ground Loop | JOHNSON CONTROLS | DQ036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217642881 |  | Ground Loop | GeoSmart Energy | S3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642883 |  | Ground Loop | GeoSmart Energy | S3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642884 |  | Ground Loop | GeoSmart Energy | S3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
7410095 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
7410164 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
7410223 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
7410291 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
7410355 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
7410435 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
7410657 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
7410825 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
7410908 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
7411002 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
7411100 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
215224606 |  | Ground Loop | CARRIER | 50WD*009***4*(J-R)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224607 |  | Ground Loop | CARRIER | 50WD*012***3*(A-H)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224608 |  | Ground Loop | CARRIER | 50WD*012***3*(J-R)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224609 |  | Ground Loop | CARRIER | 50WD*012***4*(A-H)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224610 |  | Ground Loop | CARRIER | 50WD*012***4*(J-R)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224611 |  | Ground Loop | CARRIER | 50WD*015***3*(A-H)** |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224612 |  | Ground Loop | CARRIER | 50WD*015***3*(J-R)** |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224613 |  | Ground Loop | CARRIER | 50WD*015***4*(A-H)** |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
215224614 |  | Ground Loop | CARRIER | 50WD*015***4*(J-R)** |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
215224615 |  | Ground Loop | CARRIER | 50WD*018***3*(A-H)** |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224616 |  | Ground Loop | CARRIER | 50WD*018***3*(J-R)** |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224617 |  | Ground Loop | CARRIER | 50WD*018***4*(A-H)** |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
215224618 |  | Ground Loop | CARRIER | 50WD*018***4*(J-R)** |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224619 |  | Ground Loop | CARRIER | 50WD*024***3*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224620 |  | Ground Loop | CARRIER | 50WD*024***3*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224621 |  | Ground Loop | CARRIER | 50WD*024***4*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224622 |  | Ground Loop | CARRIER | 50WD*024***4*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224623 |  | Ground Loop | CARRIER | 50WD*024***5*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224624 |  | Ground Loop | CARRIER | 50WD*024***5*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224625 |  | Ground Loop | CARRIER | 50WD*024***6*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224626 |  | Ground Loop | CARRIER | 50WD*024***6*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218472132 |  | Ground Loop | YORK | AD024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218472133 |  | Ground Loop | YORK | AD024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224089 |  | Ground Loop | BOSCH | CF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224090 |  | Ground Loop | BOSCH | CF024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224091 |  | Ground Loop | BOSCH | CF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224092 |  | Ground Loop | BOSCH | CF024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
207348682 |  | Ground Loop | WaterFurnace | URS060*0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348683 |  | Ground Loop | WaterFurnace | URS060*0*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348684 |  | Ground Loop | WaterFurnace | URS060*3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348685 |  | Ground Loop | WaterFurnace | URS060*3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348686 |  | Ground Loop | WaterFurnace | URS060*3*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348687 |  | Ground Loop | WaterFurnace | URS060*4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348688 |  | Ground Loop | WaterFurnace | URS060*4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348689 |  | Ground Loop | WaterFurnace | URS060*4*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207348707 |  | Ground Loop | WaterFurnace | URD038*0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348708 |  | Ground Loop | WaterFurnace | URD038*0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348709 |  | Ground Loop | WaterFurnace | URD038*0*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348710 |  | Ground Loop | WaterFurnace | URD038*3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348711 |  | Ground Loop | WaterFurnace | URD038*3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348712 |  | Ground Loop | WaterFurnace | URD038*3*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348713 |  | Ground Loop | WaterFurnace | URD038*4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348714 |  | Ground Loop | WaterFurnace | URD038*4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348715 |  | Ground Loop | WaterFurnace | URD038*4*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207348716 |  | Ground Loop | WaterFurnace | URD049*0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348717 |  | Ground Loop | WaterFurnace | URD049*0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348718 |  | Ground Loop | WaterFurnace | URD049*0*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348719 |  | Ground Loop | WaterFurnace | URD049*3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348720 |  | Ground Loop | WaterFurnace | URD049*3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348721 |  | Ground Loop | WaterFurnace | URD049*3*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348722 |  | Ground Loop | WaterFurnace | URD049*4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348723 |  | Ground Loop | WaterFurnace | URD049*4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348724 |  | Ground Loop | WaterFurnace | URD049*4*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207348725 |  | Ground Loop | WaterFurnace | URD064*0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348726 |  | Ground Loop | WaterFurnace | URD064*0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348727 |  | Ground Loop | WaterFurnace | URD064*0*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348728 |  | Ground Loop | WaterFurnace | URD064*3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348729 |  | Ground Loop | WaterFurnace | URD064*3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348730 |  | Ground Loop | WaterFurnace | URD064*3*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348731 |  | Ground Loop | WaterFurnace | URD064*4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348732 |  | Ground Loop | WaterFurnace | URD064*4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348733 |  | Ground Loop | WaterFurnace | URD064*4*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207348734 |  | Ground Loop | WaterFurnace | URD072*0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348735 |  | Ground Loop | WaterFurnace | URD072*0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348736 |  | Ground Loop | WaterFurnace | URD072*0*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348737 |  | Ground Loop | WaterFurnace | URD072*3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348738 |  | Ground Loop | WaterFurnace | URD072*3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5615037 |  | Ground Loop | DAIKIN | WCCW5030*K*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625 | No
5615042 |  | Ground Loop | DAIKIN | WCCW5036*E*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15 | No
5615043 |  | Ground Loop | DAIKIN | WCCW5036*F*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15 | No
5615044 |  | Ground Loop | DAIKIN | WCCW5036*J*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15 | No
5615045 |  | Ground Loop | DAIKIN | WCCW5036*K*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15 | No
5615050 |  | Ground Loop | DAIKIN | WCCW5042*E*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083 | No
5615051 |  | Ground Loop | DAIKIN | WCCW5042*F*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083 | No
5615052 |  | Ground Loop | DAIKIN | WCCW5042*K*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083 | No
5615053 |  | Ground Loop | DAIKIN | WCCW5042*L*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083 | No
5646343 |  | Ground Loop | GEOCOMFORT | GXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | Yes
5646344 |  | Ground Loop | HYDRON MODULE | HXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | Yes
5646345 |  | Ground Loop | TETCO | TXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | Yes
5646346 |  | Ground Loop | GEOCOMFORT | GXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646347 |  | Ground Loop | HYDRON MODULE | HXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646348 |  | Ground Loop | TETCO | TXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646349 |  | Ground Loop | GEOCOMFORT | GXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646350 |  | Ground Loop | HYDRON MODULE | HXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646351 |  | Ground Loop | TETCO | TXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667 | No
5646371 |  | Ground Loop | GEOCOMFORT | GXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | Yes
5646372 |  | Ground Loop | HYDRON MODULE | HXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | Yes
5646373 |  | Ground Loop | TETCO | TXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | Yes
5646374 |  | Ground Loop | GEOCOMFORT | GXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646375 |  | Ground Loop | HYDRON MODULE | HXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646376 |  | Ground Loop | TETCO | TXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646377 |  | Ground Loop | GEOCOMFORT | GXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646378 |  | Ground Loop | HYDRON MODULE | HXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646379 |  | Ground Loop | TETCO | TXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417 | No
5646381 |  | Ground Loop | GEOCOMFORT | GCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | Yes
5646382 |  | Ground Loop | HYDRON MODULE | HCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | Yes
5646383 |  | Ground Loop | TETCO | TCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167 | Yes
206438789 |  | Ground Loop | FHP | EP030-1HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438790 |  | Ground Loop | FHP | EP060-4HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438791 |  | Ground Loop | FHP | EP060-3HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438792 |  | Ground Loop | FHP | EP060-1HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438793 |  | Ground Loop | FHP | EP070-1HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438794 |  | Ground Loop | FHP | EP070-3HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438795 |  | Ground Loop | FHP | EP070-4HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
207323881 |  | Ground Loop | WaterFurnace | NDZ026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
207323882 |  | Ground Loop | WaterFurnace | NDZ026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
207323883 |  | Ground Loop | WaterFurnace | NDS026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207323884 |  | Ground Loop | WaterFurnace | NDS026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207323885 |  | Ground Loop | WaterFurnace | NDZ038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207323886 |  | Ground Loop | WaterFurnace | NDZ038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207323887 |  | Ground Loop | WaterFurnace | NDS038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207323888 |  | Ground Loop | WaterFurnace | NDZ049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
207323889 |  | Ground Loop | WaterFurnace | NDZ049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
207323890 |  | Ground Loop | WaterFurnace | NDS049H1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207323891 |  | Ground Loop | WaterFurnace | NDS049H1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207323892 |  | Ground Loop | WaterFurnace | NDZ064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
207323893 |  | Ground Loop | WaterFurnace | NDZ064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
207323894 |  | Ground Loop | WaterFurnace | NDS064H1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207323895 |  | Ground Loop | WaterFurnace | NDS064H1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207323900 |  | Ground Loop | WaterFurnace | NDS038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207323901 |  | Ground Loop | WaterFurnace | NSZ022H1* | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
207323902 |  | Ground Loop | WaterFurnace | NSZ030H1* | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
207323903 |  | Ground Loop | WaterFurnace | NSZ036J1* | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
207323904 |  | Ground Loop | WaterFurnace | NSZ042J1* | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
207323905 |  | Ground Loop | WaterFurnace | NSZ048J1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
207323906 |  | Ground Loop | WaterFurnace | NSZ048J1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
207323907 |  | Ground Loop | WaterFurnace | NSZ060J1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
207323908 |  | Ground Loop | WaterFurnace | NSZ060J1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
207323909 |  | Ground Loop | WaterFurnace | NSZ070H1* | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
207323910 |  | Ground Loop | WaterFurnace | NSZ022H1* | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
207323911 |  | Ground Loop | WaterFurnace | NSZ030H1* | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
207323912 |  | Ground Loop | WaterFurnace | NSZ036J1* | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
207323913 |  | Ground Loop | WaterFurnace | NSZ042J1* | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
207323914 |  | Ground Loop | WaterFurnace | NSZ070H1* | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
215415816 |  | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)015A*VB |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415817 |  | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)015A*VC |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415820 |  | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)018A*VB |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415821 |  | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)018A*VC |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415822 |  | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)024A*B |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | No
215415823 |  | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)024A*C |  | 25000 | 18 | 18400 | 3.9 | 2.0833 | No
215415830 |  | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)048A*B |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | No
215415831 |  | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)048A*C |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833 | No
215415832 |  | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)060A*B |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | No
215415833 |  | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)060A*C |  | 61500 | 17.8 | 44600 | 3.7 | 5.125 | No
215415834 |  | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415835 |  | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415836 |  | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415837 |  | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415840 |  | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415841 |  | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
218353053 |  | Ground Loop | SKYMARK | PE072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218353054 |  | Ground Loop | SKYMARK | PE072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218353055 |  | Ground Loop | SKYMARK | PE096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
218353056 |  | Ground Loop | SKYMARK | PE096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
218353063 |  | Ground Loop | SKYMARK | PQ024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353064 |  | Ground Loop | SKYMARK | PQ024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353065 |  | Ground Loop | SKYMARK | PQ024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353066 |  | Ground Loop | SKYMARK | PQ024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353067 |  | Ground Loop | SKYMARK | PQ024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353068 |  | Ground Loop | SKYMARK | PQ024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353069 |  | Ground Loop | SKYMARK | PQ024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218353070 |  | Ground Loop | SKYMARK | PQ024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218353071 |  | Ground Loop | SKYMARK | PQ036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218353072 |  | Ground Loop | SKYMARK | PQ036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218353073 |  | Ground Loop | SKYMARK | PQ036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218353074 |  | Ground Loop | SKYMARK | PQ036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218353075 |  | Ground Loop | SKYMARK | PQ048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
218353076 |  | Ground Loop | SKYMARK | PQ048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218353077 |  | Ground Loop | SKYMARK | PQ048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
211594262 |  | Ground Loop | TRANE | EXHG0704 |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
211594263 |  | Ground Loop | TRANE | DXHG024B |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
211594264 |  | Ground Loop | TRANE | DXHG0244 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
211594265 |  | Ground Loop | TRANE | DXHG0247 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
211594266 |  | Ground Loop | TRANE | DXHG036B |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
211594267 |  | Ground Loop | TRANE | DXHG0364 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
211594268 |  | Ground Loop | TRANE | DXHG0367 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
211594269 |  | Ground Loop | TRANE | DXHG048B |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
211594270 |  | Ground Loop | TRANE | DXHG0484 |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
211594271 |  | Ground Loop | TRANE | DXHG060B |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
211594272 |  | Ground Loop | TRANE | DXHG0604 |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
215748220 |  | Ground Loop | ClimateMaster | SMS(S,M)15A*Q |  | 14800 | 17.5 | 11100 | 3.6 | 1.2333 | No
215748221 |  | Ground Loop | ClimateMaster | SMT(S,M)15A*Q |  | 15400 | 18.8 | 11000 | 3.7 | 1.2833 | No
215748224 |  | Ground Loop | ClimateMaster | SMT(S,M)18A*Q |  | 19000 | 17.8 | 13600 | 3.6 | 1.5833 | No
215748226 |  | Ground Loop | ClimateMaster | SMS(S,M)24A*Q |  | 24800 | 18.6 | 18400 | 3.6 | 2.0667 | No
215748227 |  | Ground Loop | ClimateMaster | SMT(S,M)24A*Q |  | 25900 | 20.4 | 18000 | 3.7 | 2.1583 | No
215748230 |  | Ground Loop | ClimateMaster | SMT(S,M)30A*Q |  | 30000 | 19 | 22300 | 3.7 | 2.5 | No
218157947 |  | Ground Loop | YORK | Y5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157948 |  | Ground Loop | YORK | Y5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157949 |  | Ground Loop | YORK | Y5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157950 |  | Ground Loop | YORK | Y5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157951 |  | Ground Loop | YORK | Y5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157952 |  | Ground Loop | YORK | Y5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157953 |  | Ground Loop | YORK | Y5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157954 |  | Ground Loop | YORK | Y5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157955 |  | Ground Loop | YORK | Y5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157956 |  | Ground Loop | YORK | Y5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157957 |  | Ground Loop | YORK | Y5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
218157958 |  | Ground Loop | YORK | Y5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
9910568 |  | Ground Loop | HYDRON MODULE | HZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910569 |  | Ground Loop | TETCO | TZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910570 |  | Ground Loop | GEOCOMFORT | GZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910571 |  | Ground Loop | HYDRON MODULE | HZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910572 |  | Ground Loop | TETCO | TZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910573 |  | Ground Loop | GEOCOMFORT | GZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910574 |  | Ground Loop | HYDRON MODULE | HZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910575 |  | Ground Loop | TETCO | TZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910576 |  | Ground Loop | GEOCOMFORT | GZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910577 |  | Ground Loop | HYDRON MODULE | HZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910578 |  | Ground Loop | TETCO | TZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1 | No
9910584 |  | Ground Loop | GEOCOMFORT | GZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | Yes
9910585 |  | Ground Loop | HYDRON MODULE | HZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | Yes
9910586 |  | Ground Loop | TETCO | TZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | Yes
9910587 |  | Ground Loop | GEOCOMFORT | GZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910588 |  | Ground Loop | HYDRON MODULE | HZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910589 |  | Ground Loop | TETCO | TZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910590 |  | Ground Loop | GEOCOMFORT | GZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910591 |  | Ground Loop | HYDRON MODULE | HZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910592 |  | Ground Loop | TETCO | TZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910593 |  | Ground Loop | GEOCOMFORT | GZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910594 |  | Ground Loop | HYDRON MODULE | HZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910595 |  | Ground Loop | TETCO | TZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583 | No
9910600 |  | Ground Loop | GEOCOMFORT | GZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | Yes
9910601 |  | Ground Loop | HYDRON MODULE | HZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | Yes
9910602 |  | Ground Loop | TETCO | TZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | Yes
9910603 |  | Ground Loop | GEOCOMFORT | GZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910604 |  | Ground Loop | HYDRON MODULE | HZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910605 |  | Ground Loop | TETCO | TZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910606 |  | Ground Loop | GEOCOMFORT | GZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910607 |  | Ground Loop | HYDRON MODULE | HZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910608 |  | Ground Loop | TETCO | TZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910609 |  | Ground Loop | GEOCOMFORT | GZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910610 |  | Ground Loop | HYDRON MODULE | HZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910611 |  | Ground Loop | TETCO | TZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910612 |  | Ground Loop | GEOCOMFORT | GZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910613 |  | Ground Loop | HYDRON MODULE | HZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910614 |  | Ground Loop | TETCO | TZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525 | No
9910620 |  | Ground Loop | GEOCOMFORT | GZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | Yes
9910621 |  | Ground Loop | HYDRON MODULE | HZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | Yes
9910622 |  | Ground Loop | TETCO | TZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | Yes
9910623 |  | Ground Loop | GEOCOMFORT | GZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910624 |  | Ground Loop | HYDRON MODULE | HZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910625 |  | Ground Loop | TETCO | TZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910626 |  | Ground Loop | GEOCOMFORT | GZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910627 |  | Ground Loop | HYDRON MODULE | HZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910628 |  | Ground Loop | TETCO | TZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910629 |  | Ground Loop | GEOCOMFORT | GZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910630 |  | Ground Loop | HYDRON MODULE | HZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910631 |  | Ground Loop | TETCO | TZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2 | No
9910636 |  | Ground Loop | GEOCOMFORT | GZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910637 |  | Ground Loop | HYDRON MODULE | HZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | Yes
9910638 |  | Ground Loop | TETCO | TZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | Yes
9910639 |  | Ground Loop | GEOCOMFORT | GZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910640 |  | Ground Loop | HYDRON MODULE | HZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910641 |  | Ground Loop | TETCO | TZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
205973168 |  | Ground Loop | Enertech | ERE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175 | No
205973779 |  | Ground Loop | COMFORT-AIRE | HEV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
9910756 |  | Ground Loop | HYDRON MODULE | HZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
206185527 |  | Ground Loop | DAIKIN | WGCH015J1*G/J*T |  | 14800 | 18 | 10500 | 3.6 | 1.2333 | No
206185528 |  | Ground Loop | DAIKIN | WGCH015J1*G/J*C |  | 14800 | 18 | 10500 | 3.6 | 1.2333 | No
206185532 |  | Ground Loop | DAIKIN | WGCH019E1*G/J*P |  | 18000 | 17.9 | 13600 | 3.8 | 1.5 | No
206185533 |  | Ground Loop | DAIKIN | WGCH019E1*G/J*T |  | 18300 | 19 | 13200 | 3.9 | 1.525 | No
206185538 |  | Ground Loop | DAIKIN | WGCH019J1*G/J*T |  | 18300 | 17.6 | 13200 | 3.8 | 1.525 | No
206185539 |  | Ground Loop | DAIKIN | WGCH019J1*G/J*C |  | 18300 | 17.6 | 13200 | 3.8 | 1.525 | No
5220666 |  | Ground Loop | DAIKIN | WGSV/WGSH019B*E |  | 18700 | 18.7 | 13800 | 4.1 | 1.5583 | No
5220667 |  | Ground Loop | DAIKIN | WGSV/WGSH019B*J |  | 18700 | 18.7 | 13800 | 4.1 | 1.5583 | No
5220670 |  | Ground Loop | DAIKIN | WGSV/WGSH024B*E |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917 | No
5220671 |  | Ground Loop | DAIKIN | WGSV/WGSH024B*F |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917 | No
5220672 |  | Ground Loop | DAIKIN | WGSV/WGSH024B*J |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917 | No
5220673 |  | Ground Loop | DAIKIN | WGSV/WGSH024B*K |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917 | No
5220675 |  | Ground Loop | DAIKIN | WGSV/WGSH030B*E |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083 | No
5220676 |  | Ground Loop | DAIKIN | WGSV/WGSH030B*F |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083 | No
5220677 |  | Ground Loop | DAIKIN | WGSV/WGSH030B*J |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083 | No
5220678 |  | Ground Loop | DAIKIN | WGSV/WGSH030B*K |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083 | No
5220681 |  | Ground Loop | DAIKIN | WGSV/WGSH036B*E |  | 38500 | 22 | 26200 | 4.3 | 3.2083 | No
207216514 |  | Ground Loop | GEOSTAR | GDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
207216515 |  | Ground Loop | GEOSTAR | GDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
207216516 |  | Ground Loop | GEOSTAR | GDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
207216517 |  | Ground Loop | GEOSTAR | GDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
207216518 |  | Ground Loop | GEOSTAR | GDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
207216519 |  | Ground Loop | GEOSTAR | GDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
201907621 |  | Ground Loop | WaterFurnace | URS048*0*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907622 |  | Ground Loop | WaterFurnace | URS048*3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907623 |  | Ground Loop | WaterFurnace | URS048*3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907624 |  | Ground Loop | WaterFurnace | URS048*3*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907625 |  | Ground Loop | WaterFurnace | URS048*4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907626 |  | Ground Loop | WaterFurnace | URS048*4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907627 |  | Ground Loop | WaterFurnace | URS048*4*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907628 |  | Ground Loop | WaterFurnace | URD038*4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
201907629 |  | Ground Loop | WaterFurnace | URD038*4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
201907630 |  | Ground Loop | WaterFurnace | URD038*4*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
201907631 |  | Ground Loop | WaterFurnace | URD049*4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
201907632 |  | Ground Loop | WaterFurnace | URD049*4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
201907633 |  | Ground Loop | WaterFurnace | URD049*4*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
201926691 |  | Ground Loop | WaterFurnace | URS060*0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926694 |  | Ground Loop | WaterFurnace | URS060*0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926696 |  | Ground Loop | WaterFurnace | URS060*0*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926699 |  | Ground Loop | WaterFurnace | URS060*3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926702 |  | Ground Loop | WaterFurnace | URS060*3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926705 |  | Ground Loop | WaterFurnace | URS060*3*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926708 |  | Ground Loop | WaterFurnace | URS060*4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926711 |  | Ground Loop | WaterFurnace | URS060*4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926714 |  | Ground Loop | WaterFurnace | URS060*4*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
201926717 |  | Ground Loop | WaterFurnace | URS070*0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926719 |  | Ground Loop | WaterFurnace | URS070*0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926724 |  | Ground Loop | WaterFurnace | URS070*0*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926727 |  | Ground Loop | WaterFurnace | URS070*3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926730 |  | Ground Loop | WaterFurnace | URS070*3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926733 |  | Ground Loop | WaterFurnace | URS070*3*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926736 |  | Ground Loop | WaterFurnace | URS070*4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926738 |  | Ground Loop | WaterFurnace | URS070*4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926741 |  | Ground Loop | WaterFurnace | URS070*4*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
201926779 |  | Ground Loop | WaterFurnace | URD064*4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
201926783 |  | Ground Loop | WaterFurnace | URD064*4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
201926787 |  | Ground Loop | WaterFurnace | URD064*4*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
201926799 |  | Ground Loop | WaterFurnace | URD072*4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
201926802 |  | Ground Loop | WaterFurnace | URD072*4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
201926804 |  | Ground Loop | WaterFurnace | URD072*4*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
201926809 |  | Ground Loop | WaterFurnace | URT096*4*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65 | No
201930362 |  | Ground Loop | GEOCOMFORT | GZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | Yes
206422417 |  | Ground Loop | CENTURY | HBH/V015*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
206422418 |  | Ground Loop | COMFORT-AIRE | HBH/V015*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
206422419 |  | Ground Loop | CENTURY | HBH/V018*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
206422420 |  | Ground Loop | COMFORT-AIRE | HBH/V018*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625 | No
206438719 |  | Ground Loop | BOSCH | EP009-1HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438720 |  | Ground Loop | BOSCH | EP009-2HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438721 |  | Ground Loop | BOSCH | EP012-0HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438723 |  | Ground Loop | BOSCH | EP012-0VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438725 |  | Ground Loop | BOSCH | EP012-1HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438727 |  | Ground Loop | BOSCH | EP012-1VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438729 |  | Ground Loop | BOSCH | EP012-2HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438731 |  | Ground Loop | BOSCH | EP012-2VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
215224293 |  | Ground Loop | BOSCH-GEO | RF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
215224294 |  | Ground Loop | BOSCH-GEO | RF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
215224295 |  | Ground Loop | BOSCH-GEO | RF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
215224296 |  | Ground Loop | BOSCH-GEO | RF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
215224297 |  | Ground Loop | BOSCH-GEO | RF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
215224298 |  | Ground Loop | BOSCH-GEO | RF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
215224299 |  | Ground Loop | BOSCH-GEO | RF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | Yes
215224300 |  | Ground Loop | BOSCH-GEO | RF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | Yes
215224301 |  | Ground Loop | BOSCH-GEO | RF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224302 |  | Ground Loop | BOSCH-GEO | RF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224305 |  | Ground Loop | BOSCH-GEO | RF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224306 |  | Ground Loop | BOSCH-GEO | RF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224477 |  | Ground Loop | FHP | CF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
216802025 |  | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**5*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216802027 |  | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**6*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216802029 |  | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**6*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
216979809 |  | Ground Loop | CARRIER | GCA24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979810 |  | Ground Loop | BRYANT | GCA24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979811 |  | Ground Loop | CARRIER | GCA24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979812 |  | Ground Loop | BRYANT | GCA24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979813 |  | Ground Loop | CARRIER | GCA24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979814 |  | Ground Loop | BRYANT | GCA24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216979815 |  | Ground Loop | CARRIER | GCA24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216979816 |  | Ground Loop | BRYANT | GCA24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
211594119 |  | Ground Loop | TRANE | GEHG009A |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167 | No
211594120 |  | Ground Loop | TRANE | GEHG012A |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083 | No
211594121 |  | Ground Loop | TRANE | GEHG015A |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917 | No
211594122 |  | Ground Loop | TRANE | GEHG018A |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083 | No
211594123 |  | Ground Loop | TRANE | GEHG024A |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
211594124 |  | Ground Loop | TRANE | GEHG030A |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
211594125 |  | Ground Loop | TRANE | GEHG036A |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
211594129 |  | Ground Loop | TRANE | EXHG009A |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167 | No
211594130 |  | Ground Loop | TRANE | EXHG012A |  | 12300 | 19.5 | 9300 | 4 | 1.025 | No
211594131 |  | Ground Loop | TRANE | EXHG015A |  | 15800 | 19 | 12100 | 3.8 | 1.3167 | No
211594132 |  | Ground Loop | TRANE | EXHG018A |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333 | No
211594133 |  | Ground Loop | TRANE | EXHG024A |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
211594134 |  | Ground Loop | TRANE | EXHG030A |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
211594135 |  | Ground Loop | TRANE | EXHG036A |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
211594136 |  | Ground Loop | TRANE | EXHG042A |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
211594137 |  | Ground Loop | TRANE | EXHG048A |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
211594138 |  | Ground Loop | TRANE | EXHG060A |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
211594139 |  | Ground Loop | TRANE | EXHG070A |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
9008839 |  | Ground Loop | BOSCH | ES025-1CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
9008840 |  | Ground Loop | BOSCH | ES025-2CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
9009353 |  | Ground Loop | FHP | ES025-1CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
9009366 |  | Ground Loop | FHP | ES025-2CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917 | No
202921913 |  | Ground Loop | BOSCH | EP036-3HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921914 |  | Ground Loop | BOSCH | EP036-4HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921915 |  | Ground Loop | BOSCH-GEO | BP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921952 |  | Ground Loop | FHP | EP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921953 |  | Ground Loop | FHP | EP036-3HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921954 |  | Ground Loop | FHP | EP036-4HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202921956 |  | Ground Loop | BOSCH | BP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202921957 |  | Ground Loop | FHP | EP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921958 |  | Ground Loop | FHP | EP036-3VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921959 |  | Ground Loop | FHP | EP036-4VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921960 |  | Ground Loop | BOSCH | BP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922686 |  | Ground Loop | CARRIER | 50PSH036***3/CA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922689 |  | Ground Loop | CARRIER | 50PSH036***5/EA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922692 |  | Ground Loop | CARRIER | 50PSH036***6/FA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922695 |  | Ground Loop | CARRIER | GB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
207349388 |  | Ground Loop | WaterFurnace | NBV/NBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349389 |  | Ground Loop | WaterFurnace | NBV/NBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349390 |  | Ground Loop | WaterFurnace | NBV/NBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349391 |  | Ground Loop | WaterFurnace | NBV/NBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349392 |  | Ground Loop | WaterFurnace | NBV/NBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349393 |  | Ground Loop | WaterFurnace | NBV/NBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349394 |  | Ground Loop | WaterFurnace | NBV/NBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207349395 |  | Ground Loop | WaterFurnace | NBV/NBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349396 |  | Ground Loop | WaterFurnace | NBV/NBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349397 |  | Ground Loop | WaterFurnace | NBV/NBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349398 |  | Ground Loop | WaterFurnace | NBV/NBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349399 |  | Ground Loop | WaterFurnace | NBV/NBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349400 |  | Ground Loop | WaterFurnace | NBV/NBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207349401 |  | Ground Loop | WaterFurnace | NBV/NBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349402 |  | Ground Loop | WaterFurnace | NBV/NBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349403 |  | Ground Loop | WaterFurnace | NBV/NBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349404 |  | Ground Loop | WaterFurnace | NBV/NBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349405 |  | Ground Loop | WaterFurnace | NBV/NBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349406 |  | Ground Loop | WaterFurnace | NBV/NBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207349407 |  | Ground Loop | WaterFurnace | NBV/NBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349408 |  | Ground Loop | WaterFurnace | NBV/NBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349409 |  | Ground Loop | WaterFurnace | NBV/NBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349410 |  | Ground Loop | WaterFurnace | NBV/NBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349411 |  | Ground Loop | WaterFurnace | NBV/NBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349412 |  | Ground Loop | WaterFurnace | NBV/NBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207657647 |  | Ground Loop | ClimateMaster | TSM15 D |  | 15500 | 18.8 | 11000 | 3.6 | 1.2917 | No
215400183 |  | Ground Loop | DAIKIN | WSSV024K3*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215400186 |  | Ground Loop | DAIKIN | WSSV024J1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215400187 |  | Ground Loop | DAIKIN | WSSV024K3*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
215400190 |  | Ground Loop | DAIKIN | WSSV030J1*H*T |  | 30200 | 20.49 | 20700 | 3.83 | 2.5167 | No
218471794 |  | Ground Loop | YORK | QD012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
218471795 |  | Ground Loop | YORK | QD012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
218471796 |  | Ground Loop | YORK | QD015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | Yes
218471797 |  | Ground Loop | YORK | QD015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | Yes
218471798 |  | Ground Loop | YORK | QD018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
218471799 |  | Ground Loop | YORK | QD018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
218471802 |  | Ground Loop | YORK | QD024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
218471803 |  | Ground Loop | YORK | QD024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
218471830 |  | Ground Loop | YORK | QQ024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
218471831 |  | Ground Loop | YORK | AQ024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218471832 |  | Ground Loop | YORK | AQ024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218471833 |  | Ground Loop | YORK | QQ024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
218471834 |  | Ground Loop | YORK | AQ024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218471835 |  | Ground Loop | YORK | AQ024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218471836 |  | Ground Loop | YORK | QQ024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
218471837 |  | Ground Loop | YORK | AQ024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
202434510 |  | Ground Loop | BOSCH | SV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434511 |  | Ground Loop | BOSCH | SV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
216625485 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625486 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625487 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625488 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625489 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625490 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625491 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625492 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625493 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625494 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625495 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625496 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625497 |  | Ground Loop | GEOSTAR | G5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
216625498 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625499 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625500 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625501 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625502 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625503 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625504 |  | Ground Loop | GEOSTAR | G5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625505 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625506 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625507 |  | Ground Loop | GEOSTAR | G5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
3706370 |  | Ground Loop | GEOSTAR | ZS018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
3706371 |  | Ground Loop | GEOSTAR | ZS023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3706373 |  | Ground Loop | GEOSTAR | ZS023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3706374 |  | Ground Loop | GEOSTAR | ZS023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3706375 |  | Ground Loop | GEOSTAR | ZS023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
3706376 |  | Ground Loop | GEOSTAR | ZS024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3706377 |  | Ground Loop | GEOSTAR | ZS024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3706378 |  | Ground Loop | GEOSTAR | ZS024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3706379 |  | Ground Loop | GEOSTAR | ZS024**4*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3706380 |  | Ground Loop | GEOSTAR | ZS030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3706381 |  | Ground Loop | GEOSTAR | ZS030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3706382 |  | Ground Loop | GEOSTAR | ZS030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3706383 |  | Ground Loop | GEOSTAR | ZS030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
3706391 |  | Ground Loop | GEOSTAR | ZS042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3706392 |  | Ground Loop | GEOSTAR | ZS042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3706393 |  | Ground Loop | GEOSTAR | ZS042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
3706394 |  | Ground Loop | GEOSTAR | ZS048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3706395 |  | Ground Loop | GEOSTAR | ZS048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3706396 |  | Ground Loop | GEOSTAR | ZS048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125 | No
3706397 |  | Ground Loop | GEOSTAR | ZS060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3706398 |  | Ground Loop | GEOSTAR | ZS060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3706399 |  | Ground Loop | GEOSTAR | ZS060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075 | No
3811559 |  | Ground Loop | WaterFurnace | USV/USH024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3811671 |  | Ground Loop | WaterFurnace | USV/USH024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
3811673 |  | Ground Loop | WaterFurnace | USV/USH024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4236565 |  | Ground Loop | DAIKIN | WVFW1030*E***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583 | No
4236634 |  | Ground Loop | DAIKIN | WVFW1030*F***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583 | No
4236635 |  | Ground Loop | DAIKIN | WVFW1030*J***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583 | No
4504310 |  | Ground Loop | BOSCH-GEO | BP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
4509712 |  | Ground Loop | BOSCH-GEO | BP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
4510474 |  | Ground Loop | BOSCH-GEO | BP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
4547265 |  | Ground Loop | DUAL AIR | CFX024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | Yes
4547266 |  | Ground Loop | DUAL AIR | CFX031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | Yes
4547267 |  | Ground Loop | DUAL AIR | CFX036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | Yes
4547268 |  | Ground Loop | DUAL AIR | CFX041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | Yes
4547869 |  | Ground Loop | MIAMI HEAT PUMP | HPX024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | Yes
4547870 |  | Ground Loop | MIAMI HEAT PUMP | HPX031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | Yes
4547871 |  | Ground Loop | MIAMI HEAT PUMP | HPX036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | Yes
4547872 |  | Ground Loop | MIAMI HEAT PUMP | HPX041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | Yes
4651271 |  | Ground Loop | WaterFurnace | USH023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651272 |  | Ground Loop | WaterFurnace | USH023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651273 |  | Ground Loop | WaterFurnace | USH023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651274 |  | Ground Loop | WaterFurnace | USH023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
4651339 |  | Ground Loop | WaterFurnace | USV/USH024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651340 |  | Ground Loop | WaterFurnace | USV/USH024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651341 |  | Ground Loop | WaterFurnace | USV/USH024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651342 |  | Ground Loop | WaterFurnace | USV/USH024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
4651403 |  | Ground Loop | WaterFurnace | USV/USH030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
4651404 |  | Ground Loop | WaterFurnace | USV/USH030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
202434652 |  | Ground Loop | CARRIER | 50PCV024J/K*C3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
215685119 |  | Ground Loop | Dandelion Geo | DPG2048 |  | 50440 | 17.1 | 42300 | 4.7 | 4.2033 | Yes
215685120 |  | Ground Loop | Dandelion Geo | DPG2060 |  | 63000 | 17.6 | 54570 | 4.6 | 5.25 | Yes
8738051 |  | Ground Loop | GEOCOMFORT | GVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | Yes
8738052 |  | Ground Loop | HYDRON MODULE | HVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | Yes
8738053 |  | Ground Loop | TETCO | TVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | Yes
8738054 |  | Ground Loop | GEOCOMFORT | GVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738055 |  | Ground Loop | HYDRON MODULE | HVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738056 |  | Ground Loop | TETCO | TVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738057 |  | Ground Loop | GEOCOMFORT | GVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738058 |  | Ground Loop | HYDRON MODULE | HVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738059 |  | Ground Loop | TETCO | TVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738060 |  | Ground Loop | GEOCOMFORT | GVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738061 |  | Ground Loop | HYDRON MODULE | HVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738062 |  | Ground Loop | TETCO | TVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333 | No
8738067 |  | Ground Loop | GEOCOMFORT | GVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | Yes
8738068 |  | Ground Loop | HYDRON MODULE | HVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | Yes
8738069 |  | Ground Loop | TETCO | TVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | Yes
8738070 |  | Ground Loop | GEOCOMFORT | GVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738071 |  | Ground Loop | HYDRON MODULE | HVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738072 |  | Ground Loop | TETCO | TVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
8738073 |  | Ground Loop | GEOCOMFORT | GVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083 | No
216714645 |  | Ground Loop | GEOSTAR | G3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714646 |  | Ground Loop | GEOSTAR | G3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714647 |  | Ground Loop | GEOSTAR | G3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714648 |  | Ground Loop | GEOSTAR | G3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714649 |  | Ground Loop | GEOSTAR | G3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
216714656 |  | Ground Loop | GEOSTAR | G3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714657 |  | Ground Loop | GEOSTAR | G3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714658 |  | Ground Loop | GEOSTAR | G3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714659 |  | Ground Loop | GEOSTAR | G3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714660 |  | Ground Loop | GEOSTAR | G3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216714661 |  | Ground Loop | GEOSTAR | G3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
216726174 |  | Ground Loop | DAIKIN | WSRC007*A*G/J |  | 7400 | 19.4 | 4800 | 3.6 | 0.61667 | No
216726178 |  | Ground Loop | DAIKIN | WSRC009*A*G/J |  | 9100 | 18.9 | 6500 | 3.6 | 0.75833 | No
207335135 |  | Ground Loop | GEOSTAR | 101/102J018**1*(1,4)***** |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
207335136 |  | Ground Loop | GEOSTAR | 101/102J030**1*(1,4)***** |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
207335137 |  | Ground Loop | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | Yes
207335138 |  | Ground Loop | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
207335139 |  | Ground Loop | GEOSTAR | 101/102K048**1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
207335140 |  | Ground Loop | GEOSTAR | 101/102K060**1*(1,4)****** |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
207335141 |  | Ground Loop | GEOSTAR | 101/102J070**1*(1,4)***** |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
207335142 |  | Ground Loop | GEOSTAR | 101/102J026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
215399774 |  | Ground Loop | DAIKIN | WSMV015A1*G/J*T |  | 16300 | 21.12 | 11000 | 3.64 | 1.3583 | No
215399775 |  | Ground Loop | DAIKIN | WSMV015J1*G/J*T |  | 16300 | 21.12 | 11100 | 3.64 | 1.3583 | No
215399778 |  | Ground Loop | DAIKIN | WSMV015A1*G/J*C |  | 16300 | 21.12 | 11000 | 3.64 | 1.3583 | No
215399779 |  | Ground Loop | DAIKIN | WSMV015J1*G/J*C |  | 16300 | 21.12 | 11100 | 3.64 | 1.3583 | No
215399788 |  | Ground Loop | DAIKIN | WSMV024J1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
215399789 |  | Ground Loop | DAIKIN | WSMV024K3*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
215399792 |  | Ground Loop | DAIKIN | WSMV024J1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215399793 |  | Ground Loop | DAIKIN | WSMV024K3*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215399796 |  | Ground Loop | DAIKIN | WSMV024J1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215399797 |  | Ground Loop | DAIKIN | WSMV024K3*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
215399812 |  | Ground Loop | DAIKIN | WSMV036J1*G/J*P |  | 37600 | 18.26 | 28000 | 3.6 | 3.1333 | No
215399816 |  | Ground Loop | DAIKIN | WSMV036J1*G/J*T |  | 37500 | 18.76 | 28000 | 3.72 | 3.125 | No
215399817 |  | Ground Loop | DAIKIN | WSMV036K3*G/J*T |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917 | No
215399820 |  | Ground Loop | DAIKIN | WSMV036J1*G/J*C |  | 37500 | 18.76 | 28000 | 3.72 | 3.125 | No
202434486 |  | Ground Loop | BOSCH | SV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434487 |  | Ground Loop | BOSCH | SV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434492 |  | Ground Loop | BOSCH | SV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434493 |  | Ground Loop | BOSCH | SV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434494 |  | Ground Loop | BOSCH | SV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434495 |  | Ground Loop | BOSCH | SV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434500 |  | Ground Loop | BOSCH | SV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434501 |  | Ground Loop | BOSCH | SV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434502 |  | Ground Loop | BOSCH | SV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434503 |  | Ground Loop | BOSCH | SV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434508 |  | Ground Loop | BOSCH | SV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434509 |  | Ground Loop | BOSCH | SV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
215268358 |  | Ground Loop | WaterFurnace | V3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268359 |  | Ground Loop | WaterFurnace | V3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268365 |  | Ground Loop | WaterFurnace | V3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268366 |  | Ground Loop | WaterFurnace | V3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268367 |  | Ground Loop | WaterFurnace | V3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268368 |  | Ground Loop | WaterFurnace | V3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268369 |  | Ground Loop | WaterFurnace | V3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268664 |  | Ground Loop | WaterFurnace | V5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
215268665 |  | Ground Loop | WaterFurnace | V5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
215268666 |  | Ground Loop | WaterFurnace | V5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
215268667 |  | Ground Loop | WaterFurnace | V5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268668 |  | Ground Loop | WaterFurnace | V5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268669 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268670 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268671 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268672 |  | Ground Loop | WaterFurnace | V5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268673 |  | Ground Loop | WaterFurnace | V5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268675 |  | Ground Loop | WaterFurnace | V5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
215268676 |  | Ground Loop | WaterFurnace | V5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
215268677 |  | Ground Loop | WaterFurnace | V5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
215268678 |  | Ground Loop | WaterFurnace | V5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
215268679 |  | Ground Loop | WaterFurnace | V5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
215268680 |  | Ground Loop | WaterFurnace | V5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
215268681 |  | Ground Loop | WaterFurnace | V5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
215268682 |  | Ground Loop | WaterFurnace | V5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268683 |  | Ground Loop | WaterFurnace | V5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268684 |  | Ground Loop | WaterFurnace | V5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268685 |  | Ground Loop | WaterFurnace | V5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268686 |  | Ground Loop | WaterFurnace | V5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268687 |  | Ground Loop | WaterFurnace | V5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268688 |  | Ground Loop | WaterFurnace | V5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
215268689 |  | Ground Loop | WaterFurnace | V5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268690 |  | Ground Loop | WaterFurnace | V5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268691 |  | Ground Loop | WaterFurnace | V5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268692 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268693 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268694 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268695 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268696 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268697 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268698 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268699 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268700 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268701 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
217351788 |  | Ground Loop | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
202147015 |  | Ground Loop | TETCO | TZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147016 |  | Ground Loop | TETCO | TZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147017 |  | Ground Loop | TETCO | TZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147018 |  | Ground Loop | GEOCOMFORT | GZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | Yes
202147019 |  | Ground Loop | GEOCOMFORT | GZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147020 |  | Ground Loop | GEOCOMFORT | GZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147021 |  | Ground Loop | GEOCOMFORT | GZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147022 |  | Ground Loop | GEOCOMFORT | GZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | Yes
202147023 |  | Ground Loop | GEOCOMFORT | GZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147024 |  | Ground Loop | HYDRON MODULE | HZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | Yes
202147025 |  | Ground Loop | HYDRON MODULE | HZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147026 |  | Ground Loop | HYDRON MODULE | HZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147027 |  | Ground Loop | HYDRON MODULE | HZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147028 |  | Ground Loop | HYDRON MODULE | HZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | Yes
202147029 |  | Ground Loop | HYDRON MODULE | HZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147030 |  | Ground Loop | TETCO | TZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | Yes
202147031 |  | Ground Loop | TETCO | TZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147032 |  | Ground Loop | TETCO | TZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147033 |  | Ground Loop | TETCO | TZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425 | No
202147034 |  | Ground Loop | TETCO | TZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | Yes
202147035 |  | Ground Loop | TETCO | TZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147040 |  | Ground Loop | GEOCOMFORT | GZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | Yes
202147041 |  | Ground Loop | GEOCOMFORT | GZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147042 |  | Ground Loop | GEOCOMFORT | GZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147047 |  | Ground Loop | HYDRON MODULE | HZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | Yes
202147048 |  | Ground Loop | HYDRON MODULE | HZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147049 |  | Ground Loop | HYDRON MODULE | HZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147054 |  | Ground Loop | TETCO | TZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | Yes
202147055 |  | Ground Loop | TETCO | TZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
202147056 |  | Ground Loop | TETCO | TZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083 | No
206726680 |  | Ground Loop | WaterFurnace | UVV/UVH024**0*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125 | No
206726691 |  | Ground Loop | WaterFurnace | UVV/UVH024**3*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125 | No
206726692 |  | Ground Loop | WaterFurnace | UVV/UVH024**4*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125 | No
206726812 |  | Ground Loop | GEOCOMFORT | GBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | Yes
206726813 |  | Ground Loop | GEOCOMFORT | GBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
206726814 |  | Ground Loop | HYDRON MODULE | HBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | Yes
206726815 |  | Ground Loop | HYDRON MODULE | HBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
206726816 |  | Ground Loop | TETCO | TBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | Yes
206726817 |  | Ground Loop | TETCO | TBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
206726818 |  | Ground Loop | GEOCOMFORT | GBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
206726819 |  | Ground Loop | GEOCOMFORT | GBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | No
206726820 |  | Ground Loop | HYDRON MODULE | HBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
206726821 |  | Ground Loop | HYDRON MODULE | HBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | No
206726822 |  | Ground Loop | TETCO | TBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417 | No
206726823 |  | Ground Loop | TETCO | TBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | No
206726824 |  | Ground Loop | GEOCOMFORT | GBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | Yes
206726825 |  | Ground Loop | GEOCOMFORT | GBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
206726826 |  | Ground Loop | HYDRON MODULE | HBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333 | Yes
218157883 |  | Ground Loop | YORK | Y5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | Yes
218157884 |  | Ground Loop | YORK | Y5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | Yes
218157885 |  | Ground Loop | YORK | Y5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | Yes
218157886 |  | Ground Loop | YORK | Y5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | Yes
218157887 |  | Ground Loop | YORK | Y5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | Yes
218157888 |  | Ground Loop | YORK | Y5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | Yes
218157889 |  | Ground Loop | YORK | Y5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | Yes
218157890 |  | Ground Loop | YORK | Y5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | Yes
218157898 |  | Ground Loop | YORK | Y5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
218157899 |  | Ground Loop | YORK | Y5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
218157900 |  | Ground Loop | YORK | Y5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
218157901 |  | Ground Loop | YORK | Y5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
218157902 |  | Ground Loop | YORK | Y5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
9114310 |  | Ground Loop | HYDRON MODULE | HZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114311 |  | Ground Loop | TETCO | TZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114312 |  | Ground Loop | GEOCOMFORT | GZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114313 |  | Ground Loop | HYDRON MODULE | HZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114314 |  | Ground Loop | TETCO | TZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114315 |  | Ground Loop | GEOCOMFORT | GZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114316 |  | Ground Loop | HYDRON MODULE | HZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114317 |  | Ground Loop | TETCO | TZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114322 |  | Ground Loop | GEOCOMFORT | GZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | Yes
9114323 |  | Ground Loop | HYDRON MODULE | HZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | Yes
9114324 |  | Ground Loop | TETCO | TZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | Yes
9114325 |  | Ground Loop | GEOCOMFORT | GZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114326 |  | Ground Loop | HYDRON MODULE | HZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114327 |  | Ground Loop | TETCO | TZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114328 |  | Ground Loop | GEOCOMFORT | GZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114329 |  | Ground Loop | HYDRON MODULE | HZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9114330 |  | Ground Loop | TETCO | TZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667 | No
9850201 |  | Ground Loop | DAIKIN | WVFW1030*K***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583 | No
9910449 |  | Ground Loop | GEOCOMFORT | GZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | Yes
9910450 |  | Ground Loop | HYDRON MODULE | HZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | Yes
9910451 |  | Ground Loop | TETCO | TZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | Yes
9910452 |  | Ground Loop | GEOCOMFORT | GZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | No
9910453 |  | Ground Loop | HYDRON MODULE | HZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | No
9910454 |  | Ground Loop | TETCO | TZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333 | No
9910540 |  | Ground Loop | GEOCOMFORT | GZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | Yes
9910541 |  | Ground Loop | HYDRON MODULE | HZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | Yes
9910542 |  | Ground Loop | TETCO | TZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | Yes
9910543 |  | Ground Loop | GEOCOMFORT | GZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | No
9910544 |  | Ground Loop | HYDRON MODULE | HZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083 | No
218471584 |  | Ground Loop | YORK | AE072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218471585 |  | Ground Loop | YORK | AE072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218471586 |  | Ground Loop | YORK | AE096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
218471587 |  | Ground Loop | YORK | AE096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
202434155 |  | Ground Loop | BOSCH | LV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434156 |  | Ground Loop | BOSCH | LV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434157 |  | Ground Loop | BOSCH | LV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434161 |  | Ground Loop | BOSCH | LV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434162 |  | Ground Loop | BOSCH | LV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434163 |  | Ground Loop | BOSCH | LV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434167 |  | Ground Loop | BOSCH | LV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434168 |  | Ground Loop | BOSCH | LV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434169 |  | Ground Loop | BOSCH | LV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434173 |  | Ground Loop | BOSCH | LV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434174 |  | Ground Loop | BOSCH | LV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434175 |  | Ground Loop | BOSCH | LV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
201756620 |  | Ground Loop | NORTHERN HEAT PUMP | RA-VE-041-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175 | No
201756621 |  | Ground Loop | NORTHSTAR SERIES | RA-VE-041-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175 | No
201756622 |  | Ground Loop | NORTHERN HEAT PUMP | RA-VE-053-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833 | No
201756623 |  | Ground Loop | NORTHSTAR SERIES | RA-VE-053-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833 | No
201864513 |  | Ground Loop | GEOCOMFORT | GZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864514 |  | Ground Loop | HYDRON MODULE | HZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864515 |  | Ground Loop | TETCO | TZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864519 |  | Ground Loop | GEOCOMFORT | GZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864521 |  | Ground Loop | HYDRON MODULE | HZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201864523 |  | Ground Loop | TETCO | TZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | No
201907610 |  | Ground Loop | WaterFurnace | URS036*0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907611 |  | Ground Loop | WaterFurnace | URS036*0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907612 |  | Ground Loop | WaterFurnace | URS036*0*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907613 |  | Ground Loop | WaterFurnace | URS036*3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
206346978 |  | Ground Loop | DAIKIN | WVFW*060*E***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
206346979 |  | Ground Loop | DAIKIN | WVFW*060*F***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
206346980 |  | Ground Loop | DAIKIN | WVFW*060*K***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
206347002 |  | Ground Loop | DAIKIN | WCCW*030*E***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
206347003 |  | Ground Loop | DAIKIN | WCCW*030*F***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
217642915 |  | Ground Loop | GeoSmart Energy | S3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642916 |  | Ground Loop | GeoSmart Energy | S3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642917 |  | Ground Loop | GeoSmart Energy | S3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642918 |  | Ground Loop | GeoSmart Energy | S3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642919 |  | Ground Loop | GeoSmart Energy | S3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642920 |  | Ground Loop | GeoSmart Energy | S3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642921 |  | Ground Loop | GeoSmart Energy | S3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642922 |  | Ground Loop | GeoSmart Energy | S3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
217642928 |  | Ground Loop | GeoSmart Energy | S3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642929 |  | Ground Loop | GeoSmart Energy | S3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642930 |  | Ground Loop | GeoSmart Energy | S3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642931 |  | Ground Loop | GeoSmart Energy | S3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642932 |  | Ground Loop | GeoSmart Energy | S3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
7414470 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
7414553 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7414651 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7414828 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
7414896 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7415098 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7415209 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
7415301 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7415373 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
7415455 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
7415878 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7416559 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7416688 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
7416782 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7416889 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7416979 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
7417060 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7417146 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7417250 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
7417329 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7417419 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
7417586 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417698 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417776 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417867 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417918 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7417992 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7418047 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7418154 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
7418360 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418435 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418635 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418715 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418887 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7418965 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
7419321 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419403 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419527 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419618 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419733 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7419797 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7421327 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421397 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421438 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421969 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
7421970 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
215893695 |  | Ground Loop | DUAL AIR | CFF031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | No
215893697 |  | Ground Loop | DUAL AIR | CFF036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | No
215893699 |  | Ground Loop | DUAL AIR | CFF041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | No
215893703 |  | Ground Loop | MIAMI HEAT PUMP | HPF024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | No
215893704 |  | Ground Loop | MIAMI HEAT PUMP | HPF031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | No
215893706 |  | Ground Loop | MIAMI HEAT PUMP | HPF036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | No
215893707 |  | Ground Loop | MIAMI HEAT PUMP | HPF041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | No
215893711 |  | Ground Loop | DUAL AIR | CFF049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833 | No
215893713 |  | Ground Loop | MIAMI HEAT PUMP | HPF049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833 | No
216014181 |  | Ground Loop | RHEEM | RPVV/H/D036D |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | Yes
216054107 |  | Ground Loop | WaterFurnace | W5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667 | Yes
216054108 |  | Ground Loop | WaterFurnace | W5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917 | Yes
216054109 |  | Ground Loop | WaterFurnace | W5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083 | Yes
216054110 |  | Ground Loop | WaterFurnace | W5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583 | Yes
216054475 |  | Ground Loop | GEOCOMFORT | GBS018* | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
216054476 |  | Ground Loop | GEOCOMFORT | GBT024* | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
216054477 |  | Ground Loop | GEOCOMFORT | GBT036* | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
216054478 |  | Ground Loop | GEOCOMFORT | GBT048* | EAD048 | 47800 | 17.3 | 41000 | 3.6 | 3.9833 | Yes
216054479 |  | Ground Loop | GEOCOMFORT | GVS009* |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833 | Yes
216054480 |  | Ground Loop | GEOCOMFORT | GVS012* |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167 | Yes
216054481 |  | Ground Loop | GEOCOMFORT | GVS018* |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | Yes
215851830 |  | Ground Loop | DAIKIN | WSTV060L3*G/J*C |  | 63100 | 19.01 | 46800 | 3.98 | 5.2583 | No
215852848 |  | Ground Loop | DAIKIN | WSTH024E1*G/J*C |  | 25100 | 19.92 | 17200 | 3.92 | 2.0917 | No
215852849 |  | Ground Loop | DAIKIN | WSTH024F3*G/J*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917 | No
215852852 |  | Ground Loop | DAIKIN | WSTH030E1*G/J*C |  | 32700 | 19.69 | 20600 | 3.75 | 2.725 | No
215852853 |  | Ground Loop | DAIKIN | WSTH030F3*G/J*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725 | No
215852856 |  | Ground Loop | DAIKIN | WSTH036E1*G/J*C |  | 38700 | 20.64 | 25900 | 3.75 | 3.225 | No
215852857 |  | Ground Loop | DAIKIN | WSTH036F3*G/J*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225 | No
215852860 |  | Ground Loop | DAIKIN | WSTH042E1*G/J*C |  | 45900 | 20.06 | 28400 | 3.7 | 3.825 | No
215852861 |  | Ground Loop | DAIKIN | WSTH042F3*G/J*C |  | 45900 | 19.66 | 28400 | 3.63 | 3.825 | No
215852864 |  | Ground Loop | DAIKIN | WSTH060E1*G/J*C |  | 61600 | 19 | 44200 | 3.7 | 5.1333 | No
215852865 |  | Ground Loop | DAIKIN | WSTH060F3*G/J*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333 | No
215852872 |  | Ground Loop | DAIKIN | WSTV030E1*G/J*C |  | 32200 | 19.48 | 20800 | 3.78 | 2.6833 | No
215852873 |  | Ground Loop | DAIKIN | WSTV030F3*G/J*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833 | No
215852876 |  | Ground Loop | DAIKIN | WSTV036E1*G/J*C |  | 39100 | 21.12 | 25600 | 3.68 | 3.2583 | No
215852877 |  | Ground Loop | DAIKIN | WSTV036F3*G/J*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583 | No
215852880 |  | Ground Loop | DAIKIN | WSTV042E1*G/J*C |  | 44800 | 19.54 | 27600 | 3.74 | 3.7333 | No
215852881 |  | Ground Loop | DAIKIN | WSTV042F3*G/J*C |  | 44800 | 19.15 | 27600 | 3.66 | 3.7333 | No
215852886 |  | Ground Loop | DAIKIN | WSTV060E1*G/J*C |  | 63100 | 19.6 | 46800 | 4.1 | 5.2583 | No
215852887 |  | Ground Loop | DAIKIN | WSTV060F3*G/J*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583 | No
215866226 |  | Ground Loop | ClimateMaster | SMS15A*L |  | 14800 | 17.5 | 11000 | 3.6 | 1.2333 | No
215866227 |  | Ground Loop | ClimateMaster | SMT15A*L |  | 15400 | 18.8 | 11000 | 3.7 | 1.2833 | No
215866229 |  | Ground Loop | ClimateMaster | SMT18A*L |  | 18900 | 17.8 | 13500 | 3.6 | 1.575 | No
215866231 |  | Ground Loop | ClimateMaster | SMT24A*L |  | 25900 | 20.5 | 18000 | 3.7 | 2.1583 | No
215866233 |  | Ground Loop | ClimateMaster | SMT30A*L |  | 30000 | 19 | 22300 | 3.7 | 2.5 | No
218338480 |  | Ground Loop | YORK | Y5AV084*D4**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
218338486 |  | Ground Loop | YORK | Y5AV084*D3**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
215268740 |  | Ground Loop | WaterFurnace | V5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268741 |  | Ground Loop | WaterFurnace | V5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268742 |  | Ground Loop | WaterFurnace | V5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268743 |  | Ground Loop | WaterFurnace | V5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268744 |  | Ground Loop | WaterFurnace | V5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268745 |  | Ground Loop | WaterFurnace | V5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268746 |  | Ground Loop | WaterFurnace | V5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268747 |  | Ground Loop | WaterFurnace | V5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268748 |  | Ground Loop | WaterFurnace | V5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268749 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268750 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268751 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268752 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268753 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268754 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268755 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268756 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268757 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216979888 |  | Ground Loop | TEMPSTAR | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979889 |  | Ground Loop | COMFORTMAKER | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979890 |  | Ground Loop | DAY & NIGHT | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979891 |  | Ground Loop | HEIL | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979892 |  | Ground Loop | ARCOAIRE | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979893 |  | Ground Loop | KEEPRITE | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979894 |  | Ground Loop | TEMPSTAR | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979895 |  | Ground Loop | COMFORTMAKER | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216979896 |  | Ground Loop | DAY & NIGHT | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
217014524 |  | Ground Loop | CARRIER | GCA72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014525 |  | Ground Loop | BRYANT | GCA72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014528 |  | Ground Loop | CARRIER | GCA72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014529 |  | Ground Loop | BRYANT | GCA72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014532 |  | Ground Loop | HEIL | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014533 |  | Ground Loop | ARCOAIRE | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014534 |  | Ground Loop | KEEPRITE | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014535 |  | Ground Loop | TEMPSTAR | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014536 |  | Ground Loop | COMFORTMAKER | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014537 |  | Ground Loop | DAY & NIGHT | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014544 |  | Ground Loop | HEIL | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014545 |  | Ground Loop | ARCOAIRE | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014546 |  | Ground Loop | KEEPRITE | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014547 |  | Ground Loop | TEMPSTAR | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014548 |  | Ground Loop | COMFORTMAKER | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
217014549 |  | Ground Loop | DAY & NIGHT | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | Yes
215746915 |  | Ground Loop | TRANE | GSK036A3 |  | 41280 | 22.1 | 29804 | 4.28 | 3.44 | No
215746916 |  | Ground Loop | TRANE | GSK048A3 |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966 | No
215746918 |  | Ground Loop | TRANE | GSK060A3 |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603 | No
215746919 |  | Ground Loop | TRANE | GSK072A3 |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341 | No
215746920 |  | Ground Loop | TRANE | GSK090A3 |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743 | No
215746921 |  | Ground Loop | TRANE | GSK102A3 |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454 | No
215746922 |  | Ground Loop | TRANE | GSK120A3 |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112 | No
215746923 |  | Ground Loop | TRANE | GSK036A4 |  | 41280 | 22.1 | 29804 | 4.28 | 3.44 | No
215746924 |  | Ground Loop | TRANE | GSK036AW |  | 41280 | 22.1 | 29804 | 4.28 | 3.44 | No
215746925 |  | Ground Loop | TRANE | GSK048A4 |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966 | No
215746926 |  | Ground Loop | TRANE | GSK048AW |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966 | No
215746927 |  | Ground Loop | TRANE | GSK060A4 |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603 | No
215746928 |  | Ground Loop | TRANE | GSK060AW |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603 | No
215746929 |  | Ground Loop | TRANE | GSK072A4 |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341 | No
215746930 |  | Ground Loop | TRANE | GSK072AW |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341 | No
215746931 |  | Ground Loop | TRANE | GSK090A4 |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743 | No
215746932 |  | Ground Loop | TRANE | GSK090AW |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743 | No
215746933 |  | Ground Loop | TRANE | GSK102A4 |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454 | No
215746934 |  | Ground Loop | TRANE | GSK102AW |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454 | No
215746935 |  | Ground Loop | TRANE | GSK120A4 |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112 | No
215746936 |  | Ground Loop | TRANE | GSK120AW |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112 | No
218471911 |  | Ground Loop | YORK | AZ060-1CSC-*****A | JDE60F5XX2DS1 | 60800 | 17.7 | 50000 | 4 | 5.0667 | No
218471912 |  | Ground Loop | YORK | AZ060-1CSN-*****A | JDE60F5XX2DS1 | 60600 | 17.5 | 51200 | 4.2 | 5.05 | No
218471913 |  | Ground Loop | YORK | QZ060-1CSC-*****A | JDE60F5XX2DS1 | 60800 | 17.7 | 50000 | 4 | 5.0667 | Yes
218471914 |  | Ground Loop | YORK | QZ060-1CSN-*****A | JDE60F5XX2DS1 | 60600 | 17.5 | 51200 | 4.2 | 5.05 | Yes
218471921 |  | Ground Loop | YORK | AE072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
218471922 |  | Ground Loop | YORK | AE096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
217754427 |  | Ground Loop | DAIKIN | WSSV024K1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
217754429 |  | Ground Loop | DAIKIN | WSSV024F1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
217754430 |  | Ground Loop | DAIKIN | WSSV024K1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
217754432 |  | Ground Loop | DAIKIN | WSSV030F1*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
217754433 |  | Ground Loop | DAIKIN | WSSV030K1*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
217754435 |  | Ground Loop | DAIKIN | WSSV030F1*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
217754436 |  | Ground Loop | DAIKIN | WSSV030K1*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
217754438 |  | Ground Loop | DAIKIN | WSSV036F1*H*T |  | 40500 | 21.18 | 27600 | 3.83 | 3.375 | No
217754439 |  | Ground Loop | DAIKIN | WSSV036K1*H*T |  | 40500 | 21.09 | 27600 | 3.83 | 3.375 | No
217754441 |  | Ground Loop | DAIKIN | WSSV036F1*H*C |  | 40500 | 21.18 | 27600 | 3.83 | 3.375 | No
217754442 |  | Ground Loop | DAIKIN | WSSV036K1*H*C |  | 40500 | 21.09 | 27600 | 3.83 | 3.375 | No
217754444 |  | Ground Loop | DAIKIN | WSSV042F1*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217754445 |  | Ground Loop | DAIKIN | WSSV042K1*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217754447 |  | Ground Loop | DAIKIN | WSSV042F1*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217754448 |  | Ground Loop | DAIKIN | WSSV042K1*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587 | No
217754450 |  | Ground Loop | DAIKIN | WSSV048F1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754451 |  | Ground Loop | DAIKIN | WSSV048K1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754452 |  | Ground Loop | DAIKIN | WSSV048L1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754454 |  | Ground Loop | DAIKIN | WSSV048F1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754455 |  | Ground Loop | DAIKIN | WSSV048K1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754456 |  | Ground Loop | DAIKIN | WSSV048L1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35 | No
217754458 |  | Ground Loop | DAIKIN | WSSV060F1*H*T |  | 66300 | 19.8 | 48800 | 3.96 | 5.525 | No
217754459 |  | Ground Loop | DAIKIN | WSSV060K1*H*T |  | 66300 | 19.8 | 48800 | 3.92 | 5.525 | No
217754460 |  | Ground Loop | DAIKIN | WSSV060L1*H*T |  | 66300 | 19.4 | 48800 | 3.88 | 5.525 | No
217754462 |  | Ground Loop | DAIKIN | WSSV060F1*H*C |  | 66300 | 19.8 | 48800 | 3.96 | 5.525 | No
217754463 |  | Ground Loop | DAIKIN | WSSV060K1*H*C |  | 66300 | 19.8 | 48800 | 3.92 | 5.525 | No
217754464 |  | Ground Loop | DAIKIN | WSSV060L1*H*C |  | 66300 | 19.4 | 48800 | 3.88 | 5.525 | No
217754466 |  | Ground Loop | DAIKIN | WSSV070F1*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
217754467 |  | Ground Loop | DAIKIN | WSSV070K1*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
217754468 |  | Ground Loop | DAIKIN | WSSV070L1*H*T |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833 | No
207177431 |  | Ground Loop | TRANE | GEVG009A |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167 | No
207177432 |  | Ground Loop | TRANE | GEVG0097 |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167 | No
207177433 |  | Ground Loop | TRANE | GEVG012A |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083 | No
207177434 |  | Ground Loop | TRANE | GEVG0127 |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083 | No
207177435 |  | Ground Loop | TRANE | GEVG015A |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917 | No
202434375 |  | Ground Loop | FHP | LV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434380 |  | Ground Loop | FHP | LV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434381 |  | Ground Loop | FHP | LV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434382 |  | Ground Loop | FHP | LV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434383 |  | Ground Loop | FHP | LV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434388 |  | Ground Loop | FHP | LV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434389 |  | Ground Loop | FHP | LV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434390 |  | Ground Loop | FHP | LV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434391 |  | Ground Loop | FHP | LV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434396 |  | Ground Loop | FHP | LV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434397 |  | Ground Loop | FHP | LV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207177447 |  | Ground Loop | TRANE | GEVG036A |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
207177448 |  | Ground Loop | TRANE | GEVG036B |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
207177449 |  | Ground Loop | TRANE | GEVG0364 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
207177450 |  | Ground Loop | TRANE | GEVG0367 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
207177460 |  | Ground Loop | TRANE | EXVG009A |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167 | No
207177461 |  | Ground Loop | TRANE | EXVG0097 |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167 | No
207177462 |  | Ground Loop | TRANE | EXVG012A |  | 12300 | 19.5 | 9300 | 4 | 1.025 | No
207177463 |  | Ground Loop | TRANE | EXVG0127 |  | 12300 | 19.5 | 9300 | 4 | 1.025 | No
207177464 |  | Ground Loop | TRANE | EXVG015A |  | 15800 | 19 | 12100 | 3.8 | 1.3167 | No
207177465 |  | Ground Loop | TRANE | EXVG0157 |  | 15800 | 19 | 12100 | 3.8 | 1.3167 | No
207177466 |  | Ground Loop | TRANE | EXVG018A |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333 | No
207177467 |  | Ground Loop | TRANE | EXVG0187 |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333 | No
207177468 |  | Ground Loop | TRANE | EXVG024A |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
207177469 |  | Ground Loop | TRANE | EXVG024B |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
207177470 |  | Ground Loop | TRANE | EXVG0244 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
207177471 |  | Ground Loop | TRANE | EXVG0247 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
207177472 |  | Ground Loop | TRANE | EXVG030A |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
207177473 |  | Ground Loop | TRANE | EXVG030B |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
207177474 |  | Ground Loop | TRANE | EXVG0304 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
207177475 |  | Ground Loop | TRANE | EXVG0307 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
207177476 |  | Ground Loop | TRANE | EXVG036A |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
207177477 |  | Ground Loop | TRANE | EXVG036B |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
207177478 |  | Ground Loop | TRANE | EXVG0364 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
207177479 |  | Ground Loop | TRANE | EXVG0367 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
207177480 |  | Ground Loop | TRANE | EXVG042A |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
207177481 |  | Ground Loop | TRANE | EXVG042B |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
207177482 |  | Ground Loop | TRANE | EXVG0424 |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
207177483 |  | Ground Loop | TRANE | EXVG048A |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
207177484 |  | Ground Loop | TRANE | EXVG048B |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
207177485 |  | Ground Loop | TRANE | EXVG0484 |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
207177486 |  | Ground Loop | TRANE | EXVG060A |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
207177487 |  | Ground Loop | TRANE | EXVG060B |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
207177488 |  | Ground Loop | TRANE | EXVG0604 |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
207177489 |  | Ground Loop | TRANE | EXVG070A |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
207177490 |  | Ground Loop | TRANE | EXVG070B |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
207177491 |  | Ground Loop | TRANE | EXVG0704 |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
207177492 |  | Ground Loop | TRANE | DXVG024A |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
207177493 |  | Ground Loop | TRANE | DXVG024B |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
207177494 |  | Ground Loop | TRANE | DXVG0244 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
207177495 |  | Ground Loop | TRANE | DXVG0247 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
207177496 |  | Ground Loop | TRANE | DXVG036A |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
207177497 |  | Ground Loop | TRANE | DXVG036B |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
207177498 |  | Ground Loop | TRANE | DXVG0364 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
207177499 |  | Ground Loop | TRANE | DXVG0367 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
207177500 |  | Ground Loop | TRANE | DXVG048A |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
207177501 |  | Ground Loop | TRANE | DXVG048B |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
207177502 |  | Ground Loop | TRANE | DXVG0484 |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
202146914 |  | Ground Loop | GEOCOMFORT | GZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | No
202146915 |  | Ground Loop | GEOCOMFORT | GZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | Yes
202146916 |  | Ground Loop | HYDRON MODULE | HZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | Yes
202146917 |  | Ground Loop | HYDRON MODULE | HZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | No
202146918 |  | Ground Loop | HYDRON MODULE | HZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | Yes
202146919 |  | Ground Loop | TETCO | TZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | Yes
202146920 |  | Ground Loop | TETCO | TZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083 | No
202146921 |  | Ground Loop | TETCO | TZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | Yes
202146922 |  | Ground Loop | GEOCOMFORT | GZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | Yes
202146923 |  | Ground Loop | GEOCOMFORT | GZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | No
202146924 |  | Ground Loop | GEOCOMFORT | GZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | Yes
202146925 |  | Ground Loop | GEOCOMFORT | GZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | No
202146926 |  | Ground Loop | HYDRON MODULE | HZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | Yes
202146927 |  | Ground Loop | HYDRON MODULE | HZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | No
202146928 |  | Ground Loop | HYDRON MODULE | HZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | Yes
202146929 |  | Ground Loop | HYDRON MODULE | HZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | No
202146930 |  | Ground Loop | TETCO | TZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | Yes
202146931 |  | Ground Loop | TETCO | TZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917 | No
202146932 |  | Ground Loop | TETCO | TZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | Yes
202146933 |  | Ground Loop | TETCO | TZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833 | No
202146936 |  | Ground Loop | GEOCOMFORT | GZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | Yes
202146939 |  | Ground Loop | HYDRON MODULE | HZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | Yes
202146942 |  | Ground Loop | TETCO | TZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | Yes
202146943 |  | Ground Loop | GEOCOMFORT | GZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | Yes
202146944 |  | Ground Loop | GEOCOMFORT | GZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146945 |  | Ground Loop | GEOCOMFORT | GZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146946 |  | Ground Loop | GEOCOMFORT | GZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146947 |  | Ground Loop | GEOCOMFORT | GZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
206438813 |  | Ground Loop | FHP | EP012-1VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438814 |  | Ground Loop | FHP | EP012-1HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438817 |  | Ground Loop | FHP | EP012-0VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438818 |  | Ground Loop | FHP | EP012-2VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438819 |  | Ground Loop | FHP | EP012-0HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438820 |  | Ground Loop | FHP | EP012-2HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438871 |  | Ground Loop | CARRIER | 50PSH/V009***3/CA* |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438872 |  | Ground Loop | CARRIER | 50PSH/V009***4/DA* |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438873 |  | Ground Loop | CARRIER | 50PSH/V012***3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438874 |  | Ground Loop | CARRIER | 50PSH/V015***3/CA* |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438875 |  | Ground Loop | CARRIER | 50PSH/V015***4/DA* |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438876 |  | Ground Loop | CARRIER | 50PSH/V030***4/DA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438877 |  | Ground Loop | CARRIER | 50PSH/V030***6/FA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438878 |  | Ground Loop | CARRIER | 50PSH/V030***5/EA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438879 |  | Ground Loop | CARRIER | 50PSH/V030***3/CA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438880 |  | Ground Loop | CARRIER | 50PSH/V060***6/FA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438881 |  | Ground Loop | CARRIER | 50PSH/V060***5/EA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438882 |  | Ground Loop | CARRIER | 50PSH/V060***3/CA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438883 |  | Ground Loop | CARRIER | 50PSH/V070***3/CA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438884 |  | Ground Loop | CARRIER | 50PSH/V070***5/EA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438885 |  | Ground Loop | CARRIER | 50PSH/V070***6/FA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
218432051 |  | Ground Loop | UNILUX VHP | UZHP05L |  | 14600 | 17.1 | 10800 | 3.71 | 1.2167 | No
218432054 |  | Ground Loop | UNILUX VHP | UZHP10L |  | 30400 | 17.77 | 22400 | 3.61 | 2.5333 | No
218432055 |  | Ground Loop | UNILUX VHP | UZHP12L |  | 37400 | 18.72 | 25400 | 3.61 | 3.1167 | No
218433695 |  | Ground Loop | BOSCH-GEO | CP024-1CSC-*****A | BIVB-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | No
218433696 |  | Ground Loop | BOSCH-GEO | CP024-1CSN-*****A | BIVB-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | No
218433697 |  | Ground Loop | BOSCH-GEO | CP036-1CSC-*****A | BIVB-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | No
218433698 |  | Ground Loop | BOSCH-GEO | CP036-1CSN-*****A | BIVB-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | No
218433699 |  | Ground Loop | BOSCH-GEO | CP048-1CSC-*****A | BIVB-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | No
218433700 |  | Ground Loop | BOSCH-GEO | CP048-1CSN-*****A | BIVB-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | No
218433701 |  | Ground Loop | BOSCH-GEO | CP060-1CSC-*****A | BIVB-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | No
218433702 |  | Ground Loop | BOSCH-GEO | CP060-1CSN-*****A | BIVB-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | No
218433703 |  | Ground Loop | BOSCH-GEO | RP024-1CSC-*****A | BIVB-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | Yes
218433704 |  | Ground Loop | BOSCH-GEO | RP024-1CSN-*****A | BIVB-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | Yes
218433705 |  | Ground Loop | BOSCH-GEO | RP036-1CSC-*****A | BIVB-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | Yes
218433706 |  | Ground Loop | BOSCH-GEO | RP036-1CSN-*****A | BIVB-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | Yes
218433707 |  | Ground Loop | BOSCH-GEO | RP048-1CSC-*****A | BIVB-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | Yes
218433708 |  | Ground Loop | BOSCH-GEO | RP048-1CSN-*****A | BIVB-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | Yes
218433709 |  | Ground Loop | BOSCH-GEO | RP060-1CSC-*****A | BIVB-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | Yes
218433710 |  | Ground Loop | BOSCH-GEO | RP060-1CSN-*****A | BIVB-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | Yes
218433932 |  | Ground Loop | BOSCH | RP024-1CSC-*****A | BIVB-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | Yes
218433933 |  | Ground Loop | BOSCH | RP024-1CSN-*****A | BIVB-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | Yes
218433934 |  | Ground Loop | BOSCH | RP036-1CSC-*****A | BIVB-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | Yes
218433935 |  | Ground Loop | BOSCH | RP036-1CSN-*****A | BIVB-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | Yes
218433936 |  | Ground Loop | BOSCH | RP048-1CSC-*****A | BIVB-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | Yes
218433937 |  | Ground Loop | BOSCH | RP048-1CSN-*****A | BIVB-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | Yes
218433938 |  | Ground Loop | BOSCH | RP060-1CSC-*****A | BIVB-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | Yes
218433939 |  | Ground Loop | BOSCH | RP060-1CSN-*****A | BIVB-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | Yes
218433940 |  | Ground Loop | BOSCH | CP024-1CSC-*****A | BIVB-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | No
218433941 |  | Ground Loop | BOSCH | CP024-1CSN-*****A | BIVB-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | No
218433942 |  | Ground Loop | BOSCH | CP036-1CSC-*****A | BIVB-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | No
218433943 |  | Ground Loop | BOSCH | CP036-1CSN-*****A | BIVB-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | No
218433944 |  | Ground Loop | BOSCH | CP048-1CSC-*****A | BIVB-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | No
218433945 |  | Ground Loop | BOSCH | CP048-1CSN-*****A | BIVB-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | No
218433946 |  | Ground Loop | BOSCH | CP060-1CSC-*****A | BIVB-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | No
218433947 |  | Ground Loop | BOSCH | CP060-1CSN-*****A | BIVB-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | No
207200602 |  | Ground Loop | GeoSmart Energy | GTZ049*1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
207200603 |  | Ground Loop | GeoSmart Energy | GTS064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207200604 |  | Ground Loop | GeoSmart Energy | GTS064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
207200605 |  | Ground Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
207200606 |  | Ground Loop | GeoSmart Energy | GSZ042*1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
207200607 |  | Ground Loop | GeoSmart Energy | GTZ038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207200608 |  | Ground Loop | GeoSmart Energy | GTS038*1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207200609 |  | Ground Loop | GeoSmart Energy | GTS038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
207200613 |  | Ground Loop | GeoSmart Energy | QT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
207216511 |  | Ground Loop | GEOSTAR | GDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
207216512 |  | Ground Loop | GEOSTAR | GDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
207216513 |  | Ground Loop | GEOSTAR | GDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206347004 |  | Ground Loop | DAIKIN | WCCW*030*J***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
206347005 |  | Ground Loop | DAIKIN | WCCW*030*K***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
206347006 |  | Ground Loop | DAIKIN | WCCW*036*E***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
206347007 |  | Ground Loop | DAIKIN | WCCW*036*F***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
206347008 |  | Ground Loop | DAIKIN | WCCW*036*J***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
206347009 |  | Ground Loop | DAIKIN | WCCW*036*K***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
206347010 |  | Ground Loop | DAIKIN | WCCW*042*E***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
206347011 |  | Ground Loop | DAIKIN | WCCW*042*F***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
206347012 |  | Ground Loop | DAIKIN | WCCW*042*K***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
206347013 |  | Ground Loop | DAIKIN | WCCW*048*E***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
206347014 |  | Ground Loop | DAIKIN | WCCW*048*F***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
206347015 |  | Ground Loop | DAIKIN | WCCW*048*K***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
206347016 |  | Ground Loop | DAIKIN | WCCW*060*E***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
206347017 |  | Ground Loop | DAIKIN | WCCW*060*F***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
206347018 |  | Ground Loop | DAIKIN | WCCW*060*K***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
206347036 |  | Ground Loop | DAIKIN | WCCW*015*J***14* |  | 16800 | 20.8 | 11500 | 3.8 | 1.4 | No
206347038 |  | Ground Loop | DAIKIN | WCCW*015*E***14* |  | 17200 | 20.8 | 11500 | 4 | 1.4333 | No
202211066 |  | Ground Loop | WaterFurnace | URT096*3*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65 | No
202262237 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
202262238 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ042J1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
202272873 |  | Ground Loop | BOSCH-GEO | BP018-1VT*******C |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
202326797 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
202326829 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
202328436 |  | Ground Loop | BOSCH | BP018-1VT*******C |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
206900557 |  | Ground Loop | GEOSTAR | GDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900558 |  | Ground Loop | GEOSTAR | GDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900559 |  | Ground Loop | GEOSTAR | GDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900560 |  | Ground Loop | GEOSTAR | GDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900561 |  | Ground Loop | GEOSTAR | GDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900571 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900572 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900573 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900574 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900575 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900576 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900577 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900578 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900579 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
217351730 |  | Ground Loop | CARRIER | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
207348666 |  | Ground Loop | WaterFurnace | URS048*3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348667 |  | Ground Loop | WaterFurnace | URS048*3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348668 |  | Ground Loop | WaterFurnace | URS048*3*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348669 |  | Ground Loop | WaterFurnace | URS048*4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348670 |  | Ground Loop | WaterFurnace | URS048*4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348671 |  | Ground Loop | WaterFurnace | URS048*4*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348672 |  | Ground Loop | WaterFurnace | URS070*0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348673 |  | Ground Loop | WaterFurnace | URS070*0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348674 |  | Ground Loop | WaterFurnace | URS070*0*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348675 |  | Ground Loop | WaterFurnace | URS070*3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348676 |  | Ground Loop | WaterFurnace | URS070*3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348677 |  | Ground Loop | WaterFurnace | URS070*3*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348678 |  | Ground Loop | WaterFurnace | URS070*4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348679 |  | Ground Loop | WaterFurnace | URS070*4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348680 |  | Ground Loop | WaterFurnace | URS070*4*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
207348681 |  | Ground Loop | WaterFurnace | URS060*0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
202132024 |  | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-038-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175 | No
202132025 |  | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-050-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833 | No
202132026 |  | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-060-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15 | No
202146863 |  | Ground Loop | GEOCOMFORT | GZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | Yes
202146864 |  | Ground Loop | GEOCOMFORT | GZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146865 |  | Ground Loop | GEOCOMFORT | GZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146866 |  | Ground Loop | HYDRON MODULE | HZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | Yes
202146867 |  | Ground Loop | HYDRON MODULE | HZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146868 |  | Ground Loop | HYDRON MODULE | HZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146869 |  | Ground Loop | TETCO | TZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | Yes
202146870 |  | Ground Loop | TETCO | TZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146871 |  | Ground Loop | TETCO | TZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202146872 |  | Ground Loop | GEOCOMFORT | GZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | Yes
202146873 |  | Ground Loop | GEOCOMFORT | GZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146874 |  | Ground Loop | GEOCOMFORT | GZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146875 |  | Ground Loop | GEOCOMFORT | GZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146876 |  | Ground Loop | HYDRON MODULE | HZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | Yes
202146877 |  | Ground Loop | HYDRON MODULE | HZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146878 |  | Ground Loop | HYDRON MODULE | HZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146879 |  | Ground Loop | HYDRON MODULE | HZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146880 |  | Ground Loop | TETCO | TZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | Yes
202146881 |  | Ground Loop | TETCO | TZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146882 |  | Ground Loop | TETCO | TZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146883 |  | Ground Loop | TETCO | TZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | No
202146884 |  | Ground Loop | GEOCOMFORT | GZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | Yes
202146885 |  | Ground Loop | GEOCOMFORT | GZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146886 |  | Ground Loop | GEOCOMFORT | GZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146887 |  | Ground Loop | HYDRON MODULE | HZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | Yes
202146888 |  | Ground Loop | HYDRON MODULE | HZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146889 |  | Ground Loop | HYDRON MODULE | HZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
202146890 |  | Ground Loop | TETCO | TZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | Yes
202146891 |  | Ground Loop | TETCO | TZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | No
206438761 |  | Ground Loop | BOSCH | EP012-1HZ/VT*-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438762 |  | Ground Loop | BOSCH | EP015-1HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438763 |  | Ground Loop | BOSCH | EP060-1HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
206438764 |  | Ground Loop | BOSCH | EP070-1HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
206438781 |  | Ground Loop | FHP | EP009-1HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438782 |  | Ground Loop | FHP | EP009-2HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
206438783 |  | Ground Loop | FHP | EP012-1HZ/VT*-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438784 |  | Ground Loop | FHP | EP015-1HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438785 |  | Ground Loop | FHP | EP015-2HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
206438786 |  | Ground Loop | FHP | EP030-2HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438787 |  | Ground Loop | FHP | EP030-4HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
206438788 |  | Ground Loop | FHP | EP030-3HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
205973780 |  | Ground Loop | CENTURY | HEV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
205996643 |  | Ground Loop | Johnson Controls | JEV/H/D026B B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | No
205996644 |  | Ground Loop | Johnson Controls | JEV/H/D038B B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25 | No
205996645 |  | Ground Loop | Johnson Controls | JEV/H/D049B B |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | No
205996646 |  | Ground Loop | Johnson Controls | JEV/H/D064B B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | No
206185518 |  | Ground Loop | DAIKIN | WGCH015A1*G/J*T |  | 15300 | 18 | 10700 | 3.6 | 1.275 | No
206185519 |  | Ground Loop | DAIKIN | WGCH015A1*G/J*C |  | 15300 | 18 | 10700 | 3.6 | 1.275 | No
7170606 |  | Ground Loop | GEOCOMFORT | GVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | Yes
7170607 |  | Ground Loop | HYDRON MODULE | HVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | Yes
7170608 |  | Ground Loop | TETCO | TVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667 | Yes
7170609 |  | Ground Loop | GEOCOMFORT | GVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | Yes
7170610 |  | Ground Loop | HYDRON MODULE | HVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | Yes
7170611 |  | Ground Loop | TETCO | TVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083 | Yes
7170612 |  | Ground Loop | GEOCOMFORT | GVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | Yes
7170613 |  | Ground Loop | HYDRON MODULE | HVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | Yes
7170614 |  | Ground Loop | TETCO | TVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15 | Yes
203265288 |  | Ground Loop | BOSCH-GEO | SM048-1VT/CFC-*****A |  | 51300 | 18.15 | 36900 | 3.9 | 4.275 | Yes
203265289 |  | Ground Loop | BOSCH-GEO | SM048-1VT/CFN-*****A |  | 51300 | 17.7 | 36900 | 3.6 | 4.275 | Yes
203265290 |  | Ground Loop | BOSCH-GEO | SM048-1HZC-*****A |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265291 |  | Ground Loop | BOSCH-GEO | SM048-1HZN-*****A |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203265529 |  | Ground Loop | BOSCH | SM048-1HZC-*****A |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265533 |  | Ground Loop | BOSCH | SM048-1HZC-*****C |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265538 |  | Ground Loop | BOSCH | SM048-1HZN-*****A |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203265540 |  | Ground Loop | BOSCH | SM048-1HZN-*****C |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203265973 |  | Ground Loop | CARRIER | GC048V/C**C***1**1 |  | 51300 | 18.15 | 36900 | 3.9 | 4.275 | Yes
203265976 |  | Ground Loop | BRYANT | GC048V/C**C***1*X1 |  | 51300 | 18.15 | 36900 | 3.9 | 4.275 | Yes
203265980 |  | Ground Loop | CARRIER | GC048V/C**N***1**1 |  | 51300 | 17.7 | 36900 | 3.6 | 4.275 | Yes
203265983 |  | Ground Loop | BRYANT | GC048V/C**N***1*X1 |  | 51300 | 17.7 | 36900 | 3.6 | 4.275 | Yes
203265987 |  | Ground Loop | CARRIER | GC048H**C***1**1 |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265989 |  | Ground Loop | BRYANT | GC048H**C***1*X1 |  | 51300 | 18.75 | 36900 | 4.1 | 4.275 | Yes
203265990 |  | Ground Loop | CARRIER | GC048H**N***1**1 |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203265991 |  | Ground Loop | BRYANT | GC048H**N***1*X1 |  | 51300 | 18 | 36900 | 4.1 | 4.275 | Yes
203268807 |  | Ground Loop | BOSCH | SM060-1HZ*******C |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
203303751 |  | Ground Loop | BOSCH-GEO | BP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203303774 |  | Ground Loop | BOSCH | BP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303777 |  | Ground Loop | CARRIER | GB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203303778 |  | Ground Loop | BRYANT | GB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303779 |  | Ground Loop | HEIL | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203303780 |  | Ground Loop | ARCOAIRE | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303781 |  | Ground Loop | KEEPRITE | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303782 |  | Ground Loop | TEMPSTAR | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303783 |  | Ground Loop | COMFORTMAKER | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
203303784 |  | Ground Loop | DAY & NIGHT | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | Yes
215415788 |  | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)036A*VB |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
215415789 |  | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)036A*VC |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
203380971 |  | Ground Loop | BOSCH | EP048-4VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203380972 |  | Ground Loop | BOSCH | EP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203380973 |  | Ground Loop | BOSCH | EP048-3HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203380974 |  | Ground Loop | BOSCH | EP048-4HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383876 |  | Ground Loop | CARRIER | 50PSV018***3/CA |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203383877 |  | Ground Loop | CARRIER | 50PSV018***4/DA |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203383878 |  | Ground Loop | CARRIER | 50PSH018***3/CA |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203383879 |  | Ground Loop | CARRIER | 50PSH018***4/DA |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203383880 |  | Ground Loop | CARRIER | 50PSV042***3/CA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383881 |  | Ground Loop | CARRIER | 50PSV042***5/EA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383882 |  | Ground Loop | CARRIER | 50PSV042***6/FA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383883 |  | Ground Loop | CARRIER | 50PSH042***3/CA |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383884 |  | Ground Loop | CARRIER | 50PSH042***5/EA |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383885 |  | Ground Loop | CARRIER | 50PSH042***6/FA |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383886 |  | Ground Loop | CARRIER | 50PSV048***3/CA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383887 |  | Ground Loop | CARRIER | 50PSV048***5/EA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383888 |  | Ground Loop | CARRIER | 50PSV048***6/FA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383889 |  | Ground Loop | CARRIER | 50PSH048***3/CA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383890 |  | Ground Loop | CARRIER | 50PSH048***5/EA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383891 |  | Ground Loop | CARRIER | 50PSH048***6/FA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383892 |  | Ground Loop | FHP | EP018-1VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203383893 |  | Ground Loop | FHP | EP018-2VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
203383894 |  | Ground Loop | FHP | EP018-1HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203383895 |  | Ground Loop | FHP | EP018-2HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083 | No
203383896 |  | Ground Loop | FHP | EP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383897 |  | Ground Loop | FHP | EP042-3VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383898 |  | Ground Loop | FHP | EP042-4VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833 | No
203383899 |  | Ground Loop | FHP | EP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383900 |  | Ground Loop | FHP | EP042-3HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383901 |  | Ground Loop | FHP | EP042-4HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833 | No
203383902 |  | Ground Loop | FHP | EP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383903 |  | Ground Loop | FHP | EP048-3VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383904 |  | Ground Loop | FHP | EP048-4VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
203383905 |  | Ground Loop | FHP | EP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383906 |  | Ground Loop | FHP | EP048-3HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
203383907 |  | Ground Loop | FHP | EP048-4HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9 | No
211594212 |  | Ground Loop | TRANE | DXHG024A |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583 | No
211594213 |  | Ground Loop | TRANE | DXHG036A |  | 34500 | 19.7 | 25500 | 4.1 | 2.875 | No
211594214 |  | Ground Loop | TRANE | DXHG048A |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833 | No
211594215 |  | Ground Loop | TRANE | DXHG060A |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
211594216 |  | Ground Loop | TRANE | DXHG070A |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
211594223 |  | Ground Loop | TRANE | GEHG0097 |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167 | No
211594224 |  | Ground Loop | TRANE | GEHG0127 |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083 | No
211594225 |  | Ground Loop | TRANE | GEHG0157 |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917 | No
211594226 |  | Ground Loop | TRANE | GEHG0187 |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083 | No
211594227 |  | Ground Loop | TRANE | GEHG024B |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
211594228 |  | Ground Loop | TRANE | GEHG0244 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
211594229 |  | Ground Loop | TRANE | GEHG0247 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667 | No
211594230 |  | Ground Loop | TRANE | GEHG030B |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
211594231 |  | Ground Loop | TRANE | GEHG0304 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
211594232 |  | Ground Loop | TRANE | GEHG0307 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167 | No
211594233 |  | Ground Loop | TRANE | GEHG036B |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
211594234 |  | Ground Loop | TRANE | GEHG0364 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
211594235 |  | Ground Loop | TRANE | GEHG0367 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083 | No
211594242 |  | Ground Loop | TRANE | EXHG0097 |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167 | No
211594243 |  | Ground Loop | TRANE | EXHG0127 |  | 12300 | 19.5 | 9300 | 4 | 1.025 | No
211594244 |  | Ground Loop | TRANE | EXHG0157 |  | 15800 | 19 | 12100 | 3.8 | 1.3167 | No
211594245 |  | Ground Loop | TRANE | EXHG0187 |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333 | No
211594246 |  | Ground Loop | TRANE | EXHG024B |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
211594247 |  | Ground Loop | TRANE | EXHG0244 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
211594248 |  | Ground Loop | TRANE | EXHG0247 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333 | No
211594249 |  | Ground Loop | TRANE | EXHG030B |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
211594250 |  | Ground Loop | TRANE | EXHG0304 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
211594251 |  | Ground Loop | TRANE | EXHG0307 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333 | No
211594252 |  | Ground Loop | TRANE | EXHG036B |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
211594253 |  | Ground Loop | TRANE | EXHG0364 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
211594254 |  | Ground Loop | TRANE | EXHG0367 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917 | No
211594255 |  | Ground Loop | TRANE | EXHG042B |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
211594256 |  | Ground Loop | TRANE | EXHG0424 |  | 40500 | 21.1 | 29400 | 4.3 | 3.375 | No
211594257 |  | Ground Loop | TRANE | EXHG048B |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
211594258 |  | Ground Loop | TRANE | EXHG0484 |  | 47100 | 20.3 | 34600 | 4.3 | 3.925 | No
211594259 |  | Ground Loop | TRANE | EXHG060B |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
211594260 |  | Ground Loop | TRANE | EXHG0604 |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083 | No
211594261 |  | Ground Loop | TRANE | EXHG070B |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083 | No
218472164 |  | Ground Loop | YORK | AQ024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218472165 |  | Ground Loop | YORK | AQ024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218472166 |  | Ground Loop | YORK | AQ024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218472167 |  | Ground Loop | YORK | AQ024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218472168 |  | Ground Loop | YORK | AQ024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218472169 |  | Ground Loop | YORK | AQ024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
218472170 |  | Ground Loop | YORK | AQ024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218472171 |  | Ground Loop | YORK | AQ024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
218472172 |  | Ground Loop | YORK | AQ036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218472173 |  | Ground Loop | YORK | AQ036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
218472174 |  | Ground Loop | YORK | AQ036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218472175 |  | Ground Loop | YORK | AQ036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
218472176 |  | Ground Loop | YORK | AQ048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
218472177 |  | Ground Loop | YORK | AQ048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
218472178 |  | Ground Loop | YORK | AQ060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
218472179 |  | Ground Loop | YORK | AQ060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
5295984 |  | Ground Loop | WaterFurnace | NBV/NBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295985 |  | Ground Loop | WaterFurnace | NBV/NBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295986 |  | Ground Loop | WaterFurnace | NBV/NBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295987 |  | Ground Loop | WaterFurnace | NBV/NBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295988 |  | Ground Loop | WaterFurnace | NBV/NBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295989 |  | Ground Loop | WaterFurnace | NBV/NBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295990 |  | Ground Loop | WaterFurnace | NBV/NBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295991 |  | Ground Loop | WaterFurnace | NBV/NBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
5295992 |  | Ground Loop | WaterFurnace | NBV/NBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
5295993 |  | Ground Loop | WaterFurnace | NBV/NBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
5295994 |  | Ground Loop | WaterFurnace | NBV/NBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
5295995 |  | Ground Loop | WaterFurnace | NBV/NBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
5295996 |  | Ground Loop | WaterFurnace | NBV/NBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5295997 |  | Ground Loop | WaterFurnace | NBV/NBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5295998 |  | Ground Loop | WaterFurnace | NBV/NBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5295999 |  | Ground Loop | WaterFurnace | NBV/NBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296000 |  | Ground Loop | WaterFurnace | NBV/NBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296001 |  | Ground Loop | WaterFurnace | NBV/NBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296002 |  | Ground Loop | WaterFurnace | NBV/NBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296003 |  | Ground Loop | WaterFurnace | NBV/NBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
5296004 |  | Ground Loop | WaterFurnace | NBV/NBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
5296005 |  | Ground Loop | WaterFurnace | NBV/NBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
5296006 |  | Ground Loop | WaterFurnace | NBV/NBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
5296007 |  | Ground Loop | WaterFurnace | NBV/NBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
5296008 |  | Ground Loop | WaterFurnace | NBV/NBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296009 |  | Ground Loop | WaterFurnace | NBV/NBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296010 |  | Ground Loop | WaterFurnace | NBV/NBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296011 |  | Ground Loop | WaterFurnace | NBV/NBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296012 |  | Ground Loop | WaterFurnace | NBV/NBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296013 |  | Ground Loop | WaterFurnace | NBV/NBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296014 |  | Ground Loop | WaterFurnace | NBV/NBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296015 |  | Ground Loop | WaterFurnace | NBV/NBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
5296225 |  | Ground Loop | WaterFurnace | NBV/NBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296226 |  | Ground Loop | WaterFurnace | NBV/NBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296227 |  | Ground Loop | WaterFurnace | NBV/NBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296228 |  | Ground Loop | WaterFurnace | NBV/NBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296229 |  | Ground Loop | WaterFurnace | NBV/NBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5296230 |  | Ground Loop | WaterFurnace | NBV/NBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
5315758 |  | Ground Loop | WaterFurnace | NBV/NBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315759 |  | Ground Loop | WaterFurnace | NBV/NBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315760 |  | Ground Loop | WaterFurnace | NBV/NBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315761 |  | Ground Loop | WaterFurnace | NBV/NBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315762 |  | Ground Loop | WaterFurnace | NBV/NBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315763 |  | Ground Loop | WaterFurnace | NBV/NBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5315774 |  | Ground Loop | WaterFurnace | NBV/NBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
5315776 |  | Ground Loop | WaterFurnace | NBV/NBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
5315777 |  | Ground Loop | WaterFurnace | NBV/NBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
5315778 |  | Ground Loop | WaterFurnace | NBV/NBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
202434438 |  | Ground Loop | FHP | LV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434439 |  | Ground Loop | FHP | LV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434444 |  | Ground Loop | FHP | LV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434445 |  | Ground Loop | FHP | LV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434446 |  | Ground Loop | FHP | LV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434447 |  | Ground Loop | FHP | LV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
215268318 |  | Ground Loop | WaterFurnace | V3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268320 |  | Ground Loop | WaterFurnace | V3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268321 |  | Ground Loop | WaterFurnace | V3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268323 |  | Ground Loop | WaterFurnace | V3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
215268334 |  | Ground Loop | WaterFurnace | V3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268335 |  | Ground Loop | WaterFurnace | V3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268336 |  | Ground Loop | WaterFurnace | V3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268337 |  | Ground Loop | WaterFurnace | V3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268338 |  | Ground Loop | WaterFurnace | V3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268339 |  | Ground Loop | WaterFurnace | V3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268340 |  | Ground Loop | WaterFurnace | V3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
215268348 |  | Ground Loop | WaterFurnace | V3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268349 |  | Ground Loop | WaterFurnace | V3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268350 |  | Ground Loop | WaterFurnace | V3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268351 |  | Ground Loop | WaterFurnace | V3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268352 |  | Ground Loop | WaterFurnace | V3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268353 |  | Ground Loop | WaterFurnace | V3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268354 |  | Ground Loop | WaterFurnace | V3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
215268355 |  | Ground Loop | WaterFurnace | V3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268356 |  | Ground Loop | WaterFurnace | V3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
215268357 |  | Ground Loop | WaterFurnace | V3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5 | No
10259063 |  | Ground Loop | HYDRON MODULE | HZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | Yes
10259064 |  | Ground Loop | TETCO | TZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | Yes
10259065 |  | Ground Loop | GEOCOMFORT | GZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | No
10259066 |  | Ground Loop | HYDRON MODULE | HZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | No
10259067 |  | Ground Loop | TETCO | TZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525 | No
10271778 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10271930 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
10271959 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ022H1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10271961 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ022H1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
10271981 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ030H1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10271985 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ030H1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
10272006 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048H1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10272008 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048H1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
10272012 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060H1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10272014 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060H1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
10272021 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ070H1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10272215 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10272216 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10272219 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10272220 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10272221 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10272222 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10298936 |  | Ground Loop | WaterFurnace | UVV/UVH036**0*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25 | No
10298937 |  | Ground Loop | WaterFurnace | UVV/UVH036**3*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25 | No
10298938 |  | Ground Loop | WaterFurnace | UVV/UVH036**4*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25 | No
10298941 |  | Ground Loop | WaterFurnace | UVV/UVH048**0*1 |  | 48000 | 20 | 38000 | 3.8 | 4 | No
10298942 |  | Ground Loop | WaterFurnace | UVV/UVH048**3*1 |  | 48000 | 20 | 38000 | 3.8 | 4 | No
10298943 |  | Ground Loop | WaterFurnace | UVV/UVH048**4*1 |  | 48000 | 20 | 38000 | 3.8 | 4 | No
10298944 |  | Ground Loop | WaterFurnace | UVV/UVH060**0*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667 | No
10298946 |  | Ground Loop | WaterFurnace | UVV/UVH060**3*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667 | No
10298947 |  | Ground Loop | WaterFurnace | UVV/UVH060**4*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667 | No
10304639 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10304640 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10304641 |  | Ground Loop | GeoSmart Energy | GTZ026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10304642 |  | Ground Loop | GEOSTAR | 103H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
10304646 |  | Ground Loop | GEOSTAR | 103H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10304657 |  | Ground Loop | GeoSmart Energy | GTZ026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | Yes
10305457 |  | Ground Loop | GEOSTAR | 104H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10305458 |  | Ground Loop | GEOSTAR | 104H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316642 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAST026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316643 |  | Ground Loop | GeoSmart Energy | GTS026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316644 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAST026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316645 |  | Ground Loop | GeoSmart Energy | GTS026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
10316654 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAST049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316655 |  | Ground Loop | GEOSTAR | 104H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316656 |  | Ground Loop | GeoSmart Energy | GTS049*1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316657 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAST049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316658 |  | Ground Loop | GeoSmart Energy | GTS049*1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10316660 |  | Ground Loop | GEOSTAR | 104H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
206185640 |  | Ground Loop | DAIKIN | WGCH048E1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185641 |  | Ground Loop | DAIKIN | WGCH048E1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185646 |  | Ground Loop | DAIKIN | WGCH048F1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185647 |  | Ground Loop | DAIKIN | WGCH048F1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185652 |  | Ground Loop | DAIKIN | WGCH048K1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
206185653 |  | Ground Loop | DAIKIN | WGCH048K1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917 | No
217351847 |  | Ground Loop | DAY & NIGHT | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351849 |  | Ground Loop | DAY & NIGHT | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351850 |  | Ground Loop | DAY & NIGHT | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351851 |  | Ground Loop | DAY & NIGHT | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351852 |  | Ground Loop | DAY & NIGHT | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351853 |  | Ground Loop | DAY & NIGHT | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351855 |  | Ground Loop | DAY & NIGHT | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351856 |  | Ground Loop | DAY & NIGHT | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351857 |  | Ground Loop | DAY & NIGHT | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351865 |  | Ground Loop | HEIL | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351866 |  | Ground Loop | HEIL | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351869 |  | Ground Loop | HEIL | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351870 |  | Ground Loop | HEIL | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351871 |  | Ground Loop | HEIL | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351873 |  | Ground Loop | HEIL | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351874 |  | Ground Loop | HEIL | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351876 |  | Ground Loop | HEIL | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351877 |  | Ground Loop | HEIL | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351878 |  | Ground Loop | HEIL | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351879 |  | Ground Loop | HEIL | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351880 |  | Ground Loop | HEIL | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351882 |  | Ground Loop | HEIL | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351883 |  | Ground Loop | HEIL | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351884 |  | Ground Loop | HEIL | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351892 |  | Ground Loop | KEEPRITE | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351893 |  | Ground Loop | KEEPRITE | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351896 |  | Ground Loop | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351897 |  | Ground Loop | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351898 |  | Ground Loop | KEEPRITE | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
208771547 |  | Ground Loop | HYDROTECH | WSV6012B* |  | 12500 | 19 | 9000 | 3.6 | 1.0417 | Yes
208771548 |  | Ground Loop | HYDROTECH | WSV6024B* |  | 24000 | 18 | 17500 | 3.6 | 2 | Yes
208771549 |  | Ground Loop | HYDROTECH | WSV6030B* |  | 33500 | 17.5 | 25000 | 3.6 | 2.7917 | Yes
208856966 |  | Ground Loop | HYDROTECH | WSV6060B* |  | 63000 | 18 | 42500 | 3.6 | 5.25 | Yes
208856967 |  | Ground Loop | HYDROTECH | WSV6072B* |  | 73500 | 18 | 52000 | 3.6 | 6.125 | Yes
208856972 |  | Ground Loop | AE Air | WSV6012B* |  | 12500 | 19 | 9000 | 3.6 | 1.0417 | Yes
208856973 |  | Ground Loop | AE Air | WSV6024B* |  | 24000 | 18 | 17500 | 3.6 | 2 | Yes
208856974 |  | Ground Loop | AE Air | WSV6030B* |  | 33500 | 17.5 | 25000 | 3.6 | 2.7917 | Yes
208856975 |  | Ground Loop | AE Air | WSV6060B* |  | 63000 | 18 | 42500 | 3.6 | 5.25 | Yes
208856976 |  | Ground Loop | AE Air | WSV6072B* |  | 73500 | 18 | 52000 | 3.6 | 6.125 | Yes
215415844 |  | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
215415845 |  | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
216739946 |  | Ground Loop | DAIKIN | WSNH060E1*G/J*C |  | 61200 | 17.3 | 49000 | 3.9 | 5.1 | No
216739947 |  | Ground Loop | DAIKIN | WSNH060F3*G/J*C |  | 61200 | 17 | 49000 | 3.9 | 5.1 | No
216739948 |  | Ground Loop | DAIKIN | WSNH060K3*G/J*C |  | 61200 | 17 | 49000 | 3.9 | 5.1 | No
216739957 |  | Ground Loop | DAIKIN | WSNV030E1*G/J*C |  | 31900 | 18.9 | 20500 | 3.6 | 2.6583 | No
216739965 |  | Ground Loop | DAIKIN | WSNV036E1*G/J*C |  | 37300 | 20.3 | 26100 | 3.8 | 3.1083 | No
216739966 |  | Ground Loop | DAIKIN | WSNV036F3*G/J*C |  | 37300 | 19.9 | 26100 | 3.8 | 3.1083 | No
216739967 |  | Ground Loop | DAIKIN | WSNV036J1*G/J*C |  | 37300 | 19.9 | 26100 | 3.8 | 3.1083 | No
216739968 |  | Ground Loop | DAIKIN | WSNV036K3*G/J*C |  | 37300 | 19.7 | 26100 | 3.7 | 3.1083 | No
216739972 |  | Ground Loop | DAIKIN | WSNV042E1*G/J*C |  | 44700 | 19.3 | 29000 | 3.6 | 3.725 | No
216739978 |  | Ground Loop | DAIKIN | WSNV048E1*G/J*C |  | 51100 | 19.5 | 35000 | 3.8 | 4.2583 | No
216739979 |  | Ground Loop | DAIKIN | WSNV048F3*G/J*C |  | 51100 | 19.1 | 35000 | 3.8 | 4.2583 | No
216739980 |  | Ground Loop | DAIKIN | WSNV048K3*G/J*C |  | 51100 | 19.1 | 35000 | 3.8 | 4.2583 | No
216739984 |  | Ground Loop | DAIKIN | WSNV060E1*G/J*C |  | 62200 | 17.8 | 46200 | 3.8 | 5.1833 | No
216739985 |  | Ground Loop | DAIKIN | WSNV060F3*G/J*C |  | 62200 | 17.4 | 46200 | 3.7 | 5.1833 | No
216739986 |  | Ground Loop | DAIKIN | WSNV060K3*G/J*C |  | 62200 | 17.4 | 46200 | 3.7 | 5.1833 | No
213154468 |  | Ground Loop | GeoSmart Energy | GS036**1*1********L |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | Yes
213154469 |  | Ground Loop | GeoSmart Energy | GS042**1*1********L |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
213154470 |  | Ground Loop | GeoSmart Energy | GS048**1*1********L |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
213154471 |  | Ground Loop | GeoSmart Energy | GS060**1*1********L |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
213154472 |  | Ground Loop | GeoSmart Energy | GS070**1*1********L |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
213154473 |  | Ground Loop | GeoSmart Energy | GT026**1*1********L |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
213154474 |  | Ground Loop | GeoSmart Energy | GT038**1*1********L |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
213154475 |  | Ground Loop | GeoSmart Energy | GT049**1*1********L |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
213154476 |  | Ground Loop | GeoSmart Energy | GT064**1*1********L |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
213154477 |  | Ground Loop | GeoSmart Energy | GT072**1*1********L |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
215824878 |  | Ground Loop | ICE AIR LLC | 8VSHPGE09**C |  | 11000 | 21.3 | 6500 | 3.64 | 0.91667 | No
215824879 |  | Ground Loop | ICE AIR LLC | 8VSHPGE12**C |  | 13800 | 20.1 | 9000 | 3.7 | 1.15 | No
215824880 |  | Ground Loop | ICE AIR LLC | 8VSHPGE15**C |  | 15000 | 17.5 | 10500 | 3.7 | 1.25 | No
215824881 |  | Ground Loop | ICE AIR LLC | 8VSHPGE18**C |  | 19500 | 18.7 | 13400 | 3.63 | 1.625 | No
215824882 |  | Ground Loop | ICE AIR LLC | 8VSHPGE24**C |  | 24800 | 18.4 | 17000 | 3.66 | 2.0667 | No
215824883 |  | Ground Loop | ICE AIR LLC | 8VSHPGE30**C |  | 30000 | 17.3 | 21900 | 3.6 | 2.5 | No
215824884 |  | Ground Loop | ICE AIR LLC | 8VSHPGE06**C |  | 8800 | 19.6 | 5800 | 3.6 | 0.73333 | No
215827077 |  | Ground Loop | DAIKIN | WSLH072F1*G/J |  | 73500 | 18 | 53600 | 3.6 | 6.125 | No
215827078 |  | Ground Loop | DAIKIN | WSLH072K1*G/J |  | 73500 | 18 | 53600 | 3.6 | 6.125 | No
215827083 |  | Ground Loop | DAIKIN | WSLH096F1*G/J |  | 98000 | 17.9 | 72000 | 3.6 | 8.1667 | No
215827084 |  | Ground Loop | DAIKIN | WSLH096K1*G/J |  | 98000 | 17.9 | 72000 | 3.6 | 8.1667 | No
217903432 |  | Ground Loop | WaterFurnace | V5R036*S3**5* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903433 |  | Ground Loop | WaterFurnace | V5R036*S4**1* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903434 |  | Ground Loop | WaterFurnace | V5R036*S4**4* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903435 |  | Ground Loop | WaterFurnace | V5R036*S4**5* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903436 |  | Ground Loop | WaterFurnace | V5R048*S3**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903437 |  | Ground Loop | WaterFurnace | V5R048*S3**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903438 |  | Ground Loop | WaterFurnace | V5R048*S3**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903439 |  | Ground Loop | WaterFurnace | V5R048*S4**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903440 |  | Ground Loop | WaterFurnace | V5R048*S4**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903441 |  | Ground Loop | WaterFurnace | V5R048*S4**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903442 |  | Ground Loop | WaterFurnace | V5R060*S3**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903443 |  | Ground Loop | WaterFurnace | V5R060*S3**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903444 |  | Ground Loop | WaterFurnace | V5R060*S3**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903445 |  | Ground Loop | WaterFurnace | V5R060*S4**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903446 |  | Ground Loop | WaterFurnace | V5R060*S4**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903447 |  | Ground Loop | WaterFurnace | V5R060*S4**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903448 |  | Ground Loop | WaterFurnace | V5R072*S3**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903449 |  | Ground Loop | WaterFurnace | V5R072*S3**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903450 |  | Ground Loop | WaterFurnace | V5R072*S3**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903451 |  | Ground Loop | WaterFurnace | V5R072*S4**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
202147061 |  | Ground Loop | GEOCOMFORT | GZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | Yes
202147062 |  | Ground Loop | GEOCOMFORT | GZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147067 |  | Ground Loop | HYDRON MODULE | HZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | Yes
202147068 |  | Ground Loop | HYDRON MODULE | HZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147073 |  | Ground Loop | TETCO | TZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | Yes
202147074 |  | Ground Loop | TETCO | TZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147690 |  | Ground Loop | GEOCOMFORT | GZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202147691 |  | Ground Loop | HYDRON MODULE | HZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202147692 |  | Ground Loop | TETCO | TZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | No
202147693 |  | Ground Loop | TETCO | TZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | No
202147697 |  | Ground Loop | GEOCOMFORT | GZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | No
202147698 |  | Ground Loop | HYDRON MODULE | HZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | No
202147699 |  | Ground Loop | TETCO | TZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | No
202147700 |  | Ground Loop | GEOCOMFORT | GZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | No
202147701 |  | Ground Loop | HYDRON MODULE | HZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | No
202147702 |  | Ground Loop | TETCO | TZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | No
202147703 |  | Ground Loop | GEOCOMFORT | GZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147704 |  | Ground Loop | GEOCOMFORT | GZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147705 |  | Ground Loop | HYDRON MODULE | HZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147706 |  | Ground Loop | HYDRON MODULE | HZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147707 |  | Ground Loop | TETCO | TZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147708 |  | Ground Loop | TETCO | TZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202147709 |  | Ground Loop | GEOCOMFORT | GZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147710 |  | Ground Loop | HYDRON MODULE | HZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147711 |  | Ground Loop | TETCO | TZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917 | No
202147712 |  | Ground Loop | GEOCOMFORT | GZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147713 |  | Ground Loop | HYDRON MODULE | HZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202147714 |  | Ground Loop | TETCO | TZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75 | No
202211042 |  | Ground Loop | WaterFurnace | URD038*0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211043 |  | Ground Loop | WaterFurnace | URD038*0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211044 |  | Ground Loop | WaterFurnace | URD038*0*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214063791 |  | Ground Loop | GeoSmart Energy | GBV/GBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067547 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
214067548 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214067549 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214067550 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
214067551 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214067552 |  | Ground Loop | GeoSmart Energy | GBV/GBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
214067553 |  | Ground Loop | GeoSmart Energy | GBV/GBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214067554 |  | Ground Loop | GeoSmart Energy | GBV/GBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214067555 |  | Ground Loop | GeoSmart Energy | GBV/GBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214067556 |  | Ground Loop | GeoSmart Energy | GBV/GBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214067557 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
214067558 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214067559 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214067560 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
214067561 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214067562 |  | Ground Loop | GeoSmart Energy | GBV/GBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
214067563 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
214067564 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067565 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067566 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
214067567 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067568 |  | Ground Loop | GeoSmart Energy | GBV/GBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
214067569 |  | Ground Loop | GeoSmart Energy | GBV/GBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214067570 |  | Ground Loop | GeoSmart Energy | GBV/GBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214067571 |  | Ground Loop | GeoSmart Energy | GBV/GBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214067572 |  | Ground Loop | GeoSmart Energy | GBV/GBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214067574 |  | Ground Loop | GeoSmart Energy | GBV/GBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214067575 |  | Ground Loop | GeoSmart Energy | GBV/GBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214067577 |  | Ground Loop | GeoSmart Energy | GBV/GBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214067578 |  | Ground Loop | GeoSmart Energy | GBV/GBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214067581 |  | Ground Loop | GeoSmart Energy | GBV/GBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067582 |  | Ground Loop | GeoSmart Energy | GBV/GBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067584 |  | Ground Loop | GeoSmart Energy | GBV/GBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214067585 |  | Ground Loop | GeoSmart Energy | GBV/GBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214067586 |  | Ground Loop | GeoSmart Energy | GBV/GBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214067587 |  | Ground Loop | GeoSmart Energy | GBV/GBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
214067588 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
214067589 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214067590 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214067591 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
214067592 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
207822807 |  | Ground Loop | HYDROTECH | HRCX30*-6 |  | 28000 | 18 | 20000 | 3.6 | 2.3333 | Yes
207822813 |  | Ground Loop | HYDROTECH | HRCX36*-6 |  | 34100 | 17.1 | 25000 | 3.6 | 2.8417 | Yes
208106952 |  | Ground Loop | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
208106953 |  | Ground Loop | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
208106954 |  | Ground Loop | 5 SERIES GEO-READY | NGV/NGH064*1*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
208450079 |  | Ground Loop | AE Air | HRCX18*-6 |  | 18000 | 17.1 | 13000 | 3.6 | 1.5 | Yes
208450080 |  | Ground Loop | AE Air | HRCX09*-6 |  | 10000 | 19 | 6800 | 3.6 | 0.83333 | Yes
208450081 |  | Ground Loop | AE Air | HRCX24*-6 |  | 24000 | 19 | 17000 | 3.6 | 2 | Yes
208450082 |  | Ground Loop | AE Air | HRCX12*-6 |  | 11800 | 18 | 8000 | 3.6 | 0.98333 | Yes
208450083 |  | Ground Loop | AE Air | HRCX30*-6 |  | 28000 | 18 | 20000 | 3.6 | 2.3333 | Yes
208450084 |  | Ground Loop | AE Air | HRCX36*-6 |  | 34100 | 17.1 | 25000 | 3.6 | 2.8417 | Yes
208556796 |  | Ground Loop | GEOCOMFORT | GRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125 | Yes
208556798 |  | Ground Loop | HYDRON MODULE | HRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125 | Yes
208556799 |  | Ground Loop | TETCO | TRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125 | Yes
208556801 |  | Ground Loop | GEOCOMFORT | GRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15 | No
208556804 |  | Ground Loop | HYDRON MODULE | HRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15 | Yes
208556806 |  | Ground Loop | TETCO | TRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15 | Yes
208556808 |  | Ground Loop | GEOCOMFORT | GRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417 | Yes
208556810 |  | Ground Loop | HYDRON MODULE | HRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417 | Yes
208556812 |  | Ground Loop | TETCO | TRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417 | Yes
208556818 |  | Ground Loop | GEOCOMFORT | GRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417 | Yes
208556821 |  | Ground Loop | HYDRON MODULE | HRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417 | Yes
208556822 |  | Ground Loop | TETCO | TRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417 | Yes
208556825 |  | Ground Loop | GEOCOMFORT | GRT048 | EED048 | 49800 | 17.4 | 38200 | 3.8 | 4.15 | Yes
208556827 |  | Ground Loop | HYDRON MODULE | HRT048 | EED048 | 49800 | 17.4 | 38200 | 3.8 | 4.15 | Yes
208556829 |  | Ground Loop | TETCO | TRT048 | EED060 | 49800 | 17.4 | 38200 | 3.8 | 4.15 | Yes
208556831 |  | Ground Loop | GEOCOMFORT | GRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333 | Yes
208556832 |  | Ground Loop | HYDRON MODULE | HRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333 | Yes
208556834 |  | Ground Loop | TETCO | TRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333 | Yes
218338436 |  | Ground Loop | GEOSTAR | G5AV084*D4**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
218338442 |  | Ground Loop | GEOSTAR | G5AV084*D3**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
218338443 |  | Ground Loop | GEOSTAR | G5AV084*D5**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
218338454 |  | Ground Loop | GeoSmart Energy | S5AV084*D4**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
218338460 |  | Ground Loop | GeoSmart Energy | S5AV084*D3**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
218338461 |  | Ground Loop | GeoSmart Energy | S5AV084*D5**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
10316661 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAST064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316662 |  | Ground Loop | GEOSTAR | 104H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316663 |  | Ground Loop | GeoSmart Energy | GTS064*1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316664 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAST064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316666 |  | Ground Loop | GEOSTAR | 104H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10316667 |  | Ground Loop | GeoSmart Energy | GTS064*1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
10318010 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10318016 |  | Ground Loop | GeoSmart Energy | GSZ022*1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10318017 |  | Ground Loop | GEOSTAR | 103H022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
10318018 |  | Ground Loop | GeoSmart Energy | GSZ022*1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | Yes
10318019 |  | Ground Loop | GEOSTAR | 103H022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10318020 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583 | No
10318021 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10318022 |  | Ground Loop | GEOSTAR | 103H030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
10318023 |  | Ground Loop | GeoSmart Energy | GSZ030*1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10318024 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10318025 |  | Ground Loop | GeoSmart Energy | GSZ030*1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | Yes
10318026 |  | Ground Loop | GEOSTAR | 103H030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05 | No
10318045 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10318046 |  | Ground Loop | GeoSmart Energy | GSZ048*1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10318047 |  | Ground Loop | GEOSTAR | 103H048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
10318048 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10318049 |  | Ground Loop | GeoSmart Energy | GSZ048*1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
10318050 |  | Ground Loop | GEOSTAR | 103H048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | Yes
10318051 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10318052 |  | Ground Loop | GeoSmart Energy | GSZ060*1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10318054 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10318055 |  | Ground Loop | GeoSmart Energy | GSZ060*1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
10318056 |  | Ground Loop | GEOSTAR | 103H060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | Yes
10318060 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10318061 |  | Ground Loop | GEOSTAR | 103H070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10318062 |  | Ground Loop | GeoSmart Energy | GSZ070*1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417 | No
10346237 |  | Ground Loop | GEOCOMFORT | GZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
214771947 |  | Ground Loop | TRANE | GEHK024A |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214771948 |  | Ground Loop | TRANE | GEHK030A |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214771951 |  | Ground Loop | TRANE | GEHK048A |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214771952 |  | Ground Loop | TRANE | GEHK060A |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214771953 |  | Ground Loop | TRANE | EXHK009A |  | 9000 | 21.2 | 6100 | 3.91 | 0.75 | No
214771954 |  | Ground Loop | TRANE | EXHK012A |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167 | No
214771955 |  | Ground Loop | TRANE | EXHK015A |  | 16200 | 18.7 | 11800 | 3.73 | 1.35 | No
214771956 |  | Ground Loop | TRANE | EXHK018A |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417 | No
214771957 |  | Ground Loop | TRANE | EXHK024A |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214771958 |  | Ground Loop | TRANE | EXHK030A |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214771959 |  | Ground Loop | TRANE | EXHK036A |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214771960 |  | Ground Loop | TRANE | EXHK042A |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214771961 |  | Ground Loop | TRANE | EXHK048A |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214771962 |  | Ground Loop | TRANE | EXHK060A |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214771963 |  | Ground Loop | TRANE | EXHK070A |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772055 |  | Ground Loop | TRANE | GEVK0097 |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333 | No
214772057 |  | Ground Loop | TRANE | GEVK0157 |  | 15900 | 18.2 | 12500 | 3.85 | 1.325 | No
214772058 |  | Ground Loop | TRANE | GEVK0187 |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417 | No
214772059 |  | Ground Loop | TRANE | GEVK024B |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772060 |  | Ground Loop | TRANE | GEVK0244 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772061 |  | Ground Loop | TRANE | GEVK0247 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772062 |  | Ground Loop | TRANE | GEVK030B |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772063 |  | Ground Loop | TRANE | GEVK0304 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772064 |  | Ground Loop | TRANE | GEVK0307 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772070 |  | Ground Loop | TRANE | GEVK048B |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214772071 |  | Ground Loop | TRANE | GEVK0484 |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214772072 |  | Ground Loop | TRANE | GEVK060B |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214772073 |  | Ground Loop | TRANE | GEVK0604 |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214772074 |  | Ground Loop | TRANE | EXVK0097 |  | 9000 | 21.2 | 6100 | 3.91 | 0.75 | No
214772075 |  | Ground Loop | TRANE | EXVK0127 |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167 | No
214772076 |  | Ground Loop | TRANE | EXVK0157 |  | 16200 | 18.7 | 11800 | 3.73 | 1.35 | No
214772077 |  | Ground Loop | TRANE | EXVK0187 |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417 | No
214772078 |  | Ground Loop | TRANE | EXVK024B |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772079 |  | Ground Loop | TRANE | EXVK0244 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772080 |  | Ground Loop | TRANE | EXVK0247 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772081 |  | Ground Loop | TRANE | EXVK030B |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772082 |  | Ground Loop | TRANE | EXVK0304 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772083 |  | Ground Loop | TRANE | EXVK0307 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772084 |  | Ground Loop | TRANE | EXVK036B |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772085 |  | Ground Loop | TRANE | EXVK0364 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
202443461 |  | Ground Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
202443462 |  | Ground Loop | GeoSmart Energy | GSZ042*1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
202443463 |  | Ground Loop | GeoSmart Energy | GTZ038*1*J | SAH038* | 36000 | 19 | 27900 | 4 | 3 | No
202443470 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
202443471 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
202443472 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
202443473 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAST038**1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3 | Yes
217752745 |  | Ground Loop | DAIKIN | WSTV024K1*H*C |  | 22400 | 17.45 | 17200 | 3.86 | 1.8667 | No
217752747 |  | Ground Loop | DAIKIN | WSTV030K1*H*C |  | 32200 | 18.9 | 20800 | 3.66 | 2.6833 | No
217752751 |  | Ground Loop | DAIKIN | WSTV042K1*H*C |  | 44800 | 18.96 | 27600 | 3.62 | 3.7333 | No
217752754 |  | Ground Loop | DAIKIN | WSTV048K1*H*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667 | No
217752755 |  | Ground Loop | DAIKIN | WSTV048L1*H*C |  | 52400 | 19.56 | 35200 | 3.78 | 4.3667 | No
217752758 |  | Ground Loop | DAIKIN | WSTV060K1*H*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583 | No
217752759 |  | Ground Loop | DAIKIN | WSTV060L1*H*C |  | 63100 | 19.01 | 46800 | 3.98 | 5.2583 | No
217752762 |  | Ground Loop | DAIKIN | WSTV070K1*H*C |  | 74600 | 18.62 | 56000 | 3.92 | 6.2167 | No
217752763 |  | Ground Loop | DAIKIN | WSTV070L1*H*C |  | 74600 | 18.43 | 56000 | 3.88 | 6.2167 | No
217754378 |  | Ground Loop | DAIKIN | WSSH024F1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217754379 |  | Ground Loop | DAIKIN | WSSH024K1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217754381 |  | Ground Loop | DAIKIN | WSSH024F1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217754382 |  | Ground Loop | DAIKIN | WSSH024K1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
217754384 |  | Ground Loop | DAIKIN | WSSH030F1*H*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
217754385 |  | Ground Loop | DAIKIN | WSSH030K1*H*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
217754387 |  | Ground Loop | DAIKIN | WSSH030F1*H*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
217754388 |  | Ground Loop | DAIKIN | WSSH030K1*H*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
217754390 |  | Ground Loop | DAIKIN | WSSH036F1*H*T |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583 | No
217754391 |  | Ground Loop | DAIKIN | WSSH036K1*H*T |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583 | No
215268763 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268764 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268765 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268766 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268767 |  | Ground Loop | WaterFurnace | V5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268768 |  | Ground Loop | WaterFurnace | V5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268769 |  | Ground Loop | WaterFurnace | V5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268770 |  | Ground Loop | WaterFurnace | V5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268771 |  | Ground Loop | WaterFurnace | V5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268772 |  | Ground Loop | WaterFurnace | V5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268773 |  | Ground Loop | WaterFurnace | V5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268774 |  | Ground Loop | WaterFurnace | V5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268775 |  | Ground Loop | WaterFurnace | V5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268776 |  | Ground Loop | WaterFurnace | V5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268777 |  | Ground Loop | WaterFurnace | V5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268778 |  | Ground Loop | WaterFurnace | V5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
215268779 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268780 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268781 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268782 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268783 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268784 |  | Ground Loop | WaterFurnace | V5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215268785 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268786 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268787 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268788 |  | Ground Loop | WaterFurnace | V5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
215268789 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268790 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268791 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268792 |  | Ground Loop | WaterFurnace | V5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
215268793 |  | Ground Loop | WaterFurnace | V5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268794 |  | Ground Loop | WaterFurnace | V5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
215268795 |  | Ground Loop | WaterFurnace | V5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
215268796 |  | Ground Loop | WaterFurnace | V5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
217351900 |  | Ground Loop | KEEPRITE | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351901 |  | Ground Loop | KEEPRITE | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351903 |  | Ground Loop | KEEPRITE | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351904 |  | Ground Loop | KEEPRITE | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351905 |  | Ground Loop | KEEPRITE | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351906 |  | Ground Loop | KEEPRITE | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351907 |  | Ground Loop | KEEPRITE | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351909 |  | Ground Loop | KEEPRITE | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351910 |  | Ground Loop | KEEPRITE | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351911 |  | Ground Loop | KEEPRITE | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
202350452 |  | Ground Loop | AAON, Inc. | M2-007-4-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7 | No
202350453 |  | Ground Loop | AAON, Inc. | M2-007-4-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583 | No
202350454 |  | Ground Loop | AAON, Inc. | M2-007-4-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417 | No
202350455 |  | Ground Loop | AAON, Inc. | M2-007-4-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5 | No
207083905 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083907 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083909 |  | Ground Loop | CARRIER | 50PCV024J/K*C/A4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083911 |  | Ground Loop | CARRIER | 50PCV024J/K*N/J4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083913 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083915 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083917 |  | Ground Loop | CARRIER | 50PCV024J/K*C/A5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083919 |  | Ground Loop | CARRIER | 50PCV024J/K*N/J5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083921 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083923 |  | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
207083925 |  | Ground Loop | CARRIER | 50PCV024J/K*C/A6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
207083927 |  | Ground Loop | CARRIER | 50PCV024J/K*N/J6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
215224539 |  | Ground Loop | FHP | CF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224540 |  | Ground Loop | FHP | CF024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224541 |  | Ground Loop | FHP | CF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224542 |  | Ground Loop | FHP | CF024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218157987 |  | Ground Loop | YORK | Y5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157988 |  | Ground Loop | YORK | Y5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157989 |  | Ground Loop | YORK | Y5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157990 |  | Ground Loop | YORK | Y5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157991 |  | Ground Loop | YORK | Y5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157992 |  | Ground Loop | YORK | Y5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157993 |  | Ground Loop | YORK | Y5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157994 |  | Ground Loop | YORK | Y5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157995 |  | Ground Loop | YORK | Y5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | No
218157996 |  | Ground Loop | YORK | Y5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218157997 |  | Ground Loop | YORK | Y5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218157998 |  | Ground Loop | YORK | Y5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218157999 |  | Ground Loop | YORK | Y5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218158000 |  | Ground Loop | YORK | Y5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218158001 |  | Ground Loop | YORK | Y5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218158002 |  | Ground Loop | YORK | Y5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218158003 |  | Ground Loop | YORK | Y5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218158004 |  | Ground Loop | YORK | Y5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218158005 |  | Ground Loop | YORK | Y5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
218158006 |  | Ground Loop | YORK | Y5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
218158007 |  | Ground Loop | YORK | Y5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
218158008 |  | Ground Loop | YORK | Y5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
218158009 |  | Ground Loop | YORK | Y5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
218158010 |  | Ground Loop | YORK | Y5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
218158011 |  | Ground Loop | YORK | Y5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | No
218158012 |  | Ground Loop | YORK | Y5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
218158013 |  | Ground Loop | YORK | Y5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
218158014 |  | Ground Loop | YORK | Y5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
9910642 |  | Ground Loop | GEOCOMFORT | GZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910643 |  | Ground Loop | HYDRON MODULE | HZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910644 |  | Ground Loop | TETCO | TZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910645 |  | Ground Loop | GEOCOMFORT | GZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910646 |  | Ground Loop | HYDRON MODULE | HZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910647 |  | Ground Loop | TETCO | TZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910648 |  | Ground Loop | GEOCOMFORT | GZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910649 |  | Ground Loop | HYDRON MODULE | HZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910650 |  | Ground Loop | TETCO | TZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333 | No
9910660 |  | Ground Loop | GEOCOMFORT | GZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | Yes
9910661 |  | Ground Loop | HYDRON MODULE | HZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | Yes
9910662 |  | Ground Loop | TETCO | TZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | Yes
9910663 |  | Ground Loop | GEOCOMFORT | GZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910664 |  | Ground Loop | HYDRON MODULE | HZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910665 |  | Ground Loop | TETCO | TZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910666 |  | Ground Loop | GEOCOMFORT | GZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910667 |  | Ground Loop | HYDRON MODULE | HZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910668 |  | Ground Loop | TETCO | TZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675 | No
9910672 |  | Ground Loop | GEOCOMFORT | GZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | Yes
9910673 |  | Ground Loop | HYDRON MODULE | HZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | Yes
9910674 |  | Ground Loop | TETCO | TZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | Yes
9910675 |  | Ground Loop | GEOCOMFORT | GZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910676 |  | Ground Loop | HYDRON MODULE | HZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910677 |  | Ground Loop | TETCO | TZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910678 |  | Ground Loop | GEOCOMFORT | GZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910679 |  | Ground Loop | HYDRON MODULE | HZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910680 |  | Ground Loop | TETCO | TZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910681 |  | Ground Loop | GEOCOMFORT | GZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910682 |  | Ground Loop | HYDRON MODULE | HZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910683 |  | Ground Loop | TETCO | TZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167 | No
9910696 |  | Ground Loop | GEOCOMFORT | GZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | Yes
9910697 |  | Ground Loop | HYDRON MODULE | HZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | Yes
9910698 |  | Ground Loop | TETCO | TZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | Yes
9910699 |  | Ground Loop | GEOCOMFORT | GZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910700 |  | Ground Loop | HYDRON MODULE | HZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910701 |  | Ground Loop | TETCO | TZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910702 |  | Ground Loop | GEOCOMFORT | GZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910703 |  | Ground Loop | HYDRON MODULE | HZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910704 |  | Ground Loop | TETCO | TZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2 | No
9910708 |  | Ground Loop | GEOCOMFORT | GZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | Yes
9910709 |  | Ground Loop | HYDRON MODULE | HZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | Yes
9910710 |  | Ground Loop | TETCO | TZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | Yes
9910711 |  | Ground Loop | GEOCOMFORT | GZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910712 |  | Ground Loop | HYDRON MODULE | HZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910713 |  | Ground Loop | TETCO | TZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910714 |  | Ground Loop | GEOCOMFORT | GZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910715 |  | Ground Loop | HYDRON MODULE | HZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910716 |  | Ground Loop | TETCO | TZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910717 |  | Ground Loop | GEOCOMFORT | GZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910718 |  | Ground Loop | HYDRON MODULE | HZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910719 |  | Ground Loop | TETCO | TZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417 | No
9910752 |  | Ground Loop | GEOCOMFORT | GZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | Yes
9910753 |  | Ground Loop | HYDRON MODULE | HZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | Yes
9910754 |  | Ground Loop | TETCO | TZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | Yes
9910755 |  | Ground Loop | GEOCOMFORT | GZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583 | No
215224496 |  | Ground Loop | FHP | CF018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
215224497 |  | Ground Loop | FHP | CF024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224498 |  | Ground Loop | FHP | CF024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224499 |  | Ground Loop | FHP | CF024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224500 |  | Ground Loop | FHP | CF024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
4947178 |  | Ground Loop | TRANE | VSVE0241 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583 | No
4947179 |  | Ground Loop | TRANE | VSVE0242 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583 | No
4947180 |  | Ground Loop | TRANE | VSVE0244 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583 | No
4947183 |  | Ground Loop | TRANE | VSVE0331 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583 | No
4947184 |  | Ground Loop | TRANE | VSVE0332 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583 | No
4947185 |  | Ground Loop | TRANE | VSVE0334 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583 | No
4947240 |  | Ground Loop | TRANE | VSVE0501 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083 | No
4947241 |  | Ground Loop | TRANE | VSVE0502 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083 | No
4947242 |  | Ground Loop | TRANE | VSVE0504 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083 | No
5211514 |  | Ground Loop | DAIKIN | WGSV/WGSH007B*A |  | 8400 | 18.1 | 6200 | 3.9 | 0.7 | No
5211515 |  | Ground Loop | DAIKIN | WGSV/WGSH007B*E |  | 8400 | 18.1 | 6200 | 3.9 | 0.7 | No
5211516 |  | Ground Loop | DAIKIN | WGSV/WGSH007B*J |  | 8400 | 18.1 | 6200 | 3.9 | 0.7 | No
5220636 |  | Ground Loop | DAIKIN | WGSV/WGSH012B*A |  | 13300 | 18.1 | 10000 | 3.9 | 1.1083 | No
5220637 |  | Ground Loop | DAIKIN | WGSV/WGSH012B*E |  | 13300 | 18.1 | 10000 | 3.9 | 1.1083 | No
5220638 |  | Ground Loop | DAIKIN | WGSV/WGSH012B*J |  | 13300 | 17.2 | 10000 | 3.8 | 1.1083 | No
5220663 |  | Ground Loop | DAIKIN | WGSV/WGSH015B*E |  | 16000 | 21.2 | 11700 | 4.1 | 1.3333 | No
5220664 |  | Ground Loop | DAIKIN | WGSV/WGSH015B*J |  | 16000 | 19.1 | 11700 | 3.8 | 1.3333 | No
216508982 |  | Ground Loop | ClimateMaster | SJ/PN024A | SKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975 | Yes
216508983 |  | Ground Loop | ClimateMaster | SJ/PN036A | SKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667 | Yes
218353153 |  | Ground Loop | SKYMARK | PD012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218353154 |  | Ground Loop | SKYMARK | PD012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218353155 |  | Ground Loop | SKYMARK | PD012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218353156 |  | Ground Loop | SKYMARK | PD015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
218353157 |  | Ground Loop | SKYMARK | PD015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
218353158 |  | Ground Loop | SKYMARK | PD015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
218353159 |  | Ground Loop | SKYMARK | PD015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
218353160 |  | Ground Loop | SKYMARK | PD018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
218353161 |  | Ground Loop | SKYMARK | PD018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
218353162 |  | Ground Loop | SKYMARK | PD018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
218353163 |  | Ground Loop | SKYMARK | PD018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
218353166 |  | Ground Loop | SKYMARK | PD024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353167 |  | Ground Loop | SKYMARK | PD024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353170 |  | Ground Loop | SKYMARK | PD024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353171 |  | Ground Loop | SKYMARK | PD024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
201907614 |  | Ground Loop | WaterFurnace | URS036*3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907615 |  | Ground Loop | WaterFurnace | URS036*3*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907616 |  | Ground Loop | WaterFurnace | URS036*4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907617 |  | Ground Loop | WaterFurnace | URS036*4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907618 |  | Ground Loop | WaterFurnace | URS036*4*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
201907619 |  | Ground Loop | WaterFurnace | URS048*0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
201907620 |  | Ground Loop | WaterFurnace | URS048*0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
202434117 |  | Ground Loop | BOSCH | LV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434119 |  | Ground Loop | BOSCH | LV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434121 |  | Ground Loop | BOSCH | LV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434123 |  | Ground Loop | BOSCH | LV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417 | No
202434125 |  | Ground Loop | BOSCH | LV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434127 |  | Ground Loop | BOSCH | LV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434143 |  | Ground Loop | BOSCH | LV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434144 |  | Ground Loop | BOSCH | LV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434145 |  | Ground Loop | BOSCH | LV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434149 |  | Ground Loop | BOSCH | LV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434150 |  | Ground Loop | BOSCH | LV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434151 |  | Ground Loop | BOSCH | LV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
7487669 |  | Ground Loop | TETCO | TYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417 | No
7499543 |  | Ground Loop | FHP | LM024-1CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7499546 |  | Ground Loop | FHP | LM024-2CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7499547 |  | Ground Loop | FHP | LM024-3CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7499548 |  | Ground Loop | FHP | LM024-4CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
7499550 |  | Ground Loop | FHP | LM036-1VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
203372397 |  | Ground Loop | HEIL | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
203372398 |  | Ground Loop | ARCOAIRE | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372399 |  | Ground Loop | KEEPRITE | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372400 |  | Ground Loop | TEMPSTAR | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372401 |  | Ground Loop | COMFORTMAKER | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372402 |  | Ground Loop | DAY & NIGHT | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | Yes
203372403 |  | Ground Loop | HEIL | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
203372404 |  | Ground Loop | ARCOAIRE | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
203372405 |  | Ground Loop | KEEPRITE | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | Yes
6501931 |  | Ground Loop | GEOSTAR | GBV/GBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501932 |  | Ground Loop | GEOSTAR | GBV/GBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501933 |  | Ground Loop | GEOSTAR | GBV/GBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
6501934 |  | Ground Loop | GEOSTAR | GBV/GBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501935 |  | Ground Loop | GEOSTAR | GBV/GBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501936 |  | Ground Loop | GEOSTAR | GBV/GBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
6501937 |  | Ground Loop | GEOSTAR | GBV/GBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501938 |  | Ground Loop | GEOSTAR | GBV/GBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501939 |  | Ground Loop | GEOSTAR | GBV/GBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
6501940 |  | Ground Loop | GEOSTAR | GBV/GBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501941 |  | Ground Loop | GEOSTAR | GBV/GBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
6501942 |  | Ground Loop | GEOSTAR | GBV/GBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501943 |  | Ground Loop | GEOSTAR | GBV/GBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501944 |  | Ground Loop | GEOSTAR | GBV/GBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501945 |  | Ground Loop | GEOSTAR | GBV/GBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501946 |  | Ground Loop | GEOSTAR | GBV/GBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501947 |  | Ground Loop | GEOSTAR | GBV/GBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501948 |  | Ground Loop | GEOSTAR | GBV/GBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501949 |  | Ground Loop | GEOSTAR | GBV/GBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
6501951 |  | Ground Loop | GEOSTAR | GBV/GBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501952 |  | Ground Loop | GEOSTAR | GBV/GBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501954 |  | Ground Loop | GEOSTAR | GBV/GBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501955 |  | Ground Loop | GEOSTAR | GBV/GBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501957 |  | Ground Loop | GEOSTAR | GBV/GBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501958 |  | Ground Loop | GEOSTAR | GBV/GBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
6501961 |  | Ground Loop | GEOSTAR | GBV/GBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501962 |  | Ground Loop | GEOSTAR | GBV/GBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501964 |  | Ground Loop | GEOSTAR | GBV/GBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501965 |  | Ground Loop | GEOSTAR | GBV/GBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501967 |  | Ground Loop | GEOSTAR | GBV/GBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
202835053 |  | Ground Loop | BOSCH | SM036-1HZ*-*****C |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | Yes
202835056 |  | Ground Loop | BOSCH | SM024-1VT*-*****C |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417 | Yes
202835057 |  | Ground Loop | BOSCH | SM060-1VT*-*****C |  | 63900 | 18.6 | 48600 | 4 | 5.325 | Yes
202836307 |  | Ground Loop | BOSCH | SM036-1VT*-*****C |  | 40200 | 21 | 28200 | 4.3 | 3.35 | Yes
202836309 |  | Ground Loop | BOSCH | SM048-1VT*-*****C |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167 | Yes
202921908 |  | Ground Loop | BOSCH | EP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921909 |  | Ground Loop | BOSCH | EP036-3VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921910 |  | Ground Loop | BOSCH | EP036-4VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921911 |  | Ground Loop | BOSCH-GEO | BP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202921912 |  | Ground Loop | BOSCH | EP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
215223500 |  | Ground Loop | WaterFurnace | V5AV084*D3**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
215223501 |  | Ground Loop | WaterFurnace | V5AV084*D5**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5 | No
216767332 |  | Ground Loop | TETCO | TYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583 | Yes
216767333 |  | Ground Loop | HYDRON MODULE | HVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
216767334 |  | Ground Loop | HYDRON MODULE | HVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
216767335 |  | Ground Loop | HYDRON MODULE | HVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
216767336 |  | Ground Loop | HYDRON MODULE | HVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
216767337 |  | Ground Loop | HYDRON MODULE | HVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917 | Yes
216767338 |  | Ground Loop | HYDRON MODULE | HYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
216767339 |  | Ground Loop | HYDRON MODULE | HYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083 | Yes
216767340 |  | Ground Loop | HYDRON MODULE | HYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325 | Yes
216767341 |  | Ground Loop | HYDRON MODULE | HVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
216767342 |  | Ground Loop | HYDRON MODULE | HYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583 | Yes
216767344 |  | Ground Loop | HYDRON MODULE | HYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583 | Yes
216772562 |  | Ground Loop | Enertech | EBS018* | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167 | Yes
216772563 |  | Ground Loop | Enertech | EBT024* | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
216772564 |  | Ground Loop | Enertech | EBT036* | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075 | Yes
216772565 |  | Ground Loop | Enertech | EBT048* | EAD048 | 47800 | 17.3 | 41000 | 3.6 | 3.9833 | Yes
216772567 |  | Ground Loop | Enertech | EVS012* |  | 12625 | 18.2 | 9475 | 3.6 | 1.0521 | Yes
216772568 |  | Ground Loop | Enertech | EVS018* |  | 22275 | 24.1 | 15400 | 4.24 | 1.8562 | Yes
216772569 |  | Ground Loop | Enertech | EVT024* |  | 25775 | 20.5 | 19400 | 4.09 | 2.1479 | Yes
216772570 |  | Ground Loop | Enertech | EVT030* |  | 32900 | 19.8 | 24425 | 3.98 | 2.7417 | Yes
216772571 |  | Ground Loop | Enertech | EVT036* |  | 38450 | 18.8 | 29500 | 3.94 | 3.2042 | Yes
216772572 |  | Ground Loop | Enertech | EVT042* |  | 45900 | 19.4 | 32975 | 4.14 | 3.825 | Yes
216772573 |  | Ground Loop | Enertech | EVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917 | Yes
216772574 |  | Ground Loop | Enertech | EYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583 | Yes
216772575 |  | Ground Loop | Enertech | EYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083 | Yes
216772576 |  | Ground Loop | Enertech | EYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325 | Yes
216772579 |  | Ground Loop | Enertech | EZT024* |  | 26400 | 18.8 | 18400 | 3.9 | 2.2 | Yes
216772580 |  | Ground Loop | Enertech | EZT030* |  | 32625 | 17.6 | 24400 | 3.7 | 2.7188 | Yes
216772581 |  | Ground Loop | Enertech | EZT036* |  | 36725 | 18.9 | 28375 | 3.84 | 3.0604 | Yes
216772582 |  | Ground Loop | Enertech | EZT042* |  | 44750 | 18.8 | 32900 | 3.67 | 3.7292 | Yes
216772583 |  | Ground Loop | Enertech | EZT048* |  | 48700 | 17.3 | 36900 | 3.7 | 4.0583 | Yes
216772584 |  | Ground Loop | Enertech | EZT060* |  | 58875 | 17.4 | 44550 | 3.6 | 4.9062 | Yes
216772586 |  | Ground Loop | Enertech | EVS015* |  | 16725 | 24.1 | 11500 | 4.3 | 1.3938 | Yes
218471790 |  | Ground Loop | YORK | QD007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
218471791 |  | Ground Loop | YORK | QD007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
218471792 |  | Ground Loop | YORK | QD009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
218471793 |  | Ground Loop | YORK | QD009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
214772149 |  | Ground Loop | TRANE | DXVK0364 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772150 |  | Ground Loop | TRANE | DXVK048B |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772151 |  | Ground Loop | TRANE | DXVK0484 |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772152 |  | Ground Loop | TRANE | DXVK060B |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772153 |  | Ground Loop | TRANE | DXVK0604 |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772154 |  | Ground Loop | TRANE | DXVK070B |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772155 |  | Ground Loop | TRANE | DXVK0704 |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772156 |  | Ground Loop | TRANE | DXHK024B |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772157 |  | Ground Loop | TRANE | DXHK0244 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772158 |  | Ground Loop | TRANE | DXHK036B |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772159 |  | Ground Loop | TRANE | DXHK0364 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772160 |  | Ground Loop | TRANE | DXHK048B |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772161 |  | Ground Loop | TRANE | DXHK0484 |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772162 |  | Ground Loop | TRANE | DXHK060B |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772163 |  | Ground Loop | TRANE | DXHK0604 |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772164 |  | Ground Loop | TRANE | DXHK070B |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772165 |  | Ground Loop | TRANE | DXHK0704 |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
214772166 |  | Ground Loop | TRANE | DXVK0247 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772167 |  | Ground Loop | TRANE | DXVK0367 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772168 |  | Ground Loop | TRANE | DXHK0247 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772169 |  | Ground Loop | TRANE | DXHK0367 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214773312 |  | Ground Loop | TRANE | GEVK090 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667 | No
214776121 |  | Ground Loop | TRANE | GEVK120 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85 | No
214776125 |  | Ground Loop | TRANE | GEVK0904 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667 | No
214776126 |  | Ground Loop | TRANE | GEVK0908 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667 | No
214776135 |  | Ground Loop | TRANE | GEVK1203 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85 | No
214776136 |  | Ground Loop | TRANE | GEVK1208 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85 | No
214776169 |  | Ground Loop | TRANE | GETK0151-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167 | No
214776171 |  | Ground Loop | TRANE | GETK0241-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1 | No
216621360 |  | Ground Loop | GEOSTAR | G5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216621361 |  | Ground Loop | GEOSTAR | G5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216621362 |  | Ground Loop | GEOSTAR | G5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
216625456 |  | Ground Loop | GEOSTAR | G5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833 | No
216625457 |  | Ground Loop | GEOSTAR | G5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625458 |  | Ground Loop | GEOSTAR | G5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625459 |  | Ground Loop | GEOSTAR | G5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
216625460 |  | Ground Loop | GEOSTAR | G5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625461 |  | Ground Loop | GEOSTAR | G5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625462 |  | Ground Loop | GEOSTAR | G5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
216625463 |  | Ground Loop | GEOSTAR | G5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625464 |  | Ground Loop | GEOSTAR | G5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625465 |  | Ground Loop | GEOSTAR | G5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625466 |  | Ground Loop | GEOSTAR | G5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625467 |  | Ground Loop | GEOSTAR | G5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625468 |  | Ground Loop | GEOSTAR | G5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625469 |  | Ground Loop | GEOSTAR | G5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
216625470 |  | Ground Loop | GEOSTAR | G5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625471 |  | Ground Loop | GEOSTAR | G5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625472 |  | Ground Loop | GEOSTAR | G5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625473 |  | Ground Loop | GEOSTAR | G5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625474 |  | Ground Loop | GEOSTAR | G5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625475 |  | Ground Loop | GEOSTAR | G5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625476 |  | Ground Loop | GEOSTAR | G5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
216625477 |  | Ground Loop | GEOSTAR | G5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625478 |  | Ground Loop | GEOSTAR | G5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625479 |  | Ground Loop | GEOSTAR | G5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625480 |  | Ground Loop | GEOSTAR | G5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
216625481 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625482 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625483 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
216625484 |  | Ground Loop | GEOSTAR | G5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
209180330 |  | Ground Loop | HYDROTECH | WSV6018B* |  | 18000 | 17.2 | 13500 | 3.6 | 1.5 | Yes
209180331 |  | Ground Loop | HYDROTECH | WSV6036B* |  | 37000 | 18 | 28000 | 3.6 | 3.0833 | Yes
209180332 |  | Ground Loop | HYDROTECH | WSV6042B* |  | 42000 | 18.5 | 30000 | 3.6 | 3.5 | Yes
209180334 |  | Ground Loop | HYDROTECH | WSV6048B* |  | 51000 | 17.7 | 37000 | 3.6 | 4.25 | Yes
209180335 |  | Ground Loop | AE Air | WSV6018B* |  | 18000 | 17.2 | 13500 | 3.6 | 1.5 | Yes
209180336 |  | Ground Loop | AE Air | WSV6036B* |  | 37000 | 18 | 28000 | 3.6 | 3.0833 | Yes
209180337 |  | Ground Loop | AE Air | WSV6042B* |  | 42000 | 18.5 | 30000 | 3.6 | 3.5 | Yes
209180338 |  | Ground Loop | AE Air | WSV6048B* |  | 51000 | 17.7 | 37000 | 3.6 | 4.25 | Yes
209323637 |  | Ground Loop | HYDROTECH | WSV6009B* |  | 10000 | 19 | 7500 | 3.7 | 0.83333 | Yes
209323638 |  | Ground Loop | AE Air | WSV6009B* |  | 10000 | 19 | 7500 | 3.7 | 0.83333 | Yes
209945912 |  | Ground Loop | WaterFurnace | NBV/NBH009**0*6 |  | 9800 | 17.1 | 7800 | 3.6 | 0.81667 | No
209945913 |  | Ground Loop | WaterFurnace | NBV/NBH009**2*6 |  | 9800 | 17.1 | 7800 | 3.6 | 0.81667 | No
209945914 |  | Ground Loop | WaterFurnace | NBV/NBH012**0*6 |  | 12200 | 17.1 | 9500 | 3.6 | 1.0167 | No
209945915 |  | Ground Loop | WaterFurnace | NBV/NBH012**2*6 |  | 12200 | 17.1 | 9500 | 3.6 | 1.0167 | No
210286836 |  | Ground Loop | Energy Catalyst | DHHP036TV | DHHP036TV | 37500 | 17 | 29300 | 4.3 | 3.125 | Yes
210286837 |  | Ground Loop | Energy Catalyst | DHHP036TH | DHHP036TH | 37500 | 17 | 29300 | 4.3 | 3.125 | Yes
215415917 |  | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | Yes
215415918 |  | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | Yes
215415919 |  | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | No
215415920 |  | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917 | No
215415921 |  | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 39200 | 19.5 | 28400 | 4.2 | 3.2667 | No
215415922 |  | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 39200 | 19.5 | 28400 | 4.2 | 3.2667 | No
215415923 |  | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 52000 | 20.2 | 37600 | 4.1 | 4.3333 | No
215415924 |  | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 52000 | 20.2 | 37600 | 4.1 | 4.3333 | No
215415925 |  | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | No
215415926 |  | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167 | No
215415927 |  | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | No
215415928 |  | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225 | No
206346948 |  | Ground Loop | DAIKIN | WVFW*024*E***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
206346949 |  | Ground Loop | DAIKIN | WVFW*024*F***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
206346950 |  | Ground Loop | DAIKIN | WVFW*024*J***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
206346954 |  | Ground Loop | DAIKIN | WVFW*030*E***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
206346955 |  | Ground Loop | DAIKIN | WVFW*030*F***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
206346956 |  | Ground Loop | DAIKIN | WVFW*030*J***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
206346966 |  | Ground Loop | DAIKIN | WVFW*042*E***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
206346967 |  | Ground Loop | DAIKIN | WVFW*042*F***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
206346968 |  | Ground Loop | DAIKIN | WVFW*042*K***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
206346972 |  | Ground Loop | DAIKIN | WVFW*048*E***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
206346973 |  | Ground Loop | DAIKIN | WVFW*048*F***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
206346974 |  | Ground Loop | DAIKIN | WVFW*048*K***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
206194171 |  | Ground Loop | Johnson Controls | JSH/V/D030C*K B |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333 | Yes
206194172 |  | Ground Loop | SKYMARK | JSH/V/D030C*K C |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333 | Yes
206194173 |  | Ground Loop | Johnson Controls | JSH/V/D048C*K B |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167 | No
206194174 |  | Ground Loop | SKYMARK | JSH/V/D048C*K C |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167 | No
206194175 |  | Ground Loop | Johnson Controls | JSH/V/D060C*K B |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667 | No
206194176 |  | Ground Loop | SKYMARK | JSH/V/D060C*K C |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667 | No
206194177 |  | Ground Loop | Johnson Controls | JSH/V/D070C*K B |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833 | No
206194178 |  | Ground Loop | SKYMARK | JSH/V/D070C*K C |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833 | No
206223145 |  | Ground Loop | ClimateMaster | TRT060D |  | 64500 | 17.9 | 46000 | 3.7 | 5.375 | No
206223146 |  | Ground Loop | CENTURY | HZS024B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
206223147 |  | Ground Loop | COMFORT-AIRE | HZS024B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
206223148 |  | Ground Loop | CENTURY | HZS024B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
206223149 |  | Ground Loop | COMFORT-AIRE | HZS024B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
206223150 |  | Ground Loop | CENTURY | HZS036B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
206223151 |  | Ground Loop | COMFORT-AIRE | HZS036B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
206229666 |  | Ground Loop | BOSCH | EP024-1HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229667 |  | Ground Loop | BOSCH | EP024-2HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229668 |  | Ground Loop | BOSCH | EP024-3HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229669 |  | Ground Loop | BOSCH | EP024-4HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229674 |  | Ground Loop | FHP | EP024-1HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229675 |  | Ground Loop | FHP | EP024-2HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229676 |  | Ground Loop | FHP | EP024-3HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
206229677 |  | Ground Loop | FHP | EP024-4HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
202330514 |  | Ground Loop | AAON, Inc. | M2-003-1-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917 | No
202330518 |  | Ground Loop | AAON, Inc. | M2-003-2-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917 | No
202330522 |  | Ground Loop | AAON, Inc. | M2-003-3-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917 | No
202330526 |  | Ground Loop | AAON, Inc. | M2-003-4-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917 | No
202330529 |  | Ground Loop | AAON, Inc. | M2-004-1-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667 | No
202330530 |  | Ground Loop | AAON, Inc. | M2-004-1-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325 | No
202330531 |  | Ground Loop | AAON, Inc. | M2-004-1-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1 | No
202330532 |  | Ground Loop | AAON, Inc. | M2-004-1-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417 | No
202330533 |  | Ground Loop | AAON, Inc. | M2-004-2-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667 | No
202330534 |  | Ground Loop | AAON, Inc. | M2-004-2-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325 | No
202330535 |  | Ground Loop | AAON, Inc. | M2-004-2-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1 | No
202330536 |  | Ground Loop | AAON, Inc. | M2-004-2-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417 | No
202330537 |  | Ground Loop | AAON, Inc. | M2-004-3-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667 | No
202330538 |  | Ground Loop | AAON, Inc. | M2-004-3-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325 | No
202330539 |  | Ground Loop | AAON, Inc. | M2-004-3-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1 | No
202330540 |  | Ground Loop | AAON, Inc. | M2-004-3-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417 | No
202330541 |  | Ground Loop | AAON, Inc. | M2-004-4-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667 | No
202330542 |  | Ground Loop | AAON, Inc. | M2-004-4-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325 | No
202330543 |  | Ground Loop | AAON, Inc. | M2-004-4-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1 | No
202330544 |  | Ground Loop | AAON, Inc. | M2-004-4-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417 | No
216979867 |  | Ground Loop | HEIL | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979868 |  | Ground Loop | ARCOAIRE | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979869 |  | Ground Loop | KEEPRITE | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979870 |  | Ground Loop | TEMPSTAR | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979871 |  | Ground Loop | COMFORTMAKER | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979872 |  | Ground Loop | DAY & NIGHT | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216979873 |  | Ground Loop | HEIL | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979874 |  | Ground Loop | ARCOAIRE | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979875 |  | Ground Loop | KEEPRITE | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979876 |  | Ground Loop | TEMPSTAR | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979877 |  | Ground Loop | COMFORTMAKER | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979878 |  | Ground Loop | DAY & NIGHT | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216979879 |  | Ground Loop | HEIL | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979880 |  | Ground Loop | ARCOAIRE | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979881 |  | Ground Loop | KEEPRITE | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979882 |  | Ground Loop | TEMPSTAR | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979883 |  | Ground Loop | COMFORTMAKER | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979884 |  | Ground Loop | DAY & NIGHT | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216979885 |  | Ground Loop | HEIL | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216979886 |  | Ground Loop | ARCOAIRE | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216979887 |  | Ground Loop | KEEPRITE | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216625824 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625825 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625826 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625827 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | No
216625828 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625829 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
202147004 |  | Ground Loop | HYDRON MODULE | HZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147005 |  | Ground Loop | HYDRON MODULE | HZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | Yes
202147006 |  | Ground Loop | HYDRON MODULE | HZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147007 |  | Ground Loop | HYDRON MODULE | HZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147008 |  | Ground Loop | HYDRON MODULE | HZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147009 |  | Ground Loop | TETCO | TZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | Yes
202147010 |  | Ground Loop | TETCO | TZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147011 |  | Ground Loop | TETCO | TZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147012 |  | Ground Loop | TETCO | TZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147013 |  | Ground Loop | TETCO | TZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147014 |  | Ground Loop | TETCO | TZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | Yes
213502562 |  | Ground Loop | DAIKIN | WSMH030E1*G/J*T |  | 29500 | 20.6 | 21900 | 4 | 2.4583 | No
213502563 |  | Ground Loop | DAIKIN | WSMH030E1*G/J*C |  | 29500 | 20.6 | 21900 | 4 | 2.4583 | No
213502567 |  | Ground Loop | DAIKIN | WSMH036E1*G/J*P |  | 37800 | 18.8 | 30700 | 3.9 | 3.15 | No
213502568 |  | Ground Loop | DAIKIN | WSMH036E1*G/J*T |  | 38000 | 19.9 | 30000 | 4 | 3.1667 | No
213502569 |  | Ground Loop | DAIKIN | WSMH036E1*G/J*C |  | 38000 | 19.9 | 30000 | 4 | 3.1667 | No
213502573 |  | Ground Loop | DAIKIN | WSCH042E1*G/J*P |  | 39900 | 17.5 | 32500 | 3.7 | 3.325 | No
213502574 |  | Ground Loop | DAIKIN | WSCH042E1*G/J*T |  | 40800 | 19.4 | 31600 | 3.8 | 3.4 | No
213502575 |  | Ground Loop | DAIKIN | WSCH042E1*G/J*C |  | 40800 | 19.4 | 31600 | 3.8 | 3.4 | No
217967044 |  | Ground Loop | TRANE | VSHK0504 |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417 | No
217967045 |  | Ground Loop | TRANE | VSVK0504 |  | 50400 | 19.3 | 40400 | 4.3 | 4.2 | No
217967046 |  | Ground Loop | TRANE | VSHK0604 |  | 61900 | 17 | 51400 | 3.9 | 5.1583 | No
217967047 |  | Ground Loop | TRANE | VSVK0604 |  | 61200 | 17.9 | 49500 | 4.1 | 5.1 | No
218002304 |  | Ground Loop | Viessmann | 100-WA-AP1T027020 |  | 24700 | 18.9 | 18200 | 3.9 | 2.0583 | Yes
218002305 |  | Ground Loop | Viessmann | 100-WA-AP1T040029 |  | 38500 | 19 | 29700 | 4.1 | 3.2083 | Yes
218002306 |  | Ground Loop | Viessmann | 100-WA-AP1T052038 |  | 52000 | 19.5 | 38400 | 4.1 | 4.3333 | Yes
218002307 |  | Ground Loop | Viessmann | 100-WA-AP1T066049 |  | 60900 | 17 | 43900 | 3.8 | 5.075 | Yes
216743538 |  | Ground Loop | DAIKIN | WSNH048E1*G/J*C |  | 49100 | 18.8 | 38500 | 3.6 | 4.0917 | No
216743541 |  | Ground Loop | DAIKIN | WSNV024E1*G/J*C |  | 25100 | 18.8 | 18200 | 3.8 | 2.0917 | No
216743542 |  | Ground Loop | DAIKIN | WSNV024F3*G/J*C |  | 25100 | 18.4 | 18200 | 3.8 | 2.0917 | No
216743543 |  | Ground Loop | DAIKIN | WSNV024J1*G/J*C |  | 25100 | 18.4 | 18200 | 3.8 | 2.0917 | No
216743544 |  | Ground Loop | DAIKIN | WSNV024K3*G/J*C |  | 25100 | 18.2 | 18200 | 3.7 | 2.0917 | No
216743617 |  | Ground Loop | BOSCH-GEO | RP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216743618 |  | Ground Loop | BOSCH | CP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743619 |  | Ground Loop | BOSCH | CP024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743620 |  | Ground Loop | BOSCH | CP024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743621 |  | Ground Loop | BOSCH | CP024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743622 |  | Ground Loop | BOSCH-GEO | RP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216743623 |  | Ground Loop | BOSCH | CP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743624 |  | Ground Loop | BOSCH | CP024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743625 |  | Ground Loop | BOSCH | CP024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743626 |  | Ground Loop | BOSCH | CP024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743627 |  | Ground Loop | BOSCH-GEO | RP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | Yes
216743628 |  | Ground Loop | BOSCH | CP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743629 |  | Ground Loop | BOSCH | CP024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743630 |  | Ground Loop | BOSCH | CP024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743631 |  | Ground Loop | BOSCH | CP024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
216743632 |  | Ground Loop | BOSCH-GEO | RP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | Yes
216743633 |  | Ground Loop | BOSCH | CP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743634 |  | Ground Loop | BOSCH | CP024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743635 |  | Ground Loop | BOSCH | CP024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743636 |  | Ground Loop | BOSCH | CP024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
216743637 |  | Ground Loop | BOSCH-GEO | RP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | Yes
216743638 |  | Ground Loop | BOSCH | CP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216743639 |  | Ground Loop | BOSCH | CP036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216743640 |  | Ground Loop | BOSCH | CP036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216743641 |  | Ground Loop | BOSCH | CP036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
216743642 |  | Ground Loop | BOSCH-GEO | RP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | Yes
216743643 |  | Ground Loop | BOSCH | CP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216743644 |  | Ground Loop | BOSCH | CP036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216743645 |  | Ground Loop | BOSCH | CP036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216743646 |  | Ground Loop | BOSCH | CP036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
216743647 |  | Ground Loop | BOSCH-GEO | RP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | Yes
216743648 |  | Ground Loop | BOSCH | CP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216743649 |  | Ground Loop | BOSCH | CP048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216743650 |  | Ground Loop | BOSCH | CP048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
216743651 |  | Ground Loop | BOSCH-GEO | RP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | Yes
216743652 |  | Ground Loop | BOSCH | CP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216743653 |  | Ground Loop | BOSCH | CP048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216743654 |  | Ground Loop | BOSCH | CP048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
216743655 |  | Ground Loop | BOSCH-GEO | RP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | Yes
216743656 |  | Ground Loop | BOSCH | CP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216743657 |  | Ground Loop | BOSCH | CP060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216743658 |  | Ground Loop | BOSCH | CP060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
216743659 |  | Ground Loop | BOSCH-GEO | RP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | Yes
216743660 |  | Ground Loop | BOSCH | CP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
216743661 |  | Ground Loop | BOSCH | CP060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
218470791 |  | Ground Loop | Dandelion Geothermal | AXU036 |  | 38800 | 20.8 | 29700 | 3.8 | 3.2333 | Yes
4219425 |  | Ground Loop | NORDIC | R55HACW-P-1T-*-SDE** |  | 45400 | 17 | 35600 | 3.8 | 3.7833 | Yes
202434484 |  | Ground Loop | BOSCH | SV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
202434485 |  | Ground Loop | BOSCH | SV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15 | No
217642886 |  | Ground Loop | GeoSmart Energy | S3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
217642897 |  | Ground Loop | GeoSmart Energy | S3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642898 |  | Ground Loop | GeoSmart Energy | S3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642899 |  | Ground Loop | GeoSmart Energy | S3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642900 |  | Ground Loop | GeoSmart Energy | S3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642901 |  | Ground Loop | GeoSmart Energy | S3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642902 |  | Ground Loop | GeoSmart Energy | S3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642903 |  | Ground Loop | GeoSmart Energy | S3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667 | No
217642911 |  | Ground Loop | GeoSmart Energy | S3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642912 |  | Ground Loop | GeoSmart Energy | S3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642913 |  | Ground Loop | GeoSmart Energy | S3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
217642914 |  | Ground Loop | GeoSmart Energy | S3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3 | No
214595658 |  | Ground Loop | AAON, Inc. | RN-009-2-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595659 |  | Ground Loop | AAON, Inc. | RN-009-3-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595660 |  | Ground Loop | AAON, Inc. | RN-009-4-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595661 |  | Ground Loop | AAON, Inc. | RN-009-2-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595662 |  | Ground Loop | AAON, Inc. | RN-009-3-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
214595663 |  | Ground Loop | AAON, Inc. | RN-009-4-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425 | No
215893693 |  | Ground Loop | DUAL AIR | CFF024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | No
205503116 |  | Ground Loop | BOSCH-GEO | SM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125 | Yes
205503120 |  | Ground Loop | BOSCH-GEO | LM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125 | No
205503124 |  | Ground Loop | BOSCH | SM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125 | Yes
205503128 |  | Ground Loop | FHP | LM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125 | No
205652453 |  | Ground Loop | BOSCH-GEO | SM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083 | Yes
205652454 |  | Ground Loop | BOSCH-GEO | SM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417 | Yes
214067603 |  | Ground Loop | GeoSmart Energy | GBV/GBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214067604 |  | Ground Loop | GeoSmart Energy | GBV/GBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214067606 |  | Ground Loop | GeoSmart Energy | GBV/GBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067607 |  | Ground Loop | GeoSmart Energy | GBV/GBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067608 |  | Ground Loop | GeoSmart Energy | GBV/GBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067609 |  | Ground Loop | GeoSmart Energy | GBV/GBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
214067866 |  | Ground Loop | GeoSmart Energy | GBV/GBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067867 |  | Ground Loop | GeoSmart Energy | GBV/GBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067871 |  | Ground Loop | GeoSmart Energy | GBV/GBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214067872 |  | Ground Loop | GeoSmart Energy | GBV/GBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
214390535 |  | Ground Loop | Dandelion Geo | DP1G060V3A1000S |  | 62000 | 17 | 53000 | 4.5 | 5.1667 | Yes
214437585 |  | Ground Loop | Dandelion Geo | DP1G036V3A1000S |  | 39200 | 19.8 | 31000 | 4.6 | 3.2667 | Yes
214437586 |  | Ground Loop | Dandelion Geo | DP1G048V3A1000S |  | 51500 | 18.8 | 41500 | 4.4 | 4.2917 | Yes
207198436 |  | Ground Loop | BOSCH | QV030-4VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198437 |  | Ground Loop | BOSCH | QV036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198440 |  | Ground Loop | BOSCH | QV036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198441 |  | Ground Loop | BOSCH | QV036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198443 |  | Ground Loop | BOSCH | QV036-2HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198446 |  | Ground Loop | BOSCH | QV036-2VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198447 |  | Ground Loop | BOSCH | QV036-2VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198449 |  | Ground Loop | BOSCH | QV036-3HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198452 |  | Ground Loop | BOSCH | QV036-3VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198454 |  | Ground Loop | BOSCH | QV036-3VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207198455 |  | Ground Loop | BOSCH | QV036-4HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198458 |  | Ground Loop | BOSCH | QV036-4VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198460 |  | Ground Loop | BOSCH | QV036-4VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
215268702 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268703 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268704 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268705 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268706 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268707 |  | Ground Loop | WaterFurnace | V5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268708 |  | Ground Loop | WaterFurnace | V5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268709 |  | Ground Loop | WaterFurnace | V5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268710 |  | Ground Loop | WaterFurnace | V5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268711 |  | Ground Loop | WaterFurnace | V5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268712 |  | Ground Loop | WaterFurnace | V5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268713 |  | Ground Loop | WaterFurnace | V5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268714 |  | Ground Loop | WaterFurnace | V5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268715 |  | Ground Loop | WaterFurnace | V5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268716 |  | Ground Loop | WaterFurnace | V5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
215268717 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268718 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268719 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268720 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268721 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268722 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268723 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268724 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268725 |  | Ground Loop | WaterFurnace | V5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
215268726 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268727 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268728 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268729 |  | Ground Loop | WaterFurnace | V5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25 | No
215268730 |  | Ground Loop | WaterFurnace | V5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268731 |  | Ground Loop | WaterFurnace | V5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
215268732 |  | Ground Loop | WaterFurnace | V5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268733 |  | Ground Loop | WaterFurnace | V5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333 | No
215268734 |  | Ground Loop | WaterFurnace | V5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125 | No
215268735 |  | Ground Loop | WaterFurnace | V5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
215268736 |  | Ground Loop | WaterFurnace | V5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
215268737 |  | Ground Loop | WaterFurnace | V5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268738 |  | Ground Loop | WaterFurnace | V5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
215268739 |  | Ground Loop | WaterFurnace | V5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
213307834 |  | Ground Loop | GeoSmart Energy | QT038**1*(1,2)*****K |  | 36000 | 18.7 | 27400 | 3.9 | 3 | Yes
213307835 |  | Ground Loop | GeoSmart Energy | QT049**1*(1,2)*****J |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | Yes
213307837 |  | Ground Loop | GeoSmart Energy | QT072**1*1*****J |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | Yes
213502489 |  | Ground Loop | DAIKIN | WSMH007A1*G/J*T |  | 7400 | 18.8 | 5500 | 3.6 | 0.61667 | No
213502493 |  | Ground Loop | DAIKIN | WSMH007E1*G/J*T |  | 7600 | 19 | 5500 | 3.6 | 0.63333 | No
215827089 |  | Ground Loop | DAIKIN | WSLH120F1*G/J |  | 123000 | 17.1 | 90000 | 3.7 | 10.25 | No
215827090 |  | Ground Loop | DAIKIN | WSLH120K1*G/J |  | 123000 | 17.1 | 90000 | 3.6 | 10.25 | No
215827091 |  | Ground Loop | DAIKIN | WSLH120L1*G/J |  | 123000 | 17.1 | 90000 | 3.6 | 10.25 | No
215402564 |  | Ground Loop | DAIKIN | WSSV030E1*H*C |  | 30200 | 21.8 | 20700 | 3.83 | 2.5167 | No
215402565 |  | Ground Loop | DAIKIN | WSSV030F3*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167 | No
215402568 |  | Ground Loop | DAIKIN | WSSV036E1*H*T |  | 40500 | 21.9 | 27600 | 3.84 | 3.375 | No
215402569 |  | Ground Loop | DAIKIN | WSSV036F3*H*T |  | 40500 | 21.18 | 27600 | 3.83 | 3.375 | No
215402572 |  | Ground Loop | DAIKIN | WSSV036E1*H*C |  | 40500 | 21.9 | 27600 | 3.84 | 3.375 | No
215402573 |  | Ground Loop | DAIKIN | WSSV036F3*H*C |  | 40500 | 21.18 | 27600 | 3.83 | 3.375 | No
215405064 |  | Ground Loop | DAIKIN | WSSV060E1*H*T |  | 66300 | 20 | 48800 | 4 | 5.525 | No
215405065 |  | Ground Loop | DAIKIN | WSSV060F3*H*T |  | 66300 | 19.8 | 48800 | 3.96 | 5.525 | No
215405066 |  | Ground Loop | DAIKIN | WSSV060K3*H*T |  | 66300 | 19.8 | 48800 | 3.92 | 5.525 | No
215405067 |  | Ground Loop | DAIKIN | WSSV060L3*H*T |  | 66300 | 19.4 | 48800 | 3.88 | 5.525 | No
215405068 |  | Ground Loop | DAIKIN | WSSV060E1*H*C |  | 66300 | 20 | 48800 | 4 | 5.525 | No
215405069 |  | Ground Loop | DAIKIN | WSSV060F3*H*C |  | 66300 | 19.8 | 48800 | 3.96 | 5.525 | No
215405070 |  | Ground Loop | DAIKIN | WSSV060K3*H*C |  | 66300 | 19.8 | 48800 | 3.92 | 5.525 | No
215405071 |  | Ground Loop | DAIKIN | WSSV060L3*H*C |  | 66300 | 19.4 | 48800 | 3.88 | 5.525 | No
215405076 |  | Ground Loop | DAIKIN | WSSV070E1*H*T |  | 75400 | 19.4 | 54700 | 3.8 | 6.2833 | No
215405077 |  | Ground Loop | DAIKIN | WSSV070F3*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
215405078 |  | Ground Loop | DAIKIN | WSSV070K3*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
215405079 |  | Ground Loop | DAIKIN | WSSV070L3*H*T |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833 | No
217754586 |  | Ground Loop | DAIKIN | WSMH042K1*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
217754591 |  | Ground Loop | DAIKIN | WSMH048E1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
217754592 |  | Ground Loop | DAIKIN | WSMH048F1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
217754593 |  | Ground Loop | DAIKIN | WSMH048K1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
217754594 |  | Ground Loop | DAIKIN | WSMH048L1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
217754598 |  | Ground Loop | DAIKIN | WSMH048E1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754599 |  | Ground Loop | DAIKIN | WSMH048F1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754600 |  | Ground Loop | DAIKIN | WSMH048K1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
10259035 |  | Ground Loop | GEOCOMFORT | GZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | Yes
10259036 |  | Ground Loop | HYDRON MODULE | HZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | Yes
10259037 |  | Ground Loop | TETCO | TZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | Yes
10259038 |  | Ground Loop | GEOCOMFORT | GZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | No
10259039 |  | Ground Loop | HYDRON MODULE | HZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | No
10259040 |  | Ground Loop | TETCO | TZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667 | No
10259044 |  | Ground Loop | GEOCOMFORT | GZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | Yes
10259045 |  | Ground Loop | HYDRON MODULE | HZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | Yes
10259046 |  | Ground Loop | TETCO | TZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | Yes
10259047 |  | Ground Loop | GEOCOMFORT | GZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | No
10259048 |  | Ground Loop | HYDRON MODULE | HZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | No
10259049 |  | Ground Loop | TETCO | TZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275 | No
10259054 |  | Ground Loop | GEOCOMFORT | GZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | Yes
10259055 |  | Ground Loop | HYDRON MODULE | HZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | Yes
10259056 |  | Ground Loop | TETCO | TZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | Yes
10259057 |  | Ground Loop | GEOCOMFORT | GZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | No
10259058 |  | Ground Loop | HYDRON MODULE | HZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083 | No
7519776 |  | Ground Loop | HYDRON MODULE | HVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519777 |  | Ground Loop | TETCO | TVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7520238 |  | Ground Loop | GEOCOMFORT | GVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | Yes
7520239 |  | Ground Loop | HYDRON MODULE | HVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | Yes
7520240 |  | Ground Loop | TETCO | TVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | Yes
7520241 |  | Ground Loop | GEOCOMFORT | GVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520242 |  | Ground Loop | HYDRON MODULE | HVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520243 |  | Ground Loop | TETCO | TVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520244 |  | Ground Loop | TETCO | TVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520245 |  | Ground Loop | HYDRON MODULE | HVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520246 |  | Ground Loop | GEOCOMFORT | GVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520247 |  | Ground Loop | HYDRON MODULE | HVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520248 |  | Ground Loop | TETCO | TVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520249 |  | Ground Loop | GEOCOMFORT | GVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167 | No
7520250 |  | Ground Loop | GEOCOMFORT | GVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | Yes
7520251 |  | Ground Loop | HYDRON MODULE | HVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | Yes
7520252 |  | Ground Loop | TETCO | TVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | Yes
7520253 |  | Ground Loop | GEOCOMFORT | GVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520254 |  | Ground Loop | HYDRON MODULE | HVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520255 |  | Ground Loop | TETCO | TVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520256 |  | Ground Loop | GEOCOMFORT | GVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520257 |  | Ground Loop | HYDRON MODULE | HVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520258 |  | Ground Loop | TETCO | TVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520259 |  | Ground Loop | GEOCOMFORT | GVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520260 |  | Ground Loop | HYDRON MODULE | HVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7520261 |  | Ground Loop | TETCO | TVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333 | No
7523956 |  | Ground Loop | GEOCOMFORT | GVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | Yes
7523957 |  | Ground Loop | HYDRON MODULE | HVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | Yes
7523958 |  | Ground Loop | TETCO | TVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | Yes
7523959 |  | Ground Loop | GEOCOMFORT | GVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | No
7523960 |  | Ground Loop | HYDRON MODULE | HVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | No
7523961 |  | Ground Loop | TETCO | TVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083 | No
203459712 |  | Ground Loop | BOSCH-GEO | LM036-1CSC-*****B | LM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583 | No
3706350 |  | Ground Loop | GEOSTAR | ZS015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
3706351 |  | Ground Loop | GEOSTAR | ZS015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
3706369 |  | Ground Loop | GEOSTAR | ZS018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
215224782 |  | Ground Loop | CARRIER | GBA18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224783 |  | Ground Loop | BRYANT | GBA18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224784 |  | Ground Loop | CARRIER | GBA18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224785 |  | Ground Loop | BRYANT | GBA18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224786 |  | Ground Loop | CARRIER | GBA24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224787 |  | Ground Loop | BRYANT | GBA24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224788 |  | Ground Loop | CARRIER | GBA24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224789 |  | Ground Loop | BRYANT | GBA24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224810 |  | Ground Loop | HEIL | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224811 |  | Ground Loop | ARCOAIRE | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224812 |  | Ground Loop | KEEPRITE | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224813 |  | Ground Loop | TEMPSTAR | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224814 |  | Ground Loop | COMFORTMAKER | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224815 |  | Ground Loop | DAY & NIGHT | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224816 |  | Ground Loop | HEIL | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224817 |  | Ground Loop | ARCOAIRE | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224818 |  | Ground Loop | KEEPRITE | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224819 |  | Ground Loop | TEMPSTAR | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224820 |  | Ground Loop | COMFORTMAKER | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224821 |  | Ground Loop | DAY & NIGHT | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224822 |  | Ground Loop | HEIL | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224823 |  | Ground Loop | ARCOAIRE | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224824 |  | Ground Loop | KEEPRITE | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224825 |  | Ground Loop | TEMPSTAR | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224826 |  | Ground Loop | COMFORTMAKER | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
217193306 |  | Ground Loop | WaterFurnace | V7A(V/H)024*V0**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125 | No
217193307 |  | Ground Loop | WaterFurnace | V7A(V/H)036*V0**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25 | No
217193308 |  | Ground Loop | WaterFurnace | V7A(V/H)048*V0**1* |  | 48000 | 20 | 38000 | 3.8 | 4 | No
217193309 |  | Ground Loop | WaterFurnace | V7A(V/H)060*V0**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083 | No
217193552 |  | Ground Loop | WaterFurnace | V7A(V/H)024*V3**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125 | No
217193553 |  | Ground Loop | WaterFurnace | V7A(V/H)024*V4**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125 | No
217193554 |  | Ground Loop | WaterFurnace | V7A(V/H)036*V3**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25 | No
217193555 |  | Ground Loop | WaterFurnace | V7A(V/H)036*V4**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25 | No
217193556 |  | Ground Loop | WaterFurnace | V7A(V/H)048*V3**1* |  | 48000 | 20 | 38000 | 3.8 | 4 | No
217193557 |  | Ground Loop | WaterFurnace | V7A(V/H)048*V4**1* |  | 48000 | 20 | 38000 | 3.8 | 4 | No
217193558 |  | Ground Loop | WaterFurnace | V7A(V/H)060*V3**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083 | No
217193559 |  | Ground Loop | WaterFurnace | V7A(V/H)060*V4**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083 | No
217212043 |  | Ground Loop | FHP | CP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212044 |  | Ground Loop | FHP | CP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212045 |  | Ground Loop | FHP | CP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212046 |  | Ground Loop | FHP | CP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212048 |  | Ground Loop | FHP | CP024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212049 |  | Ground Loop | FHP | CP024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212050 |  | Ground Loop | FHP | CP024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212051 |  | Ground Loop | FHP | CP024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212052 |  | Ground Loop | FHP | CP024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212054 |  | Ground Loop | FHP | CP024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212055 |  | Ground Loop | FHP | CP024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212056 |  | Ground Loop | FHP | CP024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212057 |  | Ground Loop | FHP | CP024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212059 |  | Ground Loop | FHP | CP024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212060 |  | Ground Loop | FHP | CP024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125 | No
217212061 |  | Ground Loop | FHP | CP024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833 | No
217212062 |  | Ground Loop | FHP | CP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
217212064 |  | Ground Loop | FHP | CP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217212065 |  | Ground Loop | FHP | CP036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
217212066 |  | Ground Loop | FHP | CP036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217212067 |  | Ground Loop | FHP | CP036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
217212068 |  | Ground Loop | FHP | CP036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217212070 |  | Ground Loop | FHP | CP036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25 | No
217212071 |  | Ground Loop | FHP | CP036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083 | No
217212072 |  | Ground Loop | FHP | CP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
217212073 |  | Ground Loop | FHP | CP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
217212074 |  | Ground Loop | FHP | CP048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
963507 |  | Ground Loop | WaterFurnace | NLV/NXV080T*3 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
963508 |  | Ground Loop | WaterFurnace | NLV/NXV080T*4 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
963509 |  | Ground Loop | WaterFurnace | NLV/NXV080T*5 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167 | No
963510 |  | Ground Loop | WaterFurnace | NLV/NXV095T*3 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
963511 |  | Ground Loop | WaterFurnace | NLV/NXV095T*4 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
963512 |  | Ground Loop | WaterFurnace | NLV/NXV095T*5 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167 | No
963513 |  | Ground Loop | WaterFurnace | NLV/NXV120T*3 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
963514 |  | Ground Loop | WaterFurnace | NLV/NXV120T*4 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
963515 |  | Ground Loop | WaterFurnace | NLV/NXV120T*5 |  | 122000 | 18 | 83000 | 3.6 | 10.1667 | No
1483426 |  | Ground Loop | BOSCH | BP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
1483428 |  | Ground Loop | BOSCH | BP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
1483429 |  | Ground Loop | BOSCH | BP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
218494308 |  | Ground Loop | ClimateMaster | SMT(S,M)18A*L |  | 18900 | 17.8 | 13500 | 3.6 | 1.575 | No
218494310 |  | Ground Loop | ClimateMaster | SMT(S,M)24A*L |  | 25900 | 20.5 | 18000 | 3.7 | 2.1583 | No
218494315 |  | Ground Loop | ClimateMaster | SMT(S,M)30A*L |  | 30000 | 19 | 22300 | 3.7 | 2.5 | No
5315780 |  | Ground Loop | WaterFurnace | NBV/NBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315781 |  | Ground Loop | WaterFurnace | NBV/NBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315782 |  | Ground Loop | WaterFurnace | NBV/NBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315783 |  | Ground Loop | WaterFurnace | NBV/NBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315784 |  | Ground Loop | WaterFurnace | NBV/NBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5315785 |  | Ground Loop | WaterFurnace | NBV/NBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
5316500 |  | Ground Loop | WaterFurnace | NBV/NBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316501 |  | Ground Loop | WaterFurnace | NBV/NBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316502 |  | Ground Loop | WaterFurnace | NBV/NBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316503 |  | Ground Loop | WaterFurnace | NBV/NBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316504 |  | Ground Loop | WaterFurnace | NBV/NBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316505 |  | Ground Loop | WaterFurnace | NBV/NBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
5316510 |  | Ground Loop | WaterFurnace | NBV/NBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316511 |  | Ground Loop | WaterFurnace | NBV/NBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316512 |  | Ground Loop | WaterFurnace | NBV/NBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316513 |  | Ground Loop | WaterFurnace | NBV/NBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316514 |  | Ground Loop | WaterFurnace | NBV/NBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316515 |  | Ground Loop | WaterFurnace | NBV/NBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5316516 |  | Ground Loop | WaterFurnace | NBV/NBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
5317193 |  | Ground Loop | WaterFurnace | NBV/NBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317194 |  | Ground Loop | WaterFurnace | NBV/NBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317195 |  | Ground Loop | WaterFurnace | NBV/NBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317196 |  | Ground Loop | WaterFurnace | NBV/NBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317197 |  | Ground Loop | WaterFurnace | NBV/NBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317198 |  | Ground Loop | WaterFurnace | NBV/NBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317199 |  | Ground Loop | WaterFurnace | NBV/NBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317200 |  | Ground Loop | WaterFurnace | NBV/NBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5317201 |  | Ground Loop | WaterFurnace | NBV/NBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317202 |  | Ground Loop | WaterFurnace | NBV/NBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317203 |  | Ground Loop | WaterFurnace | NBV/NBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317205 |  | Ground Loop | WaterFurnace | NBV/NBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317206 |  | Ground Loop | WaterFurnace | NBV/NBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317207 |  | Ground Loop | WaterFurnace | NBV/NBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
5317209 |  | Ground Loop | WaterFurnace | NBV/NBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317210 |  | Ground Loop | WaterFurnace | NBV/NBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317211 |  | Ground Loop | WaterFurnace | NBV/NBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317270 |  | Ground Loop | WaterFurnace | NBV/NBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317328 |  | Ground Loop | WaterFurnace | NBV/NBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317329 |  | Ground Loop | WaterFurnace | NBV/NBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
5317330 |  | Ground Loop | WaterFurnace | NBV/NBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317331 |  | Ground Loop | WaterFurnace | NBV/NBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317332 |  | Ground Loop | WaterFurnace | NBV/NBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317333 |  | Ground Loop | WaterFurnace | NBV/NBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317334 |  | Ground Loop | WaterFurnace | NBV/NBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5317335 |  | Ground Loop | WaterFurnace | NBV/NBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
5440541 |  | Ground Loop | GEOCOMFORT | GXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | Yes
5440542 |  | Ground Loop | HYDRON MODULE | HXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | Yes
5440543 |  | Ground Loop | TETCO | TXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | Yes
5440554 |  | Ground Loop | GEOCOMFORT | GXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | Yes
218353355 |  | Ground Loop | JOHNSON CONTROLS | DD009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218353356 |  | Ground Loop | JOHNSON CONTROLS | DD009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
218353357 |  | Ground Loop | JOHNSON CONTROLS | DD012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218353358 |  | Ground Loop | JOHNSON CONTROLS | DD012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218353359 |  | Ground Loop | JOHNSON CONTROLS | DD012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218353360 |  | Ground Loop | JOHNSON CONTROLS | DD012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
218353361 |  | Ground Loop | JOHNSON CONTROLS | DD015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
218353362 |  | Ground Loop | JOHNSON CONTROLS | DD015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
218353363 |  | Ground Loop | JOHNSON CONTROLS | DD015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
218353364 |  | Ground Loop | JOHNSON CONTROLS | DD015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | No
218353365 |  | Ground Loop | JOHNSON CONTROLS | DD018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
218353366 |  | Ground Loop | JOHNSON CONTROLS | DD018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
218353367 |  | Ground Loop | JOHNSON CONTROLS | DD018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | No
218353368 |  | Ground Loop | JOHNSON CONTROLS | DD018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | No
218353371 |  | Ground Loop | JOHNSON CONTROLS | DD024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353372 |  | Ground Loop | JOHNSON CONTROLS | DD024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353375 |  | Ground Loop | JOHNSON CONTROLS | DD024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353376 |  | Ground Loop | JOHNSON CONTROLS | DD024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353379 |  | Ground Loop | JOHNSON CONTROLS | DD024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353380 |  | Ground Loop | JOHNSON CONTROLS | DD024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353383 |  | Ground Loop | JOHNSON CONTROLS | DD024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218353384 |  | Ground Loop | JOHNSON CONTROLS | DD024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
202146948 |  | Ground Loop | GEOCOMFORT | GZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | Yes
202146949 |  | Ground Loop | GEOCOMFORT | GZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146950 |  | Ground Loop | GEOCOMFORT | GZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146951 |  | Ground Loop | GEOCOMFORT | GZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146952 |  | Ground Loop | HYDRON MODULE | HZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | Yes
202146953 |  | Ground Loop | HYDRON MODULE | HZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146954 |  | Ground Loop | HYDRON MODULE | HZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146955 |  | Ground Loop | HYDRON MODULE | HZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146956 |  | Ground Loop | HYDRON MODULE | HZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146957 |  | Ground Loop | HYDRON MODULE | HZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | Yes
202146958 |  | Ground Loop | HYDRON MODULE | HZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146959 |  | Ground Loop | HYDRON MODULE | HZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146960 |  | Ground Loop | HYDRON MODULE | HZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146961 |  | Ground Loop | TETCO | TZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | Yes
202146962 |  | Ground Loop | TETCO | TZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146963 |  | Ground Loop | TETCO | TZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146964 |  | Ground Loop | TETCO | TZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146965 |  | Ground Loop | TETCO | TZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417 | No
202146966 |  | Ground Loop | TETCO | TZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | Yes
202146967 |  | Ground Loop | TETCO | TZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146968 |  | Ground Loop | TETCO | TZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146969 |  | Ground Loop | TETCO | TZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833 | No
202146970 |  | Ground Loop | GEOCOMFORT | GZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | Yes
202146971 |  | Ground Loop | GEOCOMFORT | GZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146972 |  | Ground Loop | GEOCOMFORT | GZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146973 |  | Ground Loop | GEOCOMFORT | GZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146974 |  | Ground Loop | GEOCOMFORT | GZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146975 |  | Ground Loop | GEOCOMFORT | GZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | Yes
202146976 |  | Ground Loop | GEOCOMFORT | GZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202146977 |  | Ground Loop | HYDRON MODULE | HZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | Yes
202146978 |  | Ground Loop | HYDRON MODULE | HZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146979 |  | Ground Loop | HYDRON MODULE | HZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
6501887 |  | Ground Loop | GEOSTAR | GBV/GBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
6501888 |  | Ground Loop | GEOSTAR | GBV/GBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
6501889 |  | Ground Loop | GEOSTAR | GBV/GBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
6501890 |  | Ground Loop | GEOSTAR | GBV/GBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
6501891 |  | Ground Loop | GEOSTAR | GBV/GBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
6501892 |  | Ground Loop | GEOSTAR | GBV/GBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
6501894 |  | Ground Loop | GEOSTAR | GBV/GBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
6501895 |  | Ground Loop | GEOSTAR | GBV/GBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
6501897 |  | Ground Loop | GEOSTAR | GBV/GBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
6501898 |  | Ground Loop | GEOSTAR | GBV/GBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
6501899 |  | Ground Loop | GEOSTAR | GBV/GBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
6501900 |  | Ground Loop | GEOSTAR | GBV/GBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501901 |  | Ground Loop | GEOSTAR | GBV/GBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501902 |  | Ground Loop | GEOSTAR | GBV/GBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
6501903 |  | Ground Loop | GEOSTAR | GBV/GBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501904 |  | Ground Loop | GEOSTAR | GBV/GBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501905 |  | Ground Loop | GEOSTAR | GBV/GBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
6501906 |  | Ground Loop | GEOSTAR | GBV/GBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501907 |  | Ground Loop | GEOSTAR | GBV/GBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501908 |  | Ground Loop | GEOSTAR | GBV/GBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
6501909 |  | Ground Loop | GEOSTAR | GBV/GBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501910 |  | Ground Loop | GEOSTAR | GBV/GBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667 | No
6501911 |  | Ground Loop | GEOSTAR | GBV/GBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207348739 |  | Ground Loop | WaterFurnace | URD072*3*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348740 |  | Ground Loop | WaterFurnace | URD072*4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348741 |  | Ground Loop | WaterFurnace | URD072*4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207348742 |  | Ground Loop | WaterFurnace | URD072*4*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207349379 |  | Ground Loop | WaterFurnace | NBV/NBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349380 |  | Ground Loop | WaterFurnace | NBV/NBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349381 |  | Ground Loop | WaterFurnace | NBV/NBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349382 |  | Ground Loop | WaterFurnace | NBV/NBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349383 |  | Ground Loop | WaterFurnace | NBV/NBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349384 |  | Ground Loop | WaterFurnace | NBV/NBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
204835632 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
204835633 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205129920 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
205129921 |  | Ground Loop | GEOSTAR | 103J036**1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
205145424 |  | Ground Loop | GEOCOMFORT | GVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
205145425 |  | Ground Loop | GEOCOMFORT | GVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145426 |  | Ground Loop | GEOCOMFORT | GVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145427 |  | Ground Loop | HYDRON MODULE | HVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
205145428 |  | Ground Loop | HYDRON MODULE | HVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145429 |  | Ground Loop | HYDRON MODULE | HVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145430 |  | Ground Loop | TETCO | TVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | Yes
205145431 |  | Ground Loop | TETCO | TVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145432 |  | Ground Loop | TETCO | TVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145433 |  | Ground Loop | GEOCOMFORT | GVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
205145434 |  | Ground Loop | GEOCOMFORT | GVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145435 |  | Ground Loop | GEOCOMFORT | GVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145436 |  | Ground Loop | HYDRON MODULE | HVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
205145437 |  | Ground Loop | HYDRON MODULE | HVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145438 |  | Ground Loop | HYDRON MODULE | HVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145439 |  | Ground Loop | TETCO | TVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
205145527 |  | Ground Loop | GEOCOMFORT | GVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145528 |  | Ground Loop | HYDRON MODULE | HVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145529 |  | Ground Loop | TETCO | TVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833 | No
205145530 |  | Ground Loop | TETCO | TVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | Yes
205145531 |  | Ground Loop | TETCO | TVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825 | No
213710613 |  | Ground Loop | DAIKIN | WSSH012E1*H*T |  | 12000 | 20.3 | 9100 | 3.9 | 1 | No
213710616 |  | Ground Loop | DAIKIN | WSSH012J1*H*T |  | 12200 | 19 | 9100 | 3.8 | 1.0167 | No
213710620 |  | Ground Loop | DAIKIN | WSSH015A1*H*T |  | 17100 | 23.7 | 11000 | 3.9 | 1.425 | No
213710622 |  | Ground Loop | DAIKIN | WSSH015A1*H*C |  | 17100 | 23.7 | 11000 | 3.9 | 1.425 | No
213710624 |  | Ground Loop | DAIKIN | WSSH015E1*H*T |  | 17100 | 23.69 | 11000 | 3.9 | 1.425 | No
213710625 |  | Ground Loop | DAIKIN | WSSH015E1*H*C |  | 17100 | 23.69 | 11000 | 3.9 | 1.425 | No
213710629 |  | Ground Loop | DAIKIN | WSSH015J1*H*T |  | 17000 | 22 | 10900 | 3.9 | 1.4167 | No
213710630 |  | Ground Loop | DAIKIN | WSSH015J1*H*C |  | 17000 | 22 | 10900 | 3.9 | 1.4167 | No
213710633 |  | Ground Loop | DAIKIN | WSSH019E1*H*T |  | 20700 | 21.1 | 14100 | 3.8 | 1.725 | No
213710634 |  | Ground Loop | DAIKIN | WSSH019E1*H*C |  | 20700 | 21.1 | 14100 | 3.8 | 1.725 | No
213710638 |  | Ground Loop | DAIKIN | WSSH019J1*H*T |  | 20700 | 21.1 | 14100 | 3.8 | 1.725 | No
213710639 |  | Ground Loop | DAIKIN | WSSH019J1*H*C |  | 20700 | 21.1 | 14100 | 3.8 | 1.725 | No
213710641 |  | Ground Loop | DAIKIN | WSSH024E1*H*T |  | 25700 | 21.7 | 16900 | 4 | 2.1417 | No
213710643 |  | Ground Loop | DAIKIN | WSSH024E1*H*C |  | 25700 | 21.7 | 16900 | 4 | 2.1417 | No
213710645 |  | Ground Loop | DAIKIN | WSSH030E1*H*T |  | 30600 | 22.5 | 21200 | 4.2 | 2.55 | No
213710646 |  | Ground Loop | DAIKIN | WSSH030E1*H*C |  | 30600 | 22.5 | 21200 | 4.2 | 2.55 | No
213710648 |  | Ground Loop | DAIKIN | WSSH036E1*H*T |  | 40300 | 22 | 27600 | 3.7 | 3.3583 | No
213710650 |  | Ground Loop | DAIKIN | WSSH036E1*H*C |  | 40300 | 22 | 27600 | 3.7 | 3.3583 | No
213710652 |  | Ground Loop | DAIKIN | WSSH042E1*H*T |  | 44000 | 21.7 | 29000 | 3.9 | 3.6667 | No
213710653 |  | Ground Loop | DAIKIN | WSSH042E1*H*C |  | 44000 | 21.7 | 29000 | 3.9 | 3.6667 | No
213710655 |  | Ground Loop | DAIKIN | WSSH048E1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
213710657 |  | Ground Loop | DAIKIN | WSSH048E1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
214595621 |  | Ground Loop | AAON, Inc. | M2-004-2-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325 | No
214595625 |  | Ground Loop | AAON, Inc. | M2-004-3-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325 | No
214595629 |  | Ground Loop | AAON, Inc. | M2-004-4-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325 | No
215866540 |  | Ground Loop | DAIKIN | WSTH048E1*G/J*C |  | 49300 | 19.59 | 36300 | 3.87 | 4.1083 | No
215866541 |  | Ground Loop | DAIKIN | WSTH048F3*G/J*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083 | No
215866542 |  | Ground Loop | DAIKIN | WSTV024E1*G/J*C |  | 22400 | 17.99 | 17200 | 3.98 | 1.8667 | No
215866543 |  | Ground Loop | DAIKIN | WSTV024F3*G/J*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667 | No
215866544 |  | Ground Loop | DAIKIN | WSTV048E1*G/J*C |  | 52400 | 20.17 | 35200 | 3.9 | 4.3667 | No
215866545 |  | Ground Loop | DAIKIN | WSTV048F3*G/J*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667 | No
5220682 |  | Ground Loop | DAIKIN | WGSV/WGSH036B*F |  | 38500 | 22 | 26200 | 4.3 | 3.2083 | No
5220683 |  | Ground Loop | DAIKIN | WGSV/WGSH036B*J |  | 38500 | 22 | 26200 | 4.3 | 3.2083 | No
5220684 |  | Ground Loop | DAIKIN | WGSV/WGSH036B*K |  | 38500 | 22 | 26200 | 4.3 | 3.2083 | No
5220686 |  | Ground Loop | DAIKIN | WGSV/WGSH042B*E |  | 45500 | 20.2 | 31300 | 4 | 3.7917 | No
5220687 |  | Ground Loop | DAIKIN | WGSV/WGSH042B*F |  | 45500 | 20.2 | 31300 | 4 | 3.7917 | No
5220688 |  | Ground Loop | DAIKIN | WGSV/WGSH042B*K |  | 45500 | 20.2 | 31300 | 4 | 3.7917 | No
5220690 |  | Ground Loop | DAIKIN | WGSV/WGSH048B*E |  | 52700 | 19.9 | 36900 | 4 | 4.3917 | No
5220691 |  | Ground Loop | DAIKIN | WGSV/WGSH048B*F |  | 52700 | 19.9 | 36900 | 4 | 4.3917 | No
5220693 |  | Ground Loop | DAIKIN | WGSV/WGSH048B*K |  | 52700 | 19.9 | 36900 | 4 | 4.3917 | No
5220700 |  | Ground Loop | DAIKIN | WGSV/WGSH060B*E |  | 66300 | 20 | 46500 | 3.8 | 5.525 | No
5220701 |  | Ground Loop | DAIKIN | WGSV/WGSH060B*F |  | 66300 | 20 | 46500 | 3.8 | 5.525 | No
5220702 |  | Ground Loop | DAIKIN | WGSV/WGSH060B*K |  | 66300 | 20 | 46500 | 3.8 | 5.525 | No
5220703 |  | Ground Loop | DAIKIN | WGSV/WGSH070B*E |  | 75700 | 18 | 55800 | 3.7 | 6.3083 | No
5220704 |  | Ground Loop | DAIKIN | WGSV/WGSH070B*F |  | 75700 | 18 | 55800 | 3.7 | 6.3083 | No
5220705 |  | Ground Loop | DAIKIN | WGSV/WGSH070B*K |  | 75700 | 18 | 55800 | 3.7 | 6.3083 | No
5220707 |  | Ground Loop | DAIKIN | WGTV/WGTH026B*E |  | 27600 | 19.27 | 18100 | 4.1 | 2.3 | No
5220708 |  | Ground Loop | DAIKIN | WGTV/WGTH026B*F |  | 27600 | 19.27 | 18100 | 4.1 | 2.3 | No
5220709 |  | Ground Loop | DAIKIN | WGTV/WGTH026B*J |  | 27600 | 19.27 | 18100 | 4.1 | 2.3 | No
5220710 |  | Ground Loop | DAIKIN | WGTV/WGTH026B*K |  | 27600 | 19.27 | 18100 | 4.1 | 2.3 | No
5220933 |  | Ground Loop | DAIKIN | WGTV/WGTH032B*E |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167 | No
5220934 |  | Ground Loop | DAIKIN | WGTV/WGTH032B*F |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167 | No
5220935 |  | Ground Loop | DAIKIN | WGTV/WGTH032B*J |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167 | No
5220936 |  | Ground Loop | DAIKIN | WGTV/WGTH032B*K |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167 | No
5220980 |  | Ground Loop | DAIKIN | WGTV/WGTH038B*E |  | 40200 | 20.1 | 28100 | 4.2 | 3.35 | No
5220981 |  | Ground Loop | DAIKIN | WGTV/WGTH038B*F |  | 40200 | 20.1 | 28100 | 4.2 | 3.35 | No
5220982 |  | Ground Loop | DAIKIN | WGTV/WGTH038B*K |  | 40200 | 20.1 | 28100 | 4.2 | 3.35 | No
5220983 |  | Ground Loop | DAIKIN | WGTV/WGTH044B*E |  | 45900 | 19.8 | 31700 | 4 | 3.825 | No
5220984 |  | Ground Loop | DAIKIN | WGTV/WGTH044B*F |  | 45900 | 19.8 | 31700 | 4 | 3.825 | No
5220985 |  | Ground Loop | DAIKIN | WGTV/WGTH044B*K |  | 45900 | 19.8 | 31700 | 4 | 3.825 | No
5220987 |  | Ground Loop | DAIKIN | WGTV/WGTH049B*E |  | 50600 | 19.2 | 35900 | 4 | 4.2167 | No
5220988 |  | Ground Loop | DAIKIN | WGTV/WGTH049B*F |  | 50600 | 19.2 | 35900 | 4 | 4.2167 | No
5220989 |  | Ground Loop | DAIKIN | WGTV/WGTH049B*K |  | 50600 | 19.2 | 35900 | 4 | 4.2167 | No
5220990 |  | Ground Loop | DAIKIN | WGTV/WGTH064B*E |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917 | No
5220991 |  | Ground Loop | DAIKIN | WGTV/WGTH064B*F |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917 | No
5220992 |  | Ground Loop | DAIKIN | WGTV/WGTH064B*K |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917 | No
5295936 |  | Ground Loop | WaterFurnace | NBV/NBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
5295937 |  | Ground Loop | WaterFurnace | NBV/NBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25 | No
5295944 |  | Ground Loop | WaterFurnace | NBV/NBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
5295945 |  | Ground Loop | WaterFurnace | NBV/NBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
5295947 |  | Ground Loop | WaterFurnace | NBV/NBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
5295948 |  | Ground Loop | WaterFurnace | NBV/NBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25 | No
5295964 |  | Ground Loop | WaterFurnace | NBV/NBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
5295966 |  | Ground Loop | WaterFurnace | NBV/NBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
5295968 |  | Ground Loop | WaterFurnace | NBV/NBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
5295969 |  | Ground Loop | WaterFurnace | NBV/NBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
5295980 |  | Ground Loop | WaterFurnace | NBV/NBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
5295981 |  | Ground Loop | WaterFurnace | NBV/NBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
5295982 |  | Ground Loop | WaterFurnace | NBV/NBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
5295983 |  | Ground Loop | WaterFurnace | NBV/NBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667 | No
9114306 |  | Ground Loop | GEOCOMFORT | GZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
9114307 |  | Ground Loop | HYDRON MODULE | HZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | Yes
9114308 |  | Ground Loop | TETCO | TZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | Yes
9114309 |  | Ground Loop | GEOCOMFORT | GZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1 | No
205767606 |  | Ground Loop | ClimateMaster | VEV/H/D0930 |  | 24000 | 24.3 | 30000 | 3.6 | 2 | Yes
205767612 |  | Ground Loop | ClimateMaster | TZV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
205767615 |  | Ground Loop | ClimateMaster | QEV/H/D0930 |  | 24000 | 24.3 | 30000 | 3.6 | 2 | Yes
205767616 |  | Ground Loop | ClimateMaster | TYV/H060B |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | No
205767623 |  | Ground Loop | ClimateMaster | TCH/V015A*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
205767624 |  | Ground Loop | ClimateMaster | TRH/V015A*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333 | No
205767626 |  | Ground Loop | ClimateMaster | TES/P038B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
205780261 |  | Ground Loop | GEOSTAR | 111J038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
205782086 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ042J1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
205782087 |  | Ground Loop | GEOSTAR | 103J042**1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
205782239 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
205782240 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | No
205782241 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205782242 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAST038**1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205782243 |  | Ground Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55 | Yes
205782244 |  | Ground Loop | GeoSmart Energy | GSZ042*1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15 | Yes
205782245 |  | Ground Loop | GeoSmart Energy | GTZ038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205782246 |  | Ground Loop | GeoSmart Energy | GTS038*1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
205782247 |  | Ground Loop | GeoSmart Energy | GTS038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
205782567 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YACT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
205782571 |  | Ground Loop | GeoSmart Energy | QT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
205788273 |  | Ground Loop | Johnson Controls | JSH/V/D018B B |  | 19500 | 18.4 | 14500 | 3.6 | 1.625 | No
205788274 |  | Ground Loop | SKYMARK | JSH/V/D018B C |  | 19500 | 18.4 | 14500 | 3.6 | 1.625 | No
205788275 |  | Ground Loop | Johnson Controls | JSH/V/D018B*K B |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833 | No
205788276 |  | Ground Loop | SKYMARK | JSH/V/D018B*K C |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833 | No
205788277 |  | Ground Loop | Johnson Controls | JSH/V/D024C B |  | 25300 | 18.9 | 19200 | 4 | 2.1083 | No
205788278 |  | Ground Loop | SKYMARK | JSH/V/D024C C |  | 25300 | 18.9 | 19200 | 4 | 2.1083 | No
205788279 |  | Ground Loop | Johnson Controls | JSH/V/D024C*K B |  | 25500 | 20.9 | 19100 | 4.2 | 2.125 | No
205788280 |  | Ground Loop | SKYMARK | JSH/V/D024C*K C |  | 25500 | 20.9 | 19100 | 4.2 | 2.125 | No
205788281 |  | Ground Loop | Johnson Controls | JSH/V/D030C B |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333 | No
205788282 |  | Ground Loop | SKYMARK | JSH/V/D030C C |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333 | No
205788283 |  | Ground Loop | Johnson Controls | JSH/V/D036C B |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583 | No
205788284 |  | Ground Loop | SKYMARK | JSH/V/D036C C |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583 | No
214772086 |  | Ground Loop | TRANE | EXVK0367 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772087 |  | Ground Loop | TRANE | EXVK042B |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214772088 |  | Ground Loop | TRANE | EXVK0424 |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214772089 |  | Ground Loop | TRANE | EXVK048B |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214772090 |  | Ground Loop | TRANE | EXVK0484 |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214772091 |  | Ground Loop | TRANE | EXVK060B |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214772092 |  | Ground Loop | TRANE | EXVK0604 |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214772093 |  | Ground Loop | TRANE | EXVK070B |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772094 |  | Ground Loop | TRANE | EXVK0704 |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772095 |  | Ground Loop | TRANE | DXVK024A |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214772096 |  | Ground Loop | TRANE | DXVK036A |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167 | No
214772097 |  | Ground Loop | TRANE | DXVK048A |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583 | No
214772098 |  | Ground Loop | TRANE | DXVK060A |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083 | No
214772099 |  | Ground Loop | TRANE | DXVK070A |  | 65100 | 18.9 | 51700 | 4.1 | 5.425 | No
213710596 |  | Ground Loop | DAIKIN | WSSH007A1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625 | No
213710598 |  | Ground Loop | DAIKIN | WSSH007E1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625 | No
213710600 |  | Ground Loop | DAIKIN | WSSH007J1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625 | No
213710604 |  | Ground Loop | DAIKIN | WSSH009A1*H*T |  | 9500 | 21 | 7000 | 3.91 | 0.79167 | No
213710605 |  | Ground Loop | DAIKIN | WSSH009E1*H*T |  | 9500 | 21 | 7000 | 3.91 | 0.79167 | No
213710611 |  | Ground Loop | DAIKIN | WSSH012A1*H*T |  | 12200 | 20.1 | 9100 | 3.9 | 1.0167 | No
207177503 |  | Ground Loop | TRANE | DXVG060A |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
207177504 |  | Ground Loop | TRANE | DXVG060B |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
207177505 |  | Ground Loop | TRANE | DXVG0604 |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917 | No
207177506 |  | Ground Loop | TRANE | DXVG070A |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
207177507 |  | Ground Loop | TRANE | DXVG070B |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
207177508 |  | Ground Loop | TRANE | DXVG0704 |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
207178484 |  | Ground Loop | GEOSTAR | 163H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207178485 |  | Ground Loop | GEOSTAR | 164H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207178486 |  | Ground Loop | GEOSTAR | 164H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207178492 |  | Ground Loop | GEOSTAR | 163J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207178493 |  | Ground Loop | GEOSTAR | 164J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207178495 |  | Ground Loop | GEOSTAR | 163J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207178496 |  | Ground Loop | GEOSTAR | 163J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
207178497 |  | Ground Loop | GEOSTAR | 163J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207178498 |  | Ground Loop | GEOSTAR | 163J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207178499 |  | Ground Loop | GEOSTAR | 164J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207178500 |  | Ground Loop | GEOSTAR | 163J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207178519 |  | Ground Loop | GEOSTAR | 164H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207178520 |  | Ground Loop | GEOSTAR | 164H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207178521 |  | Ground Loop | GEOSTAR | 164H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207178522 |  | Ground Loop | GEOSTAR | 164H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
207178525 |  | Ground Loop | GEOSTAR | 161/162J064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
207178536 |  | Ground Loop | GEOSTAR | 163H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207198394 |  | Ground Loop | BOSCH | QV024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198395 |  | Ground Loop | BOSCH | QV024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198401 |  | Ground Loop | BOSCH | QV024-2HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198402 |  | Ground Loop | BOSCH | QV024-2HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198406 |  | Ground Loop | BOSCH | QV024-3HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198407 |  | Ground Loop | BOSCH | QV024-3HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
217897449 |  | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
217897450 |  | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
217897453 |  | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
217897454 |  | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
217897455 |  | Ground Loop | CENTURY | MJN024A | MKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975 | Yes
217897456 |  | Ground Loop | COMFORT-AIRE | MJN024A | MKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975 | Yes
217897457 |  | Ground Loop | CENTURY | MJN036A | MKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667 | Yes
217897458 |  | Ground Loop | COMFORT-AIRE | MJN036A | MKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667 | Yes
217897463 |  | Ground Loop | CENTURY | MJN024A | MAN024A | 23900 | 19 | 17900 | 4 | 1.9917 | Yes
217897464 |  | Ground Loop | COMFORT-AIRE | MJN024A | MAN024A | 23900 | 19 | 17900 | 4 | 1.9917 | Yes
217897465 |  | Ground Loop | CENTURY | MJN036A | MAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917 | Yes
217897466 |  | Ground Loop | COMFORT-AIRE | MJN036A | MAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917 | Yes
217897467 |  | Ground Loop | CENTURY | MJN048A | MAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833 | Yes
217897468 |  | Ground Loop | COMFORT-AIRE | MJN048A | MAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833 | Yes
217897469 |  | Ground Loop | CENTURY | MJN060A | MAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167 | Yes
217897470 |  | Ground Loop | COMFORT-AIRE | MJN060A | MAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167 | Yes
217903418 |  | Ground Loop | WaterFurnace | V5R036*S0**1* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903419 |  | Ground Loop | WaterFurnace | V5R036*S0**4* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903420 |  | Ground Loop | WaterFurnace | V5R036*S0**5* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903421 |  | Ground Loop | WaterFurnace | V5R048*S0**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903422 |  | Ground Loop | WaterFurnace | V5R048*S0**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903423 |  | Ground Loop | WaterFurnace | V5R048*S0**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833 | No
217903424 |  | Ground Loop | WaterFurnace | V5R060*S0**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903425 |  | Ground Loop | WaterFurnace | V5R060*S0**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903426 |  | Ground Loop | WaterFurnace | V5R060*S0**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417 | No
217903427 |  | Ground Loop | WaterFurnace | V5R072*S0**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903428 |  | Ground Loop | WaterFurnace | V5R072*S0**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903429 |  | Ground Loop | WaterFurnace | V5R072*S0**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903430 |  | Ground Loop | WaterFurnace | V5R036*S3**1* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
217903431 |  | Ground Loop | WaterFurnace | V5R036*S3**4* |  | 36000 | 20.6 | 25000 | 4 | 3 | No
9035995 |  | Ground Loop | TETCO | TZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | Yes
9035996 |  | Ground Loop | GEOCOMFORT | GZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9035997 |  | Ground Loop | HYDRON MODULE | HZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9035998 |  | Ground Loop | TETCO | TZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9035999 |  | Ground Loop | GEOCOMFORT | GZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036000 |  | Ground Loop | HYDRON MODULE | HZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036001 |  | Ground Loop | TETCO | TZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036002 |  | Ground Loop | GEOCOMFORT | GZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036003 |  | Ground Loop | HYDRON MODULE | HZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036004 |  | Ground Loop | TETCO | TZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333 | No
9036975 |  | Ground Loop | GEOCOMFORT | GZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | Yes
9036998 |  | Ground Loop | HYDRON MODULE | HZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | Yes
9037017 |  | Ground Loop | TETCO | TZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | Yes
9037062 |  | Ground Loop | GEOCOMFORT | GZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037081 |  | Ground Loop | HYDRON MODULE | HZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037097 |  | Ground Loop | TETCO | TZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037137 |  | Ground Loop | GEOCOMFORT | GZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037158 |  | Ground Loop | HYDRON MODULE | HZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037175 |  | Ground Loop | TETCO | TZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037215 |  | Ground Loop | GEOCOMFORT | GZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
207348654 |  | Ground Loop | WaterFurnace | URS036*0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348655 |  | Ground Loop | WaterFurnace | URS036*0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348656 |  | Ground Loop | WaterFurnace | URS036*0*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348657 |  | Ground Loop | WaterFurnace | URS036*3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348658 |  | Ground Loop | WaterFurnace | URS036*3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348659 |  | Ground Loop | WaterFurnace | URS036*3*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348660 |  | Ground Loop | WaterFurnace | URS036*4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348661 |  | Ground Loop | WaterFurnace | URS036*4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348662 |  | Ground Loop | WaterFurnace | URS036*4*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207348663 |  | Ground Loop | WaterFurnace | URS048*0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348664 |  | Ground Loop | WaterFurnace | URS048*0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
207348665 |  | Ground Loop | WaterFurnace | URS048*0*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5440555 |  | Ground Loop | HYDRON MODULE | HXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | Yes
5440557 |  | Ground Loop | TETCO | TXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | Yes
5440573 |  | Ground Loop | GEOCOMFORT | GXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440574 |  | Ground Loop | HYDRON MODULE | HXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440575 |  | Ground Loop | TETCO | TXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440576 |  | Ground Loop | GEOCOMFORT | GXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440577 |  | Ground Loop | HYDRON MODULE | HXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440578 |  | Ground Loop | TETCO | TXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440703 |  | Ground Loop | GEOCOMFORT | GXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440704 |  | Ground Loop | HYDRON MODULE | HXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440705 |  | Ground Loop | TETCO | TXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25 | No
5440708 |  | Ground Loop | GEOCOMFORT | GXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440709 |  | Ground Loop | HYDRON MODULE | HXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5440710 |  | Ground Loop | TETCO | TXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925 | No
5599272 |  | Ground Loop | BOSCH-GEO | SM036-1CF/HZ/VT |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
5599275 |  | Ground Loop | BOSCH-GEO | SM060-1CF/HZ/VT |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
5615034 |  | Ground Loop | DAIKIN | WCCW5030*E*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625 | No
5615035 |  | Ground Loop | DAIKIN | WCCW5030*F*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625 | No
5615036 |  | Ground Loop | DAIKIN | WCCW5030*J*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625 | No
202434716 |  | Ground Loop | CARRIER | 50PCV036J/K*C3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434717 |  | Ground Loop | CARRIER | 50PCV036J/K*C5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434718 |  | Ground Loop | CARRIER | 50PCV036J/K*C6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434719 |  | Ground Loop | CARRIER | 50PCV036J/K*C4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434724 |  | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434725 |  | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434726 |  | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
202434727 |  | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207198813 |  | Ground Loop | BOSCH | WQ024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198814 |  | Ground Loop | BOSCH | WQ024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198817 |  | Ground Loop | BOSCH | WQ030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198818 |  | Ground Loop | BOSCH | WQ030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198819 |  | Ground Loop | BOSCH | WQ030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198820 |  | Ground Loop | BOSCH | WQ030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
207198821 |  | Ground Loop | BOSCH | WQ036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667 | No
207198823 |  | Ground Loop | BOSCH | WQ036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625 | No
207198824 |  | Ground Loop | BOSCH | WQ036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583 | No
207335143 |  | Ground Loop | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335144 |  | Ground Loop | GEOSTAR | 101/102K049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335145 |  | Ground Loop | GEOSTAR | 101/102K064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335146 |  | Ground Loop | GEOSTAR | 101/102J072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335147 |  | Ground Loop | GEOSTAR | 161/162K064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335247 |  | Ground Loop | GEOSTAR | 101/102J022**1*(1,4)***** |  | 19200 | 18.7 | 19200 | 4 | 1.6 | Yes
207335249 |  | Ground Loop | GEOSTAR | 161/162J026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335251 |  | Ground Loop | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335253 |  | Ground Loop | GEOSTAR | 161/162K049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335255 |  | Ground Loop | GEOSTAR | 161/162J072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335335 |  | Ground Loop | GEOSTAR | 111J049**1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | Yes
207335337 |  | Ground Loop | GEOSTAR | 111J072**1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | Yes
207335338 |  | Ground Loop | GEOSTAR | 111K038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3 | Yes
207335397 |  | Ground Loop | GeoSmart Energy | GT026**1*(1,4)*J |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335398 |  | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335399 |  | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335400 |  | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335401 |  | Ground Loop | GeoSmart Energy | GT072**1*(1,4)*J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335403 |  | Ground Loop | GeoSmart Energy | GS018**1*(1,4)*J |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
207335406 |  | Ground Loop | GeoSmart Energy | GS022**1*(1,4)*J |  | 19200 | 18.7 | 15000 | 4 | 1.6 | Yes
207335407 |  | Ground Loop | GeoSmart Energy | GS030**1*(0,3)*J |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | Yes
207335408 |  | Ground Loop | GeoSmart Energy | GS030**1*(1,4)*J |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
207335409 |  | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*K |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | Yes
207335410 |  | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*K |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | Yes
207335413 |  | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*K |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
207335414 |  | Ground Loop | GeoSmart Energy | GS060**1*(1,4)*K |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
207335415 |  | Ground Loop | GeoSmart Energy | GS060**1*0*K |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | Yes
207335416 |  | Ground Loop | GeoSmart Energy | GS070**1*(1,4)*J |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
207335514 |  | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
207335571 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****J |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | Yes
207335572 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(1,4)****J |  | 19200 | 18.7 | 15000 | 4 | 1.6 | Yes
207335573 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | Yes
207335574 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*K |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | Yes
207335575 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | Yes
207335576 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*K |  | 45900 | 18.8 | 36400 | 4 | 3.825 | Yes
207335577 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****K |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | Yes
207335578 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****J |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | Yes
207335579 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****J |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335580 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335581 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335582 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335583 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335584 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****H |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335585 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
207335586 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335587 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335588 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207335589 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****J |  | 26400 | 19.6 | 19500 | 4 | 2.2 | Yes
207335590 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | Yes
215399821 |  | Ground Loop | DAIKIN | WSMV036K3*G/J*C |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917 | No
215399825 |  | Ground Loop | DAIKIN | WSMV042K3*G/J*T |  | 42600 | 19.67 | 29700 | 3.63 | 3.55 | No
215399827 |  | Ground Loop | DAIKIN | WSMV042K3*G/J*C |  | 42600 | 19.67 | 29700 | 3.63 | 3.55 | No
215399830 |  | Ground Loop | DAIKIN | WSMV048K3*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
215399831 |  | Ground Loop | DAIKIN | WSMV048L3*G/J*P |  | 49700 | 18.61 | 36700 | 3.64 | 4.1417 | No
215399834 |  | Ground Loop | DAIKIN | WSMV048K3*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215399835 |  | Ground Loop | DAIKIN | WSMV048L3*G/J*T |  | 49300 | 19.09 | 36000 | 3.75 | 4.1083 | No
215399838 |  | Ground Loop | DAIKIN | WSMV048K3*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215399839 |  | Ground Loop | DAIKIN | WSMV048L3*G/J*C |  | 49300 | 19.09 | 36000 | 3.75 | 4.1083 | No
217752725 |  | Ground Loop | DAIKIN | WSTH024K1*H*C |  | 25100 | 19.32 | 17200 | 3.8 | 2.0917 | No
217752727 |  | Ground Loop | DAIKIN | WSTH030K1*H*C |  | 32700 | 19.1 | 20600 | 3.64 | 2.725 | No
217752729 |  | Ground Loop | DAIKIN | WSTH036K1*H*C |  | 38700 | 20.02 | 25900 | 3.64 | 3.225 | No
217752734 |  | Ground Loop | DAIKIN | WSTH048K1*H*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083 | No
217752735 |  | Ground Loop | DAIKIN | WSTH048L1*H*C |  | 49300 | 19 | 36300 | 3.76 | 4.1083 | No
217752738 |  | Ground Loop | DAIKIN | WSTH060K1*H*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333 | No
7519769 |  | Ground Loop | GEOCOMFORT | GVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519770 |  | Ground Loop | HYDRON MODULE | HVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519771 |  | Ground Loop | TETCO | TVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519772 |  | Ground Loop | GEOCOMFORT | GVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519773 |  | Ground Loop | HYDRON MODULE | HVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519774 |  | Ground Loop | TETCO | TVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
7519775 |  | Ground Loop | GEOCOMFORT | GVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25 | No
218471760 |  | Ground Loop | YORK | AD024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218471761 |  | Ground Loop | YORK | AD024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
204100658 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204100659 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204100660 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204100661 |  | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204101161 |  | Ground Loop | 5 SERIES | NDV/NDH064J1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
204117015 |  | Ground Loop | GEOSTAR | 101/102J064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
204117016 |  | Ground Loop | GEOSTAR | 103J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204117017 |  | Ground Loop | GEOSTAR | 103J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204272856 |  | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
204272857 |  | Ground Loop | GeoSmart Energy | GTS064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204272858 |  | Ground Loop | GeoSmart Energy | GTS064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204272859 |  | Ground Loop | GeoSmart Energy | GTZ064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204272860 |  | Ground Loop | GeoSmart Energy | GTZ064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204272890 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
204272892 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | No
204272893 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833 | Yes
204276830 |  | Ground Loop | GEOSTAR | 104J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
214067593 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
214067594 |  | Ground Loop | GeoSmart Energy | GBV/GBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
214067595 |  | Ground Loop | GeoSmart Energy | GBV/GBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214067596 |  | Ground Loop | GeoSmart Energy | GBV/GBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214067597 |  | Ground Loop | GeoSmart Energy | GBV/GBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214067598 |  | Ground Loop | GeoSmart Energy | GBV/GBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
214067600 |  | Ground Loop | GeoSmart Energy | GBV/GBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214067601 |  | Ground Loop | GeoSmart Energy | GBV/GBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
215837917 |  | Ground Loop | DAIKIN | WSSH070F3*G/J*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
215837919 |  | Ground Loop | DAIKIN | WSSH070K3*G/J*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
215837926 |  | Ground Loop | DAIKIN | WSSH070F3*G/J*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
215837927 |  | Ground Loop | DAIKIN | WSSH070K3*G/J*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083 | No
215851758 |  | Ground Loop | DAIKIN | WSTH024J1*G/J*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917 | No
215851759 |  | Ground Loop | DAIKIN | WSTH024K3*G/J*C |  | 25100 | 19.32 | 17200 | 3.8 | 2.0917 | No
215851764 |  | Ground Loop | DAIKIN | WSTH030J1*G/J*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725 | No
215851765 |  | Ground Loop | DAIKIN | WSTH030K3*G/J*C |  | 32700 | 19.1 | 20600 | 3.64 | 2.725 | No
215851770 |  | Ground Loop | DAIKIN | WSTH036J1*G/J*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225 | No
215851772 |  | Ground Loop | DAIKIN | WSTH036K3*G/J*C |  | 38700 | 20.02 | 25900 | 3.64 | 3.225 | No
215851780 |  | Ground Loop | DAIKIN | WSTH048K3*G/J*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083 | No
215851781 |  | Ground Loop | DAIKIN | WSTH048L3*G/J*C |  | 49300 | 19 | 36300 | 3.76 | 4.1083 | No
215851786 |  | Ground Loop | DAIKIN | WSTH060K3*G/J*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333 | No
215851798 |  | Ground Loop | DAIKIN | WSTV024J1*G/J*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667 | No
215851800 |  | Ground Loop | DAIKIN | WSTV024K3*G/J*C |  | 22400 | 17.45 | 17200 | 3.86 | 1.8667 | No
215851805 |  | Ground Loop | DAIKIN | WSTV030J1*G/J*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833 | No
215851806 |  | Ground Loop | DAIKIN | WSTV030K3*G/J*C |  | 32200 | 18.9 | 20800 | 3.66 | 2.6833 | No
215851812 |  | Ground Loop | DAIKIN | WSTV036J1*G/J*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583 | No
215851817 |  | Ground Loop | DAIKIN | WSTV042K3*G/J*C |  | 44800 | 18.96 | 27600 | 3.62 | 3.7333 | No
215851821 |  | Ground Loop | DAIKIN | WSTV048K3*G/J*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667 | No
215851823 |  | Ground Loop | DAIKIN | WSTV048L3*G/J*C |  | 52400 | 19.56 | 35200 | 3.78 | 4.3667 | No
215851828 |  | Ground Loop | DAIKIN | WSTV060K3*G/J*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583 | No
218158127 |  | Ground Loop | YORK | Y3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667 | No
213714597 |  | Ground Loop | DAIKIN | WSSH070E1*H*T |  | 73300 | 19.73 | 53600 | 3.64 | 6.1083 | No
213714598 |  | Ground Loop | DAIKIN | WSSH070E1*H*C |  | 73300 | 19.73 | 53600 | 3.64 | 6.1083 | No
215837756 |  | Ground Loop | DAIKIN | WSMH042F3*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
215837757 |  | Ground Loop | DAIKIN | WSMH042K3*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4 | No
215837763 |  | Ground Loop | DAIKIN | WSMH048F3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
215837764 |  | Ground Loop | DAIKIN | WSMH048K3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
215837766 |  | Ground Loop | DAIKIN | WSMH048L3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075 | No
215837771 |  | Ground Loop | DAIKIN | WSMH048F3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837773 |  | Ground Loop | DAIKIN | WSMH048K3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837774 |  | Ground Loop | DAIKIN | WSMH048L3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837780 |  | Ground Loop | DAIKIN | WSMH048F3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837781 |  | Ground Loop | DAIKIN | WSMH048K3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837783 |  | Ground Loop | DAIKIN | WSMH048L3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
215837814 |  | Ground Loop | DAIKIN | WSSH024F3*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837815 |  | Ground Loop | DAIKIN | WSSH024J1*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837817 |  | Ground Loop | DAIKIN | WSSH024K3*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837822 |  | Ground Loop | DAIKIN | WSSH024F3*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837824 |  | Ground Loop | DAIKIN | WSSH024J1*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837825 |  | Ground Loop | DAIKIN | WSSH024K3*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417 | No
215837831 |  | Ground Loop | DAIKIN | WSSH030F3*G/J*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55 | No
218158015 |  | Ground Loop | YORK | Y5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
218158016 |  | Ground Loop | YORK | Y5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
218158017 |  | Ground Loop | YORK | Y5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25 | No
218158018 |  | Ground Loop | YORK | Y5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
218158019 |  | Ground Loop | YORK | Y5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
218158020 |  | Ground Loop | YORK | Y5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
218158021 |  | Ground Loop | YORK | Y5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | No
218352929 |  | Ground Loop | SKYMARK | PD024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
218352930 |  | Ground Loop | SKYMARK | PD024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | No
215224679 |  | Ground Loop | BOSCH | RF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
215224680 |  | Ground Loop | BOSCH | RF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | Yes
215224681 |  | Ground Loop | BOSCH | RF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
215224682 |  | Ground Loop | BOSCH | RF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | Yes
215224683 |  | Ground Loop | BOSCH | RF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
215224684 |  | Ground Loop | BOSCH | RF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | Yes
215224685 |  | Ground Loop | BOSCH | RF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | Yes
215224686 |  | Ground Loop | BOSCH | RF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917 | Yes
215224687 |  | Ground Loop | BOSCH | RF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667 | Yes
215224688 |  | Ground Loop | BOSCH | RF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417 | Yes
215224691 |  | Ground Loop | BOSCH | RF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
215224692 |  | Ground Loop | BOSCH | RF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833 | Yes
217212076 |  | Ground Loop | FHP | CP048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
217212077 |  | Ground Loop | FHP | CP048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25 | No
217212078 |  | Ground Loop | FHP | CP048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083 | No
217212079 |  | Ground Loop | FHP | CP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
217212080 |  | Ground Loop | FHP | CP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
217212082 |  | Ground Loop | FHP | CP060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
217212083 |  | Ground Loop | FHP | CP060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
217212084 |  | Ground Loop | FHP | CP060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25 | No
217212085 |  | Ground Loop | FHP | CP060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
217212086 |  | Ground Loop | FHP | CP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212089 |  | Ground Loop | FHP | CP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212091 |  | Ground Loop | FHP | CP070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
217212094 |  | Ground Loop | FHP | CP070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
214772101 |  | Ground Loop | TRANE | GEHK0097 |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333 | No
214772103 |  | Ground Loop | TRANE | GEHK0157 |  | 15900 | 18.2 | 12500 | 3.85 | 1.325 | No
214772104 |  | Ground Loop | TRANE | GEHK0187 |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417 | No
214772105 |  | Ground Loop | TRANE | GEHK024B |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772106 |  | Ground Loop | TRANE | GEHK0244 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772107 |  | Ground Loop | TRANE | GEHK0247 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167 | No
214772108 |  | Ground Loop | TRANE | GEHK030B |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772109 |  | Ground Loop | TRANE | GEHK0304 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772110 |  | Ground Loop | TRANE | GEHK0307 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5 | No
214772116 |  | Ground Loop | TRANE | GEHK048B |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214772117 |  | Ground Loop | TRANE | GEHK0484 |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417 | No
214772118 |  | Ground Loop | TRANE | GEHK060B |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214772119 |  | Ground Loop | TRANE | GEHK0604 |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083 | No
214772120 |  | Ground Loop | TRANE | EXHK0097 |  | 9000 | 21.2 | 6100 | 3.91 | 0.75 | No
214772121 |  | Ground Loop | TRANE | EXHK0127 |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167 | No
214772122 |  | Ground Loop | TRANE | EXHK0157 |  | 16200 | 18.7 | 11800 | 3.73 | 1.35 | No
214772123 |  | Ground Loop | TRANE | EXHK0187 |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417 | No
214772124 |  | Ground Loop | TRANE | EXHK024B |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772125 |  | Ground Loop | TRANE | EXHK0244 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772126 |  | Ground Loop | TRANE | EXHK0247 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833 | No
214772127 |  | Ground Loop | TRANE | EXHK030B |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772128 |  | Ground Loop | TRANE | EXHK0304 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772129 |  | Ground Loop | TRANE | EXHK0307 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65 | No
214772130 |  | Ground Loop | TRANE | EXHK036B |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772131 |  | Ground Loop | TRANE | EXHK0364 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772132 |  | Ground Loop | TRANE | EXHK0367 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05 | No
214772133 |  | Ground Loop | TRANE | EXHK042B |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214772134 |  | Ground Loop | TRANE | EXHK0424 |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083 | No
214772135 |  | Ground Loop | TRANE | EXHK048B |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214772136 |  | Ground Loop | TRANE | EXHK0484 |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083 | No
214772137 |  | Ground Loop | TRANE | EXHK060B |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214772138 |  | Ground Loop | TRANE | EXHK0604 |  | 62700 | 19.7 | 45200 | 3.82 | 5.225 | No
214772139 |  | Ground Loop | TRANE | EXHK070B |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772140 |  | Ground Loop | TRANE | EXHK0704 |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917 | No
214772141 |  | Ground Loop | TRANE | DXHK024A |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417 | No
214776189 |  | Ground Loop | TRANE | GETK0152-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167 | No
214776190 |  | Ground Loop | TRANE | GETK0157-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167 | No
214776193 |  | Ground Loop | TRANE | GETK0242-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1 | No
214776194 |  | Ground Loop | TRANE | GETK0247-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1 | No
214796343 |  | Ground Loop | WaterFurnace | W5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | Yes
214796344 |  | Ground Loop | WaterFurnace | W5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | Yes
214796345 |  | Ground Loop | WaterFurnace | W5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | Yes
214796346 |  | Ground Loop | WaterFurnace | W5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | Yes
214796347 |  | Ground Loop | WaterFurnace | W5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | Yes
214796667 |  | Ground Loop | WaterFurnace | W5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | Yes
214796668 |  | Ground Loop | WaterFurnace | W5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | Yes
214796669 |  | Ground Loop | WaterFurnace | W5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | Yes
214810491 |  | Ground Loop | GEOSTAR | G5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | Yes
214810492 |  | Ground Loop | GEOSTAR | G5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | Yes
214810493 |  | Ground Loop | GEOSTAR | G5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | Yes
214810494 |  | Ground Loop | GEOSTAR | G5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | Yes
214810495 |  | Ground Loop | GEOSTAR | G5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | Yes
214810496 |  | Ground Loop | GEOSTAR | G5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | Yes
214810497 |  | Ground Loop | GEOSTAR | G5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | Yes
214810498 |  | Ground Loop | GEOSTAR | G5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | Yes
214823444 |  | Ground Loop | GeoSmart Energy | S5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | Yes
214823445 |  | Ground Loop | GeoSmart Energy | S5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | Yes
214823446 |  | Ground Loop | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | Yes
214823447 |  | Ground Loop | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | Yes
214823448 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475 | Yes
214823449 |  | Ground Loop | GeoSmart Energy | S5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083 | Yes
214823450 |  | Ground Loop | GeoSmart Energy | S5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5 | Yes
214823451 |  | Ground Loop | GeoSmart Energy | S5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167 | Yes
214837733 |  | Ground Loop | BOSCH | EC072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837734 |  | Ground Loop | BOSCH | EC072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837735 |  | Ground Loop | BOSCH | EC072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167 | No
214837736 |  | Ground Loop | BOSCH | EC096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837737 |  | Ground Loop | BOSCH | EC096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
214837738 |  | Ground Loop | BOSCH | EC096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667 | No
207198410 |  | Ground Loop | BOSCH | QV024-4HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083 | No
207198411 |  | Ground Loop | BOSCH | QV024-4HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083 | No
207198416 |  | Ground Loop | BOSCH | QV030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958 | No
207198417 |  | Ground Loop | BOSCH | QV030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708 | No
207198419 |  | Ground Loop | BOSCH | QV030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958 | No
207198420 |  | Ground Loop | BOSCH | QV030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708 | No
217351731 |  | Ground Loop | CARRIER | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351734 |  | Ground Loop | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351735 |  | Ground Loop | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351736 |  | Ground Loop | CARRIER | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351738 |  | Ground Loop | CARRIER | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351739 |  | Ground Loop | CARRIER | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351741 |  | Ground Loop | CARRIER | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351742 |  | Ground Loop | CARRIER | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351743 |  | Ground Loop | CARRIER | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351744 |  | Ground Loop | CARRIER | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351745 |  | Ground Loop | CARRIER | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351747 |  | Ground Loop | CARRIER | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351748 |  | Ground Loop | CARRIER | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351749 |  | Ground Loop | CARRIER | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351757 |  | Ground Loop | BRYANT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351758 |  | Ground Loop | BRYANT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351761 |  | Ground Loop | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351762 |  | Ground Loop | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351763 |  | Ground Loop | BRYANT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351765 |  | Ground Loop | BRYANT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351766 |  | Ground Loop | BRYANT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351768 |  | Ground Loop | BRYANT | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351769 |  | Ground Loop | BRYANT | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351770 |  | Ground Loop | BRYANT | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351771 |  | Ground Loop | BRYANT | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351772 |  | Ground Loop | BRYANT | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351774 |  | Ground Loop | BRYANT | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351775 |  | Ground Loop | BRYANT | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351776 |  | Ground Loop | BRYANT | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351784 |  | Ground Loop | ARCOAIRE | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351785 |  | Ground Loop | ARCOAIRE | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
9037240 |  | Ground Loop | HYDRON MODULE | HZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9037275 |  | Ground Loop | TETCO | TZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833 | No
9038310 |  | Ground Loop | GEOCOMFORT | GZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | Yes
9038311 |  | Ground Loop | HYDRON MODULE | HZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | Yes
9038312 |  | Ground Loop | TETCO | TZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | Yes
9038313 |  | Ground Loop | GEOCOMFORT | GZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038314 |  | Ground Loop | HYDRON MODULE | HZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038315 |  | Ground Loop | TETCO | TZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038316 |  | Ground Loop | GEOCOMFORT | GZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038317 |  | Ground Loop | HYDRON MODULE | HZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038318 |  | Ground Loop | TETCO | TZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038319 |  | Ground Loop | GEOCOMFORT | GZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038320 |  | Ground Loop | HYDRON MODULE | HZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9038321 |  | Ground Loop | TETCO | TZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15 | No
9063210 |  | Ground Loop | DAIKIN | W.CCW.2.072.*.*.*.*.*.*.L |  | 80100 | 17.1 | 58700 | 3.75 | 6.675 | No
9100310 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100311 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100313 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100314 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100316 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100317 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100319 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100320 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917 | No
9100326 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
205767490 |  | Ground Loop | ClimateMaster | TSH/V/D018B*K |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833 | No
205767513 |  | Ground Loop | ClimateMaster | TSH/V/D024C |  | 25300 | 18.9 | 19200 | 4 | 2.1083 | Yes
205767514 |  | Ground Loop | ClimateMaster | TSH/V/D024C*K |  | 25500 | 20.9 | 19100 | 4.2 | 2.125 | Yes
205767515 |  | Ground Loop | ClimateMaster | TSH/V/D030C |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333 | Yes
205767516 |  | Ground Loop | ClimateMaster | TSH/V/D030C*K |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333 | Yes
205767517 |  | Ground Loop | ClimateMaster | TSH/V/D036C |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583 | Yes
205767518 |  | Ground Loop | ClimateMaster | TSH/V/D036C*K |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833 | Yes
205767519 |  | Ground Loop | ClimateMaster | TSH/V/D042C |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417 | Yes
205767520 |  | Ground Loop | ClimateMaster | TSH/V/D042C*K |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917 | Yes
205767521 |  | Ground Loop | ClimateMaster | TSH/V/D048C*K |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167 | Yes
205767522 |  | Ground Loop | ClimateMaster | TSH/V/D060C |  | 63900 | 17.2 | 46900 | 3.7 | 5.325 | Yes
205767523 |  | Ground Loop | ClimateMaster | TSH/V/D060C*K |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667 | Yes
205767525 |  | Ground Loop | ClimateMaster | TSH/V/D070C*K |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833 | Yes
205767532 |  | Ground Loop | ClimateMaster | TSM15 B |  | 15500 | 18.8 | 11000 | 3.6 | 1.2917 | No
216054489 |  | Ground Loop | GEOCOMFORT | GYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325 | Yes
216054492 |  | Ground Loop | GEOCOMFORT | GZT024* |  | 26400 | 18.3 | 18300 | 3.9 | 2.2 | Yes
216054493 |  | Ground Loop | GEOCOMFORT | GZT030* |  | 31500 | 17.5 | 23300 | 3.7 | 2.625 | Yes
216054494 |  | Ground Loop | GEOCOMFORT | GZT036* |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583 | Yes
216054495 |  | Ground Loop | GEOCOMFORT | GZT042* |  | 43000 | 18 | 32900 | 3.6 | 3.5833 | Yes
216054496 |  | Ground Loop | GEOCOMFORT | GZT048* |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583 | Yes
216054499 |  | Ground Loop | GEOCOMFORT | GVS015* |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333 | Yes
216057509 |  | Ground Loop | GEOCOMFORT | GBT060* | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
216057511 |  | Ground Loop | GEOCOMFORT | GVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
216057512 |  | Ground Loop | GEOCOMFORT | GYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583 | Yes
216057513 |  | Ground Loop | GEOCOMFORT | GZS015* |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833 | Yes
216057515 |  | Ground Loop | GEOCOMFORT | GZS018* |  | 20100 | 18.7 | 14100 | 3.7 | 1.675 | Yes
216057517 |  | Ground Loop | GEOCOMFORT | GYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583 | Yes
216128491 |  | Ground Loop | GEOSTAR | G5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667 | Yes
216128493 |  | Ground Loop | GEOSTAR | G5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917 | Yes
216128495 |  | Ground Loop | GEOSTAR | G5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083 | Yes
216128497 |  | Ground Loop | GEOSTAR | G5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583 | Yes
216411469 |  | Ground Loop | ClimateMaster | SJ/PN024A | SAN024A | 23900 | 19 | 17900 | 4 | 1.9917 | Yes
216411470 |  | Ground Loop | ClimateMaster | SJ/PN036A | SAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917 | Yes
216411471 |  | Ground Loop | ClimateMaster | SJ/PN048A | SAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833 | Yes
216411472 |  | Ground Loop | ClimateMaster | SJ/PN060A | SAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167 | Yes
216419856 |  | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
216419857 |  | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
216419860 |  | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215405084 |  | Ground Loop | DAIKIN | WSSV070E1*H*C |  | 75400 | 19.4 | 54700 | 3.8 | 6.2833 | No
215405085 |  | Ground Loop | DAIKIN | WSSV070F3*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
215405086 |  | Ground Loop | DAIKIN | WSSV070K3*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
215405087 |  | Ground Loop | DAIKIN | WSSV070L3*H*C |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833 | No
215415734 |  | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)024A*B |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415735 |  | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)024A*C |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415736 |  | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)024A*VB |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415737 |  | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)024A*VC |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415740 |  | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)030A*VB |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415741 |  | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)030A*VC |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415744 |  | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)036A*VB |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
215415745 |  | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)036A*VC |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333 | No
215415772 |  | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)015A*VB |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415773 |  | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)015A*VC |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667 | No
215415776 |  | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)018A*VB |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415777 |  | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)018A*VC |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167 | No
215415778 |  | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)024A*B |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415779 |  | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)024A*C |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333 | No
215415780 |  | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)024A*VB |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415781 |  | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)024A*VC |  | 25800 | 18 | 19000 | 3.7 | 2.15 | No
215415784 |  | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)030A*VB |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
215415785 |  | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)030A*VC |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417 | No
217754657 |  | Ground Loop | DAIKIN | WSMV036F1*G/J*T |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917 | No
217754658 |  | Ground Loop | DAIKIN | WSMV036K1*G/J*T |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917 | No
217754661 |  | Ground Loop | DAIKIN | WSMV036F1*G/J*C |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917 | No
217754662 |  | Ground Loop | DAIKIN | WSMV036K1*G/J*C |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917 | No
217754670 |  | Ground Loop | DAIKIN | WSMV042K1*G/J*T |  | 42600 | 19.67 | 29700 | 3.63 | 3.55 | No
8740369 |  | Ground Loop | HYDRON MODULE | HVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | Yes
8740370 |  | Ground Loop | TETCO | TVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | Yes
8740371 |  | Ground Loop | GEOCOMFORT | GVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740372 |  | Ground Loop | HYDRON MODULE | HVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740373 |  | Ground Loop | TETCO | TVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740374 |  | Ground Loop | GEOCOMFORT | GVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740375 |  | Ground Loop | HYDRON MODULE | HVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8740376 |  | Ground Loop | TETCO | TVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3 | No
8791878 |  | Ground Loop | GEOSTAR | 101/102H060**1*(1,4)***** |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
8791879 |  | Ground Loop | GeoSmart Energy | GS060**1*(1,4)********H |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
8791880 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****H |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
8791883 |  | Ground Loop | GEOSTAR | 101/102H060**1*0***** |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
8791884 |  | Ground Loop | GeoSmart Energy | GS060**1*0********H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
8791885 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*0****H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
8964157 |  | Ground Loop | BRYANT | GC036C/H/V******1*X1 + UI |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | Yes
8964158 |  | Ground Loop | CARRIER | GC036C/H/V******1**1 + UI |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | Yes
8964161 |  | Ground Loop | BRYANT | GC060C/H/V******1*X1 + UI |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
8964162 |  | Ground Loop | CARRIER | GC060C/H/V******1**1 + UI |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | Yes
204276831 |  | Ground Loop | GEOSTAR | 103J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | Yes
204278291 |  | Ground Loop | WaterFurnace | SDV038J1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
204346746 |  | Ground Loop | GeoCool | GCHPV/H/D024T**A*** |  | 27000 | 17.95 | 18500 | 4.2 | 2.25 | No
204346873 |  | Ground Loop | GeoCool | GCHPV/H/D036T**A*** |  | 39000 | 17.86 | 26900 | 4.4 | 3.25 | No
215837669 |  | Ground Loop | DAIKIN | WSMH024F3*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
215837671 |  | Ground Loop | DAIKIN | WSMH024J1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
215837672 |  | Ground Loop | DAIKIN | WSMH024K3*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333 | No
218157903 |  | Ground Loop | YORK | Y5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917 | No
218157904 |  | Ground Loop | YORK | Y5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
218157905 |  | Ground Loop | YORK | Y5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583 | No
218157906 |  | Ground Loop | YORK | Y5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
218157907 |  | Ground Loop | YORK | Y5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
218157908 |  | Ground Loop | YORK | Y5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
218157909 |  | Ground Loop | YORK | Y5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417 | No
218157910 |  | Ground Loop | YORK | Y5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
218157911 |  | Ground Loop | YORK | Y5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
218157912 |  | Ground Loop | YORK | Y5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
218157913 |  | Ground Loop | YORK | Y5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
218157914 |  | Ground Loop | YORK | Y5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
218157915 |  | Ground Loop | YORK | Y5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
218157916 |  | Ground Loop | YORK | Y5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
218157917 |  | Ground Loop | YORK | Y5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833 | No
218157918 |  | Ground Loop | YORK | Y5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218157919 |  | Ground Loop | YORK | Y5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218157920 |  | Ground Loop | YORK | Y5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218157921 |  | Ground Loop | YORK | Y5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218157922 |  | Ground Loop | YORK | Y5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218157923 |  | Ground Loop | YORK | Y5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218157924 |  | Ground Loop | YORK | Y5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218157925 |  | Ground Loop | YORK | Y5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667 | No
218157926 |  | Ground Loop | YORK | Y5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
218157927 |  | Ground Loop | YORK | Y5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
218157928 |  | Ground Loop | YORK | Y5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
218157929 |  | Ground Loop | YORK | Y5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
218157930 |  | Ground Loop | YORK | Y5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
218157931 |  | Ground Loop | YORK | Y5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
218157932 |  | Ground Loop | YORK | Y5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
218157933 |  | Ground Loop | YORK | Y5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917 | No
218157934 |  | Ground Loop | YORK | Y5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
218157935 |  | Ground Loop | YORK | Y5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
218157936 |  | Ground Loop | YORK | Y5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
218157937 |  | Ground Loop | YORK | Y5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
218157938 |  | Ground Loop | YORK | Y5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
218157939 |  | Ground Loop | YORK | Y5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
218157940 |  | Ground Loop | YORK | Y5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
218157941 |  | Ground Loop | YORK | Y5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5 | No
218157942 |  | Ground Loop | YORK | Y5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157943 |  | Ground Loop | YORK | Y5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157944 |  | Ground Loop | YORK | Y5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157945 |  | Ground Loop | YORK | Y5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
218157946 |  | Ground Loop | YORK | Y5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083 | No
215827092 |  | Ground Loop | DAIKIN | WSLV072F1*G/J |  | 77000 | 19 | 53000 | 3.7 | 6.4167 | No
215827094 |  | Ground Loop | DAIKIN | WSLV072K1*G/J |  | 77000 | 19 | 53000 | 3.7 | 6.4167 | No
215827096 |  | Ground Loop | DAIKIN | WSLV072L1*G/J |  | 77000 | 19 | 53000 | 3.6 | 6.4167 | No
215827098 |  | Ground Loop | DAIKIN | WSLV096F1*G/J |  | 99500 | 19.4 | 74100 | 3.9 | 8.2917 | No
215827100 |  | Ground Loop | DAIKIN | WSLV096K1*G/J |  | 99500 | 19.4 | 74100 | 3.9 | 8.2917 | No
215827102 |  | Ground Loop | DAIKIN | WSLV096L1*G/J |  | 99500 | 18.7 | 74100 | 3.7 | 8.2917 | No
215827106 |  | Ground Loop | DAIKIN | WSLV120K1*G/J |  | 124600 | 17 | 95600 | 3.6 | 10.3833 | No
215832281 |  | Ground Loop | HYDROTECH | WSH6009D* |  | 9500 | 18.9 | 6500 | 3.6 | 0.79167 | No
215832282 |  | Ground Loop | HYDROTECH | WSH6012D* |  | 12000 | 17.9 | 8500 | 3.8 | 1 | No
215832283 |  | Ground Loop | HYDROTECH | WSH6018D* |  | 19000 | 18 | 12000 | 3.6 | 1.5833 | No
215832284 |  | Ground Loop | HYDROTECH | WSH6024D* |  | 26000 | 18.4 | 17500 | 3.6 | 2.1667 | No
215832285 |  | Ground Loop | HYDROTECH | WSH6030D* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
215832286 |  | Ground Loop | HYDROTECH | WSH6036D* |  | 36400 | 18 | 28000 | 3.6 | 3.0333 | No
215832287 |  | Ground Loop | HYDROTECH | WSH6042D* |  | 43500 | 18.5 | 31000 | 3.8 | 3.625 | No
215832288 |  | Ground Loop | HYDROTECH | WSH6048D* |  | 49500 | 18 | 36000 | 3.6 | 4.125 | No
215832289 |  | Ground Loop | HYDROTECH | WSH6060D* |  | 60000 | 18.1 | 41000 | 3.6 | 5 | No
215832290 |  | Ground Loop | HYDROTECH | WSH6072D* |  | 73000 | 17.1 | 55000 | 3.6 | 6.0833 | No
215832291 |  | Ground Loop | AE Air | WSH6009D* |  | 9500 | 18.9 | 6500 | 3.6 | 0.79167 | No
215832292 |  | Ground Loop | AE Air | WSH6012D* |  | 12000 | 17.9 | 8500 | 3.8 | 1 | No
215832293 |  | Ground Loop | AE Air | WSH6018D* |  | 19000 | 18 | 12000 | 3.6 | 1.5833 | No
215832294 |  | Ground Loop | AE Air | WSH6024D* |  | 26000 | 18.4 | 17500 | 3.6 | 2.1667 | No
215832295 |  | Ground Loop | AE Air | WSH6030D* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
215832296 |  | Ground Loop | AE Air | WSH6036D* |  | 36400 | 18 | 28000 | 3.6 | 3.0333 | No
215832297 |  | Ground Loop | AE Air | WSH6042D* |  | 43500 | 18.5 | 31000 | 3.8 | 3.625 | No
215832298 |  | Ground Loop | AE Air | WSH6048D* |  | 49500 | 18 | 36000 | 3.6 | 4.125 | No
215832299 |  | Ground Loop | AE Air | WSH6060D* |  | 60000 | 18.1 | 41000 | 3.6 | 5 | No
215832300 |  | Ground Loop | AE Air | WSH6072D* |  | 73000 | 17.1 | 55000 | 3.6 | 6.0833 | No
217903488 |  | Ground Loop | WaterFurnace | V5R072*D0**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903489 |  | Ground Loop | WaterFurnace | V5R072*D3**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903490 |  | Ground Loop | WaterFurnace | V5R072*D3**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903491 |  | Ground Loop | WaterFurnace | V5R072*D3**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903492 |  | Ground Loop | WaterFurnace | V5R096*T3**5* |  | 88100 | 18 | 69900 | 3.8 | 7.3417 | No
217903493 |  | Ground Loop | WaterFurnace | V5R120*T3**5* |  | 119400 | 17.7 | 92000 | 3.8 | 9.95 | No
217967018 |  | Ground Loop | TRANE | VSHK024A |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167 | No
217754604 |  | Ground Loop | DAIKIN | WSMH048E1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754605 |  | Ground Loop | DAIKIN | WSMH048F1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754606 |  | Ground Loop | DAIKIN | WSMH048K1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075 | No
217754629 |  | Ground Loop | DAIKIN | WSMV024F1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
217754630 |  | Ground Loop | DAIKIN | WSMV024K1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125 | No
217754633 |  | Ground Loop | DAIKIN | WSMV024F1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
217754634 |  | Ground Loop | DAIKIN | WSMV024K1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
217754637 |  | Ground Loop | DAIKIN | WSMV024F1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
217754638 |  | Ground Loop | DAIKIN | WSMV024K1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333 | No
203459725 |  | Ground Loop | FHP | LM036-1CSC-*****B | LM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583 | No
203459750 |  | Ground Loop | BOSCH | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 26200 | 17 | 17700 | 3.75 | 2.1833 | No
203459757 |  | Ground Loop | FHP | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 26200 | 17 | 17700 | 3.75 | 2.1833 | No
203466717 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
203471325 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
203490411 |  | Ground Loop | GeoSmart Energy | GTZ049*1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
203490420 |  | Ground Loop | GeoSmart Energy | GTZ049*1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
203495469 |  | Ground Loop | GEOSTAR | 101/102J049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
203495470 |  | Ground Loop | GEOSTAR | 103J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
203495474 |  | Ground Loop | GEOSTAR | 103J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | Yes
203993050 |  | Ground Loop | GEOSTAR | 111H049**1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
203993052 |  | Ground Loop | GEOSTAR | 111H072**1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
211594273 |  | Ground Loop | TRANE | DXHG070B |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
211594274 |  | Ground Loop | TRANE | DXHG0704 |  | 66800 | 19.6 | 52900 | 4 | 5.5667 | No
212428693 |  | Ground Loop | HYDROTECH | WSH6009A6* |  | 9500 | 18.9 | 6800 | 3.6 | 0.79167 | Yes
212428694 |  | Ground Loop | HYDROTECH | WSH6012A6* |  | 12000 | 18.2 | 8500 | 3.8 | 1 | Yes
212428695 |  | Ground Loop | HYDROTECH | WSH6018A6* |  | 19000 | 19 | 12000 | 3.6 | 1.5833 | Yes
212428696 |  | Ground Loop | HYDROTECH | WSH6024A6* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | Yes
212428697 |  | Ground Loop | HYDROTECH | WSH6030A6* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | Yes
212428698 |  | Ground Loop | HYDROTECH | WSH6036A6* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | Yes
212428699 |  | Ground Loop | HYDROTECH | WSH6042A6* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | Yes
212428700 |  | Ground Loop | HYDROTECH | WSH6048A6* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | Yes
212428701 |  | Ground Loop | AE Air | WSH6009A6* |  | 9500 | 18.9 | 6800 | 3.6 | 0.79167 | Yes
212428702 |  | Ground Loop | AE Air | WSH6012A6* |  | 12000 | 18.2 | 8500 | 3.8 | 1 | Yes
212428703 |  | Ground Loop | AE Air | WSH6018A6* |  | 19000 | 19 | 12000 | 3.6 | 1.5833 | Yes
212428704 |  | Ground Loop | AE Air | WSH6024A6* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | Yes
212428705 |  | Ground Loop | AE Air | WSH6030A6* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | Yes
212428706 |  | Ground Loop | AE Air | WSH6036A6* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | Yes
212428707 |  | Ground Loop | AE Air | WSH6042A6* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | Yes
212428708 |  | Ground Loop | AE Air | WSH6048A6* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125 | Yes
212505502 |  | Ground Loop | HYDROTECH | WSH6060A6* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | Yes
212505503 |  | Ground Loop | HYDROTECH | WSH6072A6* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | Yes
212505505 |  | Ground Loop | AE Air | WSH6060A6* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083 | Yes
212505506 |  | Ground Loop | AE Air | WSH6072A6* |  | 72000 | 17.1 | 55000 | 3.6 | 6 | Yes
212505509 |  | Ground Loop | HYDROTECH | WSH6036AM* |  | 36500 | 18 | 27000 | 3.6 | 3.0417 | No
212505510 |  | Ground Loop | HYDROTECH | WSH6042AM* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833 | No
217351073 |  | Ground Loop | BOSCH | CP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | No
217351074 |  | Ground Loop | BOSCH | CP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | No
217351075 |  | Ground Loop | BOSCH | CP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | No
217351076 |  | Ground Loop | BOSCH | CP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | No
217351077 |  | Ground Loop | BOSCH | CP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | No
217351078 |  | Ground Loop | BOSCH | CP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | No
217351079 |  | Ground Loop | BOSCH | CP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | No
217351080 |  | Ground Loop | BOSCH | CP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | No
217351082 |  | Ground Loop | BOSCH | CP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | No
217351083 |  | Ground Loop | BOSCH | CP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | No
217351084 |  | Ground Loop | BOSCH | CP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3 | No
217351087 |  | Ground Loop | BOSCH-GEO | RP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | Yes
217351088 |  | Ground Loop | BOSCH-GEO | RP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | Yes
217351089 |  | Ground Loop | BOSCH-GEO | RP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | Yes
217351090 |  | Ground Loop | BOSCH-GEO | RP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | Yes
217351091 |  | Ground Loop | BOSCH-GEO | RP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167 | Yes
217351092 |  | Ground Loop | BOSCH-GEO | RP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833 | Yes
217351093 |  | Ground Loop | BOSCH-GEO | RP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667 | Yes
217351094 |  | Ground Loop | BOSCH-GEO | RP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05 | Yes
217351095 |  | Ground Loop | BOSCH-GEO | RP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167 | Yes
217351096 |  | Ground Loop | BOSCH-GEO | RP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667 | Yes
217351098 |  | Ground Loop | BOSCH-GEO | RP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833 | Yes
217351099 |  | Ground Loop | BOSCH-GEO | RP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833 | Yes
217351100 |  | Ground Loop | BOSCH-GEO | RP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3 | Yes
217351103 |  | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351104 |  | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351107 |  | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351108 |  | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351109 |  | Ground Loop | GEO-THERMAL SPLIT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351111 |  | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351112 |  | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351114 |  | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351115 |  | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351116 |  | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351117 |  | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351118 |  | Ground Loop | GEO-THERMAL SPLIT | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351120 |  | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351121 |  | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351122 |  | Ground Loop | GEO-THERMAL SPLIT | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
217351671 |  | Ground Loop | BOSCH | RP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667 | Yes
217351672 |  | Ground Loop | BOSCH | RP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667 | Yes
217351673 |  | Ground Loop | BOSCH | RP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833 | Yes
217351674 |  | Ground Loop | BOSCH | RP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667 | Yes
8735477 |  | Ground Loop | GEOCOMFORT | GVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | Yes
8735495 |  | Ground Loop | HYDRON MODULE | HVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | Yes
8735512 |  | Ground Loop | TETCO | TVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | Yes
8735538 |  | Ground Loop | GEOCOMFORT | GVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735552 |  | Ground Loop | HYDRON MODULE | HVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735567 |  | Ground Loop | TETCO | TVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735607 |  | Ground Loop | GEOCOMFORT | GVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735711 |  | Ground Loop | HYDRON MODULE | HVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735721 |  | Ground Loop | TETCO | TVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735754 |  | Ground Loop | GEOCOMFORT | GVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735767 |  | Ground Loop | HYDRON MODULE | HVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735778 |  | Ground Loop | TETCO | TVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275 | No
8735903 |  | Ground Loop | GEOCOMFORT | GVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | Yes
8735904 |  | Ground Loop | HYDRON MODULE | HVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | Yes
8735905 |  | Ground Loop | TETCO | TVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | Yes
8735906 |  | Ground Loop | GEOCOMFORT | GVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735907 |  | Ground Loop | HYDRON MODULE | HVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735908 |  | Ground Loop | TETCO | TVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735909 |  | Ground Loop | GEOCOMFORT | GVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735910 |  | Ground Loop | HYDRON MODULE | HVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8735911 |  | Ground Loop | TETCO | TVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7 | No
8737970 |  | Ground Loop | GEOCOMFORT | GVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | Yes
8737971 |  | Ground Loop | HYDRON MODULE | HVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | Yes
8737972 |  | Ground Loop | TETCO | TVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | Yes
8737973 |  | Ground Loop | GEOCOMFORT | GVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737974 |  | Ground Loop | HYDRON MODULE | HVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737975 |  | Ground Loop | TETCO | TVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737976 |  | Ground Loop | GEOCOMFORT | GVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737977 |  | Ground Loop | HYDRON MODULE | HVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8737978 |  | Ground Loop | TETCO | TVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125 | No
8738031 |  | Ground Loop | GEOCOMFORT | GVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
8738032 |  | Ground Loop | HYDRON MODULE | HVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
8738033 |  | Ground Loop | TETCO | TVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | Yes
8738034 |  | Ground Loop | GEOCOMFORT | GVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738035 |  | Ground Loop | HYDRON MODULE | HVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738036 |  | Ground Loop | TETCO | TVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738037 |  | Ground Loop | GEOCOMFORT | GVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738038 |  | Ground Loop | HYDRON MODULE | HVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
8738039 |  | Ground Loop | TETCO | TVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075 | No
202541572 |  | Ground Loop | BOSCH-GEO | BP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
202541573 |  | Ground Loop | BOSCH | BP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202541574 |  | Ground Loop | CARRIER | GB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | No
202541575 |  | Ground Loop | BRYANT | GB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9 | Yes
202543170 |  | Ground Loop | CARRIER | GB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | No
202543171 |  | Ground Loop | BRYANT | GB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083 | Yes
207335591 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | Yes
207335592 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | Yes
207335593 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | Yes
207337469 |  | Ground Loop | GEOSTAR | 103H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337470 |  | Ground Loop | GEOSTAR | 103H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337471 |  | Ground Loop | GEOSTAR | 163H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337472 |  | Ground Loop | GEOSTAR | 163H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337473 |  | Ground Loop | GEOSTAR | 104H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337474 |  | Ground Loop | GEOSTAR | 104H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337475 |  | Ground Loop | GEOSTAR | 164H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337476 |  | Ground Loop | GEOSTAR | 164H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95 | No
207337477 |  | Ground Loop | GEOSTAR | 103J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207337478 |  | Ground Loop | GEOSTAR | 103J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
207337479 |  | Ground Loop | GEOSTAR | 163J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3 | No
207337480 |  | Ground Loop | GEOSTAR | 163J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3 | No
202146980 |  | Ground Loop | HYDRON MODULE | HZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146981 |  | Ground Loop | HYDRON MODULE | HZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146982 |  | Ground Loop | HYDRON MODULE | HZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | Yes
202146983 |  | Ground Loop | HYDRON MODULE | HZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202146984 |  | Ground Loop | TETCO | TZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | Yes
202146985 |  | Ground Loop | TETCO | TZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146986 |  | Ground Loop | TETCO | TZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146987 |  | Ground Loop | TETCO | TZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146988 |  | Ground Loop | TETCO | TZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475 | No
202146989 |  | Ground Loop | TETCO | TZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | Yes
202146990 |  | Ground Loop | TETCO | TZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167 | No
202146991 |  | Ground Loop | GEOCOMFORT | GZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | Yes
202146992 |  | Ground Loop | GEOCOMFORT | GZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202146993 |  | Ground Loop | GEOCOMFORT | GZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202146994 |  | Ground Loop | GEOCOMFORT | GZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202146995 |  | Ground Loop | GEOCOMFORT | GZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202146996 |  | Ground Loop | GEOCOMFORT | GZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | Yes
202146997 |  | Ground Loop | GEOCOMFORT | GZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202146998 |  | Ground Loop | GEOCOMFORT | GZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202146999 |  | Ground Loop | GEOCOMFORT | GZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1 | No
202147000 |  | Ground Loop | HYDRON MODULE | HZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | Yes
202147001 |  | Ground Loop | HYDRON MODULE | HZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147002 |  | Ground Loop | HYDRON MODULE | HZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
202147003 |  | Ground Loop | HYDRON MODULE | HZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05 | No
206438903 |  | Ground Loop | CARRIER | 50PSV012**C3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438904 |  | Ground Loop | CARRIER | 50PSH012**C3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438907 |  | Ground Loop | CARRIER | 50PSV012**C0/BA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438908 |  | Ground Loop | CARRIER | 50PSV012**C4/DA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438909 |  | Ground Loop | CARRIER | 50PSH012**C0/BA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206438910 |  | Ground Loop | CARRIER | 50PSH012**C4/DA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206608717 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048J1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
206608718 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048J1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
206608719 |  | Ground Loop | GEOSTAR | 103J048**1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
206608720 |  | Ground Loop | GEOSTAR | 103J048**1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417 | No
206608721 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060J1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
206608722 |  | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060J1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
206608723 |  | Ground Loop | GEOSTAR | 103J060**1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
206608724 |  | Ground Loop | GEOSTAR | 103J060**1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
206611120 |  | Ground Loop | COMFORT-AIRE | HEH/V060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
206611121 |  | Ground Loop | CENTURY | HEH/V060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667 | Yes
207349385 |  | Ground Loop | WaterFurnace | NBV/NBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349386 |  | Ground Loop | WaterFurnace | NBV/NBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207349387 |  | Ground Loop | WaterFurnace | NBV/NBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
215400125 |  | Ground Loop | DAIKIN | WSMV036F3*G/J*C |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917 | No
215400132 |  | Ground Loop | DAIKIN | WSMV042E1*G/J*T |  | 43000 | 19.86 | 30000 | 3.66 | 3.5833 | No
215400136 |  | Ground Loop | DAIKIN | WSMV042E1*G/J*C |  | 43000 | 19.86 | 30000 | 3.66 | 3.5833 | No
215400140 |  | Ground Loop | DAIKIN | WSMV048E1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
215400141 |  | Ground Loop | DAIKIN | WSMV048F3*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833 | No
215400144 |  | Ground Loop | DAIKIN | WSMV048E1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215400145 |  | Ground Loop | DAIKIN | WSMV048F3*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215400148 |  | Ground Loop | DAIKIN | WSMV048E1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215400149 |  | Ground Loop | DAIKIN | WSMV048F3*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15 | No
215400156 |  | Ground Loop | DAIKIN | WSMV060E1*G/J*T |  | 63500 | 17.8 | 46100 | 3.7 | 5.2917 | No
215400157 |  | Ground Loop | DAIKIN | WSMV060F3*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
215400160 |  | Ground Loop | DAIKIN | WSMV060E1*G/J*C |  | 63500 | 17.8 | 46100 | 3.7 | 5.2917 | No
215400161 |  | Ground Loop | DAIKIN | WSMV060F3*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917 | No
215400171 |  | Ground Loop | DAIKIN | WSSV012E1*H*T |  | 12200 | 20.4 | 8500 | 3.61 | 1.0167 | No
215400173 |  | Ground Loop | DAIKIN | WSSV015E1*H*T |  | 17000 | 23.75 | 10500 | 3.87 | 1.4167 | No
215400175 |  | Ground Loop | DAIKIN | WSSV015E1*H*C |  | 17000 | 23.75 | 10500 | 3.87 | 1.4167 | No
215400177 |  | Ground Loop | DAIKIN | WSSV019E1*H*T |  | 20600 | 20.96 | 14100 | 3.73 | 1.7167 | No
215400179 |  | Ground Loop | DAIKIN | WSSV019E1*H*C |  | 20600 | 20.96 | 14100 | 3.73 | 1.7167 | No
215400182 |  | Ground Loop | DAIKIN | WSSV024J1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167 | No
217754470 |  | Ground Loop | DAIKIN | WSSV070F1*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
217754471 |  | Ground Loop | DAIKIN | WSSV070K1*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833 | No
217754472 |  | Ground Loop | DAIKIN | WSSV070L1*H*C |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833 | No
217754475 |  | Ground Loop | DAIKIN | WSTH024E1*H*C |  | 25100 | 19.92 | 17200 | 3.92 | 2.0917 | No
217754476 |  | Ground Loop | DAIKIN | WSTH024F1*H*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917 | No
217754479 |  | Ground Loop | DAIKIN | WSTH030E1*H*C |  | 32700 | 19.69 | 20600 | 3.75 | 2.725 | No
217754480 |  | Ground Loop | DAIKIN | WSTH030F1*H*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725 | No
217754483 |  | Ground Loop | DAIKIN | WSTH036E1*H*C |  | 38700 | 20.64 | 25900 | 3.75 | 3.225 | No
217754484 |  | Ground Loop | DAIKIN | WSTH036F1*H*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225 | No
217754487 |  | Ground Loop | DAIKIN | WSTH042E1*H*C |  | 45900 | 20.06 | 28400 | 3.7 | 3.825 | No
217754488 |  | Ground Loop | DAIKIN | WSTH042F1*H*C |  | 45900 | 19.66 | 28400 | 3.63 | 3.825 | No
217754491 |  | Ground Loop | DAIKIN | WSTH048E1*H*C |  | 49300 | 19.59 | 36300 | 3.87 | 4.1083 | No
217754492 |  | Ground Loop | DAIKIN | WSTH048F1*H*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083 | No
217754495 |  | Ground Loop | DAIKIN | WSTH060E1*H*C |  | 61600 | 19 | 44200 | 3.7 | 5.1333 | No
217754496 |  | Ground Loop | DAIKIN | WSTH060F1*H*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333 | No
202350503 |  | Ground Loop | AAON, Inc. | M2-014-4-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725 | No
207083961 |  | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083965 |  | Ground Loop | CARRIER | 50PCV036J/K*C/A3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083969 |  | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083973 |  | Ground Loop | CARRIER | 50PCV036J/K*C/A4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083977 |  | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083981 |  | Ground Loop | CARRIER | 50PCV036J/K*C/A5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083985 |  | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
207083989 |  | Ground Loop | CARRIER | 50PCV036J/K*C/A6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917 | No
215224599 |  | Ground Loop | CARRIER | 50WD*007***3*(A-H)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224600 |  | Ground Loop | CARRIER | 50WD*007***3*(J-R)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224601 |  | Ground Loop | CARRIER | 50WD*007***4*(A-H)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224602 |  | Ground Loop | CARRIER | 50WD*007***4*(J-R)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224603 |  | Ground Loop | CARRIER | 50WD*009***3*(A-H)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224604 |  | Ground Loop | CARRIER | 50WD*009***3*(J-R)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224605 |  | Ground Loop | CARRIER | 50WD*009***4*(A-H)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
217754393 |  | Ground Loop | DAIKIN | WSSH036F1*H*C |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583 | No
217754394 |  | Ground Loop | DAIKIN | WSSH036K1*H*C |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583 | No
217754396 |  | Ground Loop | DAIKIN | WSSH042F1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217754397 |  | Ground Loop | DAIKIN | WSSH042K1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217754399 |  | Ground Loop | DAIKIN | WSSH042F1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217754400 |  | Ground Loop | DAIKIN | WSSH042K1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667 | No
217754402 |  | Ground Loop | DAIKIN | WSSH048F1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754403 |  | Ground Loop | DAIKIN | WSSH048K1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754404 |  | Ground Loop | DAIKIN | WSSH048L1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754406 |  | Ground Loop | DAIKIN | WSSH048F1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754407 |  | Ground Loop | DAIKIN | WSSH048K1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217754408 |  | Ground Loop | DAIKIN | WSSH048L1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667 | No
217351919 |  | Ground Loop | TEMPSTAR | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667 | Yes
217351920 |  | Ground Loop | TEMPSTAR | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167 | Yes
217351923 |  | Ground Loop | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25 | Yes
217351924 |  | Ground Loop | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667 | Yes
217351925 |  | Ground Loop | TEMPSTAR | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417 | Yes
217351927 |  | Ground Loop | TEMPSTAR | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417 | Yes
217351928 |  | Ground Loop | TEMPSTAR | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583 | Yes
217351930 |  | Ground Loop | TEMPSTAR | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583 | Yes
217351931 |  | Ground Loop | TEMPSTAR | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167 | Yes
217351932 |  | Ground Loop | TEMPSTAR | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167 | Yes
217351933 |  | Ground Loop | TEMPSTAR | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05 | Yes
217351934 |  | Ground Loop | TEMPSTAR | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833 | Yes
217351936 |  | Ground Loop | TEMPSTAR | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325 | Yes
217351937 |  | Ground Loop | TEMPSTAR | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167 | Yes
217351938 |  | Ground Loop | TEMPSTAR | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333 | Yes
6677754 |  | Ground Loop | BOSCH | LM048-4VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
6677875 |  | Ground Loop | BOSCH | LM060-1VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | No
6677876 |  | Ground Loop | BOSCH | LM060-3VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | No
6677878 |  | Ground Loop | BOSCH | LM060-4VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425 | No
217037811 |  | Ground Loop | GeoSmart Energy | S5SS024BD1 | S5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037812 |  | Ground Loop | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037813 |  | Ground Loop | GeoSmart Energy | S5SS048BD1 | S5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037814 |  | Ground Loop | GeoSmart Energy | S5SS060BD1 | S5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037816 |  | Ground Loop | GeoSmart Energy | S5SZ024BD1 | S5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037817 |  | Ground Loop | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037818 |  | Ground Loop | GeoSmart Energy | S5SZ048BD1 | S5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037819 |  | Ground Loop | GeoSmart Energy | S5SZ060BD1 | S5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037821 |  | Ground Loop | GeoSmart Energy | S5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037822 |  | Ground Loop | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037823 |  | Ground Loop | GeoSmart Energy | S5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037824 |  | Ground Loop | GeoSmart Energy | S5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217037826 |  | Ground Loop | GeoSmart Energy | S5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833 | Yes
217037827 |  | Ground Loop | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833 | Yes
217037828 |  | Ground Loop | GeoSmart Energy | S5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925 | Yes
217037829 |  | Ground Loop | GeoSmart Energy | S5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917 | Yes
217903452 |  | Ground Loop | WaterFurnace | V5R072*S4**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903453 |  | Ground Loop | WaterFurnace | V5R072*S4**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6 | No
217903454 |  | Ground Loop | WaterFurnace | V5R036*D4**1* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903455 |  | Ground Loop | WaterFurnace | V5R036*D4**4* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903456 |  | Ground Loop | WaterFurnace | V5R036*D4**5* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903457 |  | Ground Loop | WaterFurnace | V5R048*D4**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903458 |  | Ground Loop | WaterFurnace | V5R048*D4**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903459 |  | Ground Loop | WaterFurnace | V5R048*D4**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903460 |  | Ground Loop | WaterFurnace | V5R060*D4**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903461 |  | Ground Loop | WaterFurnace | V5R060*D4**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903462 |  | Ground Loop | WaterFurnace | V5R060*D4**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903463 |  | Ground Loop | WaterFurnace | V5R072*D4**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903464 |  | Ground Loop | WaterFurnace | V5R072*D4**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903465 |  | Ground Loop | WaterFurnace | V5R072*D4**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903466 |  | Ground Loop | WaterFurnace | V5R096*T4**5* |  | 88100 | 18 | 69900 | 3.8 | 7.3417 | No
217903467 |  | Ground Loop | WaterFurnace | V5R120*T4**5* |  | 119400 | 17.7 | 92000 | 3.8 | 9.95 | No
217903468 |  | Ground Loop | WaterFurnace | V5R036*D0**1* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903469 |  | Ground Loop | WaterFurnace | V5R036*D0**4* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903470 |  | Ground Loop | WaterFurnace | V5R036*D0**5* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903471 |  | Ground Loop | WaterFurnace | V5R036*D3**1* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903472 |  | Ground Loop | WaterFurnace | V5R036*D3**4* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903473 |  | Ground Loop | WaterFurnace | V5R036*D3**5* |  | 37000 | 20 | 28400 | 4 | 3.0833 | No
217903474 |  | Ground Loop | WaterFurnace | V5R048*D0**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903475 |  | Ground Loop | WaterFurnace | V5R048*D0**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903476 |  | Ground Loop | WaterFurnace | V5R048*D0**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903477 |  | Ground Loop | WaterFurnace | V5R048*D3**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903478 |  | Ground Loop | WaterFurnace | V5R048*D3**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903479 |  | Ground Loop | WaterFurnace | V5R048*D3**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417 | No
217903480 |  | Ground Loop | WaterFurnace | V5R060*D0**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903481 |  | Ground Loop | WaterFurnace | V5R060*D0**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903482 |  | Ground Loop | WaterFurnace | V5R060*D0**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903483 |  | Ground Loop | WaterFurnace | V5R060*D3**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903484 |  | Ground Loop | WaterFurnace | V5R060*D3**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903485 |  | Ground Loop | WaterFurnace | V5R060*D3**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833 | No
217903486 |  | Ground Loop | WaterFurnace | V5R072*D0**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
217903487 |  | Ground Loop | WaterFurnace | V5R072*D0**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875 | No
9100328 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225 | No
9100330 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
9100332 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417 | No
9100334 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100335 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100337 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100338 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100340 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100341 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100343 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333 | No
9100345 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100346 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100348 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100349 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100351 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100352 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100354 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100355 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167 | No
9100357 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100358 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100359 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100361 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100362 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100364 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100365 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875 | No
9100367 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525 | No
6501968 |  | Ground Loop | GEOSTAR | GBV/GBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
6501970 |  | Ground Loop | GEOSTAR | GBV/GBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501971 |  | Ground Loop | GEOSTAR | GBV/GBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501972 |  | Ground Loop | GEOSTAR | GBV/GBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501973 |  | Ground Loop | GEOSTAR | GBV/GBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501974 |  | Ground Loop | GEOSTAR | GBV/GBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501975 |  | Ground Loop | GEOSTAR | GBV/GBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
6501976 |  | Ground Loop | GEOSTAR | GBV/GBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
6501977 |  | Ground Loop | GEOSTAR | GBV/GBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501978 |  | Ground Loop | GEOSTAR | GBV/GBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501979 |  | Ground Loop | GEOSTAR | GBV/GBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
6501980 |  | Ground Loop | GEOSTAR | GBV/GBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501981 |  | Ground Loop | GEOSTAR | GBV/GBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501982 |  | Ground Loop | GEOSTAR | GBV/GBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
6501983 |  | Ground Loop | GEOSTAR | GBV/GBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501984 |  | Ground Loop | GEOSTAR | GBV/GBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
6501985 |  | Ground Loop | GEOSTAR | GBV/GBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
6501986 |  | Ground Loop | GEOSTAR | GBV/GBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501987 |  | Ground Loop | GEOSTAR | GBV/GBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501988 |  | Ground Loop | GEOSTAR | GBV/GBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501989 |  | Ground Loop | GEOSTAR | GBV/GBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501990 |  | Ground Loop | GEOSTAR | GBV/GBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501991 |  | Ground Loop | GEOSTAR | GBV/GBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583 | No
6501993 |  | Ground Loop | GEOSTAR | GBV/GBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6501994 |  | Ground Loop | GEOSTAR | GBV/GBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6501996 |  | Ground Loop | GEOSTAR | GBV/GBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6501997 |  | Ground Loop | GEOSTAR | GBV/GBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6501999 |  | Ground Loop | GEOSTAR | GBV/GBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6502000 |  | Ground Loop | GEOSTAR | GBV/GBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
6502002 |  | Ground Loop | GEOSTAR | GBV/GBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502003 |  | Ground Loop | GEOSTAR | GBV/GBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502004 |  | Ground Loop | GEOSTAR | GBV/GBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502005 |  | Ground Loop | GEOSTAR | GBV/GBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502006 |  | Ground Loop | GEOSTAR | GBV/GBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6502007 |  | Ground Loop | GEOSTAR | GBV/GBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
6674620 |  | Ground Loop | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
6674621 |  | Ground Loop | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
6674622 |  | Ground Loop | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
6674623 |  | Ground Loop | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167 | No
6676515 |  | Ground Loop | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
6676516 |  | Ground Loop | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
6676518 |  | Ground Loop | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
6676519 |  | Ground Loop | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325 | No
6677645 |  | Ground Loop | BOSCH | LM048-1VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
6677682 |  | Ground Loop | BOSCH | LM048-3VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275 | No
202922697 |  | Ground Loop | BRYANT | GB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922700 |  | Ground Loop | HEIL | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | No
202922703 |  | Ground Loop | ARCOAIRE | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922706 |  | Ground Loop | KEEPRITE | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922708 |  | Ground Loop | TEMPSTAR | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922711 |  | Ground Loop | COMFORTMAKER | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922714 |  | Ground Loop | DAY & NIGHT | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125 | Yes
202922716 |  | Ground Loop | CARRIER | 50PSV036***3/CA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922719 |  | Ground Loop | CARRIER | 50PSV036***5/EA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922722 |  | Ground Loop | CARRIER | 50PSV036***6/FA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922725 |  | Ground Loop | CARRIER | GB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922728 |  | Ground Loop | BRYANT | GB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922731 |  | Ground Loop | HEIL | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | No
202922734 |  | Ground Loop | ARCOAIRE | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922737 |  | Ground Loop | KEEPRITE | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922740 |  | Ground Loop | TEMPSTAR | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922742 |  | Ground Loop | COMFORTMAKER | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
202922745 |  | Ground Loop | DAY & NIGHT | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125 | Yes
218353686 |  | Ground Loop | JOHNSON CONTROLS | DQ060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083 | No
218353687 |  | Ground Loop | JOHNSON CONTROLS | DQ070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353689 |  | Ground Loop | JOHNSON CONTROLS | DQ070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353691 |  | Ground Loop | JOHNSON CONTROLS | DQ070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353693 |  | Ground Loop | JOHNSON CONTROLS | DQ070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353695 |  | Ground Loop | JOHNSON CONTROLS | DQ070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218353697 |  | Ground Loop | JOHNSON CONTROLS | DQ070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333 | No
218378550 |  | Ground Loop | WaterFurnace | W5SZ030BD1 | W5BM030BN1**2 | 28400 | 17.7 | 23000 | 3.9 | 2.3667 | No
218378551 |  | Ground Loop | WaterFurnace | W5SZ042BD1 | W5BM042BN1**2 | 39500 | 18.2 | 29400 | 3.9 | 3.2917 | No
218389121 |  | Ground Loop | GEOSTAR | G5SZ030BD1 | G5BM030BN1**2 | 28400 | 17.7 | 23000 | 3.9 | 2.3667 | No
218389122 |  | Ground Loop | GEOSTAR | G5SZ042BD1 | G5BM042BN1**2 | 39500 | 18.2 | 29400 | 3.9 | 3.2917 | No
218389123 |  | Ground Loop | GeoSmart Energy | S5SZ030BD1 | S5BM030BN1**2 | 28400 | 17.7 | 23000 | 3.9 | 2.3667 | No
218389124 |  | Ground Loop | GeoSmart Energy | S5SZ042BD1 | S5BM042BN1**2 | 39500 | 18.2 | 29400 | 3.9 | 3.2917 | No
218389125 |  | Ground Loop | YORK | Y5SZ030BD1 | Y5BM030BN1**2 | 28400 | 17.7 | 23000 | 3.9 | 2.3667 | No
218389126 |  | Ground Loop | YORK | Y5SZ042BD1 | Y5BM042BN1**2 | 39500 | 18.2 | 29400 | 3.9 | 3.2917 | No
202211045 |  | Ground Loop | WaterFurnace | URD038*3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211046 |  | Ground Loop | WaterFurnace | URD038*3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211047 |  | Ground Loop | WaterFurnace | URD038*3*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202211048 |  | Ground Loop | WaterFurnace | URD049*0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
206726850 |  | Ground Loop | TETCO | TBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | Yes
206726851 |  | Ground Loop | GEOCOMFORT | GBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
206726852 |  | Ground Loop | HYDRON MODULE | HBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
206726853 |  | Ground Loop | TETCO | TBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833 | No
206726854 |  | Ground Loop | GEOCOMFORT | GBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | Yes
206726855 |  | Ground Loop | GEOCOMFORT | GBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
206726856 |  | Ground Loop | HYDRON MODULE | HBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | Yes
206726857 |  | Ground Loop | HYDRON MODULE | HBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
206726858 |  | Ground Loop | TETCO | TBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | Yes
206726859 |  | Ground Loop | TETCO | TBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | Yes
206726860 |  | Ground Loop | GEOCOMFORT | GBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
206726861 |  | Ground Loop | GEOCOMFORT | GBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | No
206726862 |  | Ground Loop | HYDRON MODULE | HBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
206726863 |  | Ground Loop | HYDRON MODULE | HBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | No
206726864 |  | Ground Loop | TETCO | TBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333 | No
206726865 |  | Ground Loop | TETCO | TBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917 | No
206726878 |  | Ground Loop | GEOCOMFORT | GBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
206726879 |  | Ground Loop | HYDRON MODULE | HBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
206726880 |  | Ground Loop | TETCO | TBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | Yes
206726881 |  | Ground Loop | GEOCOMFORT | GBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | No
206726882 |  | Ground Loop | HYDRON MODULE | HBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | No
206726883 |  | Ground Loop | TETCO | TBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917 | No
206900466 |  | Ground Loop | WaterFurnace | UDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900467 |  | Ground Loop | WaterFurnace | UDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900469 |  | Ground Loop | WaterFurnace | UDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900470 |  | Ground Loop | WaterFurnace | UDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900471 |  | Ground Loop | WaterFurnace | UDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900472 |  | Ground Loop | WaterFurnace | UDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900473 |  | Ground Loop | WaterFurnace | UDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
206900474 |  | Ground Loop | WaterFurnace | UDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900475 |  | Ground Loop | WaterFurnace | UDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667 | No
206900553 |  | Ground Loop | GEOSTAR | GDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900554 |  | Ground Loop | GEOSTAR | GDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900555 |  | Ground Loop | GEOSTAR | GDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5 | No
206900556 |  | Ground Loop | GEOSTAR | GDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333 | No
215224027 |  | Ground Loop | BOSCH | CF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224028 |  | Ground Loop | BOSCH | CF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667 | No
215224029 |  | Ground Loop | BOSCH | CF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224030 |  | Ground Loop | BOSCH | CF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667 | No
215224031 |  | Ground Loop | BOSCH | CF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224032 |  | Ground Loop | BOSCH | CF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417 | No
215224033 |  | Ground Loop | BOSCH | CF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083 | No
7795914 |  | Ground Loop | GEOCOMFORT | GVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
7795915 |  | Ground Loop | HYDRON MODULE | HVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
7795916 |  | Ground Loop | TETCO | TVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | Yes
7795918 |  | Ground Loop | GEOCOMFORT | GVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795919 |  | Ground Loop | HYDRON MODULE | HVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795920 |  | Ground Loop | TETCO | TVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795921 |  | Ground Loop | GEOCOMFORT | GVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795922 |  | Ground Loop | HYDRON MODULE | HVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795923 |  | Ground Loop | TETCO | TVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795924 |  | Ground Loop | GEOCOMFORT | GVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795925 |  | Ground Loop | HYDRON MODULE | HVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795926 |  | Ground Loop | TETCO | TVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15 | No
7795943 |  | Ground Loop | GEOCOMFORT | GVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
7795944 |  | Ground Loop | HYDRON MODULE | HVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
7795945 |  | Ground Loop | TETCO | TVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | Yes
7795946 |  | Ground Loop | GEOCOMFORT | GVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795947 |  | Ground Loop | HYDRON MODULE | HVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795948 |  | Ground Loop | TETCO | TVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795949 |  | Ground Loop | GEOCOMFORT | GVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795950 |  | Ground Loop | HYDRON MODULE | HVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795951 |  | Ground Loop | TETCO | TVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795952 |  | Ground Loop | GEOCOMFORT | GVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795953 |  | Ground Loop | HYDRON MODULE | HVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
7795954 |  | Ground Loop | TETCO | TVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167 | No
8000290 |  | Ground Loop | GEOCOOL | GCHP01024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833 | No
8000291 |  | Ground Loop | GEOCOOL | GCHP01031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6 | No
8000292 |  | Ground Loop | GEOCOOL | GCHP01036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583 | No
8000293 |  | Ground Loop | GEOCOOL | GCHP01041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375 | No
8077723 |  | Ground Loop | GEOCOMFORT | GYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | Yes
8077724 |  | Ground Loop | HYDRON MODULE | HYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | Yes
8077725 |  | Ground Loop | TETCO | TYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | Yes
8077726 |  | Ground Loop | GEOCOMFORT | GYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583 | No
204031803 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583 | No
10346238 |  | Ground Loop | HYDRON MODULE | HZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346239 |  | Ground Loop | TETCO | TZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346240 |  | Ground Loop | GEOCOMFORT | GZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346241 |  | Ground Loop | HYDRON MODULE | HZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346242 |  | Ground Loop | TETCO | TZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346243 |  | Ground Loop | GEOCOMFORT | GZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346244 |  | Ground Loop | HYDRON MODULE | HZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346245 |  | Ground Loop | TETCO | TZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346246 |  | Ground Loop | GEOCOMFORT | GZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346247 |  | Ground Loop | HYDRON MODULE | HZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346248 |  | Ground Loop | TETCO | TZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667 | No
10346253 |  | Ground Loop | GEOCOMFORT | GZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | Yes
10346254 |  | Ground Loop | HYDRON MODULE | HZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | Yes
10346255 |  | Ground Loop | TETCO | TZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | Yes
10346256 |  | Ground Loop | GEOCOMFORT | GZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346257 |  | Ground Loop | HYDRON MODULE | HZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
10346258 |  | Ground Loop | TETCO | TZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55 | No
206185754 |  | Ground Loop | DAIKIN | WGCH015E1*G/J*P |  | 15100 | 18.1 | 11100 | 3.8 | 1.2583 | No
206185755 |  | Ground Loop | DAIKIN | WGCH015E1*G/J*T |  | 15300 | 19.9 | 10700 | 3.9 | 1.275 | No
206185756 |  | Ground Loop | DAIKIN | WGCH015E1*G/J*C |  | 15300 | 19.9 | 10700 | 3.9 | 1.275 | No
206185757 |  | Ground Loop | DAIKIN | WGCH019E1*G/J*C |  | 18300 | 19 | 13200 | 3.9 | 1.525 | No
216625830 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625831 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625832 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625833 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625834 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625835 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625836 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
216625837 |  | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5 | No
202901193 |  | Ground Loop | WHALEN | VD-A-0801-*DA |  | 24500 | 17.5 | 17000 | 4 | 2.0417 | No
202923075 |  | Ground Loop | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
10268138 |  | Ground Loop | TETCO | TBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268139 |  | Ground Loop | GEOCOMFORT | GBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268140 |  | Ground Loop | HYDRON MODULE | HBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268141 |  | Ground Loop | TETCO | TBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268198 |  | Ground Loop | GEOCOMFORT | GBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268199 |  | Ground Loop | HYDRON MODULE | HBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268200 |  | Ground Loop | TETCO | TBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
202358919 |  | Ground Loop | DAIKIN | WCCW5024*F*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
202358921 |  | Ground Loop | DAIKIN | WCCW5024*J*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
202358923 |  | Ground Loop | DAIKIN | WCCW5024*K*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
202391369 |  | Ground Loop | AQUARIUS | EP012-1VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391370 |  | Ground Loop | AQUARIUS | EP012-1HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
7499466 |  | Ground Loop | FHP | EP030-2HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7499467 |  | Ground Loop | FHP | EP030-3HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7499468 |  | Ground Loop | FHP | EP030-4HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7499480 |  | Ground Loop | FHP | EP060-1HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7499482 |  | Ground Loop | FHP | EP060-3HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7499483 |  | Ground Loop | FHP | EP060-4HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7499484 |  | Ground Loop | FHP | EP070-1HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
202330350 |  | Ground Loop | AAON, Inc. | WV-012-B-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125 | No
202330351 |  | Ground Loop | AAON, Inc. | WV-012-1-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125 | No
202330352 |  | Ground Loop | AAON, Inc. | WV-012-A-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125 | No
5343215 |  | Ground Loop | DAIKIN | WVFW1060*E***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
5343216 |  | Ground Loop | DAIKIN | WVFW1060*F***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
5343217 |  | Ground Loop | DAIKIN | WVFW1060*K***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5 | No
10581116 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT064**1*1******H |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083 | No
10581118 |  | Ground Loop | GEOSTAR | 107H026**1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667 | No
10581119 |  | Ground Loop | GEOSTAR | 107H038**1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833 | No
10581120 |  | Ground Loop | GEOSTAR | 107H049**1*1 |  | 50400 | 19 | 38000 | 4 | 4.2 | No
207699054 |  | Ground Loop | UNILUX VHP | UVHP-03-G |  | 9900 | 17.22 | 7452 | 3.65 | 0.825 | No
207699055 |  | Ground Loop | UNILUX VHP | UVHP-04-G |  | 13040 | 17.32 | 10273 | 3.62 | 1.0867 | No
207699056 |  | Ground Loop | UNILUX VHP | UVHP-05-G |  | 15724 | 17.2 | 11705 | 3.61 | 1.3103 | No
207699057 |  | Ground Loop | UNILUX VHP | UVHP-06-G |  | 19621 | 17.3 | 15106 | 3.62 | 1.6351 | No
207699058 |  | Ground Loop | UNILUX VHP | UVHP-08-G |  | 26613 | 17.38 | 18707 | 3.61 | 2.2178 | No
207699059 |  | Ground Loop | UNILUX VHP | UVHP-10-G |  | 31947 | 17.27 | 21202 | 3.62 | 2.6622 | No
8849312 |  | Ground Loop | 5 SERIES | NDV/NDH026H1*(1,4) |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
214855065 |  | Ground Loop | WHALEN | CASV*030AJ**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855066 |  | Ground Loop | WHALEN | CASV*030AM**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855067 |  | Ground Loop | WHALEN | CASH*036AB**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855068 |  | Ground Loop | WHALEN | CASH*036AD**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855069 |  | Ground Loop | WHALEN | CASH*036AJ**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855070 |  | Ground Loop | WHALEN | CASH*036AM**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855071 |  | Ground Loop | WHALEN | CASV*036AB**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
204031802 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
204031808 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
203363090 |  | Ground Loop | WILLIAMS | EW010H1D*A |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833 | No
5343142 |  | Ground Loop | DAIKIN | WVFW1024*J***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
5343146 |  | Ground Loop | DAIKIN | WVFW1030*E***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
207200622 |  | Ground Loop | GeoSmart Energy | QT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
207200623 |  | Ground Loop | GeoSmart Energy | QT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
207200624 |  | Ground Loop | GeoSmart Energy | VI048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
202391373 |  | Ground Loop | AQUARIUS | EP012-0VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391374 |  | Ground Loop | AQUARIUS | EP012-2VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391375 |  | Ground Loop | AQUARIUS | EP012-0HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391376 |  | Ground Loop | AQUARIUS | EP012-2HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202330339 |  | Ground Loop | AAON, Inc. | WH-036-A-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667 | No
202330340 |  | Ground Loop | AAON, Inc. | WH-036-3-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667 | No
10268238 |  | Ground Loop | TETCO | TBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268244 |  | Ground Loop | GEOCOMFORT | GBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268245 |  | Ground Loop | HYDRON MODULE | HBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268246 |  | Ground Loop | TETCO | TBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268247 |  | Ground Loop | GEOCOMFORT | GBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268248 |  | Ground Loop | HYDRON MODULE | HBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268249 |  | Ground Loop | TETCO | TBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
207334459 |  | Ground Loop | WaterFurnace | NDP038H1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833 | No
207334460 |  | Ground Loop | WaterFurnace | NDP049H1*1 |  | 50400 | 19 | 38000 | 4 | 4.2 | No
207334462 |  | Ground Loop | WaterFurnace | NDP064H1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083 | No
207337519 |  | Ground Loop | GEOSTAR | 103H060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
202443457 |  | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
5708463 |  | Ground Loop | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5708493 |  | Ground Loop | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5708550 |  | Ground Loop | GEOSTAR | 101/102A022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5708623 |  | Ground Loop | GeoSmart Energy | GS022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
5731224 |  | Ground Loop | BARD | GTC36S2-A | GTA3600UD1AA+GTB1-A | 38400 | 17.3 | 29600 | 4 | 3.2 | No
5296263 |  | Ground Loop | TRANE | EXVF0488 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
5296264 |  | Ground Loop | TRANE | EXVF0428 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296265 |  | Ground Loop | TRANE | EXVF0481 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
5296259 |  | Ground Loop | TRANE | EXVF0421 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296260 |  | Ground Loop | TRANE | EXVF0422 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296261 |  | Ground Loop | TRANE | EXVF0423 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
5296262 |  | Ground Loop | TRANE | EXVF0424 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6 | No
202330407 |  | Ground Loop | AAON, Inc. | WV-048-2-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083 | No
202330408 |  | Ground Loop | AAON, Inc. | WV-048-3-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083 | No
5932337 |  | Ground Loop | HYDRON MODULE | HRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5932338 |  | Ground Loop | TETCO | TRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5932368 |  | Ground Loop | GEOCOMFORT | GRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5932380 |  | Ground Loop | HYDRON MODULE | HRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5932381 |  | Ground Loop | TETCO | TRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5317936 |  | Ground Loop | GEOCOMFORT | GRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5317937 |  | Ground Loop | HYDRON MODULE | HRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
5343147 |  | Ground Loop | DAIKIN | WVFW1030*F***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
5343148 |  | Ground Loop | DAIKIN | WVFW1030*J***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
5295956 |  | Ground Loop | TRANE | EXHF0363 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295957 |  | Ground Loop | TRANE | EXHF0368 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295958 |  | Ground Loop | TRANE | EXHF0364 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295959 |  | Ground Loop | TRANE | EXHF0421 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
5295961 |  | Ground Loop | TRANE | EXHF0422 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
5295963 |  | Ground Loop | TRANE | EXHF0423 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
5295965 |  | Ground Loop | TRANE | EXHF0424 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
10443502 |  | Ground Loop | GEOCOMFORT | GBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443503 |  | Ground Loop | HYDRON MODULE | HBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443504 |  | Ground Loop | TETCO | TBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443509 |  | Ground Loop | GEOCOMFORT | GBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443510 |  | Ground Loop | HYDRON MODULE | HBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443511 |  | Ground Loop | TETCO | TBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443512 |  | Ground Loop | GEOCOMFORT | GBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10268261 |  | Ground Loop | HYDRON MODULE | HBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268262 |  | Ground Loop | TETCO | TBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268263 |  | Ground Loop | GEOCOMFORT | GBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268264 |  | Ground Loop | HYDRON MODULE | HBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268265 |  | Ground Loop | TETCO | TBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
10268268 |  | Ground Loop | GEOCOMFORT | GBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268269 |  | Ground Loop | HYDRON MODULE | HBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
3919854 |  | Ground Loop | AQUARIUS | EP015-1HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
3919855 |  | Ground Loop | AQUARIUS | EP015-2HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
3919884 |  | Ground Loop | AQUARIUS | EP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
3919931 |  | Ground Loop | AQUARIUS | EP024-2HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
3920297 |  | Ground Loop | AQUARIUS | EP030-2HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
3920298 |  | Ground Loop | AQUARIUS | EP030-4HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
3920299 |  | Ground Loop | AQUARIUS | EP030-3HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
8247572 |  | Ground Loop | TRANE | DXHF0604 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
8247573 |  | Ground Loop | TRANE | DXHF0608 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
8560787 |  | Ground Loop | 5 SERIES | NSV/NSH030H1*(0,3) |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
8103479 |  | Ground Loop | TRANE | DXHF0241 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
8105907 |  | Ground Loop | TRANE | DXHF0242 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
8105909 |  | Ground Loop | TRANE | DXHF0243 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
207178547 |  | Ground Loop | GEOSTAR | 161/162H072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207200554 |  | Ground Loop | GeoSmart Energy | GT026**1*(1,4)*H |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207200555 |  | Ground Loop | GeoSmart Energy | GT072**1*(1,4)*H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
207200556 |  | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
207200557 |  | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207200560 |  | Ground Loop | GeoSmart Energy | GS018**1*(1,4)*H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
214855051 |  | Ground Loop | WHALEN | CASH*024AB**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855052 |  | Ground Loop | WHALEN | CASH*024AD**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855053 |  | Ground Loop | WHALEN | CASH*024AJ**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855054 |  | Ground Loop | WHALEN | CASH*024AM**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855055 |  | Ground Loop | WHALEN | CASV*024AB**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855056 |  | Ground Loop | WHALEN | CASV*024AD**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855057 |  | Ground Loop | WHALEN | CASV*024AJ**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
5296247 |  | Ground Loop | TRANE | EXVF0241 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125 | No
5296248 |  | Ground Loop | TRANE | EXVF0242 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125 | No
10443495 |  | Ground Loop | TETCO | TBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443496 |  | Ground Loop | GEOCOMFORT | GBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443497 |  | Ground Loop | HYDRON MODULE | HBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443498 |  | Ground Loop | TETCO | TBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443499 |  | Ground Loop | GEOCOMFORT | GBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443500 |  | Ground Loop | HYDRON MODULE | HBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443501 |  | Ground Loop | TETCO | TBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
8786549 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
8786557 |  | Ground Loop | GEOSTAR | 101/102H018**1*(1,4)***** |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
8786558 |  | Ground Loop | GeoSmart Energy | GS018**1*(1,4)********H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
8786559 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
8105931 |  | Ground Loop | TRANE | DXHF0701 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105932 |  | Ground Loop | TRANE | DXHF0702 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105933 |  | Ground Loop | TRANE | DXHF0703 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105934 |  | Ground Loop | TRANE | DXHF0704 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105935 |  | Ground Loop | TRANE | DXHF0708 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667 | No
8105950 |  | Ground Loop | TRANE | DXVF0241 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
8105955 |  | Ground Loop | TRANE | DXVF0242 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
207200563 |  | Ground Loop | GeoSmart Energy | GS030**1*(0,3)*H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
207200564 |  | Ground Loop | GeoSmart Energy | GS030**1*(1,4)*H |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
207200567 |  | Ground Loop | GeoSmart Energy | GS070**1*(1,4)*H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
214813287 |  | Ground Loop | ARCADIAN | AVHP-05-G |  | 15724 | 17.2 | 11705 | 3.61 | 1.3103 | No
214813288 |  | Ground Loop | ARCADIAN | AVHP-06-G |  | 19621 | 17.3 | 15106 | 3.62 | 1.6351 | No
214813289 |  | Ground Loop | ARCADIAN | AVHP-08-G |  | 26613 | 17.38 | 18707 | 3.61 | 2.2178 | No
214813290 |  | Ground Loop | ARCADIAN | AVHP-10-G |  | 31947 | 17.27 | 21202 | 3.62 | 2.6622 | No
202330748 |  | Ground Loop | WHALEN | CASH*036AD**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330749 |  | Ground Loop | WHALEN | CASV*036AD**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
203362373 |  | Ground Loop | WHALEN | VP-H-0814-*DD |  | 24000 | 17.1 | 17000 | 3.8 | 2 | No
203362374 |  | Ground Loop | WHALEN | VP-H-1004-*DD |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833 | No
5615055 |  | Ground Loop | DAIKIN | WCCW5042*F*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
5615056 |  | Ground Loop | DAIKIN | WCCW5042*K*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
5615061 |  | Ground Loop | DAIKIN | WCCW5048*E*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
5615062 |  | Ground Loop | DAIKIN | WCCW5048*F*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
5615063 |  | Ground Loop | DAIKIN | WCCW5048*K*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167 | No
5615068 |  | Ground Loop | DAIKIN | WCCW5060*E*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
10443513 |  | Ground Loop | HYDRON MODULE | HBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443514 |  | Ground Loop | TETCO | TBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7 | No
10443577 |  | Ground Loop | GEOCOMFORT | GBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443578 |  | Ground Loop | HYDRON MODULE | HBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443579 |  | Ground Loop | TETCO | TBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443580 |  | Ground Loop | GEOCOMFORT | GBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443581 |  | Ground Loop | HYDRON MODULE | HBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
202443458 |  | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
202443459 |  | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
202443460 |  | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
202443465 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202443466 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
4231098 |  | Ground Loop | DAIKIN | WCCW4024*K*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1 | No
9850157 |  | Ground Loop | DAIKIN | WVFW1024*K***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
9850202 |  | Ground Loop | DAIKIN | WVFW1030*K***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55 | No
9951968 |  | Ground Loop | BARD | GV27S3AA |  | 26600 | 18.1 | 20200 | 4.1 | 2.2167 | No
9951969 |  | Ground Loop | BARD | GV38S3AA |  | 38500 | 17.1 | 31400 | 4.05 | 3.2083 | No
9951970 |  | Ground Loop | BARD | GV51S3AA |  | 49500 | 17.1 | 39500 | 3.75 | 4.125 | No
8791889 |  | Ground Loop | GeoSmart Energy | GS070**1*(1,4)********H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
8791890 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
8105984 |  | Ground Loop | TRANE | DXVF0702 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
8105985 |  | Ground Loop | TRANE | DXVF0703 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
8106144 |  | Ground Loop | TRANE | DXVF0704 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
8106145 |  | Ground Loop | TRANE | DXVF0708 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
8247563 |  | Ground Loop | TRANE | DXHF0601 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
8247564 |  | Ground Loop | TRANE | DXHF0602 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
8247571 |  | Ground Loop | TRANE | DXHF0603 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417 | No
202330770 |  | Ground Loop | WHALEN | CASV*030AM**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330771 |  | Ground Loop | WHALEN | CASH*036AJ**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330772 |  | Ground Loop | WHALEN | CASV*036AJ**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330773 |  | Ground Loop | WHALEN | CASH*036AM**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330774 |  | Ground Loop | WHALEN | CASV*036AM**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214813285 |  | Ground Loop | ARCADIAN | AVHP-03-G |  | 9900 | 17.22 | 7452 | 3.65 | 0.825 | No
214813286 |  | Ground Loop | ARCADIAN | AVHP-04-G |  | 13040 | 17.32 | 10273 | 3.62 | 1.0867 | No
6936993 |  | Ground Loop | BARD | GTC60S2-A | HE49948D210B2705AW | 63000 | 18.8 | 48000 | 4.05 | 5.25 | No
6945298 |  | Ground Loop | BARD | GTC48S2-A | HE49948D210B2705AW | 51500 | 18.6 | 37000 | 3.9 | 4.2917 | No
202330308 |  | Ground Loop | AAON, Inc. | WH-036-A-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667 | No
202330309 |  | Ground Loop | AAON, Inc. | WH-036-2-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833 | No
202330310 |  | Ground Loop | AAON, Inc. | WH-036-3-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833 | No
202330311 |  | Ground Loop | AAON, Inc. | WH-036-2-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667 | No
202330312 |  | Ground Loop | AAON, Inc. | WH-036-3-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667 | No
10445242 |  | Ground Loop | WaterFurnace | SDV049H1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
10268270 |  | Ground Loop | TETCO | TBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268271 |  | Ground Loop | GEOCOMFORT | GBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268272 |  | Ground Loop | HYDRON MODULE | HBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268273 |  | Ground Loop | TETCO | TBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268274 |  | Ground Loop | GEOCOMFORT | GBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268275 |  | Ground Loop | HYDRON MODULE | HBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268276 |  | Ground Loop | TETCO | TBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
8105926 |  | Ground Loop | TRANE | DXHF0481 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105927 |  | Ground Loop | TRANE | DXHF0482 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105928 |  | Ground Loop | TRANE | DXHF0483 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105929 |  | Ground Loop | TRANE | DXHF0484 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
8105930 |  | Ground Loop | TRANE | DXHF0488 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167 | No
207178494 |  | Ground Loop | GEOSTAR | 161/162J049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
207178526 |  | Ground Loop | GEOSTAR | 161/162H026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
207178527 |  | Ground Loop | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
214855043 |  | Ground Loop | WHALEN | CASH*015AB**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
7167357 |  | Ground Loop | CARRIER | 50PSH/V060***6/FA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7167358 |  | Ground Loop | CARRIER | 50PSH/V060***5/EA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7167359 |  | Ground Loop | CARRIER | 50PSH/V060***3/CA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
7167360 |  | Ground Loop | CARRIER | 50PSH/V070***3/CA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
7167361 |  | Ground Loop | CARRIER | 50PSH/V070***5/EA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
7167362 |  | Ground Loop | CARRIER | 50PSH/V070***6/FA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
7076986 |  | Ground Loop | AQUARIUS | EP024-3HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7076987 |  | Ground Loop | AQUARIUS | EP024-4HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
202330323 |  | Ground Loop | AAON, Inc. | WH-048-1-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083 | No
202330324 |  | Ground Loop | AAON, Inc. | WH-048-A-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083 | No
202330327 |  | Ground Loop | AAON, Inc. | WH-048-2-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083 | No
202330328 |  | Ground Loop | AAON, Inc. | WH-048-3-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083 | No
5360714 |  | Ground Loop | BARD | GTC36S2-A | GTADP-3642-* | 39500 | 18.3 | 29000 | 4.2 | 3.2917 | No
5360715 |  | Ground Loop | BARD | GTC48S2-A | GTADP-4860-C | 51500 | 18.6 | 37000 | 3.9 | 4.2917 | No
5360791 |  | Ground Loop | BARD | GTC60S2-A | GTADP-4860-C | 63000 | 18.8 | 48000 | 4.05 | 5.25 | No
5615069 |  | Ground Loop | DAIKIN | WCCW5060*F*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
201846902 |  | Ground Loop | GEOSTAR | 111H038**1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3 | No
5295967 |  | Ground Loop | TRANE | EXHF0428 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625 | No
5295970 |  | Ground Loop | TRANE | EXHF0481 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
5295971 |  | Ground Loop | TRANE | EXHF0482 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
5295972 |  | Ground Loop | TRANE | EXHF0483 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
5295973 |  | Ground Loop | TRANE | EXHF0484 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
5295974 |  | Ground Loop | TRANE | EXHF0488 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917 | No
10443582 |  | Ground Loop | TETCO | TBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443583 |  | Ground Loop | GEOCOMFORT | GBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443584 |  | Ground Loop | HYDRON MODULE | HBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443585 |  | Ground Loop | TETCO | TBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443586 |  | Ground Loop | GEOCOMFORT | GBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443587 |  | Ground Loop | HYDRON MODULE | HBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
10443588 |  | Ground Loop | TETCO | TBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417 | No
202607207 |  | Ground Loop | WHALEN | VP-A-0814-*DD |  | 24000 | 17.1 | 17000 | 3.8 | 2 | No
4219442 |  | Ground Loop | NORDIC | RS25HACW-P-1T-* | AH-25-P-1-***** | 24800 | 17 | 18300 | 3.6 | 2.0667 | No
3919848 |  | Ground Loop | AQUARIUS | EP009-1HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
3919850 |  | Ground Loop | AQUARIUS | EP009-2HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
3919853 |  | Ground Loop | AQUARIUS | EP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
8786527 |  | Ground Loop | GEOSTAR | 101/102H026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
8786528 |  | Ground Loop | GeoSmart Energy | GT026**1*(1,4)********H |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
8786529 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****H |  | 26400 | 19.6 | 19500 | 4 | 2.2 | No
8786547 |  | Ground Loop | GEOSTAR | 101/102H072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
8786548 |  | Ground Loop | GeoSmart Energy | GT072**1*(1,4)********H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
8105956 |  | Ground Loop | TRANE | DXVF0243 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
8105960 |  | Ground Loop | TRANE | DXVF0244 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
8105965 |  | Ground Loop | TRANE | DXVF0247 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
8105966 |  | Ground Loop | TRANE | DXVF0248 |  | 24948 | 17.41 | 19300 | 4 | 2.079 | No
202350416 |  | Ground Loop | AAON, Inc. | RN-009-4-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583 | No
202350426 |  | Ground Loop | AAON, Inc. | RN-011-2-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775 | No
202350427 |  | Ground Loop | AAON, Inc. | RN-011-3-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775 | No
202350428 |  | Ground Loop | AAON, Inc. | RN-011-4-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775 | No
7499485 |  | Ground Loop | FHP | EP070-3HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
7499487 |  | Ground Loop | FHP | EP070-4HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
202330763 |  | Ground Loop | WHALEN | CASH*024AJ**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330764 |  | Ground Loop | WHALEN | CASV*024AJ**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330765 |  | Ground Loop | WHALEN | CASH*024AM**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330766 |  | Ground Loop | WHALEN | CASV*024AM**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330767 |  | Ground Loop | WHALEN | CASH*030AJ**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330768 |  | Ground Loop | WHALEN | CASV*030AJ**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330769 |  | Ground Loop | WHALEN | CASH*030AM**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
5677855 |  | Ground Loop | BARD | QW2S2-A |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333 | No
5677856 |  | Ground Loop | BARD | QW2S2-B |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333 | No
5677857 |  | Ground Loop | BARD | QW2S2-C |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333 | No
5696567 |  | Ground Loop | 5 SERIES | NSV/NSH022G1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
10445244 |  | Ground Loop | WaterFurnace | SDV072H1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
10447649 |  | Ground Loop | RHEEM | RPVS/EC025 | RCFL-HM2417 | 24000 | 17.4 | 18800 | 3.9 | 2 | Yes
10447650 |  | Ground Loop | RHEEM | RPVS/EC025 | RCFL-HM2621 | 26000 | 18 | 18600 | 3.8 | 2.1667 | Yes
10447662 |  | Ground Loop | RHEEM | RPVS/EC036 | RCFL-HM38** | 38000 | 17.3 | 26600 | 3.7 | 3.1667 | Yes
10581108 |  | Ground Loop | 5 SERIES | NDP026H1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667 | No
10268277 |  | Ground Loop | GEOCOMFORT | GBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268278 |  | Ground Loop | HYDRON MODULE | HBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10268279 |  | Ground Loop | TETCO | TBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833 | No
10318053 |  | Ground Loop | GEOSTAR | 103H060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
10443493 |  | Ground Loop | GEOCOMFORT | GBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
10443494 |  | Ground Loop | HYDRON MODULE | HBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675 | No
3920300 |  | Ground Loop | AQUARIUS | EP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
3920500 |  | Ground Loop | AQUARIUS | EP060-4HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
3920501 |  | Ground Loop | AQUARIUS | EP060-3HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
3920502 |  | Ground Loop | AQUARIUS | EP060-1HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125 | No
3920503 |  | Ground Loop | AQUARIUS | EP070-1HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
3920504 |  | Ground Loop | AQUARIUS | EP070-3HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
3920505 |  | Ground Loop | AQUARIUS | EP070-4HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875 | No
8560799 |  | Ground Loop | 5 SERIES | NSV/NSH018H1*(1,4) |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417 | No
8560800 |  | Ground Loop | 5 SERIES | NSV/NSH022H1*(1,4) |  | 19200 | 18.7 | 15000 | 4 | 1.6 | No
8560801 |  | Ground Loop | 5 SERIES | NSV/NSH030H1*(1,4) |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
8560806 |  | Ground Loop | 5 SERIES | NSV/NSH070H1*(1,4) |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
8570181 |  | Ground Loop | 5 SERIES | NDV/NDH072H1*(1,4) |  | 73800 | 18.2 | 55400 | 3.7 | 6.15 | No
8105911 |  | Ground Loop | TRANE | DXHF0244 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
8105912 |  | Ground Loop | TRANE | DXHF0247 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
8105913 |  | Ground Loop | TRANE | DXHF0248 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578 | No
202350098 |  | Ground Loop | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833 | No
202350414 |  | Ground Loop | AAON, Inc. | RN-009-2-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583 | No
202350415 |  | Ground Loop | AAON, Inc. | RN-009-3-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583 | No
214855058 |  | Ground Loop | WHALEN | CASV*024AM**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
214855059 |  | Ground Loop | WHALEN | CASH*030AB**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855060 |  | Ground Loop | WHALEN | CASH*030AD**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855061 |  | Ground Loop | WHALEN | CASH*030AJ**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855062 |  | Ground Loop | WHALEN | CASH*030AM**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855063 |  | Ground Loop | WHALEN | CASV*030AB**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
214855064 |  | Ground Loop | WHALEN | CASV*030AD**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
7167339 |  | Ground Loop | CARRIER | 50PSH/V015***4/DA |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
7167342 |  | Ground Loop | CARRIER | 50PSH/V024***3/CA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7167343 |  | Ground Loop | CARRIER | 50PSH/V024***4/DA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7167344 |  | Ground Loop | CARRIER | 50PSH/V030***4/DA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7167345 |  | Ground Loop | CARRIER | 50PSH/V030***6/FA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7167346 |  | Ground Loop | CARRIER | 50PSH/V030***5/EA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
7167347 |  | Ground Loop | CARRIER | 50PSH/V030***3/CA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
6965882 |  | Ground Loop | TRANE | EXVF0061 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675 | No
6965885 |  | Ground Loop | TRANE | EXVF0062 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675 | No
6965888 |  | Ground Loop | TRANE | EXVF0067 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675 | No
5613676 |  | Ground Loop | GEOSTAR | 141/142A048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
5341546 |  | Ground Loop | DAIKIN | WVFW1019*E***04 |  | 19700 | 19 | 13400 | 3.7 | 1.6417 | No
5341628 |  | Ground Loop | DAIKIN | WVFW1019*J***04 |  | 19700 | 19 | 13400 | 3.7 | 1.6417 | No
5343140 |  | Ground Loop | DAIKIN | WVFW1024*E***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
5343141 |  | Ground Loop | DAIKIN | WVFW1024*F***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917 | No
202330280 |  | Ground Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 14700 | 19.9 | 10900 | 5.2 | 1.225 | No
202330281 |  | Ground Loop | AAON, Inc. | WH-018-1-H-ACAC-C0-10-100-A |  | 17600 | 17.6 | 13500 | 4.4 | 1.4667 | No
202330282 |  | Ground Loop | AAON, Inc. | WH-018-A-H-ACAC-C0-10-100-A |  | 17600 | 17.6 | 13500 | 4.4 | 1.4667 | No
202330283 |  | Ground Loop | AAON, Inc. | WH-018-1-H-ACAC-C0-10-200-A |  | 17300 | 19.2 | 13300 | 4.7 | 1.4417 | No
202330284 |  | Ground Loop | AAON, Inc. | WH-018-A-H-ACAC-C0-10-200-A |  | 17300 | 19.2 | 13300 | 4.7 | 1.4417 | No
5440741 |  | Ground Loop | 7 SERIES | NVV/NVH048A1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
5505441 |  | Ground Loop | BARD | GTC36S2-A | HE37942D175B2505AW/HE37942D210B2505AW | 38500 | 19.3 | 27000 | 4.1 | 3.2083 | No
5612204 |  | Ground Loop | GeoSmart Energy | VI048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
10268250 |  | Ground Loop | GEOCOMFORT | GBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268251 |  | Ground Loop | HYDRON MODULE | HBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268252 |  | Ground Loop | TETCO | TBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268253 |  | Ground Loop | GEOCOMFORT | GBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268254 |  | Ground Loop | HYDRON MODULE | HBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268255 |  | Ground Loop | TETCO | TBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333 | No
10268260 |  | Ground Loop | GEOCOMFORT | GBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917 | No
212508380 |  | Ground Loop | HYDROTECH | WSH6030AN* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
212508395 |  | Ground Loop | AE Air | WSH6024AN* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | No
212508397 |  | Ground Loop | AE Air | WSH6030AN* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
202391437 |  | Ground Loop | FHP | EP012-2HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391438 |  | Ground Loop | FHP | EP012-0HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
205288519 |  | Ground Loop | BARD | QW2S3DA |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833 | No
205288520 |  | Ground Loop | BARD | QW2S3DB |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833 | No
205288643 |  | Ground Loop | BARD | QW2S3DC |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833 | No
7499450 |  | Ground Loop | FHP | EP009-1HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
7499451 |  | Ground Loop | FHP | EP009-2HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
7499453 |  | Ground Loop | FHP | EP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
7167555 |  | Ground Loop | CARRIER | 50PSH/V024***5/EA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7167556 |  | Ground Loop | CARRIER | 50PSH/V024***6/FA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
202330343 |  | Ground Loop | AAON, Inc. | WH-048-A-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667 | No
202330344 |  | Ground Loop | AAON, Inc. | WH-048-3-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667 | No
202330347 |  | Ground Loop | AAON, Inc. | WV-009-B-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667 | No
202330348 |  | Ground Loop | AAON, Inc. | WV-009-1-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667 | No
202330349 |  | Ground Loop | AAON, Inc. | WV-009-A-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667 | No
202330273 |  | Ground Loop | AAON, Inc. | WH-009-A-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775 | No
202330277 |  | Ground Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-100-A |  | 14700 | 18.2 | 11100 | 4.8 | 1.225 | No
5295949 |  | Ground Loop | TRANE | EXHF0247 |  | 24700 | 18 | 17900 | 3.6 | 2.0583 | No
5295950 |  | Ground Loop | TRANE | EXHF0301 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475 | No
5295951 |  | Ground Loop | TRANE | EXHF0302 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475 | No
5295952 |  | Ground Loop | TRANE | EXHF0307 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475 | No
5295953 |  | Ground Loop | TRANE | EXHF0361 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295954 |  | Ground Loop | TRANE | EXHF0362 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
5295955 |  | Ground Loop | TRANE | EXHF0367 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333 | No
202330278 |  | Ground Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-100-A |  | 14700 | 18.2 | 11100 | 4.8 | 1.225 | No
202330279 |  | Ground Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 14700 | 19.9 | 10900 | 5.2 | 1.225 | No
202607208 |  | Ground Loop | WHALEN | VP-A-1004-*DD |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833 | No
8789591 |  | Ground Loop | GEOSTAR | 101/102H030**1*(0,3)***** |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
8789592 |  | Ground Loop | GeoSmart Energy | GS030**1*(0,3)********H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
8789593 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325 | No
8789596 |  | Ground Loop | GEOSTAR | 101/102H030**1*(1,4)***** |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
8789597 |  | Ground Loop | GeoSmart Energy | GS030**1*(1,4)********H |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
8789598 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 28100 | 22 | 20500 | 3.9 | 2.3417 | No
8791888 |  | Ground Loop | GEOSTAR | 101/102H070**1*(1,4)***** |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583 | No
8105973 |  | Ground Loop | TRANE | DXVF0481 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105974 |  | Ground Loop | TRANE | DXVF0482 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105975 |  | Ground Loop | TRANE | DXVF0483 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105976 |  | Ground Loop | TRANE | DXVF0484 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
202350093 |  | Ground Loop | 5 SERIES | NSV/NSH036J1*(0,3) |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
202350095 |  | Ground Loop | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
202350096 |  | Ground Loop | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
214855044 |  | Ground Loop | WHALEN | CASH*015AD**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
214855045 |  | Ground Loop | WHALEN | CASV*015AB**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
214855046 |  | Ground Loop | WHALEN | CASV*015AD**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
214855047 |  | Ground Loop | WHALEN | CASH*018AB**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
214855048 |  | Ground Loop | WHALEN | CASH*018AD**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
214855049 |  | Ground Loop | WHALEN | CASV*018AB**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
214855050 |  | Ground Loop | WHALEN | CASV*018AD**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
6580833 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333 | No
6581203 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917 | No
203363320 |  | Ground Loop | WILLIAMS | EW009H1D*A |  | 24000 | 17.1 | 17000 | 3.8 | 2 | No
5343160 |  | Ground Loop | DAIKIN | WVFW1042*E***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
5343161 |  | Ground Loop | DAIKIN | WVFW1042*F***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
5343162 |  | Ground Loop | DAIKIN | WVFW1042*K***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417 | No
10581109 |  | Ground Loop | 5 SERIES | NDP038H1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833 | No
10581110 |  | Ground Loop | 5 SERIES | NDP049H1*1 |  | 50400 | 19 | 38000 | 4 | 4.2 | No
10581111 |  | Ground Loop | 5 SERIES | NDP064H1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083 | No
10581113 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT026**1*1******H |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667 | No
10581114 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833 | No
10581115 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT049**1*1******H |  | 50400 | 19 | 38000 | 4 | 4.2 | No
214855072 |  | Ground Loop | WHALEN | CASV*036AD**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855073 |  | Ground Loop | WHALEN | CASV*036AJ**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
214855074 |  | Ground Loop | WHALEN | CASV*036AM**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202350506 |  | Ground Loop | AAON, Inc. | WH-036-1-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667 | No
202350507 |  | Ground Loop | AAON, Inc. | WH-036-2-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667 | No
202350510 |  | Ground Loop | AAON, Inc. | WH-048-1-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667 | No
7499455 |  | Ground Loop | FHP | EP015-1HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
7499456 |  | Ground Loop | FHP | EP015-2HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
7499460 |  | Ground Loop | FHP | EP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7499461 |  | Ground Loop | FHP | EP024-2HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7499463 |  | Ground Loop | FHP | EP024-3HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7499464 |  | Ground Loop | FHP | EP024-4HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667 | No
7499465 |  | Ground Loop | FHP | EP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375 | No
202330422 |  | Ground Loop | AAON, Inc. | WV-036-A-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2 | No
202330424 |  | Ground Loop | AAON, Inc. | WV-036-3-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2 | No
202330392 |  | Ground Loop | AAON, Inc. | WV-036-3-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05 | No
5615040 |  | Ground Loop | DAIKIN | WCCW5030*J*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
5615041 |  | Ground Loop | DAIKIN | WCCW5030*K*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
5615046 |  | Ground Loop | DAIKIN | WCCW5036*E*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
5615047 |  | Ground Loop | DAIKIN | WCCW5036*F*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
5615048 |  | Ground Loop | DAIKIN | WCCW5036*J*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
5615049 |  | Ground Loop | DAIKIN | WCCW5036*K*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667 | No
5615054 |  | Ground Loop | DAIKIN | WCCW5042*E*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675 | No
202330305 |  | Ground Loop | AAON, Inc. | WH-036-1-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833 | No
202330306 |  | Ground Loop | AAON, Inc. | WH-036-A-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833 | No
202330307 |  | Ground Loop | AAON, Inc. | WH-036-1-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667 | No
203113881 |  | Ground Loop | GEOSTAR | 101/102J036**1*(0,3)***** |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
203113882 |  | Ground Loop | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
202391446 |  | Ground Loop | CARRIER | 50PSH012**C3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391449 |  | Ground Loop | CARRIER | 50PSV012**C0/BA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391450 |  | Ground Loop | CARRIER | 50PSV012**C4/DA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391451 |  | Ground Loop | CARRIER | 50PSH012**C0/BA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391452 |  | Ground Loop | CARRIER | 50PSH012**C4/DA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206599757 |  | Ground Loop | 5 SERIES | NSV/NSH060J1*0* |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
206599760 |  | Ground Loop | 5 SERIES | NSV/NSH060J1*(1,4)* |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
206599762 |  | Ground Loop | GEOSTAR | 101/102J060**1*0****** |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917 | No
206599765 |  | Ground Loop | GEOSTAR | 101/102J060**1*(1,4)****** |  | 62200 | 18.4 | 47900 | 4 | 5.1833 | No
205782572 |  | Ground Loop | GeoSmart Energy | QT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
205782574 |  | Ground Loop | GeoSmart Energy | QT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
206199262 |  | Ground Loop | RHEEM | RPVV/H/D026D |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667 | No
206199264 |  | Ground Loop | RHEEM | RPVV/H/D049D |  | 49600 | 19.3 | 36400 | 4 | 4.1333 | No
206199265 |  | Ground Loop | RHEEM | RPVV/H/D064D |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167 | No
203363068 |  | Ground Loop | WILLIAMS | EW009A1D*A |  | 24000 | 17.1 | 17000 | 3.8 | 2 | No
5615038 |  | Ground Loop | DAIKIN | WCCW5030*E*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
5615039 |  | Ground Loop | DAIKIN | WCCW5030*F*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333 | No
4230439 |  | Ground Loop | DAIKIN | WCCW4015*E*04* |  | 17200 | 20.8 | 11500 | 4 | 1.4333 | No
4230441 |  | Ground Loop | DAIKIN | WCCW4015*J*04* |  | 16800 | 20.8 | 11500 | 3.8 | 1.4 | No
4230746 |  | Ground Loop | DAIKIN | WCCW4019*E*04* |  | 22600 | 18.4 | 14800 | 3.8 | 1.8833 | No
4230748 |  | Ground Loop | DAIKIN | WCCW4019*J*04* |  | 22600 | 18.4 | 14800 | 3.8 | 1.8833 | No
4230750 |  | Ground Loop | DAIKIN | WCCW4024*E*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1 | No
4230752 |  | Ground Loop | DAIKIN | WCCW4024*F*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1 | No
4230754 |  | Ground Loop | DAIKIN | WCCW4024*J*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1 | No
8789586 |  | Ground Loop | GEOSTAR | 101/102H022**1*(1,4)***** |  | 19200 | 18.7 | 15500 | 4 | 1.6 | No
8105977 |  | Ground Loop | TRANE | DXVF0488 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583 | No
8105978 |  | Ground Loop | TRANE | DXVF0601 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105979 |  | Ground Loop | TRANE | DXVF0602 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105980 |  | Ground Loop | TRANE | DXVF0603 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105981 |  | Ground Loop | TRANE | DXVF0604 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105982 |  | Ground Loop | TRANE | DXVF0608 |  | 62100 | 18.2 | 51100 | 4 | 5.175 | No
8105983 |  | Ground Loop | TRANE | DXVF0701 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917 | No
207200570 |  | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417 | No
207200571 |  | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
207200572 |  | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
207200574 |  | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
7167334 |  | Ground Loop | CARRIER | 50PSH/V009***3/CA |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
7167335 |  | Ground Loop | CARRIER | 50PSH/V009***4/DA |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167 | No
7167337 |  | Ground Loop | CARRIER | 50PSH/V012***3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
7167338 |  | Ground Loop | CARRIER | 50PSH/V015***3/CA |  | 16200 | 19.8 | 11000 | 3.63 | 1.35 | No
6966727 |  | Ground Loop | TRANE | EXVF0121 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917 | No
6966753 |  | Ground Loop | TRANE | EXVF0122 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917 | No
6966789 |  | Ground Loop | TRANE | EXVF0127 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917 | No
203466716 |  | Ground Loop | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
203470607 |  | Ground Loop | 5 SERIES | NSV/NSH048J1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
5343170 |  | Ground Loop | DAIKIN | WVFW1048*E***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
5343172 |  | Ground Loop | DAIKIN | WVFW1048*F***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
5343173 |  | Ground Loop | DAIKIN | WVFW1048*K***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833 | No
5317927 |  | Ground Loop | GEOCOMFORT | GRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225 | No
5317928 |  | Ground Loop | HYDRON MODULE | HRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225 | No
5317929 |  | Ground Loop | TETCO | TRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225 | No
5317930 |  | Ground Loop | GEOCOMFORT | GRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5317931 |  | Ground Loop | HYDRON MODULE | HRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5317932 |  | Ground Loop | TETCO | TRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
5295943 |  | Ground Loop | TRANE | EXHF0241 |  | 24700 | 18 | 17900 | 3.6 | 2.0583 | No
5295946 |  | Ground Loop | TRANE | EXHF0242 |  | 24700 | 18 | 17900 | 3.6 | 2.0583 | No
202443468 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083 | No
202443469 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
207337520 |  | Ground Loop | GEOSTAR | 103H060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917 | No
207348743 |  | Ground Loop | WaterFurnace | URT096*3*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65 | No
207348744 |  | Ground Loop | WaterFurnace | URT096*4*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65 | No
202350519 |  | Ground Loop | AAON, Inc. | WV-036-1-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2 | No
202350521 |  | Ground Loop | AAON, Inc. | WV-036-2-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2 | No
202350524 |  | Ground Loop | AAON, Inc. | WV-048-1-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083 | No
202330575 |  | Ground Loop | AAON, Inc. | WH-006-A-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333 | No
202330576 |  | Ground Loop | AAON, Inc. | WV-006-B-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525 | No
202330577 |  | Ground Loop | AAON, Inc. | WV-006-1-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525 | No
202330578 |  | Ground Loop | AAON, Inc. | WV-006-A-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525 | No
202330738 |  | Ground Loop | WHALEN | CASH*024AB**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330739 |  | Ground Loop | WHALEN | CASV*024AB**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330740 |  | Ground Loop | WHALEN | CASH*024AD**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330403 |  | Ground Loop | AAON, Inc. | WV-048-1-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083 | No
202330404 |  | Ground Loop | AAON, Inc. | WV-048-A-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083 | No
10268201 |  | Ground Loop | GEOCOMFORT | GBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268202 |  | Ground Loop | HYDRON MODULE | HBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268203 |  | Ground Loop | TETCO | TBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268204 |  | Ground Loop | GEOCOMFORT | GBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268205 |  | Ground Loop | HYDRON MODULE | HBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268206 |  | Ground Loop | TETCO | TBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268207 |  | Ground Loop | GEOCOMFORT | GBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
212505504 |  | Ground Loop | AE Air | WSH6030AM* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
212505507 |  | Ground Loop | HYDROTECH | WSH6024AM* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | No
212505508 |  | Ground Loop | HYDROTECH | WSH6030AM* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5 | No
212505512 |  | Ground Loop | AE Air | WSH6024AM* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | No
212508378 |  | Ground Loop | HYDROTECH | WSH6024AN* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083 | No
202358913 |  | Ground Loop | DAIKIN | WCCW5019*E*04* |  | 20600 | 19 | 14000 | 3.7 | 1.7167 | No
202358915 |  | Ground Loop | DAIKIN | WCCW5019*J*04* |  | 20600 | 19 | 14000 | 3.7 | 1.7167 | No
202358917 |  | Ground Loop | DAIKIN | WCCW5024*E*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417 | No
202350511 |  | Ground Loop | AAON, Inc. | WH-048-2-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667 | No
202350515 |  | Ground Loop | AAON, Inc. | WV-024-1-H-DCAC-C0-10-D00-A |  | 26900 | 18.1 | 16700 | 3.82 | 2.2417 | No
202330741 |  | Ground Loop | WHALEN | CASV*024AD**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833 | No
202330742 |  | Ground Loop | WHALEN | CASH*030AB**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330743 |  | Ground Loop | WHALEN | CASV*030AB**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330744 |  | Ground Loop | WHALEN | CASH*030AD**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330745 |  | Ground Loop | WHALEN | CASV*030AD**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5 | No
202330746 |  | Ground Loop | WHALEN | CASH*036AB**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
202330747 |  | Ground Loop | WHALEN | CASV*036AB**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3 | No
203363069 |  | Ground Loop | WILLIAMS | EW010A1D*A |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833 | No
5615070 |  | Ground Loop | DAIKIN | WCCW5060*K*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417 | No
5296266 |  | Ground Loop | TRANE | EXVF0482 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
5296267 |  | Ground Loop | TRANE | EXVF0483 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
5296268 |  | Ground Loop | TRANE | EXVF0484 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917 | No
203113887 |  | Ground Loop | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 40700 | 21.7 | 28900 | 4 | 3.3917 | No
10206404 |  | Ground Loop | BARD | GTC36S2-A | HE37942D210B2505AW | 39500 | 18.3 | 29000 | 4.2 | 3.2917 | No
10206405 |  | Ground Loop | BARD | GTC36S2-A | HE37942D175B2505AW | 39500 | 18.3 | 29000 | 4.2 | 3.2917 | No
10268136 |  | Ground Loop | GEOCOMFORT | GBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
10268137 |  | Ground Loop | HYDRON MODULE | HBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333 | No
202350526 |  | Ground Loop | AAON, Inc. | WV-048-2-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083 | No
206315251 |  | Ground Loop | WHALEN | CASH*015AD**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
206315252 |  | Ground Loop | WHALEN | CASV*015AD**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
206315253 |  | Ground Loop | WHALEN | CASH*018AB**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
206315254 |  | Ground Loop | WHALEN | CASV*018AB**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
206315255 |  | Ground Loop | WHALEN | CASH*018AD**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
206315256 |  | Ground Loop | WHALEN | CASV*018AD**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417 | No
202330573 |  | Ground Loop | AAON, Inc. | WH-006-B-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333 | No
202330574 |  | Ground Loop | AAON, Inc. | WH-006-1-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333 | No
202330387 |  | Ground Loop | AAON, Inc. | WV-036-1-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05 | No
202330388 |  | Ground Loop | AAON, Inc. | WV-036-A-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05 | No
202330391 |  | Ground Loop | AAON, Inc. | WV-036-2-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05 | No
5932336 |  | Ground Loop | GEOCOMFORT | GRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083 | No
10268208 |  | Ground Loop | HYDRON MODULE | HBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268209 |  | Ground Loop | TETCO | TBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825 | No
10268233 |  | Ground Loop | GEOCOMFORT | GBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268234 |  | Ground Loop | HYDRON MODULE | HBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268235 |  | Ground Loop | TETCO | TBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268236 |  | Ground Loop | GEOCOMFORT | GBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
10268237 |  | Ground Loop | HYDRON MODULE | HBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917 | No
207334458 |  | Ground Loop | WaterFurnace | NDP026H1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667 | No
202391439 |  | Ground Loop | FHP | EP012-2VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391440 |  | Ground Loop | FHP | EP012-0VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391443 |  | Ground Loop | FHP | EP012-1HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391444 |  | Ground Loop | FHP | EP012-1VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
202391445 |  | Ground Loop | CARRIER | 50PSV012**C3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05 | No
206315249 |  | Ground Loop | WHALEN | CASH*015AB**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
206315250 |  | Ground Loop | WHALEN | CASV*015AB**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25 | No
205782568 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YACT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975 | No
205782570 |  | Ground Loop | YORK BY JOHNSON CONTROLS | YACT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083 | No
203490410 |  | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333 | No
203490416 |  | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
203494005 |  | Ground Loop | GEOSTAR | 101/102J048**1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825 | No
202330427 |  | Ground Loop | AAON, Inc. | WV-048-A-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083 | No
202330428 |  | Ground Loop | AAON, Inc. | WV-048-A-H-DCAC-C0-10-D00-A |  | 49800 | 17.5 | 44900 | 3.9 | 4.15 | No
202330429 |  | Ground Loop | AAON, Inc. | WV-048-3-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083 | No
202330418 |  | Ground Loop | AAON, Inc. | WV-024-A-H-DCAC-C0-10-D00-A |  | 26900 | 18.1 | 16700 | 3.82 | 2.2417 | No
5317938 |  | Ground Loop | TETCO | TRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083 | No
202330271 |  | Ground Loop | AAON, Inc. | WH-009-B-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775 | No
202330272 |  | Ground Loop | AAON, Inc. | WH-009-1-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775 | No
5296249 |  | Ground Loop | TRANE | EXVF0247 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125 | No
5296250 |  | Ground Loop | TRANE | EXVF0301 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333 | No
5296251 |  | Ground Loop | TRANE | EXVF0302 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333 | No
5296252 |  | Ground Loop | TRANE | EXVF0307 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333 | No

## Residential GSHP
[7 empty] | Water Loop Heat Pump |  |  |  |  | Ground Water Heat Pump |  |  |  |  | Ground Loop Heat Pump |  |  |  |  | Direct Geoexchange Heat Pump
AHRI Certified Reference Number | Date No Longer Eligible | Brand Name | AHRI Type | Program Type | Outdoor Unit Model Number | Indoor Unit Model Number(s) | Full Load WLHP Cooling Capacity (Btuh) | Full Load WLHP Cooling EER (Btuh/watt) | Full Load WLHP Heating COP | Full Load WLHP Heating Capacity (Btuh) | WLHP Tonnage | Full Load GWHP Cooling Capacity (Btuh) | Full Load GWHP Cooling EER (Btuh/watt) | Full Load GWHP Heating COP | Full Load GWHP Heating Capacity (Btuh) | GWHP Tonnage | Full Load GLHP Cooling Capacity (Btuh) | Full Load GLHP Cooling EER (Btuh/watt) | Full Load GLHP Heating COP | Full Load GLHP Heating Capacity (Btuh) | GLHP Tonnage | Refrigerant Type | Full Load DGX Cooling Capacity (Btuh) | Full Load DGX Cooling EER (Btuh/watt) | Full Load DGX Heating COP | Full Load DGX Heating Capacity (Btuh) | DGX Tonnage
203105868 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-36C1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-410A | 38000 | 19.1 | 3.9 | 38000 | 3.1667
203105870 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-42C1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-410A | 44000 | 21 | 3.9 | 44000 | 3.6667
203105871 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 51500 | 19.8 | 4 | 51500 | 4.2917
203105874 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-54C1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-410A | 56000 | 19.1 | 3.8 | 56000 | 4.6667
203105877 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-60C1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-410A | 61500 | 19.1 | 3.6 | 61500 | 5.125
203470614 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 33600 | 20.1 | 3.6 | 33600 | 2.8
203470620 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-24C1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-410A | 25400 | 19.1 | 3.9 | 25400 | 2.1167
203470621 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-30C1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-410A | 31600 | 20.1 | 3.9 | 31600 | 2.6333
204494956 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-36C1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-410A | 38000 | 19.1 | 3.9 | 38000 | 3.1667
204494957 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-42C1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-410A | 44000 | 19.1 | 3.9 | 44000 | 3.6667
204494958 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 51500 | 19.8 | 4 | 51500 | 4.2917
204494959 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-54C1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-410A | 56000 | 19.1 | 3.8 | 56000 | 4.6667
204494960 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-60C1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-410A | 61500 | 19.1 | 3.6 | 61500 | 5.125
216720848 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-24D1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-454B | 24000 | 19.1 | 3.9 | 24000 | 2
216720849 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-30D1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-454B | 31600 | 20.1 | 3.9 | 31600 | 2.6333
216720850 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 38000 | 22 | 3.9 | 38000 | 3.1667
216720851 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 44000 | 19.1 | 3.9 | 44000 | 3.6667
216720852 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 51500 | 21 | 4.1 | 51500 | 4.2917
216720853 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-54D1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-454B | 56000 | 19.1 | 3.8 | 56000 | 4.6667
216720854 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 61500 | 19.1 | 4 | 61500 | 5.125
216720855 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-24D1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-454B | 16100 | 20.1 | 4.3 | 16100 | 1.3417
216720856 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-30D1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-454B | 20100 | 20.1 | 4.3 | 20100 | 1.675
216720857 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.1 | 24100 | 2.0083
216720858 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.5 | 32200 | 2.6833
216720859 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.6 | 40200 | 3.35
216720860 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.4 | 24100 | 2.0083
216720861 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.4 | 32200 | 2.6833
216720862 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.4 | 40200 | 3.35
216720863 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.4 | 24100 | 2.0083
216720864 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.4 | 32200 | 2.6833
216720865 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.6 | 40200 | 3.35
216720866 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 4.3 | 28100 | 2.3417
216720867 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 3.9 | 28100 | 2.3417
216720868 |  | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 3.9 | 28100 | 2.3417
204088579 |  | BRAND | HRCU-DGX-CB | Direct Expansion Refrigerant | FULL-LOAD | ABC | [15 empty] | R-407C | 18000 | 16.5 | 3.6 | 18000 | 1.5
216714642 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036*S4**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
216714643 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036*S4**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
216714644 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)042*S0**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
202211049 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*0*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
202211050 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*0*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
202211051 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
202211052 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
202211053 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
202211054 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
202211055 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
202211056 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
202211057 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
202211058 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
202211059 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
215224856 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**N******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224857 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**N******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224858 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**C******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224859 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**C******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224860 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**C******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224861 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**C******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224862 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**C******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224863 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**C******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224864 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**N******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224865 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**N******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224866 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**N******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224867 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**N******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224868 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**N******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224869 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR42V/H**N******1 | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224870 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**C******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224871 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**C******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224872 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**C******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224873 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**C******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224874 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**C******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224875 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**C******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224876 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**N******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224877 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**N******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224878 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**N******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224879 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**N******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224880 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**N******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224881 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR48V/H**N******1 | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
217351675 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP048-1CSC-*****A | BIVA-48RCB-M20X | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
217351676 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP048-1CSN-*****A | BIVA-48RCB-M20X | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
217351677 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP060-1CSC-*****A | BIVA-60RCB-M20X | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
217351678 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP060-1CSN-*****A | BIVA-60RCB-M20X | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
217351679 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP024-1CSC-*****A | BMAC2430BBTA | [5 empty] | 27400 | 23.2 | 5 | 23800 | 2.2833 | 25400 | 18.1 | 4.1 | 18800 | 2.1167
217351680 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP024-1CSN-*****A | BMAC2430BBTA | [5 empty] | 27600 | 24.3 | 5.1 | 23800 | 2.3 | 26000 | 18.3 | 4.3 | 18800 | 2.1667
217351681 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP036-1CSC-*****A | BMAC3036BBTA | [5 empty] | 39600 | 21.5 | 4.8 | 37800 | 3.3 | 37000 | 16.4 | 4.1 | 29800 | 3.0833
217351682 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP036-1CSN-*****A | BMAC3036BBTA | [5 empty] | 40200 | 22.2 | 5 | 38800 | 3.35 | 38200 | 17.2 | 4.2 | 30800 | 3.1833
217351683 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP048-1CSC-*****A | BMAC4248CBTA | [5 empty] | 52000 | 21.6 | 4.5 | 45400 | 4.3333 | 50200 | 17.5 | 3.9 | 37200 | 4.1833
217351684 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP048-1CSN-*****A | BMAC4248CBTA | [5 empty] | 53400 | 22.5 | 4.7 | 46600 | 4.45 | 51600 | 17.8 | 4.1 | 38200 | 4.3
217351685 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP060-1CSC-*****A | BMAC4860CBTA | [5 empty] | 63400 | 20.5 | 4.4 | 58600 | 5.2833 | 60200 | 16.9 | 3.8 | 47600 | 5.0167
217351686 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP060-1CSN-*****A | BMAC4860CBTA | [5 empty] | 63200 | 21.1 | 4.5 | 59400 | 5.2667 | 60000 | 16.8 | 4 | 49800 | 5
217351687 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351688 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351689 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW049-1***-*****C | [6 empty] | 44000 | 21.5 | 4.25 | 50000 | 3.6667 | 42500 | 16.9 | 3.46 | 39500 | 3.5417
217351690 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW061-1***-*****C | [6 empty] | 55000 | 20.7 | 3.96 | 59500 | 4.5833 | 51500 | 15.9 | 3.16 | 47500 | 4.2917
217351692 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSC-*****A | BIVA-24RCB-M20X | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
217351693 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSN-*****A | BIVA-24RCB-M20X | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
217351694 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP036-1CSC-*****A | BIVA-36RCB-M20X | [5 empty] | 40200 | 23.4 | 4.7 | 36400 | 3.35 | 38200 | 17.6 | 4 | 29200 | 3.1833
217351695 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP036-1CSN-*****A | BIVA-36RCB-M20X | [5 empty] | 41400 | 24.1 | 4.8 | 37000 | 3.45 | 39200 | 18.6 | 4.1 | 29800 | 3.2667
217351696 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP048-1CSC-*****A | BIVA-48RCB-M20X | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
217351697 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP048-1CSN-*****A | BIVA-48RCB-M20X | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
217351698 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP060-1CSC-*****A | BIVA-60RCB-M20X | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
217351699 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP060-1CSN-*****A | BIVA-60RCB-M20X | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
217351700 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | CP024-1CSC-*****A | BMAC2430BBTA | [5 empty] | 27400 | 23.2 | 5 | 23800 | 2.2833 | 25400 | 18.1 | 4.1 | 18800 | 2.1167
217351701 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | CP024-1CSN-*****A | BMAC2430BBTA | [5 empty] | 27600 | 24.3 | 5.1 | 23800 | 2.3 | 26000 | 18.3 | 4.3 | 18800 | 2.1667
217351702 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | CP036-1CSC-*****A | BMAC3036BBTA | [5 empty] | 39600 | 21.5 | 4.8 | 37800 | 3.3 | 37000 | 16.4 | 4.1 | 29800 | 3.0833
217351703 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | CP036-1CSN-*****A | BMAC3036BBTA | [5 empty] | 40200 | 22.2 | 5 | 38800 | 3.35 | 38200 | 17.2 | 4.2 | 30800 | 3.1833
217351704 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | CP048-1CSC-*****A | BMAC4248CBTA | [5 empty] | 52000 | 21.6 | 4.5 | 45400 | 4.3333 | 50200 | 17.5 | 3.9 | 37200 | 4.1833
217351705 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | CP048-1CSN-*****A | BMAC4248CBTA | [5 empty] | 53400 | 22.5 | 4.7 | 46600 | 4.45 | 51600 | 17.8 | 4.1 | 38200 | 4.3
217351706 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | CP060-1CSC-*****A | BMAC4860CBTA | [5 empty] | 63400 | 20.5 | 4.4 | 58600 | 5.2833 | 60200 | 16.9 | 3.8 | 47600 | 5.0167
217351707 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | CP060-1CSN-*****A | BMAC4860CBTA | [5 empty] | 63200 | 21.1 | 4.5 | 59400 | 5.2667 | 60000 | 16.8 | 4 | 49800 | 5
217351708 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351709 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT025-2***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351710 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351711 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT035-2***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351713 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT061-1***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216621350 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D3**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621351 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D0**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621352 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D3**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621353 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D0**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621354 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D3**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
202084059 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024*2 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
202084060 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
202084061 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024*2 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
202084062 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT024 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
202084063 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT024*2 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
202123164 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | NVT-038-* | [6 empty] | 41100 | 18.5 | 4 | 38300 | 3.425 | 38200 | 14.2 | 3.5 | 31200 | 3.1833
202126393 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | NVT-050-* | [6 empty] | 53900 | 18.5 | 4 | 50300 | 4.4917 | 50100 | 14.2 | 3.5 | 41000 | 4.175
202130947 |  | NORTHERN HEAT PUMP | WBWHP | Water-to-Water and Brine-to-Water | NWA-024-* | [6 empty] | 27000 | 21.1 | 3.6 | 24800 | 2.25 | 23000 | 16.2 | 3.1 | 21500 | 1.9167
202130948 |  | NORTHERN HEAT PUMP | WBWHP | Water-to-Water and Brine-to-Water | NWA-036-* | [6 empty] | 40100 | 20.7 | 3.7 | 43900 | 3.3417 | 36600 | 16.1 | 3.1 | 32300 | 3.05
202130988 |  | NORTHERN HEAT PUMP | WBWHP | Water-to-Water and Brine-to-Water | NWA-050-* | [6 empty] | 55100 | 20.1 | 3.6 | 60100 | 4.5917 | 54200 | 16.1 | 3.1 | 45200 | 4.5167
3628363 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH048**0*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
3628364 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH048**3*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
3628365 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH048**4*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
3628367 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH042**0*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
3628368 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH042**3*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
3628369 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH042**4*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
3628403 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH030**0*1 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
3628404 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH030**2*1 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
3628405 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH030**3*1 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
3628406 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH030**4*1 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
3628407 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USH023**0*1 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
3628408 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH036**3*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
3628409 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH036**0*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
3628410 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH036**4*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
3628411 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USH023**3*1 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
3628412 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USH023**2*1 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
3628413 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USH023**4*1 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
217602171 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**4*(A-H)** | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
217602172 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**4*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
217602173 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**5*(A-H)** | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
217602174 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**5*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
7137594 |  | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GS060**1**1 | FE/V****006*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
7137595 |  | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GS048**1**1 | FE/V****005*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
7137597 |  | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GS024**1**1 | FE/V****003*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
7167375 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB024H/V******1*X1 | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
7167376 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB024H/V******1**1 | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
7167377 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB030H/V******1*X1 | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
7167378 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB030H/V******1**1 | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
7167538 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V024***3/CA |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7167539 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V024***5/EA |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7167540 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V024***4/DA |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7167541 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V024***6/FA |  | 25500 | 17.4 | 5.6 | 29200 | 2.125 | 29000 | 26.5 | 4.9 | 23500 | 2.4167 | 26600 | 19.9 | 3.78 | 18000 | 2.2167
7167542 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V036***3/CA |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7167543 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V036***5/EA |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7167544 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V036***4/DA |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7167545 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V036***6/FA |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7167546 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V048***3/CA | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7167547 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V048***5/EA | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7167548 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PTD/H/V048***6/FA | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7170602 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS018 | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
7170603 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS018 | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
7170604 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS018 | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
217752680 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH030K1*B*T |  | 29500 | 18.91 | 5.88 | 34500 | 2.4583
217752682 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH030K1*B*C |  | 29500 | 18.91 | 5.88 | 34500 | 2.4583
217752684 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036K1*B*T |  | 39000 | 18.59 | 5.06 | 44600 | 3.25
217752686 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036K1*B*C |  | 39000 | 18.59 | 5.06 | 44600 | 3.25
217752688 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042K1*B*T |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
7499552 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM036-2VT/CF/HZ*-*****A |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7499553 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM036-3VT/CF/HZ*-*****A |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7499554 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM036-4VT/CF/HZ*-*****A |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7499556 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM048-1VT/CF/HZ*-*****A | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7499559 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM048-3VT/CF/HZ*-*****A | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7499560 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | LM048-4VT/CF/HZ*-*****A | [6 empty] | 55300 | 23.8 | 4.55 | 46300 | 4.6083 | 51300 | 18 | 3.9 | 36900 | 4.275
7499702 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM036-1CF/HZ/VT |  | 38100 | 17.45 | 5.1 | 42800 | 3.175 | 43300 | 26 | 4.55 | 35900 | 3.6083 | 39900 | 20.2 | 3.95 | 28400 | 3.325
7519546 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS018*A | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
7519547 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS018*A | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
7519548 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS018*A | [6 empty] | 23200 | 27.5 | 5 | 20100 | 1.9333 | 21400 | 20 | 3.9 | 16300 | 1.7833
7519549 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*A | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519550 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*A | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519551 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*A | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519552 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*2 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519553 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*2 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519554 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*2 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519555 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*3 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519556 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*3 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519557 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*3 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519558 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*4 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519559 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*4 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519560 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*4 | [6 empty] | 28100 | 26 | 4.9 | 24200 | 2.3417 | 26000 | 19.7 | 4 | 19400 | 2.1667
7519561 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*A | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519562 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*A | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519563 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*A | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519564 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*2 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519565 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*2 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519566 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*2 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519567 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*3 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519568 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*3 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519569 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*3 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519570 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*4 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519571 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*4 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519572 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*4 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519573 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*A | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519574 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*A | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519575 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*A | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519576 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519577 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519578 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519579 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519580 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519581 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519582 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519583 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519584 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519727 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519748 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519756 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
203372406 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB024H/V******1**1 | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
203372407 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB024H/V******1**1 | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
203372408 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB024H/V******1**1 | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
203380957 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP018-1VT*******B | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
203380958 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP018-2VT*******B | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
203380959 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP018-1HZ*******B | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
203380960 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP018-2HZ*******B | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
203380963 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP042-1VT*******B | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
203380964 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP042-3VT*******B | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
203380965 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP042-4VT*******B | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
203380966 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP042-1HZ*******B |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203380967 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP042-3HZ*******B |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203380968 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP042-4HZ*******B |  | 38400 | 17.15 | 5.8 | 42000 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203380969 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP048-1VT*******B | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
203380970 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP048-3VT*******B | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
218353572 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DA042-1HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218353576 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DA042-1VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218353580 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DA042-3HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218353584 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DA042-3VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218353588 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DA042-4HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218353592 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DA042-4VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
202330438 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-003-2-0-BCAY-V0-10-000-A | [6 empty] | 42600 | 23.1 | 4.3 | 37100 | 3.55
202330439 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-003-3-0-BCAY-V0-10-000-A | [6 empty] | 42600 | 23.1 | 4.3 | 37100 | 3.55
202330440 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-003-4-0-BCAY-V0-10-000-A | [6 empty] | 42600 | 23.1 | 4.3 | 37100 | 3.55
202330444 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-1-0-BCAY-V0-10-000-A | [6 empty] | 54000 | 23.5 | 4.6 | 45400 | 4.5
202330445 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-1-0-DCAY-S0-10-000-A | [6 empty] | 53000 | 21.8 | 4.6 | 44700 | 4.4167
202330446 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-2-0-BCAY-V0-10-000-A | [6 empty] | 54000 | 23.5 | 4.6 | 45400 | 4.5
202330447 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-3-0-BCAY-V0-10-000-A | [6 empty] | 54000 | 23.5 | 4.6 | 45400 | 4.5
202330448 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-4-0-BCAY-V0-10-000-A | [6 empty] | 54000 | 23.5 | 4.6 | 45400 | 4.5
202330449 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-2-0-DCAY-S0-10-000-A | [6 empty] | 53000 | 21.8 | 4.6 | 44700 | 4.4167
202330450 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-3-0-DCAY-S0-10-000-A | [6 empty] | 53000 | 21.8 | 4.6 | 44700 | 4.4167
202330451 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-004-4-0-DCAY-S0-10-000-A | [6 empty] | 53000 | 21.8 | 4.6 | 44700 | 4.4167
215837877 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048F3*C/S*T |  | 48300 | 17.5 | 5 | 57000 | 4.025
215837879 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048K3*C/S*T |  | 48300 | 17.5 | 5 | 57000 | 4.025
215837880 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048L3*C/S*T |  | 48300 | 17.5 | 5 | 57000 | 4.025
215837886 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048F3*C/S*C |  | 48300 | 17.5 | 5 | 57000 | 4.025
215837887 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048K3*C/S*C |  | 48300 | 17.5 | 5 | 57000 | 4.025
215837889 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048L3*C/S*C |  | 48300 | 17.5 | 5 | 57000 | 4.025
215837895 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH060F3*C/S*T |  | 60872 | 17.22 | 5.66 | 78027 | 5.0727
215837896 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH060K3*C/S*T |  | 60872 | 17.22 | 5.66 | 78027 | 5.0727
215837904 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH060F3*C/S*C |  | 60872 | 17.22 | 5.66 | 78027 | 5.0727
215837905 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH060K3*C/S*C |  | 60872 | 17.22 | 5.66 | 78027 | 5.0727
218158071 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)006*R0**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
218158074 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)015*R0**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
218158076 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S0**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
218158078 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S0**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
218158079 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)042*S0**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
218158083 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)006*R2**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
218158086 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)015*R0**4 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
218158087 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)015*R2**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
218158088 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)015*R2**4 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
218158092 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S0**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
218158093 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S2**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
218158094 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S2**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
218158095 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S3**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
218158096 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S3**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
218158097 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S4**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
218158098 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024*S4**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
218158106 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S0**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
218158107 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S2**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
218158108 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S2**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
218158109 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S3**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
218158110 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S3**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
218158111 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S4**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
218158112 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036*S4**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
218158113 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)042*S0**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
218158114 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)042*S3**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
218158115 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)042*S3**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
218158116 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)042*S4**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
218158117 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)042*S4**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
10259059 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS017*A***1B |  | 17300 | 17.4 | 5.6 | 20400 | 1.4417 | [5 empty] | 18100 | 20.5 | 3.8 | 13000 | 1.5083
218353673 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ036-4VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218353674 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ036-4VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218353675 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ048-1VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
218353676 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ048-1VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218353677 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ048-3VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
218353678 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ048-3VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218353679 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ048-4VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
218353680 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ048-4VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218353681 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ060-1VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218353682 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ060-1VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
218353683 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ060-3VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218353684 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ060-3VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
218353685 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ060-4VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218471838 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ024-4HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218471839 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ024-1HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218471840 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ024-3HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218471841 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ024-4HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218471842 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ036-1VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218471843 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ036-3VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218471844 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ036-4VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218471845 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ036-1VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218471846 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ036-3VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218471847 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ036-4VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218471848 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ048-1VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
218471849 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ048-3VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
218471850 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ048-4VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
218471851 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ048-1VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218471852 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ048-3VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218471853 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ048-4VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218471854 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ060-1VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218471855 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ060-3VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218471856 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ060-4VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218471857 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ060-1VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
218471858 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ060-3VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
218471859 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ060-4VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
218471872 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH025-4***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218471873 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH035-4***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218471875 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH061-4***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
218471877 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | QW025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218471878 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | QW035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218471879 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | QW049-1***-*****C | [6 empty] | 44000 | 21.5 | 4.25 | 50000 | 3.6667 | 42500 | 16.9 | 3.46 | 39500 | 3.5417
218471880 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | QW061-1***-*****C | [6 empty] | 55000 | 20.7 | 3.96 | 59500 | 4.5833 | 51500 | 15.9 | 3.16 | 47500 | 4.2917
218471881 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH025-3***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218471882 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH035-3***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218471884 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH061-3***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
218471891 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | QZ024-1CSC-*****A | CDM24B5XXS1A | [5 empty] | 27400 | 23.2 | 5 | 23800 | 2.2833 | 25400 | 18.1 | 4.1 | 18800 | 2.1167
218471892 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | QZ024-1CSN-*****A | CDM24B5XXS1A | [5 empty] | 27600 | 24.3 | 5.1 | 23800 | 2.3 | 26000 | 18.3 | 4.3 | 18800 | 2.1667
218471893 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | QZ036-1CSC-*****A | CDM30B5XXS1A | [5 empty] | 39600 | 21.5 | 4.8 | 37800 | 3.3 | 37000 | 16.4 | 4.1 | 29800 | 3.0833
217351843 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 40500 | 22.3 | 4.7 | 34200 | 3.375 | 38000 | 18.1 | 3.7 | 26800 | 3.1667
217351844 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 52000 | 21.5 | 4.6 | 46500 | 4.3333 | 48500 | 17.1 | 4 | 37800 | 4.0417
217351845 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 51000 | 21 | 4.5 | 45500 | 4.25 | 47500 | 16.7 | 3.9 | 37000 | 3.9583
217351846 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*C******1 | F(C,T)MA5*60**** | [5 empty] | 63500 | 21.7 | 4.4 | 60000 | 5.2917 | 60500 | 17.6 | 3.7 | 47000 | 5.0417
7411231 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**0*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
7411301 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**2*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
7411380 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**2*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
7411778 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**2*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
7411875 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**3*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
7411949 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**3*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
7412057 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**3*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
7412158 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**4*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
7412253 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**4*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
7412381 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**4*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
7412626 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH026**0*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7412712 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH026**0*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7412777 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH026**2*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7412856 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH026**2*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7412926 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH026**3*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7413034 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH026**3*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7413487 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH026**4*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7414142 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**0*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
7414232 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**0*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
7414335 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**0*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
203325124 |  | TEMPSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X3600BL | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
203325125 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X3600BL | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
203325126 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X3600BL | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
203337768 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | CE025-1VT/HZ/CF*-*****B | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337769 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CE025-1VT/HZ/CF*-*****B | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337770 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GP024V/H/C******1**1 | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337771 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GP024V/H/C******1**1 | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337772 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HP024V/H/C******1**1 | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337773 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HP024V/H/C******1**1 | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337774 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HP024V/H/C******1**1 | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337775 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HP024V/H/C******1**1 | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337776 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HP024V/H/C******1**1 | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203337777 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HP024V/H/C******1**1 | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
203343530 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | CE049-1VT/HZ/CF*-*****B | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343532 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM024-1CS*******A | SM024-1AV/AH*-*****A | [5 empty] | 28500 | 22.2 | 4.5 | 22200 | 2.375 | 26200 | 17 | 3.75 | 17700 | 2.1833
203343533 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CE049-1VT/HZ/CF*-*****B | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343535 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM024-1CS*******A | SM024-1AV/AH*-*****A | [5 empty] | 28500 | 22.2 | 4.5 | 22200 | 2.375 | 26200 | 17 | 3.75 | 17700 | 2.1833
203343536 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GP048V/H/C******1**1 | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343537 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GP048V/H/C******1**1 | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343538 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HP048V/H/C******1**1 | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343539 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HP048V/H/C******1**1 | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343540 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HP048V/H/C******1**1 | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343541 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HP048V/H/C******1**1 | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343542 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HP048V/H/C******1**1 | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203343543 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HP048V/H/C******1**1 | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
203344888 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH009**0*6 | [6 empty] | 10300 | 22 | 4.1 | 9600 | 0.85833
203344891 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH009**9*6 | [6 empty] | 10300 | 22 | 4.1 | 9600 | 0.85833
4651405 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH030**3*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651407 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH030**4*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651417 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH036**0*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651418 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH036**2*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651419 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH036**3*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651420 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH036**4*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651530 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH042**0*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651532 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH042**3*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651533 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH042**4*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651546 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH048**0*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
4651547 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH048**3*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
4651548 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH048**4*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
4651610 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS023**0*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651611 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS023**0*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651614 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS024**0*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651615 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS024**0*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651618 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS024**2*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651619 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS024**2*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651622 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS024**3*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651623 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS024**3*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651626 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS024**4*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651627 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS024**4*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651630 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS030**0*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651631 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS030**0*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651634 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS030**2*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651635 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS030**2*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651639 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS030**3*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651640 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS030**3*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651644 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS030**4*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651645 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS030**4*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651657 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS036**0*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651658 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS036**0*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651665 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS036**2*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651666 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS036**2*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651726 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS036**3*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651727 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS036**3*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651732 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS036**4*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651733 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS036**4*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
4651865 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS023**2*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651866 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS023**2*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651869 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS023**3*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
216801936 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW035***3/CB | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801937 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW035***4/DB | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801938 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW035***5/EB | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801939 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW035***6/FB | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801943 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW061***3/CB | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801944 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW061***5/EB | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801945 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW061***6/FB | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
216801983 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**3*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801984 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**3*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801985 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**3*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801986 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**3*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801987 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**4*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801988 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**4*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801989 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**4*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801990 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**4*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801991 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**5*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801992 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**5*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801993 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**5*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801994 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**5*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801995 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**6*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801996 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(G-K;N-R)**6*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801997 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**6*(A-H)** |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216801998 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*024(L/M/S/T)**6*(J-R)** |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216801999 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*036***3*(A-H)** | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216802000 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*036***3*(J-R)** | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216802001 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*036***4*(A-H)** | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216802002 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*036***4*(J-R)** | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216802003 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*036***5*(A-H)** | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216802004 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*036***5*(J-R)** | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216802005 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*036***6*(A-H)** | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216802006 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*036***6*(J-R)** | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216802007 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*048***3*(A-H)** | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216802008 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*048***3*(J-R)** | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216802009 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*048***5*(A-H)** | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216802010 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*048***5*(J-R)** | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216802011 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*048***6*(A-H)** | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216802012 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*048***6*(J-R)** | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216802013 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***3*(A-H)** |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216802014 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***3*(J-R)** |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216802015 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***5*(A-H)** |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216802016 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***5*(J-R)** |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216802017 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***6*(A-H)** |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216802018 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***6*(J-R)** |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
218471894 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | QZ036-1CSN-*****A | CDM30B5XXS1A | [5 empty] | 40200 | 22.2 | 5 | 38800 | 3.35 | 38200 | 17.2 | 4.2 | 30800 | 3.1833
218471895 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | QZ048-1CSC-*****A | CDM48C5XXS1A | [5 empty] | 52000 | 21.6 | 4.5 | 45400 | 4.3333 | 50200 | 17.5 | 3.9 | 37200 | 4.1833
218471896 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | QZ048-1CSN-*****A | CDM48C5XXS1A | [5 empty] | 53400 | 22.5 | 4.7 | 46600 | 4.45 | 51600 | 17.8 | 4.1 | 38200 | 4.3
218471897 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | QZ060-1CSC-*****A | CDM60C5XXS1A | [5 empty] | 63400 | 20.5 | 4.4 | 58600 | 5.2833 | 60200 | 16.9 | 3.8 | 47600 | 5.0167
218471898 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | QZ060-1CSN-*****A | CDM60C5XXS1A | [5 empty] | 63200 | 21.1 | 4.5 | 59400 | 5.2667 | 60000 | 16.8 | 4 | 49800 | 5
218471899 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | AZ024-1CSC-*****A | JDE24E5XX2DS1 | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
218471900 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | AZ024-1CSN-*****A | JDE24E5XX2DS1 | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
218471901 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | QZ024-1CSC-*****A | JDE24E5XX2DS1 | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
218471902 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | QZ024-1CSN-*****A | JDE24E5XX2DS1 | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
218471903 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | AZ036-1CSC-*****A | JDE36E5XX2DS1 | [5 empty] | 40200 | 23.4 | 4.7 | 36400 | 3.35 | 38200 | 17.6 | 4 | 29200 | 3.1833
218471904 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | AZ036-1CSN-*****A | JDE36E5XX2DS1 | [5 empty] | 41400 | 24.1 | 4.8 | 37000 | 3.45 | 39200 | 18.6 | 4.1 | 29800 | 3.2667
218471905 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | QZ036-1CSC-*****A | JDE36E5XX2DS1 | [5 empty] | 40200 | 23.4 | 4.7 | 36400 | 3.35 | 38200 | 17.6 | 4 | 29200 | 3.1833
218471906 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | QZ036-1CSN-*****A | JDE36E5XX2DS1 | [5 empty] | 41400 | 24.1 | 4.8 | 37000 | 3.45 | 39200 | 18.6 | 4.1 | 29800 | 3.2667
218471907 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | AZ048-1CSC-*****A | JDE48F5XX2DS1 | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
218471908 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | AZ048-1CSN-*****A | JDE48F5XX2DS1 | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
218471909 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | QZ048-1CSC-*****A | JDE48F5XX2DS1 | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
218471910 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | QZ048-1CSN-*****A | JDE48F5XX2DS1 | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
5646384 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT036D2 | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646385 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT036D2 | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646386 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT036D2 | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646387 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT036D3 | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646388 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT036D3 | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646389 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT036D3 | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646391 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT048D | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646392 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT048D | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646393 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT048D | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646394 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT048D2 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646395 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT048D2 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646396 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT048D2 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646397 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT048D3 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646398 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT048D3 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646399 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT048D3 | [6 empty] | 53100 | 22.1 | 4.6 | 47400 | 4.425 | 49000 | 17.1 | 3.9 | 38200 | 4.0833
5646765 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT048D | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646766 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT048D | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646767 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT048D | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
215400080 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV015E1*C/S*T |  | 15500 | 17.51 | 5.09 | 17000 | 1.2917
215400082 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV015E1*C/S*C |  | 15500 | 17.51 | 5.09 | 17000 | 1.2917
215400094 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024E1*C/S*T |  | 24700 | 18.03 | 5.25 | 28600 | 2.0583
215400095 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024F3*C/S*T |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215400098 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024E1*C/S*C |  | 24700 | 18.03 | 5.25 | 28600 | 2.0583
215400099 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024F3*C/S*C |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215400114 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV036E1*C/S*P |  | 37300 | 17.25 | 5.02 | 43000 | 3.1083
215400118 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV036E1*C/S*T |  | 37200 | 17.68 | 5.17 | 43100 | 3.1
215400122 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV036E1*C/S*C |  | 37200 | 17.68 | 5.17 | 43100 | 3.1
217754425 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F1*B*T |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
218471654 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AA042-3HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218471655 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QA042-3HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218471656 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AA042-3VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218471657 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QA042-3VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218471658 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AA042-4HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218471659 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QA042-4HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218471660 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AA042-4VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218471661 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QA042-4VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839496 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WC*042(G-K;N-R)**3*(A-H)** | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839497 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WC*042(L/M/S/T)**3*(A-H)** | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839498 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WC*042(G-K;N-R)**5*(A-H)** | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839499 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WC*042(L/M/S/T)**5*(A-H)** | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839500 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WC*042(G-K;N-R)**6*(A-H)** | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839501 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WC*042(L/M/S/T)**6*(A-H)** | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
202146892 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT042*3 | [6 empty] | 46000 | 23.4 | 4.3 | 40100 | 3.8333 | 43000 | 18 | 3.6 | 32900 | 3.5833
202146893 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT048 | [6 empty] | 52200 | 22.1 | 4.4 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146894 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT048*2 | [6 empty] | 52200 | 22.1 | 4.3 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146895 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT048*3 | [6 empty] | 52200 | 22.1 | 4.3 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146896 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT048*A | [6 empty] | 52200 | 22.1 | 4.3 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146897 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT048 | [6 empty] | 52200 | 22.1 | 4.4 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146898 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT048*2 | [6 empty] | 52200 | 22.1 | 4.3 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146899 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT048*3 | [6 empty] | 52200 | 22.1 | 4.3 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146900 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT048*A | [6 empty] | 52200 | 22.1 | 4.3 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146901 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT048 | [6 empty] | 52200 | 22.1 | 4.4 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146902 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT048*2 | [6 empty] | 52200 | 22.1 | 4.3 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146903 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT048*3 | [6 empty] | 52200 | 22.1 | 4.3 | 45900 | 4.35 | 48700 | 17.3 | 3.6 | 36900 | 4.0583
202146904 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT060 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146905 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT060*2 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146906 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT060*3 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146907 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT060 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146908 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT060*2 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146909 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT060*3 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146910 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT060 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146911 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT060*2 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146912 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT060*3 | [6 empty] | 62000 | 21.2 | 4.2 | 58500 | 5.1667 | 59000 | 16.9 | 3.6 | 46800 | 4.9167
202146913 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS015 | [6 empty] | 16100 | 24.4 | 4.7 | 14300 | 1.3417 | 14500 | 17.1 | 3.9 | 11300 | 1.2083
218353078 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ048-4VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218353079 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ060-3VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218353080 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ060-3VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
218353081 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ060-4VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218353082 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ060-4VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
218353144 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD007-1VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218353145 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD007-1VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218353146 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD007-2VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218353147 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD007-2VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218353148 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD009-1VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218353149 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD009-1VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218353150 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD009-2VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218353151 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD009-2VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218353152 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD012-1VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
216739881 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036E1*C/S*C |  | 35600 | 16.5 | 4.9 | 39100 | 2.9667
216739882 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036F3*C/S*C |  | 35600 | 16.2 | 4.8 | 39100 | 2.9667
216739883 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036J1*C/S*C |  | 35600 | 16.2 | 4.8 | 39100 | 2.9667
216739884 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036K3*C/S*C |  | 35600 | 16 | 4.8 | 39100 | 2.9667
216739895 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048E1*C/S*C |  | 49200 | 16.9 | 5 | 58000 | 4.1
216739896 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048F3*C/S*C |  | 49200 | 16.5 | 4.9 | 58000 | 4.1
216739897 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048K3*C/S*C |  | 49200 | 16.5 | 4.9 | 58000 | 4.1
216739910 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024E1*C/S*C |  | 24400 | 16.9 | 5.1 | 29500 | 2.0333
216739911 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024F3*C/S*C |  | 24400 | 16.6 | 5 | 29500 | 2.0333
216739912 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024J1*C/S*C |  | 24400 | 16.6 | 5 | 29500 | 2.0333
216739913 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024K3*C/S*C |  | 24400 | 16.4 | 5 | 29500 | 2.0333
216739926 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH036E1*C/S*C |  | 35200 | 17.4 | 5.3 | 42500 | 2.9333
216739927 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH036F3*C/S*C |  | 35200 | 17.1 | 5.2 | 42500 | 2.9333
216739928 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH036J1*C/S*C |  | 35200 | 17.1 | 5.2 | 42500 | 2.9333
216739929 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH036K3*C/S*C |  | 35200 | 16.9 | 5.1 | 42500 | 2.9333
216739934 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH042E1*C/S*C |  | 42000 | 16.8 | 5 | 50200 | 3.5
218396736 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218396737 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH025-2***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218396738 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218396739 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH035-2***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217893588 |  | Engineered Comfort | WBAHP-O | Water-to-Air and Brine-to-Air | 44VHB/VCB-19 | [6 empty] | 21000 | 21.1 | 4.1 | 18500 | 1.75
217897411 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
217897412 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
217897413 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
217897414 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
217897417 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
217897418 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
217897421 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
217897422 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
217897425 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
217897426 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
217897427 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
217897428 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
217897429 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
217897430 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
207200530 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS018*1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
207200531 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS025*1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
207200532 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS040*1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
207200533 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS050*1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
207200534 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS060*1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
207200558 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GT064**1*(1,4)*J |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207200576 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ026*1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207200577 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTZ026*1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207200578 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS026*1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207200579 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS026*1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207200580 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS049*1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207200581 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS049*1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207200582 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS064*1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207200583 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS064*1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207200586 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GSZ022*1 | SAH022* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207200587 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GSZ022*1 | SRAA026* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207200588 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GSZ030*1 | SAH030* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207200589 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GSZ030*1 | SRAA026* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207200590 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GSZ048*1 | SAH048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
207200591 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GSZ048*1 | SRAA048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
207200592 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GSZ060*1 | SAH060* | [5 empty] | 61700 | 23.6 | 4.3 | 54500 | 5.1417 | 56300 | 17.7 | 3.7 | 44000 | 4.6917
207200593 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GSZ060*1 | SRAA060* | [5 empty] | 61700 | 23.6 | 4.3 | 54500 | 5.1417 | 56300 | 17.7 | 3.7 | 44000 | 4.6917
207200598 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GSZ036*1*J | SAH036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207200599 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GSZ042*1*J | SAH042* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207200600 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ038*1*J | SAH038* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207200601 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ049*1*J | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
217967019 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK024A |  | 25100 | 20.4 | 6.6 | 30500 | 2.0917 | 28300 | 38.8 | 5.6 | 24900 | 2.3583 | 26300 | 24.7 | 4.6 | 18800 | 2.1917
217967020 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK033A |  | 32200 | 15.6 | 5.9 | 43600 | 2.6833 | 35500 | 25.2 | 5.1 | 35600 | 2.9583 | 33300 | 18.1 | 4.1 | 27700 | 2.775
217967021 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK033A |  | 33300 | 17 | 6.1 | 39900 | 2.775 | 37500 | 28.8 | 5.3 | 32900 | 3.125 | 35300 | 20.3 | 4.3 | 25500 | 2.9417
217967022 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK042A |  | 40300 | 17.9 | 6.4 | 50400 | 3.3583 | 45000 | 30.2 | 5.5 | 41200 | 3.75 | 42200 | 21.3 | 4.4 | 32500 | 3.5167
217967023 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK042A |  | 42900 | 18.8 | 6.3 | 54100 | 3.575 | 46600 | 32.1 | 5.4 | 43400 | 3.8833 | 44900 | 22.7 | 4.4 | 34400 | 3.7417
217967024 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK050A |  | 49400 | 16 | 6 | 68200 | 4.1167 | 55900 | 25.5 | 5.2 | 54500 | 4.6583 | 52100 | 18.5 | 4.2 | 41300 | 4.3417
217967025 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK050A |  | 50300 | 17.4 | 5.8 | 63000 | 4.1917 | 52200 | 25.9 | 5.1 | 51500 | 4.35 | 50400 | 19.3 | 4.3 | 40400 | 4.2
217967026 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK060A |  | 58500 | 14.9 | 5.5 | 84000 | 4.875 | 63800 | 21.6 | 4.8 | 67400 | 5.3167 | 61900 | 17 | 3.9 | 51400 | 5.1583
217967027 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK060A |  | 59000 | 15.7 | 5.6 | 78800 | 4.9167 | 62300 | 22.7 | 5 | 63700 | 5.1917 | 61200 | 17.9 | 4.1 | 49500 | 5.1
217967028 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK024B |  | 24500 | 18.9 | 6.7 | 32000 | 2.0417 | 26900 | 32.5 | 5.6 | 25700 | 2.2417 | 25400 | 22.4 | 4.4 | 19200 | 2.1167
217967029 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK024B |  | 25100 | 20.4 | 6.6 | 30500 | 2.0917 | 28300 | 38.8 | 5.6 | 24900 | 2.3583 | 26300 | 24.7 | 4.6 | 18800 | 2.1917
217967030 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK033B |  | 32200 | 15.6 | 5.9 | 43600 | 2.6833 | 35500 | 25.2 | 5.1 | 35600 | 2.9583 | 33300 | 18.1 | 4.1 | 27700 | 2.775
217967031 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK033B |  | 33300 | 17 | 6.1 | 39900 | 2.775 | 37500 | 28.8 | 5.3 | 32900 | 3.125 | 35300 | 20.3 | 4.3 | 25500 | 2.9417
217967032 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK042B |  | 40300 | 17.9 | 6.4 | 50400 | 3.3583 | 45000 | 30.2 | 5.5 | 41200 | 3.75 | 42200 | 21.3 | 4.4 | 32500 | 3.5167
217967033 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK042B |  | 42900 | 18.8 | 6.3 | 54100 | 3.575 | 46600 | 32.1 | 5.4 | 43400 | 3.8833 | 44900 | 22.7 | 4.4 | 34400 | 3.7417
217967034 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK050B |  | 49400 | 16 | 6 | 68200 | 4.1167 | 55900 | 25.5 | 5.2 | 54500 | 4.6583 | 52100 | 18.5 | 4.2 | 41300 | 4.3417
217967035 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK050B |  | 50300 | 17.4 | 5.8 | 63000 | 4.1917 | 52200 | 25.9 | 5.1 | 51500 | 4.35 | 50400 | 19.3 | 4.3 | 40400 | 4.2
217967036 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK060B |  | 58500 | 14.9 | 5.5 | 84000 | 4.875 | 63800 | 21.6 | 4.8 | 67400 | 5.3167 | 61900 | 17 | 3.9 | 51400 | 5.1583
217967037 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK060B |  | 59000 | 15.7 | 5.6 | 78800 | 4.9167 | 62300 | 22.7 | 5 | 63700 | 5.1917 | 61200 | 17.9 | 4.1 | 49500 | 5.1
217967038 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK0244 |  | 24500 | 18.9 | 6.7 | 32000 | 2.0417 | 26900 | 32.5 | 5.6 | 25700 | 2.2417 | 25400 | 22.4 | 4.4 | 19200 | 2.1167
217967039 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK0244 |  | 25100 | 20.4 | 6.6 | 30500 | 2.0917 | 28300 | 38.8 | 5.6 | 24900 | 2.3583 | 26300 | 24.7 | 4.6 | 18800 | 2.1917
217967040 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK0334 |  | 32200 | 15.6 | 5.9 | 43600 | 2.6833 | 35500 | 25.2 | 5.1 | 35600 | 2.9583 | 33300 | 18.1 | 4.1 | 27700 | 2.775
217967041 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK0334 |  | 33300 | 17 | 6.1 | 39900 | 2.775 | 37500 | 28.8 | 5.3 | 32900 | 3.125 | 35300 | 20.3 | 4.3 | 25500 | 2.9417
217967042 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHK0424 |  | 40300 | 17.9 | 6.4 | 50400 | 3.3583 | 45000 | 30.2 | 5.5 | 41200 | 3.75 | 42200 | 21.3 | 4.4 | 32500 | 3.5167
217967043 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVK0424 |  | 42900 | 18.8 | 6.3 | 54100 | 3.575 | 46600 | 32.1 | 5.4 | 43400 | 3.8833 | 44900 | 22.7 | 4.4 | 34400 | 3.7417
9100383 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**4*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100384 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**4*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9105364 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS006 | [6 empty] | 7800 | 25.8 | 4.6 | 7000 | 0.65 | 7200 | 18.6 | 3.7 | 5600 | 0.6
9105366 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS006 | [6 empty] | 7800 | 25.8 | 4.6 | 7000 | 0.65 | 7200 | 18.6 | 3.7 | 5600 | 0.6
9105367 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS006 | [6 empty] | 7800 | 25.8 | 4.6 | 7000 | 0.65 | 7200 | 18.6 | 3.7 | 5600 | 0.6
9105368 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS006*A | [6 empty] | 7900 | 24 | 4.5 | 7100 | 0.65833
9105369 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS006*A | [6 empty] | 7900 | 24 | 4.5 | 7100 | 0.65833
9105370 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS006*A | [6 empty] | 7900 | 24 | 4.5 | 7100 | 0.65833
9105371 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS006*9 | [6 empty] | 7900 | 24 | 4.5 | 7100 | 0.65833
9105372 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS006*9 | [6 empty] | 7900 | 24 | 4.5 | 7100 | 0.65833
9105373 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS006*9 | [6 empty] | 7900 | 24 | 4.5 | 7100 | 0.65833
9111997 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM024-1VT/CF*-*****B |  | 26200 | 16.2 | 5.6 | 30300 | 2.1833 | 29400 | 24.85 | 4.9 | 24700 | 2.45 | 26900 | 18.9 | 4.1 | 18700 | 2.2417
9111998 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM036-1VT/CF*-*****B |  | 39300 | 18.6 | 6.2 | 46300 | 3.275 | 44300 | 27.1 | 5.4 | 36700 | 3.6917 | 40200 | 21 | 4.3 | 28200 | 3.35
9113111 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM048-1VT/CF*-*****B* | [6 empty] | 56900 | 24.3 | 4.9 | 49200 | 4.7417 | 51800 | 18.6 | 4.2 | 38200 | 4.3167
9113182 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM024-1VT/CF*-*****B |  | 26200 | 16.2 | 5.6 | 30300 | 2.1833 | 29400 | 24.85 | 4.9 | 24700 | 2.45 | 26900 | 18.9 | 4.1 | 18700 | 2.2417
9113183 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM036-1VT/CF*-*****B |  | 39300 | 18.6 | 6.2 | 46300 | 3.275 | 44300 | 27.1 | 5.4 | 36700 | 3.6917 | 40200 | 21 | 4.3 | 28200 | 3.35
9113184 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM048-1VT/CF*-*****B* | [6 empty] | 56900 | 24.3 | 4.9 | 49200 | 4.7417 | 51800 | 18.6 | 4.2 | 38200 | 4.3167
204595317 |  | GEO-THERMAL SPLIT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ036*******1**2 | CAP**36**AL* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
204595318 |  | CARRIER | WBAHP-C | Water-to-Air and Brine-to-Air | GZ036*******1**2 | CAP**36**AL* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
204595319 |  | BRYANT | WBAHP-C | Water-to-Air and Brine-to-Air | GZ036*******1**2 | CAP**36**AL* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
204595320 |  | HEIL | WBAHP-C | Water-to-Air and Brine-to-Air | HS036*******1**2 | EAM4X36L**A* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
212505511 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6048AM* | [6 empty] | 53000 | 23.6 | 4.2 | 46000 | 4.4167 | 49500 | 18.1 | 3.6 | 36000 | 4.125
212505513 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6036AM* | [6 empty] | 39000 | 23.2 | 4.1 | 34000 | 3.25 | 36500 | 18 | 3.6 | 27000 | 3.0417
212505514 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6042AM* | [6 empty] | 44500 | 23.3 | 4.3 | 40000 | 3.7083 | 43000 | 18.5 | 3.8 | 31500 | 3.5833
212505515 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6048AM* | [6 empty] | 53000 | 23.6 | 4.2 | 46000 | 4.4167 | 49500 | 18.1 | 3.6 | 36000 | 4.125
212508382 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6036AN* | [6 empty] | 39000 | 23.2 | 4.1 | 34000 | 3.25 | 36500 | 18 | 3.6 | 27000 | 3.0417
212508384 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6042AN* | [6 empty] | 44500 | 23.3 | 4.3 | 40000 | 3.7083 | 43000 | 18.5 | 3.8 | 31500 | 3.5833
212508386 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSH6048AN* | [6 empty] | 53000 | 23.6 | 4.2 | 46000 | 4.4167 | 49500 | 18.1 | 3.6 | 36000 | 4.125
212508399 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6036AN* | [6 empty] | 39000 | 23.2 | 4.1 | 34000 | 3.25 | 36500 | 18 | 3.6 | 27000 | 3.0417
212508401 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6042AN* | [6 empty] | 44500 | 23.3 | 4.3 | 40000 | 3.7083 | 43000 | 18.5 | 3.8 | 31500 | 3.5833
212508403 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6048AN* | [6 empty] | 53000 | 23.6 | 4.2 | 46000 | 4.4167 | 49500 | 18.1 | 3.6 | 36000 | 4.125
215811946 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6009D* | [6 empty] | 11000 | 26 | 4.3 | 8800 | 0.91667 | 9800 | 19 | 3.7 | 6800 | 0.81667
215811947 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6009D* | [6 empty] | 11000 | 26 | 4.3 | 8800 | 0.91667 | 9800 | 19 | 3.7 | 6800 | 0.81667
215811948 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6012D* | [6 empty] | 13500 | 26 | 4.1 | 11000 | 1.125 | 12500 | 19 | 3.6 | 9000 | 1.0417
215811950 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6012D* | [6 empty] | 13500 | 26 | 4.1 | 11000 | 1.125 | 12500 | 19 | 3.6 | 9000 | 1.0417
215811951 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6018D* | [6 empty] | 20000 | 21.1 | 4.1 | 16000 | 1.6667 | 18000 | 17.2 | 3.6 | 13000 | 1.5
215811952 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6018D* | [6 empty] | 20000 | 21.1 | 4.1 | 16000 | 1.6667 | 18000 | 17.2 | 3.6 | 13000 | 1.5
215811953 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6024D* | [6 empty] | 24000 | 23 | 4.1 | 22000 | 2 | 23000 | 18 | 3.6 | 17500 | 1.9167
215811954 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6024D* | [6 empty] | 24000 | 23 | 4.1 | 22000 | 2 | 23000 | 18 | 3.6 | 17500 | 1.9167
215811955 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6030D* | [6 empty] | 30000 | 22.5 | 4.1 | 24000 | 2.5 | 28000 | 17.5 | 3.6 | 19900 | 2.3333
215811957 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6030D* | [6 empty] | 30000 | 22.5 | 4.1 | 24000 | 2.5 | 28000 | 17.5 | 3.6 | 19900 | 2.3333
215811958 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6036D* | [6 empty] | 39000 | 22 | 4.1 | 35000 | 3.25 | 37000 | 18 | 3.6 | 28000 | 3.0833
215811959 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6036D* | [6 empty] | 39000 | 22 | 4.1 | 35000 | 3.25 | 37000 | 18 | 3.6 | 28000 | 3.0833
215811960 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6042D* | [6 empty] | 44000 | 24 | 4.3 | 37000 | 3.6667 | 42000 | 18 | 3.6 | 30000 | 3.5
215811961 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6042D* | [6 empty] | 44000 | 24 | 4.3 | 37000 | 3.6667 | 42000 | 18 | 3.6 | 30000 | 3.5
215811962 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6048D* | [6 empty] | 55000 | 23 | 4.1 | 38000 | 4.5833
215811964 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6048D* | [6 empty] | 55000 | 23 | 4.1 | 38000 | 4.5833
207337509 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H022**1 | SAH022* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207337510 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H022**1 | SRAA026* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207337511 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H030**1 | SAH030* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207337512 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H030**1 | SRAA026* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207337513 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J036**1 | SAH036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207337514 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J036**1 | SRAA036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207337515 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J042**1 | SAH042* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207337516 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J042**1 | SRAA048* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207337517 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H048**1 | SAH048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
207337518 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H048**1 | SRAA048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
207338124 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | QT064**1*1* | [6 empty] | 63900 | 21 | 4.5 | 58600 | 5.325 | 58300 | 16.2 | 3.8 | 46600 | 4.8583
207338125 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | YT024*A | [6 empty] | 25100 | 20.6 | 4.4 | 23500 | 2.0917 | 23100 | 15.6 | 3.8 | 18900 | 1.925
207338127 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 141/142C036**1*(1,2) |  | 32300 | 17.7 | 5.3 | 51000 | 2.6917 | 38000 | 31.2 | 4.5 | 41700 | 3.1667 | 35800 | 21.6 | 3.5 | 32900 | 2.9833
207338128 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 141/142C048**1*1 |  | 40700 | 16.9 | 4.9 | 67000 | 3.3917 | 49000 | 30 | 4 | 55200 | 4.0833 | 45000 | 20 | 3.4 | 43500 | 3.75
207338129 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 141/142C060**1*1 |  | 50000 | 15.9 | 4.9 | 79000 | 4.1667 | 60000 | 27.1 | 4.3 | 66000 | 5 | 56000 | 19.1 | 3.4 | 51700 | 4.6667
207338249 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETE0241-5 | [6 empty] | 25100 | 22.1 | 4.2 | 22400 | 2.0917
207338250 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETE0242-5 | [6 empty] | 25100 | 22.1 | 4.2 | 22400 | 2.0917
207338251 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETE0247-5 | [6 empty] | 25100 | 22.1 | 4.2 | 22400 | 2.0917
207337481 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104J038**1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337482 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104J038**1 | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337483 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 164J038**1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337484 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 164J038**1 | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337485 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337486 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337487 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 163J049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337488 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 163J049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337489 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104H049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337490 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104H049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337491 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 164H049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337492 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 164H049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337493 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337494 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337495 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 163J064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337496 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 163J064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337497 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104H064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337498 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104H064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337499 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 164H064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337500 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 164H064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
215399877 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048L3*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215399880 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048K3*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215399881 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048L3*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215399884 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060K3*B*T |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
215399886 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060K3*B*C |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
217752690 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042K1*B*C |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
217752692 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH048K1*B*T |  | 48300 | 17.5 | 5 | 57000 | 4.025
206703391 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921331/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703392 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921340/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703393 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921341/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703394 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931130/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703395 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931131/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
214841657 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
214841658 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
214841660 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
214841662 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
214841664 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
214841665 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
214841666 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
214841675 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
214841676 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
214841677 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)018A | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
214841678 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SC(L/R/B/P/T/K/F)018A*V | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
214841679 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
214841680 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
214841682 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
214841684 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
214841686 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
214841687 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
214841688 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
218471730 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-4VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218471731 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-4VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218471732 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-4VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
218471733 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-4VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
218471734 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-4VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
218471735 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-4VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
218471736 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD042-4VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
218471737 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD042-4VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
218471738 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD048-4VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
218471739 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD048-4VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
217754501 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024E1*B*C |  | 24300 | 17.59 | 5.81 | 28000 | 2.025
217754502 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024F1*B*C |  | 24300 | 17.24 | 5.7 | 28000 | 2.025
217754505 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030E1*B*C |  | 31200 | 16.97 | 5.52 | 34700 | 2.6
217754506 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030F1*B*C |  | 31200 | 16.63 | 5.41 | 34700 | 2.6
217754509 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036E1*B*C |  | 38100 | 18.45 | 5.18 | 41100 | 3.175
217754510 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036F1*B*C |  | 38100 | 18.08 | 5.08 | 41100 | 3.175
217754513 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042E1*B*C |  | 43500 | 17.3 | 5.06 | 50000 | 3.625
217754514 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042F1*B*C |  | 43500 | 16.95 | 4.96 | 50000 | 3.625
217754517 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048E1*B*C |  | 50800 | 17.62 | 5.52 | 58500 | 4.2333
217754518 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048F1*B*C |  | 50800 | 17.27 | 5.41 | 58500 | 4.2333
217754521 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060E1*B*C |  | 60500 | 17.3 | 5.5 | 74700 | 5.0417
217754522 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060F1*B*C |  | 60500 | 16.95 | 5.39 | 74700 | 5.0417
8560916 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS009*A | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
8560917 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS009*A | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
8560918 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS009*A | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
8560919 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS009*9 | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
8560920 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS009*9 | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
8560921 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS009*9 | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
8560930 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS012 | [6 empty] | 13400 | 24.1 | 4.3 | 12100 | 1.1167 | 11900 | 18.1 | 3.6 | 9400 | 0.99167
8560931 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS012 | [6 empty] | 13400 | 24.1 | 4.3 | 12100 | 1.1167 | 11900 | 18.1 | 3.6 | 9400 | 0.99167
8560932 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS012 | [6 empty] | 13400 | 24.1 | 4.3 | 12100 | 1.1167 | 11900 | 18.1 | 3.6 | 9400 | 0.99167
8560938 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS015 |  | 15100 | 17.5 | 6 | 17900 | 1.2583 | 17500 | 28.8 | 5.1 | 14600 | 1.4583 | 16000 | 19.8 | 4.1 | 11600 | 1.3333
8560939 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS015 |  | 15100 | 17.5 | 6 | 17900 | 1.2583 | 17500 | 28.8 | 5.1 | 14600 | 1.4583 | 16000 | 19.8 | 4.1 | 11600 | 1.3333
8560940 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS015 |  | 15100 | 17.5 | 6 | 17900 | 1.2583 | 17500 | 28.8 | 5.1 | 14600 | 1.4583 | 16000 | 19.8 | 4.1 | 11600 | 1.3333
8560941 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS015*A |  | 15100 | 17.5 | 6 | 17900 | 1.2583 | 17500 | 28.8 | 5.1 | 14600 | 1.4583 | 16000 | 19.8 | 4.1 | 11600 | 1.3333
8560942 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS015*A |  | 15100 | 17.5 | 6 | 17900 | 1.2583 | 17500 | 28.8 | 5.1 | 14600 | 1.4583 | 16000 | 19.8 | 4.1 | 11600 | 1.3333
8560943 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS015*A |  | 15100 | 17.5 | 6 | 17900 | 1.2583 | 17500 | 28.8 | 5.1 | 14600 | 1.4583 | 16000 | 19.8 | 4.1 | 11600 | 1.3333
8560946 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS015*****1 |  | 15200 | 18.8 | 6.4 | 17700 | 1.2667 | 17400 | 31.6 | 5.4 | 14400 | 1.45 | 16000 | 22.3 | 4.3 | 11500 | 1.3333
8560947 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS015*****1 |  | 15200 | 18.8 | 6.4 | 17700 | 1.2667 | 17400 | 31.6 | 5.4 | 14400 | 1.45 | 16000 | 22.3 | 4.3 | 11500 | 1.3333
8560948 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS015*****1 |  | 15200 | 18.8 | 6.4 | 17700 | 1.2667 | 17400 | 31.6 | 5.4 | 14400 | 1.45 | 16000 | 22.3 | 4.3 | 11500 | 1.3333
8560949 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS015*A***1 |  | 15200 | 18.8 | 6.4 | 17700 | 1.2667 | 17400 | 31.6 | 5.4 | 14400 | 1.45 | 16000 | 22.3 | 4.3 | 11500 | 1.3333
8560950 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS015*A***1 |  | 15200 | 18.8 | 6.4 | 17700 | 1.2667 | 17400 | 31.6 | 5.4 | 14400 | 1.45 | 16000 | 22.3 | 4.3 | 11500 | 1.3333
8560951 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS015*A***1 |  | 15200 | 18.8 | 6.4 | 17700 | 1.2667 | 17400 | 31.6 | 5.4 | 14400 | 1.45 | 16000 | 22.3 | 4.3 | 11500 | 1.3333
8332268 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT024 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8332358 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT024 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8332380 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT024 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8332431 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT024*2 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8332452 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT024*2 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8332472 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT024*2 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8332525 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT024*3 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8332545 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT024*3 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8332563 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT024*3 | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
8560913 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS009 | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
8560914 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS009 | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
8560915 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS009 | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
203113888 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J036**1 | SAH036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
203113890 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J042**1 | SAH042* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
203113892 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J038**1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
203113894 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104J038**1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
203143108 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS041 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143111 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS041*2 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143114 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS041*3 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143119 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS041*4 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143124 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS041 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143129 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS041*2 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143133 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS041*3 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143138 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS041*4 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143143 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS041 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143148 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS041*2 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143153 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS041*3 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143157 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS041*4 | [6 empty] | 41400 | 22.3 | 4.1 | 38900 | 3.45 | 38700 | 17.1 | 3.6 | 31100 | 3.225
203143746 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS041*****1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
203143749 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS041*2***1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
203143752 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS041*3***1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
203143764 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS041*****1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
203143767 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS041*2***1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
203143770 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS041*3***1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
203143781 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS041*****1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
207822237 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO09KW2BWRB | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
207822238 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO09KW2BWRH | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
207822239 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO09KW2BWBB | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
207822240 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO09KW2BWBH | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
207822249 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO12KW2BWRB | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
207822250 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO12KW2BWRH | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
207822251 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO12KW2BWBB | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
207822252 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO12KW2BWBH | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
207822261 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KW2BWRB | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
218158030 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SS024BD1 | Y5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
218158031 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SS036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
218158032 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SS048BD1 | Y5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
218158033 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SS060BD1 | Y5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
218158035 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SZ024BD1 | Y5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
218158036 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SZ036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
218158037 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SZ048BD1 | Y5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
218158038 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SZ060BD1 | Y5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
218158040 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SS024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
218158041 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
218158042 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SS048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
218158043 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SS060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
218158045 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SZ024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
218158046 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
218158047 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SZ048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
218158048 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SZ060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
218158050 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y5WZ024BS1* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
218158051 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y5WZ048BS1* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
218158052 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y5WZ060BS1* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
218158054 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S024SN10* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
218158055 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S024SN12* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
218158056 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S024SN14* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
218158057 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S048SN10* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
218158058 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S048SN13* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
218158059 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S048SN14* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
218158060 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S048SN15* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
218158061 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S060SN10* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
218158062 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S060SN13* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
218158063 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S060SN14* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
218158064 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y1(H/W)S060SN15* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
218158069 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y5WZ048BE1* | [6 empty] | 44500 | 20.1 | 3.9 | 52800 | 3.7083 | 43000 | 16.1 | 3.3 | 42800 | 3.5833
218158070 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | Y5WZ060BE1* | [6 empty] | 57100 | 20.1 | 3.7 | 66700 | 4.7583 | 54200 | 16.1 | 3.2 | 54100 | 4.5167
200083572 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HBH/V015 | [6 empty] | 16500 | 24 | 4.3 | 14100 | 1.375
200083573 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HBH/V015 | [6 empty] | 16500 | 24 | 4.3 | 14100 | 1.375
200083574 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HBH/V018 | [6 empty] | 21500 | 22 | 4.2 | 17800 | 1.7917
200083575 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HBH/V018 | [6 empty] | 21500 | 22 | 4.2 | 17800 | 1.7917
3628414 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH018**0*1 | [6 empty] | 20600 | 24 | 4.4 | 17500 | 1.7167 | 18500 | 17.5 | 3.7 | 13700 | 1.5417
3628415 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH018**2*1 | [6 empty] | 20600 | 24 | 4.4 | 17500 | 1.7167 | 18500 | 17.5 | 3.7 | 13700 | 1.5417
3628416 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH015**0*1 | [6 empty] | 16000 | 24.3 | 4.4 | 15000 | 1.3333 | 14700 | 17.5 | 3.7 | 11500 | 1.225
3628417 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH015**2*1 | [6 empty] | 16000 | 24.3 | 4.4 | 15000 | 1.3333 | 14700 | 17.5 | 3.7 | 11500 | 1.225
3655222 |  | GEOSTAR | WBAHP-O | Water-to-Air and Brine-to-Air | GCC/GCW/GCS/GCE15*0 | [6 empty] | 16200 | 22 | 4.1 | 14000 | 1.35
3655223 |  | GEOSTAR | WBAHP-O | Water-to-Air and Brine-to-Air | GCC/GCW/GCS/GCE15*2 | [6 empty] | 16200 | 22 | 4.1 | 14000 | 1.35
3696260 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS015**0*0 | [6 empty] | 16000 | 24 | 4.1 | 15000 | 1.3333
3696261 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS015**2*0 | [6 empty] | 16000 | 24 | 4.1 | 15000 | 1.3333
217212102 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP024-1HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
217212103 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP024-1HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
217212105 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP024-1VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
217212106 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP024-1VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
217212107 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP036-1VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
217212108 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP036-1VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
217212109 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP048-1VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
217212111 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP048-1VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
217212112 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP060-1VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
217212113 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RP060-1VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
217222416 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | W5WZ048BE1* | [6 empty] | 44500 | 20.1 | 3.9 | 52800 | 3.7083 | 43000 | 16.1 | 3.3 | 42800 | 3.5833
217222417 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | W5WZ060BE1* | [6 empty] | 57100 | 20.1 | 3.7 | 66700 | 4.7583 | 54200 | 16.1 | 3.2 | 54100 | 4.5167
217226665 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G5WZ048BE1* | [6 empty] | 44500 | 20.1 | 3.9 | 52800 | 3.7083 | 43000 | 16.1 | 3.3 | 42800 | 3.5833
217226666 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G5WZ060BE1* | [6 empty] | 57100 | 20.1 | 3.7 | 66700 | 4.7583 | 54200 | 16.1 | 3.2 | 54100 | 4.5167
217228467 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ048BE1* | [6 empty] | 44500 | 20.1 | 3.9 | 52800 | 3.7083 | 43000 | 16.1 | 3.3 | 42800 | 3.5833
217228468 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ060BE1* | [6 empty] | 57100 | 20.1 | 3.7 | 66700 | 4.7583 | 54200 | 16.1 | 3.2 | 54100 | 4.5167
217351071 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSC-*****A | BIVA-24RCB-M20X | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
217351072 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSN-*****A | BIVA-24RCB-M20X | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
218472190 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH025-2***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218472191 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH035-2***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218472192 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218472193 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218472195 |  | YORK | WBWHP | Water-to-Water and Brine-to-Water | AH061-1***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
218472198 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | AZ024-1CSC-*****A | CDM24B5XXS1A | [5 empty] | 27400 | 23.2 | 5 | 23800 | 2.2833 | 25400 | 18.1 | 4.1 | 18800 | 2.1167
218472199 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | AZ024-1CSN-*****A | CDM24B5XXS1A | [5 empty] | 27600 | 24.3 | 5.1 | 23800 | 2.3 | 26000 | 18.3 | 4.3 | 18800 | 2.1667
218472200 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | AZ036-1CSC-*****A | CDM30B5XXS1A | [5 empty] | 39600 | 21.5 | 4.8 | 37800 | 3.3 | 37000 | 16.4 | 4.1 | 29800 | 3.0833
218472201 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | AZ036-1CSN-*****A | CDM30B5XXS1A | [5 empty] | 40200 | 22.2 | 5 | 38800 | 3.35 | 38200 | 17.2 | 4.2 | 30800 | 3.1833
218472202 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | AZ048-1CSC-*****A | CDM48C5XXS1A | [5 empty] | 52000 | 21.6 | 4.5 | 45400 | 4.3333 | 50200 | 17.5 | 3.9 | 37200 | 4.1833
218472203 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | AZ048-1CSN-*****A | CDM48C5XXS1A | [5 empty] | 53400 | 22.5 | 4.7 | 46600 | 4.45 | 51600 | 17.8 | 4.1 | 38200 | 4.3
218472204 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | AZ060-1CSC-*****A | CDM60C5XXS1A | [5 empty] | 63400 | 20.5 | 4.4 | 58600 | 5.2833 | 60200 | 16.9 | 3.8 | 47600 | 5.0167
218472205 |  | YORK | WBAHP-C | Water-to-Air and Brine-to-Air | AZ060-1CSN-*****A | CDM60C5XXS1A | [5 empty] | 63200 | 21.1 | 4.5 | 59400 | 5.2667 | 60000 | 16.8 | 4 | 49800 | 5
216625508 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D4**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625509 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S3**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625510 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S4**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625511 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S0**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625512 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S2**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625513 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S3**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625514 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S4**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625515 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S0**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625516 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S3**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625517 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S4**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625518 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D4**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625519 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D2**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625520 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D4**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625521 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D4**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625542 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S4**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625543 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S2**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625748 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)009*R0**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
216625749 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)009*R2**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
216625750 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)012*R0**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
216625751 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)012*R2**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
216625752 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)015*R0**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216625753 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)015*R0**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216625754 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)015*R2**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216625755 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)015*R2**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216625756 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)018*D0**1 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
216625757 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)018*D0**4 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
216625758 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)018*R0**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216625759 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)018*R0**4 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216625760 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)018*R2**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216625761 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)018*R2**4 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216625762 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*D0**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216625763 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*D0**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216625764 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*D2**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216625765 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*D2**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216625766 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*D3**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216625767 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*D3**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216625768 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*D4**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216625769 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*D4**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216625770 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*S0**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625771 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*S0**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625772 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*S2**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625773 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*S2**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
218353349 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DD007-1VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218353350 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DD007-1VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218353351 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DD007-2VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218353352 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DD007-2VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218353353 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DD009-1VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218353354 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DD009-1VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
202667081 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP042-1VT*******B | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202679205 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 17.15 | 3.8 | 27400 | 3.1583
202679208 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 17.15 | 3.8 | 27400 | 3.1583
202729320 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729321 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729322 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729323 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729324 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729325 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729332 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729333 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729334 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729335 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729336 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729337 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202732300 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP042-1VT*******B | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732301 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732302 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732303 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732304 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732305 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732306 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732307 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732308 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732913 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSN-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 16.95 | 3.8 | 27400 | 3.1583
202732914 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP018-1HZ*******C | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732915 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSN-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 16.95 | 3.8 | 27400 | 3.1583
202732916 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP018-1HZ*******C | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732917 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732918 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732919 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732920 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732921 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732922 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732923 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732924 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732931 |  | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NEW040*1* | [6 empty] | 33000 | 20.1 | 4 | 40000 | 2.75 | 30600 | 16.1 | 3.3 | 34000 | 2.55
202732932 |  | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NEW050*1* | [6 empty] | 47000 | 20.1 | 3.9 | 54900 | 3.9167 | 44500 | 16.1 | 3.3 | 45000 | 3.7083
202732934 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036H3 | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
202732935 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036H4 | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
202732936 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036HW | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
202732937 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048H3 | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
202732938 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048H4 | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
202732939 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048HW | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
5646768 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT048D2 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646769 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT048D2 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646770 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT048D2 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646771 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT048D3 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646772 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT048D3 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5646773 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT048D3 | [6 empty] | 53100 | 21.8 | 4.6 | 46700 | 4.425 | 49000 | 17.1 | 3.9 | 38000 | 4.0833
5699505 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0421 |  | 44100 | 18.25 | 5.95 | 54700 | 3.675 | 50100 | 32.46 | 5.08 | 43600 | 4.175 | 46200 | 22.03 | 3.98 | 31900 | 3.85
5699525 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0422 |  | 44100 | 18.25 | 5.95 | 54700 | 3.675 | 50100 | 32.46 | 5.08 | 43600 | 4.175 | 46200 | 22.03 | 3.98 | 31900 | 3.85
5699526 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0424 |  | 44100 | 18.25 | 5.95 | 54700 | 3.675 | 50100 | 32.46 | 5.08 | 43600 | 4.175 | 46200 | 22.03 | 3.98 | 31900 | 3.85
5699527 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0601 |  | 61800 | 15.6 | 5.5 | 81200 | 5.15 | [5 empty] | 64600 | 18.3 | 4 | 50000 | 5.3833
5699534 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0602 |  | 61800 | 15.6 | 5.5 | 81200 | 5.15 | [5 empty] | 64600 | 18.3 | 4 | 50000 | 5.3833
5699535 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSVE0604 |  | 61800 | 15.6 | 5.5 | 81200 | 5.15 | [5 empty] | 64600 | 18.3 | 4 | 50000 | 5.3833
5699628 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0241 |  | 25100 | 18.3 | 6.44 | 30300 | 2.0917 | 28400 | 31.76 | 5.33 | 24300 | 2.3667 | 26200 | 21.82 | 4.35 | 18500 | 2.1833
5699631 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0242 |  | 25100 | 18.3 | 6.44 | 30300 | 2.0917 | 28400 | 31.76 | 5.33 | 24300 | 2.3667 | 26200 | 21.82 | 4.35 | 18500 | 2.1833
5699633 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0244 |  | 25100 | 18.3 | 6.44 | 30300 | 2.0917 | 28400 | 31.76 | 5.33 | 24300 | 2.3667 | 26200 | 21.82 | 4.35 | 18500 | 2.1833
5699634 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0331 |  | 33800 | 15.79 | 5.85 | 40200 | 2.8167 | 37900 | 25.01 | 4.98 | 32300 | 3.1583 | 35300 | 18.51 | 4.1 | 24700 | 2.9417
5699635 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0332 |  | 33800 | 15.79 | 5.85 | 40200 | 2.8167 | 37900 | 25.01 | 4.98 | 32300 | 3.1583 | 35300 | 18.51 | 4.1 | 24700 | 2.9417
5699637 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0334 |  | 33800 | 15.79 | 5.85 | 40200 | 2.8167 | 37900 | 25.01 | 4.98 | 32300 | 3.1583 | 35300 | 18.51 | 4.1 | 24700 | 2.9417
5699639 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0421 |  | 42600 | 18.6 | 6.7 | 51800 | 3.55 | 47300 | 30.9 | 5.6 | 42000 | 3.9417 | 44600 | 22 | 4.5 | 31500 | 3.7167
5699644 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0422 |  | 42600 | 18.6 | 6.7 | 51800 | 3.55 | 47300 | 30.9 | 5.6 | 42000 | 3.9417 | 44600 | 22 | 4.5 | 31500 | 3.7167
5699650 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0424 |  | 42600 | 18.6 | 6.7 | 51800 | 3.55 | 47300 | 30.9 | 5.6 | 42000 | 3.9417 | 44600 | 22 | 4.5 | 31500 | 3.7167
5699652 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0501 |  | 50200 | 16.5 | 5.8 | 64400 | 4.1833 | 56200 | 26 | 5.1 | 52500 | 4.6833 | 52400 | 19.3 | 4.2 | 40100 | 4.3667
5699653 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0502 |  | 50200 | 16.5 | 5.8 | 64400 | 4.1833 | 56200 | 26 | 5.1 | 52500 | 4.6833 | 52400 | 19.3 | 4.2 | 40100 | 4.3667
5699654 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0504 |  | 50200 | 16.5 | 5.8 | 64400 | 4.1833 | 56200 | 26 | 5.1 | 52500 | 4.6833 | 52400 | 19.3 | 4.2 | 40100 | 4.3667
5699655 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0601 |  | 60700 | 14.8 | 5.3 | 81600 | 5.0583 | [5 empty] | 63200 | 17 | 3.8 | 50400 | 5.2667
5699656 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0602 |  | 60700 | 14.8 | 5.3 | 81600 | 5.0583 | [5 empty] | 63200 | 17 | 3.8 | 50400 | 5.2667
5699657 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | VSHE0604 |  | 60700 | 14.8 | 5.3 | 81600 | 5.0583 | [5 empty] | 63200 | 17 | 3.8 | 50400 | 5.2667
6501883 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH009**0*0 | [6 empty] | 10800 | 22.2 | 4.4 | 10600 | 0.9
6501884 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH009**2*0 | [6 empty] | 10800 | 22.2 | 4.4 | 10600 | 0.9
6501885 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH012**0*0 | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
6501886 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH012**2*0 | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
205767541 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TCH/V018A*W/K | [6 empty] | 21500 | 23.6 | 4.5 | 17800 | 1.7917 | 19500 | 17.1 | 3.7 | 14100 | 1.625
205767542 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TCH/V024A*W/K | [6 empty] | 27000 | 21.5 | 4.3 | 23500 | 2.25
205767543 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TCH/V030A*W/K | [6 empty] | 32000 | 21.6 | 4.3 | 30500 | 2.6667
214771921 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK009A | [6 empty] | 9400 | 25.6 | 4.94 | 8600 | 0.78333 | 8800 | 19.6 | 3.96 | 6400 | 0.73333
214771922 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK012A | [6 empty] | 11900 | 22.3 | 4.45 | 11500 | 0.99167
214771923 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK015A | [6 empty] | 16800 | 24.1 | 4.69 | 16700 | 1.4 | 15900 | 18.2 | 3.85 | 12500 | 1.325
214771924 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK018A | [6 empty] | 19600 | 23.4 | 4.46 | 19500 | 1.6333 | 18500 | 17.3 | 3.76 | 15300 | 1.5417
214771925 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK024A | [6 empty] | 27000 | 25.5 | 4.5 | 26000 | 2.25 | 25400 | 18.9 | 3.65 | 19700 | 2.1167
214771926 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK030A | [6 empty] | 31700 | 23.9 | 4.31 | 29800 | 2.6417 | 30000 | 18.2 | 3.66 | 23700 | 2.5
214771927 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK036A | [6 empty] | 42500 | 22.1 | 4.17 | 39700 | 3.5417
214771928 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK042A | [6 empty] | 47100 | 24.5 | 4.14 | 46200 | 3.925
214771929 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK048A | [6 empty] | 54500 | 24 | 4.31 | 50800 | 4.5417 | 50900 | 18.4 | 3.6 | 38900 | 4.2417
214771930 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVK060A | [6 empty] | 64300 | 23.9 | 4.23 | 63700 | 5.3583 | 60100 | 18.3 | 3.65 | 50200 | 5.0083
214771931 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK009A |  | 8700 | 18.1 | 6.4 | 10700 | 0.725 | 9600 | 29.7 | 5.16 | 8500 | 0.8 | 9000 | 21.2 | 3.91 | 6100 | 0.75
214771932 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK012A |  | 11400 | 17.1 | 5.9 | 14300 | 0.95 | 12500 | 26.1 | 4.98 | 11500 | 1.0417 | 11900 | 19.8 | 3.78 | 8500 | 0.99167
214771933 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK015A | [6 empty] | 17100 | 24.6 | 4.6 | 15600 | 1.425 | 16200 | 18.7 | 3.73 | 11800 | 1.35
214771934 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK018A |  | 18900 | 17.5 | 5.43 | 23000 | 1.575 | 21100 | 29.6 | 4.77 | 18600 | 1.7583 | 19700 | 20.8 | 3.93 | 14400 | 1.6417
214771935 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK024A |  | 25300 | 18.1 | 5.55 | 32000 | 2.1083 | 27400 | 28.4 | 4.81 | 25900 | 2.2833 | 26200 | 21.2 | 3.8 | 19400 | 2.1833
214771936 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK030A |  | 30200 | 17.9 | 5.74 | 37500 | 2.5167 | 34500 | 29.3 | 4.98 | 30100 | 2.875 | 31800 | 21.3 | 4.17 | 22900 | 2.65
214771937 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK036A |  | 35000 | 17.8 | 5.62 | 43600 | 2.9167 | 39500 | 28.4 | 4.91 | 35500 | 3.2917 | 36600 | 20.8 | 4.11 | 27200 | 3.05
214771938 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK042A |  | 42000 | 17.8 | 5.93 | 48800 | 3.5 | 45300 | 27.7 | 5.07 | 39300 | 3.775 | 43300 | 20.9 | 4.1 | 30800 | 3.6083
214771939 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK048A |  | 45300 | 17.5 | 5.83 | 51800 | 3.775 | 48300 | 26.5 | 4.91 | 41800 | 4.025 | 46900 | 20.3 | 3.99 | 33900 | 3.9083
216054482 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVT024* | [6 empty] | 27600 | 23.8 | 4.6 | 23900 | 2.3 | 25800 | 18.6 | 4 | 19400 | 2.15
216054483 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVT030* | [6 empty] | 34100 | 23.1 | 4.6 | 30300 | 2.8417 | 32200 | 18.4 | 3.8 | 24300 | 2.6833
216054484 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVT036* | [6 empty] | 40000 | 22.8 | 4.6 | 36900 | 3.3333 | 37400 | 17.7 | 3.9 | 29500 | 3.1167
216054485 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVT042* | [6 empty] | 49200 | 24 | 4.6 | 40100 | 4.1 | 45900 | 18.5 | 3.9 | 32400 | 3.825
216054486 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVT048* | [6 empty] | 53600 | 24.5 | 4.9 | 48500 | 4.4667 | 50300 | 18.8 | 4 | 38500 | 4.1917
216054487 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT024* | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
216054488 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT036* | [6 empty] | 42300 | 27.9 | 5.4 | 35500 | 3.525 | 39700 | 21 | 4.3 | 27900 | 3.3083
216419863 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
216419865 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
216419867 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
216419868 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
217754549 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030F1*C/S*T |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
217754550 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030K1*C/S*T |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
217754553 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030F1*C/S*C |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
217754554 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030K1*C/S*C |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
204595321 |  | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS036*******1**2 | EAM4X36L**A* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
204595322 |  | KEEPRITE | WBAHP-C | Water-to-Air and Brine-to-Air | HS036*******1**2 | EAM4X36L**A* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
204595323 |  | TEMPSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | HS036*******1**2 | EAM4X36L**A* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
204595324 |  | COMFORTMAKER | WBAHP-C | Water-to-Air and Brine-to-Air | HS036*******1**2 | EAM4X36L**A* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
204595325 |  | DAY & NIGHT | WBAHP-C | Water-to-Air and Brine-to-Air | HS036*******1**2 | EAM4X36L**A* | [5 empty] | 40400 | 20.7 | 4.35 | 36500 | 3.3667 | 37400 | 16.9 | 3.65 | 27700 | 3.1167
205652455 |  | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | SM048-1CS*-*****A | BMAC4248CNTF | [5 empty] | 52000 | 21.6 | 4.5 | 45500 | 4.3333 | 50300 | 17.5 | 3.9 | 37200 | 4.1917
205652456 |  | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | SM060-1CS*-*****A | BMAC4860CNTF | [5 empty] | 63600 | 20.5 | 4.4 | 58600 | 5.3 | 61800 | 16.9 | 3.8 | 47700 | 5.15
205652457 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | LM048-1CS*-*****A | BVA-48WN1-M20 | [5 empty] | 54000 | 23.1 | 4.8 | 47000 | 4.5 | 51700 | 18.1 | 4 | 38000 | 4.3083
205652459 |  | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | LM048-1CS*-*****A | BMAC4248CNTF | [5 empty] | 52000 | 21.6 | 4.5 | 45500 | 4.3333 | 50300 | 17.5 | 3.9 | 37200 | 4.1917
205652460 |  | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | LM060-1CS*-*****A | BMAC4860CNTF | [5 empty] | 63600 | 20.5 | 4.4 | 58600 | 5.3 | 61800 | 16.9 | 3.8 | 47700 | 5.15
205652461 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM048-1CS*-*****A | BVA-48WN1-M20 | [5 empty] | 54000 | 23.1 | 4.8 | 47000 | 4.5 | 51700 | 18.1 | 4 | 38000 | 4.3083
205652463 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | SM048-1CS*-*****A | BMAC4248CNTF | [5 empty] | 52000 | 21.6 | 4.5 | 45500 | 4.3333 | 50300 | 17.5 | 3.9 | 37200 | 4.1917
205652464 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | SM060-1CS*-*****A | BMAC4860CNTF | [5 empty] | 63600 | 20.5 | 4.4 | 58600 | 5.3 | 61800 | 16.9 | 3.8 | 47700 | 5.15
205652465 |  | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | LM048-1CS*-*****A | BVA-48WN1-M20 | [5 empty] | 54000 | 23.1 | 4.8 | 47000 | 4.5 | 51700 | 18.1 | 4 | 38000 | 4.3083
205652467 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | LM048-1CS*-*****A | BMAC4248CNTF | [5 empty] | 52000 | 21.6 | 4.5 | 45500 | 4.3333 | 50300 | 17.5 | 3.9 | 37200 | 4.1917
205652468 |  | FHP | WBAHP-C | Water-to-Air and Brine-to-Air | LM060-1CS*-*****A | BMAC4860CNTF | [5 empty] | 63600 | 20.5 | 4.4 | 58600 | 5.3 | 61800 | 16.9 | 3.8 | 47700 | 5.15
205698260 |  | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT036*2 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698261 |  | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT036*2 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698262 |  | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT036*2 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698263 |  | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT036*3 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698264 |  | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT036*3 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698265 |  | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT036*3 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698266 |  | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT036 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698267 |  | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT036 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698268 |  | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT036 | [6 empty] | 43500 | 20.5 | 3.8 | 46100 | 3.625
205698275 |  | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT048*2 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698276 |  | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT048*2 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698277 |  | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT048*2 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698278 |  | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT048*3 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698279 |  | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT048*3 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205698280 |  | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT048*3 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205699453 |  | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT048 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205699462 |  | HYDRON MODULE | WBWHP | Water-to-Water and Brine-to-Water | HWT048 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205699463 |  | TETCO | WBWHP | Water-to-Water and Brine-to-Water | TWT048 | [6 empty] | 54300 | 19.8 | 3.6 | 55100 | 4.525
205752888 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TCH/V006A*W/K | [6 empty] | 7000 | 24 | 4.2 | 6300 | 0.58333
205754885 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V015A*W/K B | [6 empty] | 16500 | 25 | 4.5 | 14100 | 1.375 | 14800 | 18 | 3.6 | 11000 | 1.2333
205754886 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V015A*W/K C | [6 empty] | 16500 | 25 | 4.5 | 14100 | 1.375 | 14800 | 18 | 3.6 | 11000 | 1.2333
205754887 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V018A B | [6 empty] | 21500 | 22 | 4.2 | 17800 | 1.7917
205754888 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V018A C | [6 empty] | 21500 | 22 | 4.2 | 17800 | 1.7917
205754889 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V018A*W/K B | [6 empty] | 21500 | 23.6 | 4.5 | 17800 | 1.7917 | 19500 | 17.1 | 3.7 | 14100 | 1.625
205754890 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V018A*W/K C | [6 empty] | 21500 | 23.6 | 4.5 | 17800 | 1.7917 | 19500 | 17.1 | 3.7 | 14100 | 1.625
214595581 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-2-0-GCBC-V0-10-000-A | [6 empty] | 48100 | 21.3 | 4.1 | 48300 | 4.0083
214595583 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-3-0-GCBC-V0-10-000-A | [6 empty] | 48100 | 21.3 | 4.1 | 48300 | 4.0083
214595585 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-4-0-GCBC-V0-10-000-A | [6 empty] | 48100 | 21.3 | 4.1 | 48300 | 4.0083
4651870 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS023**3*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651873 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS023**4*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651874 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS023**4*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651882 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS042**0*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651883 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS042**0*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651888 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS042**3*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651889 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS042**3*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651894 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS042**4*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651895 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS042**4*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
4651936 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS048**0*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
4651937 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS048**0*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
4651942 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS048**3*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
4651943 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS048**3*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
4651948 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS048**4*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
4651949 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | ZS048**4*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
215268758 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D3**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268759 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D0**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268760 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D3**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268761 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*D0**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
215268762 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*D3**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
218396714 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH025-3***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218396715 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH025-4***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218396716 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH035-3***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218396717 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH035-4***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218396720 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH061-3***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
218396721 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH061-4***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
218396728 |  | JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | DH025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218396729 |  | JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | DH025-2***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
218396730 |  | JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | DH035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218396731 |  | JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | DH035-2***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
218396733 |  | JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | DH061-1***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
202330559 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-005-4-H-DCAC-S0-10-000-A | [6 empty] | 62100 | 21.93 | 4.1 | 50000 | 5.175
215224034 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF015-1VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224035 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF018-1VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224036 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF018-1VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224037 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF007-2VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224038 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF007-2VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224039 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF009-2VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224040 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF009-2VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224041 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF012-2VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224042 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF012-2VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224043 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF015-2VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224044 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF015-2VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224045 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF018-2VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224046 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF018-2VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224047 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-2VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224048 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-4VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224049 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-2VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224050 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-4VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224051 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-2VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224052 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-4VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224053 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-2VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224054 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-4VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224055 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-2VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224056 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-4VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224057 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-2VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224058 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-4VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224059 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-4VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224060 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-4VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224061 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-4VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224062 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-4VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224069 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-2CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
215224070 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-4CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
215224071 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-2CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
215224072 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-4CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
215224073 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-2CFC-*****A | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
215224074 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-4CFC-*****A | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
215224075 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-2CFN-*****A | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
215224076 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-4CFN-*****A | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
215224077 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-2CFC-*****A | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
216772590 |  | Enertech | WBAHP | Water-to-Air and Brine-to-Air | EVT060* | [6 empty] | 64200 | 22 | 4.49 | 58550 | 5.35 | 60900 | 17.6 | 3.8 | 46700 | 5.075
216772592 |  | Enertech | WBAHP | Water-to-Air and Brine-to-Air | EZS015* | [6 empty] | 16000 | 26.3 | 4.8 | 14300 | 1.3333 | 14525 | 18.6 | 3.9 | 11200 | 1.2104
216772593 |  | Enertech | WBAHP | Water-to-Air and Brine-to-Air | EZS017* | [6 empty] | 18475 | 22.2 | 4.38 | 15950 | 1.5396
216772594 |  | Enertech | WBAHP | Water-to-Air and Brine-to-Air | EZS018* |  | 19725 | 18 | 5.5 | 21900 | 1.6438 | 21500 | 30.1 | 4.7 | 17500 | 1.7917 | 20400 | 21.5 | 3.86 | 14100 | 1.7
216772598 |  | Enertech | WBWHP | Water-to-Water and Brine-to-Water | EWS036* | [6 empty] | 35600 | 22.9 | 4.1 | 38300 | 2.9667 | 34900 | 17.7 | 3.3 | 31000 | 2.9083
216772599 |  | Enertech | WBWHP | Water-to-Water and Brine-to-Water | EWS048* | [6 empty] | 52500 | 22.9 | 4.2 | 58700 | 4.375 | 50500 | 17.3 | 3.2 | 45200 | 4.2083
216772601 |  | Enertech | WBWHP | Water-to-Water and Brine-to-Water | EWT036* | [6 empty] | 42200 | 20.4 | 4.1 | 48000 | 3.5167 | 40200 | 15.4 | 3.3 | 38100 | 3.35
216772602 |  | Enertech | WBWHP | Water-to-Water and Brine-to-Water | EWT048* | [6 empty] | 52700 | 21.2 | 4.2 | 61100 | 4.3917 | 49500 | 16.3 | 3.5 | 49000 | 4.125
216772603 |  | Enertech | WBWHP | Water-to-Water and Brine-to-Water | EWT060* | [6 empty] | 62700 | 20.4 | 3.9 | 67000 | 5.225 | 60600 | 16.2 | 3.1 | 52900 | 5.05
216801023 |  | CARRIER | WBAHP-O | Water-to-Air and Brine-to-Air | 50PEC09****3/CG | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
216801024 |  | CARRIER | WBAHP-O | Water-to-Air and Brine-to-Air | 50PEC09****4/DG | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
216801031 |  | FHP | WBAHP-O | Water-to-Air and Brine-to-Air | CA009-1***-******E | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
216801032 |  | FHP | WBAHP-O | Water-to-Air and Brine-to-Air | CA009-2***-******E | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
216801911 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT025-2***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801912 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT025-4***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
216801913 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT035-2***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
216801914 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT035-4***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
204031812 |  | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | YAZT049**1*J | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
204088622 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM060-1CS*-*****A | SM060-1AH*-*****A | [5 empty] | 64500 | 20.5 | 4.3 | 60500 | 5.375 | 58900 | 16.25 | 3.65 | 49000 | 4.9083
204088624 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM060-1CS*-*****A | SM060-1AH*-*****A | [5 empty] | 64500 | 20.5 | 4.3 | 60500 | 5.375 | 58900 | 16.25 | 3.65 | 49000 | 4.9083
212587993 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX09*-7 | [6 empty] | 11500 | 23.9 | 4.1 | 8800 | 0.95833
212587994 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | HRCX09*-7 | [6 empty] | 11500 | 23.9 | 4.1 | 8800 | 0.95833
213087558 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDS049J1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
213087559 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDS049J1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
213087562 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDS064J1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
213087563 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDS064J1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
213154439 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS026*1******K | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
213154440 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS026*1******K | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
213154441 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS049*1******K | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
213154442 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS049*1******K | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
213154445 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS064*1******K | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
213154446 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS064*1******K | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
213154447 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS038*1******K | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
213154448 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS038*1******K | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
213154449 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | YT024**1*4********C | [6 empty] | 25100 | 20.6 | 4.4 | 23500 | 2.0917 | 23100 | 15.6 | 3.8 | 18900 | 1.925
213154450 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | YT036**1*4********C | [6 empty] | 38000 | 19.7 | 4.2 | 35500 | 3.1667 | 35100 | 15.5 | 3.6 | 26000 | 2.925
213154451 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | YT048**1*4********C | [6 empty] | 52300 | 21.8 | 4.3 | 45000 | 4.3583 | 49000 | 16.1 | 3.7 | 36000 | 4.0833
213154453 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | YT060**1*4********C | [6 empty] | 64100 | 20.7 | 4 | 56500 | 5.3417 | 59900 | 16.5 | 3.4 | 45300 | 4.9917
213154454 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ026*1******K | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
213154455 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTZ026*1******K | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
213154456 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ038*1******K | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
213154457 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTZ038*1******K | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
213154458 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ049*1******K | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
213154459 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTZ049*1******K | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
213154460 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ064*1******K | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
213154461 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTZ064*1******K | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
213154464 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS012**1*0********L | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
213154465 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS018**1*1********L | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
213154466 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS022**1*1********L | [6 empty] | 21900 | 27.5 | 5 | 19500 | 1.825 | 19200 | 18.7 | 4 | 15000 | 1.6
213154467 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GS030**1*1********L |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
206229678 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP024-1HZ/VTN-*****B | [6 empty] | 27600 | 25.1 | 4.15 | 23700 | 2.3
206229679 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP024-2HZ/VTN-*****B | [6 empty] | 27600 | 25.1 | 4.15 | 23700 | 2.3
206229680 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP024-3HZ/VTN-*****B | [6 empty] | 27600 | 25.1 | 4.15 | 23700 | 2.3
206229681 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP024-4HZ/VTN-*****B | [6 empty] | 27600 | 25.1 | 4.15 | 23700 | 2.3
206229682 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V024**C3/CA | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
206229683 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V024**C4/DA | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
206229684 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V024**C5/EA | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
206229685 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V024**C6/FA | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
206229686 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V024**N3/CA | [6 empty] | 27600 | 25.1 | 4.15 | 23700 | 2.3
206229687 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V024**N4/DA | [6 empty] | 27600 | 25.1 | 4.15 | 23700 | 2.3
206229688 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V024**N5/EA | [6 empty] | 27600 | 25.1 | 4.15 | 23700 | 2.3
206229689 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V024**N6/FA | [6 empty] | 27600 | 25.1 | 4.15 | 23700 | 2.3
206345837 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSS6006*7* | [6 empty] | 8600 | 26 | 4.5 | 7200 | 0.71667
206345838 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSS6009*7* | [6 empty] | 11200 | 26 | 4.5 | 8200 | 0.93333
206345839 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSS6012*7* | [6 empty] | 13800 | 26 | 4.5 | 10400 | 1.15
206345840 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSS6015*7* | [6 empty] | 18100 | 23.1 | 4.3 | 15500 | 1.5083
216625838 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D0**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625839 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D0**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625840 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D0**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625841 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D2**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625842 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D3**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625843 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D3**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625844 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D3**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625845 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D4**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625846 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D4**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625847 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*D4**4 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216625848 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S0**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625849 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S0**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625850 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S0**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625851 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S2**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625852 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S3**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625853 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S3**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625854 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S3**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625855 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S4**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625856 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S4**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216625857 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048*S4**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216687113 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SS024BD1 | W5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216687114 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SS036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216687115 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SS048BD1 | W5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216687116 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SS060BD1 | W5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
218353471 |  | JOHNSON CONTROLS | WBAHP-O | Water-to-Air and Brine-to-Air | DK009-1***-******E | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
218353472 |  | JOHNSON CONTROLS | WBAHP-O | Water-to-Air and Brine-to-Air | DK009-2***-******E | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
203143785 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS041*2***1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
203143790 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS041*3***1 | [6 empty] | 43000 | 23.6 | 4.4 | 39200 | 3.5833 | 39800 | 17.8 | 3.7 | 31200 | 3.3167
203238019 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP042-1HZ*******B |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203238020 |  | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036***C***1**2 | FE/V****005*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203238021 |  | GEO-THERMAL SPLIT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036***N***1**2 | FE/V****005*** | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203238919 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | SM024-1VT/CFN-*****A | [6 empty] | 29000 | 23.7 | 4.6 | 23500 | 2.4167 | 26600 | 18.2 | 3.7 | 18000 | 2.2167
203238923 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | SM024-1HZC-*****A |  | 25500 | 16.6 | 5.6 | 29200 | 2.125 | 29000 | 25.75 | 5 | 23500 | 2.4167 | 26600 | 19.9 | 3.7 | 18000 | 2.2167
203238926 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | SM024-1HZN-*****A | [6 empty] | 29000 | 24.1 | 5 | 23500 | 2.4167 | 26600 | 18.3 | 3.7 | 18000 | 2.2167
203253412 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP042-1HZ*******B |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203253413 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM024-1HZC-*****A |  | 25500 | 16.6 | 5.6 | 29200 | 2.125 | 29000 | 25.75 | 5 | 23500 | 2.4167 | 26600 | 19.9 | 3.7 | 18000 | 2.2167
203253414 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM024-1HZC-*****C |  | 25500 | 16.6 | 5.6 | 29200 | 2.125 | 29000 | 25.75 | 5 | 23500 | 2.4167 | 26600 | 19.9 | 3.7 | 18000 | 2.2167
203253415 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM024-1HZN-*****A | [6 empty] | 29000 | 24.1 | 5 | 23500 | 2.4167 | 26600 | 18.3 | 3.7 | 18000 | 2.2167
203253416 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | SM024-1HZN-*****C | [6 empty] | 29000 | 24.1 | 5 | 23500 | 2.4167 | 26600 | 18.3 | 3.7 | 18000 | 2.2167
203254574 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036***C***1**2 | FE/V****005 | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203254575 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036***C***1**2 | FE/V****005 | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203254576 |  | HEIL | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***C***1**2 | FVM4X4800BL | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203254577 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***C***1**2 | FVM4X4800BL | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203254578 |  | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***C***1**2 | FVM4X4800BL | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203254579 |  | TEMPSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***C***1**2 | FVM4X4800BL | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203254580 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***C***1**2 | FVM4X4800BL | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203254581 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***C***1**2 | FVM4X4800BL | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
203254582 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036***N***1**2 | FE/V****005 | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203254583 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036***N***1**2 | FE/V****005 | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203254584 |  | HEIL | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X4800BL | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203254585 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X4800BL | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203254586 |  | KEEPRITE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X4800BL | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203254587 |  | TEMPSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X4800BL | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203254588 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X4800BL | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203254589 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036***N***1**2 | FVM4X4800BL | [5 empty] | 41400 | 20.3 | 4.2 | 36700 | 3.45 | 39200 | 16.25 | 3.6 | 27400 | 3.2667
203254606 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254607 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254608 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254609 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254610 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254611 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254612 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254614 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254620 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GC024V/C**N***1*X1 | [6 empty] | 29000 | 23.7 | 4.6 | 23500 | 2.4167 | 26600 | 18.2 | 3.7 | 18000 | 2.2167
203254624 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GC024H**C***1*X1 |  | 25500 | 16.6 | 5.6 | 29200 | 2.125 | 29000 | 25.75 | 5 | 23500 | 2.4167 | 26600 | 19.9 | 3.7 | 18000 | 2.2167
203254626 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GC024H**N***1*X1 | [6 empty] | 29000 | 24.1 | 5 | 23500 | 2.4167 | 26600 | 18.3 | 3.7 | 18000 | 2.2167
203254744 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GC024V/C**N***1**1 | [6 empty] | 29000 | 23.7 | 4.6 | 23500 | 2.4167 | 26600 | 18.2 | 3.7 | 18000 | 2.2167
203254748 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GC024H**C***1**1 |  | 25500 | 16.6 | 5.6 | 29200 | 2.125 | 29000 | 25.75 | 5 | 23500 | 2.4167 | 26600 | 19.9 | 3.7 | 18000 | 2.2167
203254752 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GC024H**N***1**1 | [6 empty] | 29000 | 24.1 | 5 | 23500 | 2.4167 | 26600 | 18.3 | 3.7 | 18000 | 2.2167
203260718 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | SM024-1VT/CFC******A | [6 empty] | 29000 | 24.7 | 4.3 | 23500 | 2.4167 | 26600 | 18.9 | 3.7 | 18000 | 2.2167
203260866 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GC024V/C**C***1**1 + UI | [6 empty] | 29000 | 24.7 | 4.3 | 23500 | 2.4167 | 26600 | 18.9 | 3.7 | 18000 | 2.2167
203260867 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GC024V/C**C***1*X1 + UI | [6 empty] | 29000 | 24.7 | 4.3 | 23500 | 2.4167 | 26600 | 18.9 | 3.7 | 18000 | 2.2167
207822287 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO12KW2CWBB | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
207822288 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO12KW2CWBH | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
207822297 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KW2CWRB | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
207822298 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KW2CWRH | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
217048166 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S060SN14* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048167 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S060SN15* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048174 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S024SN10* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048175 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S024SN12* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048176 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S024SN14* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048794 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ024BS1* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048795 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ048BS1* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048796 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ060BS1* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
217048798 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S024SN10* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
216979817 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979818 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979819 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979820 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979821 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979822 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979823 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979824 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979825 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979826 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979827 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979828 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979837 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979838 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979839 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979840 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979841 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979842 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979843 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979844 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979845 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979846 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979847 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979848 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979849 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979850 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979851 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979852 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979853 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979854 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979855 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979856 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979857 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979858 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979859 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979860 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979861 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979862 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979863 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979864 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979865 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979866 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
9100368 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**0*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100370 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**3*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100371 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**3*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100373 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**4*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100374 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**4*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100377 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**0*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100378 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**0*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100380 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**3*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100381 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**3*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
205767548 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TRH/V018A*W/K | [6 empty] | 21500 | 23.6 | 4.5 | 17800 | 1.7917 | 19500 | 17.1 | 3.7 | 14100 | 1.625
205767549 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TRH/V024A*W/K | [6 empty] | 27000 | 21.5 | 4.3 | 23500 | 2.25
205767550 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TRH/V030A*W/K | [6 empty] | 32000 | 21.6 | 4.3 | 30500 | 2.6667
205767554 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TZV/H024C | [6 empty] | 26500 | 21.7 | 4.1 | 23000 | 2.2083 | 24600 | 16 | 3.6 | 17800 | 2.05
205767555 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TZV/H030C | [6 empty] | 32300 | 20.7 | 4.2 | 30000 | 2.6917 | 29900 | 15.7 | 3.6 | 23800 | 2.4917
205767556 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TZV/H036C | [6 empty] | 38200 | 22.3 | 4.3 | 35100 | 3.1833 | 35200 | 16.7 | 3.6 | 27300 | 2.9333
205767557 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TZV/H042C | [6 empty] | 46300 | 21.3 | 4.1 | 42300 | 3.8583 | 43100 | 16.1 | 3.4 | 33300 | 3.5917
205767558 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TZV/H048C | [6 empty] | 51800 | 20.9 | 4.4 | 45000 | 4.3167 | 48100 | 15.5 | 3.7 | 35600 | 4.0083
205767560 |  | ClimateMaster | WBWHP | Water-to-Water and Brine-to-Water | TMW036A | [6 empty] | 36200 | 23.1 | 4 | 35300 | 3.0167 | 33300 | 16.4 | 3.1 | 27400 | 2.775
205767561 |  | ClimateMaster | WBWHP | Water-to-Water and Brine-to-Water | TMW060B | [6 empty] | 56600 | 20.3 | 3.8 | 60300 | 4.7167
205767579 |  | ClimateMaster | WBWHP | Water-to-Water and Brine-to-Water | TCW036 | [6 empty] | 35600 | 20.8 | 3.6 | 34700 | 2.9667
205767580 |  | ClimateMaster | WBWHP | Water-to-Water and Brine-to-Water | TCW060 | [6 empty] | 60900 | 20.8 | 3.5 | 58600 | 5.075
205767582 |  | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | TES/P038B | TAH038C | [5 empty] | 40500 | 23.4 | 4.5 | 32700 | 3.375 | 37700 | 17.8 | 3.8 | 26200 | 3.1417
205767583 |  | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | TES/P049B | TAH049C | [5 empty] | 52800 | 23 | 4.2 | 45900 | 4.4 | 48700 | 16.9 | 3.5 | 35900 | 4.0583
205767584 |  | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | TES/P064B | TAH064C | [5 empty] | 62400 | 20.3 | 4 | 56600 | 5.2 | 57300 | 15.5 | 3.4 | 44300 | 4.775
205767586 |  | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | TES/P026B | TAH026C***A* | [5 empty] | 25600 | 22.4 | 4.5 | 24900 | 2.1333 | 24700 | 17.7 | 3.6 | 18800 | 2.0583
205767587 |  | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | TES/P026B | TAH026C***B* | [5 empty] | 27300 | 24 | 4.4 | 22800 | 2.275 | 25800 | 18.3 | 3.8 | 18700 | 2.15
205767588 |  | ClimateMaster | WBAHP-C | Water-to-Air and Brine-to-Air | TES/P026B | TAC026B***A* | [5 empty] | 25200 | 22.4 | 4.5 | 22300 | 2.1 | 24000 | 17.4 | 3.9 | 18800 | 2
205767589 |  | ClimateMaster | WBAHP-C | Water-to-Air and Brine-to-Air | TES/P026B | TAC026B***B* | [5 empty] | 26400 | 22.5 | 4.5 | 22900 | 2.2 | 26000 | 18 | 3.8 | 18600 | 2.1667
205767590 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TRE036D | [6 empty] | 39800 | 21.7 | 4.4 | 35400 | 3.3167
205767591 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TRE048D | [6 empty] | 54800 | 21.1 | 4.1 | 48500 | 4.5667
214771941 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVK070A |  | 63400 | 17.6 | 5.5 | 77000 | 5.2833
214771943 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHK009A | [6 empty] | 9400 | 25.6 | 4.94 | 8600 | 0.78333 | 8800 | 19.6 | 3.96 | 6400 | 0.73333
214771944 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHK012A | [6 empty] | 11900 | 22.3 | 4.45 | 11500 | 0.99167
214771945 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHK015A | [6 empty] | 16800 | 24.1 | 4.69 | 16700 | 1.4 | 15900 | 18.2 | 3.85 | 12500 | 1.325
214771946 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHK018A | [6 empty] | 19600 | 23.4 | 4.46 | 19500 | 1.6333 | 18500 | 17.3 | 3.76 | 15300 | 1.5417
217735426 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024J1*B*T |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
217735427 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024J1*B*C |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
217735428 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH030J1*B*T |  | 29500 | 18.14 | 5.64 | 34500 | 2.4583
217735429 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH030J1*B*C |  | 29500 | 18.14 | 5.64 | 34500 | 2.4583
217735430 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036J1*B*T |  | 39000 | 18.2 | 5.07 | 44600 | 3.25
217735431 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036J1*B*C |  | 39000 | 18.2 | 5.07 | 44600 | 3.25
217735432 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042J1*B*T |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
217735433 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042J1*B*C |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
217735434 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH024J1*B*C |  | 24500 | 17.18 | 5.19 | 26100 | 2.0417
217735436 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH030J1*B*C |  | 31400 | 16.78 | 5.26 | 34900 | 2.6167
217735438 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH036J1*B*C |  | 38000 | 18.06 | 5.25 | 42900 | 3.1667
217735440 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024J1*B*C |  | 24300 | 17.24 | 5.7 | 28000 | 2.025
217735442 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030J1*B*C |  | 31200 | 16.63 | 5.41 | 34700 | 2.6
217735444 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036J1*B*C |  | 38100 | 18.08 | 5.08 | 41100 | 3.175
217735642 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024(U/V/W/Y)**3*(A-H)** | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
217735643 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024(U/V/W/Y)**3*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
217735644 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024(U/V/W/Y)**4*(A-H)** | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
217735645 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024(U/V/W/Y)**4*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
217735646 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024(U/V/W/Y)**5*(A-H)** | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
217735647 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024(U/V/W/Y)**5*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
217735648 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024(U/V/W/Y)**6*(A-H)** | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
217735649 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024(U/V/W/Y)**6*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
217735650 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030(U/V/W/Y)**3*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
7422020 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
7422043 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
7422058 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
7422072 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**3*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
7422083 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**4*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
7422093 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**4*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
7423168 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH026**4*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7423169 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**4*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7423171 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH026**4*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
7487652 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT036 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487653 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT036 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487654 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT036 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487655 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT036*2 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487656 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT036*2 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487657 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT036*2 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487658 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT036*3 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487659 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT036*3 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487660 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT036*3 | [6 empty] | 44300 | 27 | 5.5 | 37500 | 3.6917 | 41200 | 20.9 | 4.5 | 29100 | 3.4333
7487661 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT048 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487662 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT048 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487663 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT048 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487664 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT048*2 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487665 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT048*2 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487666 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT048*2 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487667 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GYT048*3 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
7487668 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HYT048*3 | [6 empty] | 57100 | 26.2 | 5.2 | 49500 | 4.7583 | 53300 | 20.2 | 4.3 | 39900 | 4.4417
217351789 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 40500 | 22.3 | 4.7 | 34200 | 3.375 | 38000 | 18.1 | 3.7 | 26800 | 3.1667
217351790 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 52000 | 21.5 | 4.6 | 46500 | 4.3333 | 48500 | 17.1 | 4 | 37800 | 4.0417
217351791 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 51000 | 21 | 4.5 | 45500 | 4.25 | 47500 | 16.7 | 3.9 | 37000 | 3.9583
217351792 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*C******1 | F(C,T)MA5*60**** | [5 empty] | 63500 | 21.7 | 4.4 | 60000 | 5.2917 | 60500 | 17.6 | 3.7 | 47000 | 5.0417
217351793 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*N******1 | F(C,T)MA5*60**** | [5 empty] | 62500 | 21.3 | 4.3 | 59000 | 5.2083 | 59500 | 17.3 | 3.7 | 46000 | 4.9583
217351795 |  | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS024SR*C******1 | EAM5*2*M*** | [5 empty] | 27200 | 24.8 | 4.5 | 23900 | 2.2667 | 25900 | 17.5 | 3.8 | 18900 | 2.1583
217351796 |  | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS024SR*N******1 | EAM5*2*M*** | [5 empty] | 26700 | 24.3 | 4.4 | 23400 | 2.225 | 25400 | 17.1 | 3.7 | 18500 | 2.1167
217351797 |  | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS036SR*C******1 | EAM5*3*M*** | [5 empty] | 40300 | 22.8 | 4.4 | 34500 | 3.3583 | 37400 | 17.7 | 3.6 | 27600 | 3.1167
217351798 |  | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS036SR*N******1 | EAM5*3*M*** | [5 empty] | 39500 | 22.3 | 4.3 | 33800 | 3.2917 | 36600 | 17.4 | 3.6 | 27100 | 3.05
217351799 |  | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS048SR*C******1 | EAM5*4*M*** | [5 empty] | 54600 | 22.3 | 4.6 | 46600 | 4.55 | 49000 | 17.1 | 3.9 | 37900 | 4.0833
217351800 |  | ARCOAIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HS048SR*N******1 | EAM5*4*M*** | [5 empty] | 53500 | 21.9 | 4.5 | 45600 | 4.4583 | 48000 | 16.7 | 3.8 | 37100 | 4
217351806 |  | ARCOAIRE | WBWHP | Water-to-Water and Brine-to-Water | HW024WR********1 |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351807 |  | ARCOAIRE | WBWHP | Water-to-Water and Brine-to-Water | HW036WR********1 | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351808 |  | ARCOAIRE | WBWHP | Water-to-Water and Brine-to-Water | HW048WR********1 | [6 empty] | 44000 | 21.5 | 4.25 | 50000 | 3.6667 | 42500 | 16.9 | 3.46 | 39500 | 3.5417
217351809 |  | ARCOAIRE | WBWHP | Water-to-Water and Brine-to-Water | HW060WR********1 | [6 empty] | 55000 | 20.7 | 3.96 | 59500 | 4.5833 | 51500 | 15.9 | 3.16 | 47500 | 4.2917
217351811 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS024SR*C******1 | F(C,T)MA5*36**** | [5 empty] | 28200 | 24.2 | 4.9 | 23400 | 2.35 | 26000 | 18.5 | 4.1 | 18800 | 2.1667
217351812 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS024SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 27600 | 23.7 | 4.8 | 23000 | 2.3 | 25400 | 18.1 | 4 | 18400 | 2.1167
217351813 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*36**** | [5 empty] | 40000 | 21.7 | 4.6 | 36600 | 3.3333 | 36800 | 16.9 | 3.7 | 28200 | 3.0667
217351814 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 39000 | 21.3 | 4.5 | 35800 | 3.25 | 36000 | 16.6 | 3.7 | 27600 | 3
217351815 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 41000 | 22.8 | 4.8 | 34800 | 3.4167 | 39000 | 18.5 | 3.7 | 27400 | 3.25
217351816 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 40500 | 22.3 | 4.7 | 34200 | 3.375 | 38000 | 18.1 | 3.7 | 26800 | 3.1667
217351817 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 52000 | 21.5 | 4.6 | 46500 | 4.3333 | 48500 | 17.1 | 4 | 37800 | 4.0417
217351818 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS048SR*N******1 | F(C,T)MA5*48**** | [5 empty] | 51000 | 21 | 4.5 | 45500 | 4.25 | 47500 | 16.7 | 3.9 | 37000 | 3.9583
217351819 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*C******1 | F(C,T)MA5*60**** | [5 empty] | 63500 | 21.7 | 4.4 | 60000 | 5.2917 | 60500 | 17.6 | 3.7 | 47000 | 5.0417
217351820 |  | COMFORTMAKER | WBAHP-CB | Water-to-Air and Brine-to-Air | HS060SR*N******1 | F(C,T)MA5*60**** | [5 empty] | 62500 | 21.3 | 4.3 | 59000 | 5.2083 | 59500 | 17.3 | 3.7 | 46000 | 4.9583
217351822 |  | COMFORTMAKER | WBAHP-C | Water-to-Air and Brine-to-Air | HS024SR*C******1 | EAM5*2*M*** | [5 empty] | 27200 | 24.8 | 4.5 | 23900 | 2.2667 | 25900 | 17.5 | 3.8 | 18900 | 2.1583
217351823 |  | COMFORTMAKER | WBAHP-C | Water-to-Air and Brine-to-Air | HS024SR*N******1 | EAM5*2*M*** | [5 empty] | 26700 | 24.3 | 4.4 | 23400 | 2.225 | 25400 | 17.1 | 3.7 | 18500 | 2.1167
217351824 |  | COMFORTMAKER | WBAHP-C | Water-to-Air and Brine-to-Air | HS036SR*C******1 | EAM5*3*M*** | [5 empty] | 40300 | 22.8 | 4.4 | 34500 | 3.3583 | 37400 | 17.7 | 3.6 | 27600 | 3.1167
217351825 |  | COMFORTMAKER | WBAHP-C | Water-to-Air and Brine-to-Air | HS036SR*N******1 | EAM5*3*M*** | [5 empty] | 39500 | 22.3 | 4.3 | 33800 | 3.2917 | 36600 | 17.4 | 3.6 | 27100 | 3.05
217351826 |  | COMFORTMAKER | WBAHP-C | Water-to-Air and Brine-to-Air | HS048SR*C******1 | EAM5*4*M*** | [5 empty] | 54600 | 22.3 | 4.6 | 46600 | 4.55 | 49000 | 17.1 | 3.9 | 37900 | 4.0833
217351827 |  | COMFORTMAKER | WBAHP-C | Water-to-Air and Brine-to-Air | HS048SR*N******1 | EAM5*4*M*** | [5 empty] | 53500 | 21.9 | 4.5 | 45600 | 4.4583 | 48000 | 16.7 | 3.8 | 37100 | 4
217351833 |  | COMFORTMAKER | WBWHP | Water-to-Water and Brine-to-Water | HW024WR********1 |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351834 |  | COMFORTMAKER | WBWHP | Water-to-Water and Brine-to-Water | HW036WR********1 | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351835 |  | COMFORTMAKER | WBWHP | Water-to-Water and Brine-to-Water | HW048WR********1 | [6 empty] | 44000 | 21.5 | 4.25 | 50000 | 3.6667 | 42500 | 16.9 | 3.46 | 39500 | 3.5417
217351836 |  | COMFORTMAKER | WBWHP | Water-to-Water and Brine-to-Water | HW060WR********1 | [6 empty] | 55000 | 20.7 | 3.96 | 59500 | 4.5833 | 51500 | 15.9 | 3.16 | 47500 | 4.2917
217351838 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS024SR*C******1 | F(C,T)MA5*36**** | [5 empty] | 28200 | 24.2 | 4.9 | 23400 | 2.35 | 26000 | 18.5 | 4.1 | 18800 | 2.1667
217351839 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS024SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 27600 | 23.7 | 4.8 | 23000 | 2.3 | 25400 | 18.1 | 4 | 18400 | 2.1167
217351840 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*36**** | [5 empty] | 40000 | 21.7 | 4.6 | 36600 | 3.3333 | 36800 | 16.9 | 3.7 | 28200 | 3.0667
217351841 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 39000 | 21.3 | 4.5 | 35800 | 3.25 | 36000 | 16.6 | 3.7 | 27600 | 3
217351842 |  | DAY & NIGHT | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 41000 | 22.8 | 4.8 | 34800 | 3.4167 | 39000 | 18.5 | 3.7 | 27400 | 3.25
6501912 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**0*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
6501913 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**2*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
6501914 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**2*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
6501915 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**3*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
6501916 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**3*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
6501917 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**4*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
6501918 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**0*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
6501919 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**0*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
6501920 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**0*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
6501921 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**2*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
6501922 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**2*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
6501923 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**2*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
6501924 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
6501925 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
6501926 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
6501927 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
6501928 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
6501929 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
6501930 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**0*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
206726827 |  | HYDRON MODULE | WBAHP-CB | Water-to-Air and Brine-to-Air | HBT036 | EAD036 | 35200 | 16.6 | 5.3 | 46000 | 2.9333 | 39700 | 24.8 | 4.7 | 36700 | 3.3083 | 36900 | 19.2 | 3.8 | 27800 | 3.075
206726828 |  | TETCO | WBAHP-C | Water-to-Air and Brine-to-Air | TBT036 | EED036 | 35800 | 16.6 | 4.9 | 45200 | 2.9833 | 40500 | 24.6 | 4.7 | 36800 | 3.375 | 37600 | 19.2 | 3.8 | 28800 | 3.1333
206726829 |  | TETCO | WBAHP-CB | Water-to-Air and Brine-to-Air | TBT036 | EAD036 | 35200 | 16.6 | 5.3 | 46000 | 2.9333 | 39700 | 24.8 | 4.7 | 36700 | 3.3083 | 36900 | 19.2 | 3.8 | 27800 | 3.075
206726830 |  | GEOCOMFORT | WBAHP-C | Water-to-Air and Brine-to-Air | GBT036*2 | EED036 | 35800 | 16.6 | 4.9 | 45200 | 2.9833 | 40500 | 24.6 | 4.7 | 36800 | 3.375 | 37600 | 19.2 | 3.8 | 28800 | 3.1333
206726831 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBT036*2 | EAD036 | 35200 | 16.6 | 5.3 | 46000 | 2.9333 | 39700 | 24.8 | 4.7 | 36700 | 3.3083 | 36900 | 19.2 | 3.8 | 27800 | 3.075
206726832 |  | HYDRON MODULE | WBAHP-C | Water-to-Air and Brine-to-Air | HBT036*2 | EED036 | 35800 | 16.6 | 4.9 | 45200 | 2.9833 | 40500 | 24.6 | 4.7 | 36800 | 3.375 | 37600 | 19.2 | 3.8 | 28800 | 3.1333
206726833 |  | HYDRON MODULE | WBAHP-CB | Water-to-Air and Brine-to-Air | HBT036*2 | EAD036 | 35200 | 16.6 | 5.3 | 46000 | 2.9333 | 39700 | 24.8 | 4.7 | 36700 | 3.3083 | 36900 | 19.2 | 3.8 | 27800 | 3.075
206726834 |  | TETCO | WBAHP-C | Water-to-Air and Brine-to-Air | TBT036*2 | EED036 | 35800 | 16.6 | 4.9 | 45200 | 2.9833 | 40500 | 24.6 | 4.7 | 36800 | 3.375 | 37600 | 19.2 | 3.8 | 28800 | 3.1333
206726835 |  | TETCO | WBAHP-CB | Water-to-Air and Brine-to-Air | TBT036*2 | EAD036 | 35200 | 16.6 | 5.3 | 46000 | 2.9333 | 39700 | 24.8 | 4.7 | 36700 | 3.3083 | 36900 | 19.2 | 3.8 | 27800 | 3.075
206726836 |  | GEOCOMFORT | WBAHP-C | Water-to-Air and Brine-to-Air | GBT048 | EED048 | 49100 | 16.7 | 5.6 | 61600 | 4.0917 | 55000 | 24.9 | 4.9 | 50800 | 4.5833 | 51300 | 19.3 | 4.1 | 40700 | 4.275
206726837 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBT048 | EAD048 | [5 empty] | 53400 | 23.4 | 4.6 | 50800 | 4.45 | 50300 | 18.4 | 3.8 | 40700 | 4.1917
206726838 |  | HYDRON MODULE | WBAHP-C | Water-to-Air and Brine-to-Air | HBT048 | EED048 | 49100 | 16.7 | 5.6 | 61600 | 4.0917 | 55000 | 24.9 | 4.9 | 50800 | 4.5833 | 51300 | 19.3 | 4.1 | 40700 | 4.275
206726839 |  | HYDRON MODULE | WBAHP-CB | Water-to-Air and Brine-to-Air | HBT048 | EAD048 | [5 empty] | 53400 | 23.4 | 4.6 | 50800 | 4.45 | 50300 | 18.4 | 3.8 | 40700 | 4.1917
206726840 |  | TETCO | WBAHP-C | Water-to-Air and Brine-to-Air | TBT048 | EED048 | 49100 | 16.7 | 5.6 | 61600 | 4.0917 | 55000 | 24.9 | 4.9 | 50800 | 4.5833 | 51300 | 19.3 | 4.1 | 40700 | 4.275
206726841 |  | TETCO | WBAHP-CB | Water-to-Air and Brine-to-Air | TBT048 | EAD048 | [5 empty] | 53400 | 23.4 | 4.6 | 50800 | 4.45 | 50300 | 18.4 | 3.8 | 40700 | 4.1917
206726842 |  | GEOCOMFORT | WBAHP-C | Water-to-Air and Brine-to-Air | GBT048*2 | EED048 | 49100 | 16.7 | 5.6 | 61600 | 4.0917 | 55000 | 24.9 | 4.9 | 50800 | 4.5833 | 51300 | 19.3 | 4.1 | 40700 | 4.275
206726843 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBT048*2 | EAD048 | [5 empty] | 53400 | 23.4 | 4.6 | 50800 | 4.45 | 50300 | 18.4 | 3.8 | 40700 | 4.1917
206726844 |  | HYDRON MODULE | WBAHP-C | Water-to-Air and Brine-to-Air | HBT048*2 | EED048 | 49100 | 16.7 | 5.6 | 61600 | 4.0917 | 55000 | 24.9 | 4.9 | 50800 | 4.5833 | 51300 | 19.3 | 4.1 | 40700 | 4.275
206726845 |  | HYDRON MODULE | WBAHP-CB | Water-to-Air and Brine-to-Air | HBT048*2 | EAD048 | [5 empty] | 53400 | 23.4 | 4.6 | 50800 | 4.45 | 50300 | 18.4 | 3.8 | 40700 | 4.1917
206726846 |  | TETCO | WBAHP-C | Water-to-Air and Brine-to-Air | TBT048*2 | EED048 | 49100 | 16.7 | 5.6 | 61600 | 4.0917 | 55000 | 24.9 | 4.9 | 50800 | 4.5833 | 51300 | 19.3 | 4.1 | 40700 | 4.275
206726847 |  | TETCO | WBAHP-CB | Water-to-Air and Brine-to-Air | TBT048*2 | EAD048 | [5 empty] | 53400 | 23.4 | 4.6 | 50800 | 4.45 | 50300 | 18.4 | 3.8 | 40700 | 4.1917
206726848 |  | GEOCOMFORT | WBAHP-C | Water-to-Air and Brine-to-Air | GBT060 | EED060 | [5 empty] | 63600 | 21.9 | 4.5 | 60200 | 5.3 | 63400 | 17.8 | 3.8 | 48100 | 5.2833
206726849 |  | HYDRON MODULE | WBAHP-C | Water-to-Air and Brine-to-Air | HBT060 | EED060 | [5 empty] | 63600 | 21.9 | 4.5 | 60200 | 5.3 | 63400 | 17.8 | 3.8 | 48100 | 5.2833
214841697 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
214841698 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
214841699 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)018A | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
214841700 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SR(L/R/B/P/T/K/F)018A*V | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
214841701 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SZ(L/R/B/P/T/K)024A | [6 empty] | 27000 | 24.1 | 4.7 | 23500 | 2.25 | 25000 | 18 | 3.9 | 18400 | 2.0833
214841702 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SZ(L/R/B/P/T/K)030A | [6 empty] | 32900 | 21.7 | 4.1 | 28700 | 2.7417 | 30200 | 15.45 | 3.6 | 23200 | 2.5167
214841703 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SZ(L/R/B/P/T/K)036A | [6 empty] | 39300 | 20.2 | 4.2 | 36300 | 3.275 | 36400 | 16.4 | 3.6 | 28600 | 3.0333
214841704 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SZ(L/R/B/P/T/K)042A | [6 empty] | 47500 | 22.8 | 4.2 | 41000 | 3.9583 | 44500 | 17.3 | 3.5 | 32500 | 3.7083
214841705 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SZ(L/R/B/P/T/K)048A | [6 empty] | 52000 | 22.9 | 4.3 | 45000 | 4.3333 | 49000 | 17.7 | 3.7 | 36000 | 4.0833
214841707 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SY(L/R/B/P/T/K)024A | [6 empty] | 27000 | 24.1 | 4.7 | 23500 | 2.25 | 25000 | 18 | 3.9 | 18400 | 2.0833
214841708 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SY(L/R/B/P/T/K)030A | [6 empty] | 32900 | 21.7 | 4.1 | 28700 | 2.7417 | 30200 | 15.45 | 3.6 | 23200 | 2.5167
214841709 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SY(L/R/B/P/T/K)036A | [6 empty] | 39300 | 20.2 | 4.2 | 36300 | 3.275 | 36400 | 16.4 | 3.6 | 28600 | 3.0333
214841710 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SY(L/R/B/P/T/K)042A | [6 empty] | 47500 | 22.8 | 4.2 | 41000 | 3.9583 | 44500 | 17.3 | 3.5 | 32500 | 3.7083
214841711 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SY(L/R/B/P/T/K)048A | [6 empty] | 52000 | 22.9 | 4.3 | 45000 | 4.3333 | 49000 | 17.7 | 3.7 | 36000 | 4.0833
214844588 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7A(V/H)024BV1**2 |  | 22200 | 16.9 | 6 | 39200 | 1.85 | 26300 | 37.8 | 5 | 32100 | 2.1917 | 24100 | 23.6 | 4.1 | 24800 | 2.0083
214844645 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7A(V/H)036BV1**2 |  | 33500 | 15.3 | 5.4 | 51800 | 2.7917 | 38200 | 28.7 | 4.7 | 41900 | 3.1833 | 35800 | 18.1 | 3.8 | 32900 | 2.9833
214844646 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7A(V/H)048BV1**2 |  | 41500 | 16 | 4.8 | 66000 | 3.4583 | 49000 | 27.4 | 4.2 | 54500 | 4.0833 | 45000 | 18.9 | 3.6 | 42000 | 3.75
214844647 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7A(V/H)060BV1**2 |  | 50000 | 15.3 | 4.7 | 79800 | 4.1667 | 60700 | 23.4 | 4.3 | 66000 | 5.0583 | 56000 | 17.1 | 3.5 | 51700 | 4.6667
215223342 |  | WaterFurnace | WBAHP-O | Water-to-Air and Brine-to-Air | V5C(C/W/S)015**0**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
215223348 |  | WaterFurnace | WBAHP-O | Water-to-Air and Brine-to-Air | V3C(C/W/S)015**0**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
215223349 |  | WaterFurnace | WBAHP-O | Water-to-Air and Brine-to-Air | V3C(C/W/S)015**2**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
215223354 |  | WaterFurnace | WBAHP-O | Water-to-Air and Brine-to-Air | V5C(C/W/S)015**2**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
9910548 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*****1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910549 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS024*****1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910550 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS024*****1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910551 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*2***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910552 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS024*2***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910553 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS024*2***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910554 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*3***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910555 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS024*3***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910556 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS024*3***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910557 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*A***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910558 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS024*A***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910559 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS024*A***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
205788285 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JSH/V/D036C*K B |  | 33500 | 18.1 | 5.9 | 39900 | 2.7917 | 35400 | 24.9 | 4.9 | 32600 | 2.95 | 34600 | 20.4 | 4.3 | 25600 | 2.8833
205788286 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JSH/V/D036C*K C |  | 33500 | 18.1 | 5.9 | 39900 | 2.7917 | 35400 | 24.9 | 4.9 | 32600 | 2.95 | 34600 | 20.4 | 4.3 | 25600 | 2.8833
205788287 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JSH/V/D042C B |  | 38500 | 17.2 | 5.6 | 46300 | 3.2083 | 43700 | 25.4 | 4.7 | 36200 | 3.6417 | 40100 | 19.4 | 3.8 | 28700 | 3.3417
205788288 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JSH/V/D042C C |  | 38500 | 17.2 | 5.6 | 46300 | 3.2083 | 43700 | 25.4 | 4.7 | 36200 | 3.6417 | 40100 | 19.4 | 3.8 | 28700 | 3.3417
205788289 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JSH/V/D042C*K B |  | 39400 | 19.6 | 6 | 45100 | 3.2833 | 44400 | 29.5 | 5.2 | 35200 | 3.7 | 40700 | 21.9 | 4.1 | 27400 | 3.3917
205788290 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JSH/V/D042C*K C |  | 39400 | 19.6 | 6 | 45100 | 3.2833 | 44400 | 29.5 | 5.2 | 35200 | 3.7 | 40700 | 21.9 | 4.1 | 27400 | 3.3917
205901399 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V015A B | [6 empty] | 16500 | 24 | 4.3 | 14100 | 1.375
205901400 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V015A C | [6 empty] | 16500 | 24 | 4.3 | 14100 | 1.375
205958295 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CS*-*****B | BVA-36WN1-M20 | [5 empty] | 38400 | 21.3 | 4.5 | 36500 | 3.2 | 36400 | 16.8 | 3.95 | 29200 | 3.0333
205958296 |  | BOSCH-GEO | WBAHP-C | Water-to-Air and Brine-to-Air | SM036-1CS*-*****B | BMAC3036BNTD | [5 empty] | 39600 | 20.5 | 4.6 | 36000 | 3.3 | 37100 | 16.4 | 4.05 | 29800 | 3.0917
205958297 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CS*-*****B | BVA-36WN1-M20 | [5 empty] | 38400 | 21.3 | 4.5 | 36500 | 3.2 | 36400 | 16.8 | 3.95 | 29200 | 3.0333
205958298 |  | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | SM036-1CS*-*****B | BMAC3036BNTD | [5 empty] | 39600 | 20.5 | 4.6 | 36000 | 3.3 | 37100 | 16.4 | 4.05 | 29800 | 3.0917
205961527 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JRE036D | [6 empty] | 39800 | 21.7 | 4.4 | 35400 | 3.3167
205961528 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JRE048D | [6 empty] | 54800 | 21.1 | 4.1 | 48500 | 4.5667
205961533 |  | Johnson Controls | WBWHP | Water-to-Water and Brine-to-Water | JMW036A | [6 empty] | 36200 | 23.1 | 4 | 35300 | 3.0167 | 33300 | 16.4 | 3.1 | 27400 | 2.775
205961534 |  | Johnson Controls | WBWHP | Water-to-Water and Brine-to-Water | JMW060B | [6 empty] | 56600 | 20.3 | 3.8 | 60300 | 4.7167
214772142 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHK036A |  | 32100 | 17.9 | 6.1 | 41800 | 2.675 | 36700 | 27.9 | 5.3 | 33600 | 3.0583 | 33800 | 20.9 | 4.3 | 25400 | 2.8167
214772143 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHK048A |  | 44800 | 17.7 | 6.1 | 53700 | 3.7333 | 49500 | 27 | 5.3 | 42900 | 4.125 | 46300 | 20.2 | 4.3 | 32300 | 3.8583
214772144 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHK060A |  | 54500 | 18.5 | 6.2 | 67000 | 4.5417 | 60100 | 27 | 5.4 | 53800 | 5.0083 | 56500 | 21.1 | 4.3 | 41000 | 4.7083
214772145 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHK070A |  | 61800 | 16.4 | 5.6 | 81400 | 5.15
214772146 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVK024B |  | 25400 | 18.9 | 5.8 | 31100 | 2.1167 | 27100 | 27.9 | 5.2 | 25000 | 2.2583 | 25700 | 21.4 | 4.2 | 18900 | 2.1417
214772147 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVK0244 |  | 25400 | 18.9 | 5.8 | 31100 | 2.1167 | 27100 | 27.9 | 5.2 | 25000 | 2.2583 | 25700 | 21.4 | 4.2 | 18900 | 2.1417
214772148 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVK036B |  | 32100 | 17.9 | 6.1 | 41800 | 2.675 | 36700 | 27.9 | 5.3 | 33600 | 3.0583 | 33800 | 20.9 | 4.3 | 25400 | 2.8167
203363126 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**0*1* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363127 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**0*4* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363129 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**2*1* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363130 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**2*4* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363132 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**3*1* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363133 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**3*4* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363135 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**4*1* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363136 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH030**4*4* | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
203363137 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**0*0* | [6 empty] | 40000 | 22 | 4.2 | 35600 | 3.3333
203363138 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**0*1* | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
203363139 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**0*4* | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
203363140 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**2*0* | [6 empty] | 40000 | 22 | 4.2 | 35600 | 3.3333
203363141 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**2*1* | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
203363142 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**2*4* | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
203363143 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**3*0* | [6 empty] | 40000 | 22 | 4.2 | 35600 | 3.3333
203363144 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**3*1* | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
203363145 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**3*4* | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
203363146 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**4*0* | [6 empty] | 40000 | 22 | 4.2 | 35600 | 3.3333
203363147 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**4*1* | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
203363148 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH036**4*4* | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
203363150 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH042**0*1* | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
203363151 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH042**0*4* | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
203363153 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH042**3*1* | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
203363154 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH042**3*4* | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
203363156 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH042**4*1* | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
203363157 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YBSV/YBSH042**4*4* | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
209156974 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6006*6* | [6 empty] | 8600 | 26 | 4.5 | 7200 | 0.71667
209156975 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6009*6* | [6 empty] | 11200 | 26 | 4.5 | 8200 | 0.93333
209156976 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6012*6* | [6 empty] | 13800 | 26 | 4.5 | 10400 | 1.15
209156977 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6015*6* | [6 empty] | 18100 | 23.1 | 4.3 | 15500 | 1.5083
209156981 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSHXE06A6* | [6 empty] | 7800 | 23.5 | 4.3 | 6400 | 0.65
209156987 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSHXE06A7* | [6 empty] | 7800 | 23.5 | 4.3 | 6400 | 0.65
209156993 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6006*7* | [6 empty] | 8600 | 26 | 4.5 | 7200 | 0.71667
209156994 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6009*7* | [6 empty] | 11200 | 26 | 4.5 | 8200 | 0.93333
209156995 |  | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSS6012*7* | [6 empty] | 13800 | 26 | 4.5 | 10400 | 1.15
200083642 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HZV/H/D036B |  | 37700 | 17.9 | 5.8 | 45700 | 3.1417 | 42100 | 26.1 | 5.2 | 37900 | 3.5083 | 39000 | 20.3 | 4.4 | 29700 | 3.25
200083643 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HZV/H/D036B |  | 37700 | 17.9 | 5.8 | 45700 | 3.1417 | 42100 | 26.1 | 5.2 | 37900 | 3.5083 | 39000 | 20.3 | 4.4 | 29700 | 3.25
200083644 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HZV/H/D024B |  | 25000 | 17.4 | 6 | 31400 | 2.0833 | 28500 | 26.4 | 5.3 | 25800 | 2.375 | 26000 | 19.9 | 4.1 | 20200 | 2.1667
200083645 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HZV/H/D024B |  | 25000 | 17.4 | 6 | 31400 | 2.0833 | 28500 | 26.4 | 5.3 | 25800 | 2.375 | 26000 | 19.9 | 4.1 | 20200 | 2.1667
200083646 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HZV/H/D048B |  | 48600 | 16.8 | 5.1 | 56700 | 4.05 | 55000 | 25.3 | 4.6 | 46800 | 4.5833 | 49600 | 19.3 | 4 | 36400 | 4.1333
200083647 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HZV/H/D048B |  | 48600 | 16.8 | 5.1 | 56700 | 4.05 | 55000 | 25.3 | 4.6 | 46800 | 4.5833 | 49600 | 19.3 | 4 | 36400 | 4.1333
200083648 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HZV/H/D060B |  | 61500 | 16.2 | 5.4 | 77400 | 5.125
200083649 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HZV/H/D060B |  | 61500 | 16.2 | 5.4 | 77400 | 5.125
200083664 |  | COMFORT-AIRE | WBWHP | Water-to-Water and Brine-to-Water | HWW036A | [6 empty] | 36200 | 23.1 | 4 | 35300 | 3.0167 | 33300 | 16.4 | 3.1 | 27400 | 2.775
200083665 |  | CENTURY | WBWHP | Water-to-Water and Brine-to-Water | HWW036A | [6 empty] | 36200 | 23.1 | 4 | 35300 | 3.0167 | 33300 | 16.4 | 3.1 | 27400 | 2.775
200083666 |  | COMFORT-AIRE | WBWHP | Water-to-Water and Brine-to-Water | HWW060B | [6 empty] | 56600 | 20.3 | 3.8 | 60300 | 4.7167
200083667 |  | CENTURY | WBWHP | Water-to-Water and Brine-to-Water | HWW060B | [6 empty] | 56600 | 20.3 | 3.8 | 60300 | 4.7167
200083684 |  | COMFORT-AIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS024B | WDG024**A-*B | [5 empty] | 25600 | 22.4 | 4.5 | 24900 | 2.1333 | 24700 | 17.7 | 3.6 | 18800 | 2.0583
200083685 |  | CENTURY | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS024B | WDG024**A-*B | [5 empty] | 25600 | 22.4 | 4.5 | 24900 | 2.1333 | 24700 | 17.7 | 3.6 | 18800 | 2.0583
200083686 |  | COMFORT-AIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS024B | WDG024**B-*B | [5 empty] | 27300 | 24 | 4.4 | 22800 | 2.275 | 25800 | 18.3 | 3.8 | 18700 | 2.15
200083687 |  | CENTURY | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS024B | WDG024**B-*B | [5 empty] | 27300 | 24 | 4.4 | 22800 | 2.275 | 25800 | 18.3 | 3.8 | 18700 | 2.15
200083688 |  | COMFORT-AIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HZS024B | MWG24*A-B | [5 empty] | 25200 | 22.4 | 4.5 | 22300 | 2.1 | 24000 | 17.4 | 3.9 | 18800 | 2
200083689 |  | CENTURY | WBAHP-C | Water-to-Air and Brine-to-Air | HZS024B | MWG24*A-B | [5 empty] | 25200 | 22.4 | 4.5 | 22300 | 2.1 | 24000 | 17.4 | 3.9 | 18800 | 2
200083690 |  | COMFORT-AIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HZS024B | MWG24*C-B | [5 empty] | 26400 | 22.5 | 4.5 | 22900 | 2.2 | 26000 | 18 | 3.8 | 18600 | 2.1667
200083691 |  | CENTURY | WBAHP-C | Water-to-Air and Brine-to-Air | HZS024B | MWG24*C-B | [5 empty] | 26400 | 22.5 | 4.5 | 22900 | 2.2 | 26000 | 18 | 3.8 | 18600 | 2.1667
200083692 |  | COMFORT-AIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HZS024B | MWG24*B-B | [5 empty] | 25200 | 22.4 | 4.5 | 22300 | 2.1 | 24000 | 17.4 | 3.9 | 18800 | 2
200083693 |  | CENTURY | WBAHP-C | Water-to-Air and Brine-to-Air | HZS024B | MWG24*B-B | [5 empty] | 25200 | 22.4 | 4.5 | 22300 | 2.1 | 24000 | 17.4 | 3.9 | 18800 | 2
200083694 |  | COMFORT-AIRE | WBAHP-C | Water-to-Air and Brine-to-Air | HZS036B | MWG36**-B | [5 empty] | 40200 | 22.3 | 4.4 | 32800 | 3.35 | 38000 | 17.3 | 3.7 | 26600 | 3.1667
200083695 |  | CENTURY | WBAHP-C | Water-to-Air and Brine-to-Air | HZS036B | MWG36**-B | [5 empty] | 40200 | 22.3 | 4.4 | 32800 | 3.35 | 38000 | 17.3 | 3.7 | 26600 | 3.1667
200083696 |  | COMFORT-AIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS036B | WDG036***-*B | [5 empty] | 40500 | 23.4 | 4.5 | 32700 | 3.375 | 37700 | 17.8 | 3.8 | 26200 | 3.1417
200083697 |  | CENTURY | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS036B | WDG036***-*B | [5 empty] | 40500 | 23.4 | 4.5 | 32700 | 3.375 | 37700 | 17.8 | 3.8 | 26200 | 3.1417
200083700 |  | COMFORT-AIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS048B | WDG048***-*B | [5 empty] | 52800 | 23 | 4.2 | 45900 | 4.4 | 48700 | 16.9 | 3.5 | 35900 | 4.0583
200083701 |  | CENTURY | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS048B | WDG048***-*B | [5 empty] | 52800 | 23 | 4.2 | 45900 | 4.4 | 48700 | 16.9 | 3.5 | 35900 | 4.0583
200083704 |  | COMFORT-AIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS060B | WDG060***-*B | [5 empty] | 62400 | 20.3 | 4 | 56600 | 5.2 | 57300 | 15.5 | 3.4 | 44300 | 4.775
200083705 |  | CENTURY | WBAHP-CB | Water-to-Air and Brine-to-Air | HZS060B | WDG060***-*B | [5 empty] | 62400 | 20.3 | 4 | 56600 | 5.2 | 57300 | 15.5 | 3.4 | 44300 | 4.775
200083803 |  | NORTHSTAR SERIES | WBAHP-CB | Water-to-Air and Brine-to-Air | RT-SE-040-* | HE-A-**-**-36 | [5 empty] | 47000 | 20.09 | 4.05 | 41800 | 3.9167 | 43200 | 15.87 | 3.7 | 32800 | 3.6
200083807 |  | NORTHSTAR SERIES | WBAHP | Water-to-Air and Brine-to-Air | RT-VE-040-* | [6 empty] | 47000 | 20.09 | 4.05 | 41800 | 3.9167 | 43200 | 15.87 | 3.7 | 32800 | 3.6
200083808 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | RT-VE-045-* | [6 empty] | 49300 | 19.32 | 4.07 | 44600 | 4.1083 | 47600 | 14.93 | 3.59 | 35600 | 3.9667
200083809 |  | NORTHSTAR SERIES | WBAHP | Water-to-Air and Brine-to-Air | RT-VE-045-* | [6 empty] | 49300 | 19.3 | 4 | 44600 | 4.1083 | 47600 | 14.9 | 3.5 | 35600 | 3.9667
200083810 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | RT-VE-052-* | [6 empty] | 64200 | 19.13 | 4.06 | 55700 | 5.35 | 58300 | 15.02 | 3.55 | 44400 | 4.8583
200083811 |  | NORTHSTAR SERIES | WBAHP | Water-to-Air and Brine-to-Air | RT-VE-052-* | [6 empty] | 64200 | 19.1 | 4 | 55700 | 5.35
200083815 |  | NORTHSTAR SERIES | WBAHP-CO | Water-to-Air and Brine-to-Air | RT-SE-052-* | HE-A-**-**-48 | [5 empty] | 64200 | 19.13 | 4.06 | 55700 | 5.35 | 58300 | 15.02 | 3.55 | 44400 | 4.8583
201756602 |  | NORTHERN HEAT PUMP | WBWHP | Water-to-Water and Brine-to-Water | RA-WE-036-* | [6 empty] | 40100 | 20.7 | 3.7 | 43900 | 3.3417 | 36600 | 16.1 | 3.1 | 32300 | 3.05
201756603 |  | NORTHSTAR SERIES | WBWHP | Water-to-Water and Brine-to-Water | RA-WE-036-* | [6 empty] | 40100 | 20.7 | 3.7 | 43900 | 3.3417 | 36600 | 16.1 | 3.1 | 32300 | 3.05
201756610 |  | COMFORT-AIRE | WBWHP | Water-to-Water and Brine-to-Water | HNW036 | [6 empty] | 35600 | 20.8 | 3.6 | 34700 | 2.9667
201756611 |  | CENTURY | WBWHP | Water-to-Water and Brine-to-Water | HNW036 | [6 empty] | 35600 | 20.8 | 3.6 | 34700 | 2.9667
218338500 |  | YORK | WBAHP-O | Water-to-Air and Brine-to-Air | Y5C(C/W/S)015**0**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
218338506 |  | YORK | WBAHP-O | Water-to-Air and Brine-to-Air | Y3C(C/W/S)015**0**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
218338507 |  | YORK | WBAHP-O | Water-to-Air and Brine-to-Air | Y3C(C/W/S)015**2**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
218338512 |  | YORK | WBAHP-O | Water-to-Air and Brine-to-Air | Y5C(C/W/S)015**2**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
218352923 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD024-3CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
218352924 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD024-3CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
218352925 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD024-3VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218352926 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD024-3VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218352927 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PD024-4CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
10346272 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS006 | [6 empty] | 7600 | 23.2 | 4.3 | 6400 | 0.63333
10346273 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS006 | [6 empty] | 7600 | 23.2 | 4.3 | 6400 | 0.63333
10346274 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS006 | [6 empty] | 7600 | 23.2 | 4.3 | 6400 | 0.63333
10346276 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS009 | [6 empty] | 10500 | 22.9 | 4.2 | 9500 | 0.875
10346277 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS009 | [6 empty] | 10500 | 22.9 | 4.2 | 9500 | 0.875
10346278 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS009 | [6 empty] | 10500 | 22.9 | 4.2 | 9500 | 0.875
10346377 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS006*A | [6 empty] | 7200 | 22 | 4.1 | 6100 | 0.6
10346378 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS006*A | [6 empty] | 7200 | 22 | 4.1 | 6100 | 0.6
10346379 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS006*A | [6 empty] | 7200 | 22 | 4.1 | 6100 | 0.6
10346380 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS006*9 | [6 empty] | 7200 | 22 | 4.1 | 6100 | 0.6
10346381 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS006*9 | [6 empty] | 7200 | 22 | 4.1 | 6100 | 0.6
10346382 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS006*9 | [6 empty] | 7200 | 22 | 4.1 | 6100 | 0.6
10445243 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | SDV064H1*1 | [6 empty] | 63900 | 21 | 4.5 | 58600 | 5.325 | 58300 | 16.2 | 3.8 | 46600 | 4.8583
202330469 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RN-006-2-0-BCAY-V0-10-000-A | [6 empty] | 63300 | 22.2 | 4.2 | 52200 | 5.275
202330470 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RN-006-3-0-BCAY-V0-10-000-A | [6 empty] | 63300 | 22.2 | 4.2 | 52200 | 5.275
202330471 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RN-006-4-0-BCAY-V0-10-000-A | [6 empty] | 63300 | 22.2 | 4.2 | 52200 | 5.275
202330486 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-1-0-BCBC-V0-10-000-A | [6 empty] | 48100 | 21.7 | 4.2 | 50300 | 4.0083
202330488 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-2-0-BCBC-V0-10-000-A | [6 empty] | 48100 | 21.7 | 4.2 | 50300 | 4.0083
202330490 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-3-0-BCBC-V0-10-000-A | [6 empty] | 48100 | 21.7 | 4.2 | 50300 | 4.0083
202330492 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | SB-004-4-0-BCBC-V0-10-000-A | [6 empty] | 48100 | 21.7 | 4.2 | 50300 | 4.0083
216625774 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*S3**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625775 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*S3**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625776 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*S4**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625777 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024*S4**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216625778 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*D0**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625779 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*D0**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625780 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*D2**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625781 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*D2**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625782 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*D3**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625783 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*D3**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625784 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*D4**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625785 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*D4**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216625786 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*S0**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625787 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*S0**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625788 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*S2**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625789 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*S2**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625790 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*S3**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625791 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*S3**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625792 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*S4**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625793 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030*S4**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216625794 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D0**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625795 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D0**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625796 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D0**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625797 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D2**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625798 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D2**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625799 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D2**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625800 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D3**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625801 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D3**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625802 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D3**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625803 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D4**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625804 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D4**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625805 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*D4**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625806 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S0**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625807 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S0**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625808 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S0**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625809 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S2**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625810 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S2**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625811 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S2**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625812 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S3**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625813 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S3**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625814 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S3**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625815 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S4**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625816 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S4**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625817 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036*S4**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625818 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)042*D0**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625819 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)042*D0**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625820 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)042*D0**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625821 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)042*D2**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625822 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)042*D3**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625823 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)042*D3**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
207312016 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | SDV049J1*(1,2) | [6 empty] | 50200 | 23.1 | 4.5 | 46900 | 4.1833 | 47700 | 18.2 | 3.8 | 38000 | 3.975
207312017 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | SDV064J1*1 | [6 empty] | 63900 | 21 | 4.5 | 58600 | 5.325 | 58300 | 16.2 | 3.8 | 46600 | 4.8583
207312019 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | SDV038K1*(1,2) | [6 empty] | 38200 | 23.8 | 4.5 | 33200 | 3.1833 | 36000 | 18.7 | 3.9 | 27400 | 3
207312171 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NDV/NDH026J1*(1,4) |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
207312172 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NDV/NDH038K1*(1,2,4) |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207312173 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NDV/NDH049K1*(1,2,4) |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207312176 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NDV/NDH064K1*(1,4) |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207312224 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH018J1*(1,4) | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
207312225 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH030J1*(1,4) |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
207312226 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH036K1*(1,2,4) |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207312227 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH042K1*(1,2,4) |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
207312228 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH048K1*(1,2,4) | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207312262 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH012J1*0 | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
207312263 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH018J1*0 | [6 empty] | 20600 | 24.7 | 4.3 | 18700 | 1.7167
207312265 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH030J1*(0,3) |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
207312266 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH036K1*(0,3) | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
207312267 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH042K1*(0,3) | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
207312268 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH048K1*(0,3) | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
207312271 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NSV/NSH022J1*(1,4) | [6 empty] | 21900 | 27.5 | 5 | 19500 | 1.825 | 19200 | 18.7 | 4 | 15000 | 1.6
207318097 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | LD(V,H)036A | [6 empty] | 38000 | 19.7 | 4.2 | 35500 | 3.1667 | 35100 | 15.5 | 3.6 | 26000 | 2.925
207318098 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | LD(V,H)048A | [6 empty] | 52300 | 21.8 | 4.3 | 45000 | 4.3583 | 49000 | 16.1 | 3.7 | 36000 | 4.0833
213502523 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH015A1*C/S*T |  | 15500 | 17.8 | 5.9 | 19900 | 1.2917
213502524 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH015A1*C/S*C |  | 15500 | 17.8 | 5.9 | 19900 | 1.2917
213502529 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH015E1*C/S*T |  | 15500 | 17.8 | 5.9 | 20000 | 1.2917
213502530 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH015E1*C/S*C |  | 15500 | 17.8 | 5.9 | 20000 | 1.2917
213502553 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH024E1*C/S*T |  | 24800 | 17.5 | 5.6 | 30700 | 2.0667
213502554 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH024E1*C/S*C |  | 24800 | 17.5 | 5.6 | 30700 | 2.0667
213502559 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030E1*C/S*T |  | 28300 | 17.6 | 5.7 | 35300 | 2.3583
213502560 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030E1*C/S*C |  | 28300 | 17.6 | 5.7 | 35300 | 2.3583
206438732 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-2VTN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438733 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP015-2HZ/VT*-*****B | [6 empty] | 17000 | 27.25 | 4.28 | 13000 | 1.4167 | 16200 | 19.8 | 3.63 | 11000 | 1.35
206438734 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP030-1HZ/VT*-*****B | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438735 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP030-2HZ/VT*-*****B | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438736 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP030-3HZ/VT*-*****B | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438737 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP030-4HZ/VT*-*****B | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438742 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT025-2***-*****A | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
206438743 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT025-3***-*****A | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
206438744 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | WT025-4***-*****A | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
9009391 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES035-4CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
9009394 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES049-1CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
9009404 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES049-3CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
9009406 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES049-4CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
9011292 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH018**0*1 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
9032648 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX18*-6 | [6 empty] | 20000 | 22.5 | 4.1 | 16000 | 1.6667 | 18000 | 17.1 | 3.6 | 13000 | 1.5
9033424 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX09*-6 | [6 empty] | 11500 | 26.5 | 4.5 | 8800 | 0.95833 | 10000 | 19 | 3.6 | 6800 | 0.83333
9033758 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX24*-6 | [6 empty] | 26000 | 26.5 | 4.4 | 22000 | 2.1667 | 24000 | 19 | 3.6 | 17000 | 2
9033759 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX12*-6 | [6 empty] | 13000 | 25 | 4.1 | 10500 | 1.0833 | 11800 | 18 | 3.6 | 8000 | 0.98333
9035993 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024******B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9035994 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024******B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
205754895 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JCH/V030A*W/K B | [6 empty] | 32000 | 21.6 | 4.3 | 30500 | 2.6667
205754896 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JCH/V030A*W/K C | [6 empty] | 32000 | 21.6 | 4.3 | 30500 | 2.6667
205754919 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JSH/V006A B | [6 empty] | 7400 | 25.5 | 4.4 | 6300 | 0.61667
205754920 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JSH/V006A C | [6 empty] | 7400 | 25.5 | 4.4 | 6300 | 0.61667
205754921 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | JSH/V009A B | [6 empty] | 11100 | 25.2 | 4.3 | 9400 | 0.925
205754922 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | JSH/V009A C | [6 empty] | 11100 | 25.2 | 4.3 | 9400 | 0.925
205767467 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | QEV/H/D1860 |  | 48000 | 17.3 | 5.5 | 60000 | 4 | 48000 | 35.5 | 4.3 | 60000 | 4 | 48000 | 21.6 | 3.3 | 60000 | 4
205767468 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H024B | [6 empty] | 26500 | 21.7 | 4.1 | 23000 | 2.2083 | 24600 | 16 | 3.6 | 17800 | 2.05
205767469 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H030 | [6 empty] | 32300 | 20.7 | 4.2 | 30000 | 2.6917 | 29900 | 15.7 | 3.6 | 23800 | 2.4917
205767470 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H036B | [6 empty] | 38200 | 22.3 | 4.3 | 35100 | 3.1833 | 35200 | 16.7 | 3.6 | 27300 | 2.9333
205767471 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H042 | [6 empty] | 46300 | 21.3 | 4.1 | 42300 | 3.8583 | 43100 | 16.1 | 3.4 | 33300 | 3.5917
205767472 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TYV/H048 | [6 empty] | 51800 | 20.9 | 4.4 | 45000 | 4.3167 | 48100 | 15.5 | 3.7 | 35600 | 4.0083
205767473 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TEV/H/D026B |  | 25000 | 17.4 | 6 | 31400 | 2.0833 | 28500 | 26.4 | 5.3 | 25800 | 2.375 | 26000 | 19.9 | 4.1 | 20200 | 2.1667
205767474 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TEV/H/D038B |  | 37700 | 17.9 | 5.8 | 45700 | 3.1417 | 42100 | 26.1 | 5.2 | 37900 | 3.5083 | 39000 | 20.3 | 4.4 | 29700 | 3.25
205767475 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TEV/H/D049B |  | 48600 | 16.8 | 5.1 | 56700 | 4.05 | 55000 | 25.3 | 4.6 | 46800 | 4.5833 | 49600 | 19.3 | 4 | 36400 | 4.1333
205767476 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TEV/H/D064B |  | 61500 | 16.2 | 5.4 | 77400 | 5.125
205767488 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TSH/V006A | [6 empty] | 7400 | 25.5 | 4.4 | 6300 | 0.61667
205767489 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TSH/V/D018B | [6 empty] | 21300 | 24.8 | 4.5 | 18600 | 1.775 | 19500 | 18.4 | 3.6 | 14500 | 1.625
214595631 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | M2-004-4-H-FCBC-S0-10-000-A | [6 empty] | 56200 | 23.4 | 4.3 | 44400 | 4.6833
215400192 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030J1*B*C |  | 29200 | 18.02 | 5.67 | 34500 | 2.4333
215400193 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030K3*B*C |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
215400196 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036J1*B*T |  | 39000 | 17.94 | 5.35 | 44100 | 3.25
215400197 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036K3*B*T |  | 39000 | 18.32 | 5.34 | 44100 | 3.25
215400200 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036J1*B*C |  | 39000 | 17.94 | 5.35 | 44100 | 3.25
215400201 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036K3*B*C |  | 39000 | 18.32 | 5.34 | 44100 | 3.25
215400204 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042E1*B*T |  | 43000 | 18.36 | 5.43 | 47600 | 3.5833
215400205 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F3*B*T |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
215400208 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042E1*B*C |  | 43000 | 18.36 | 5.43 | 47600 | 3.5833
215400209 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F3*B*C |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
215400212 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048E1*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400213 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F3*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400216 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048E1*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400217 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F3*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400220 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060E1*B*T |  | 64000 | 17.4 | 5.3 | 78000 | 5.3333
215400221 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F3*B*T |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
215400222 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060E1*B*C |  | 64000 | 17.4 | 5.3 | 78000 | 5.3333
215400223 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F3*B*C |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
215402546 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV007E1*B*T |  | 7100 | 17.99 | 5.49 | 8100 | 0.59167
215402548 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV009E1*B*T |  | 9200 | 17.49 | 4.98 | 11000 | 0.76667
215402550 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024E1*B*T |  | 24400 | 18.37 | 5.79 | 28000 | 2.0333
215402551 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F3*B*T |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
215402554 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024E1*B*C |  | 24400 | 18.37 | 5.79 | 28000 | 2.0333
215402555 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F3*B*C |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
215402558 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030E1*B*T |  | 29200 | 19.17 | 5.67 | 34500 | 2.4333
215402559 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F3*B*T |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
205347302 |  | BOSCH-GEO | WBWHP | Water-to-Water and Brine-to-Water | TW025-1***-****CB | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349297 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | GW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349298 |  | BRYANT | WBWHP | Water-to-Water and Brine-to-Water | GW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349299 |  | HEIL | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349300 |  | ARCOAIRE | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349301 |  | KEEPRITE | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349302 |  | TEMPSTAR | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349629 |  | COMFORTMAKER | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349630 |  | DAY & NIGHT | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349631 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | GW036W**D/G***1**2 | [6 empty] | 37200 | 21.3 | 3.7 | 35800 | 3.1 | 34100 | 16.1 | 3.05 | 28300 | 2.8417
205349632 |  | BRYANT | WBWHP | Water-to-Water and Brine-to-Water | GW036W**D/G***1**2 | [6 empty] | 37200 | 21.3 | 3.7 | 35800 | 3.1 | 34100 | 16.1 | 3.05 | 28300 | 2.8417
205349633 |  | HEIL | WBWHP | Water-to-Water and Brine-to-Water | HW036W**D/G***1**2 | [6 empty] | 37200 | 21.3 | 3.7 | 35800 | 3.1 | 34100 | 16.1 | 3.05 | 28300 | 2.8417
205349634 |  | ARCOAIRE | WBWHP | Water-to-Water and Brine-to-Water | HW036W**D/G***1**2 | [6 empty] | 37200 | 21.3 | 3.7 | 35800 | 3.1 | 34100 | 16.1 | 3.05 | 28300 | 2.8417
205349635 |  | KEEPRITE | WBWHP | Water-to-Water and Brine-to-Water | HW036W**D/G***1**2 | [6 empty] | 37200 | 21.3 | 3.7 | 35800 | 3.1 | 34100 | 16.1 | 3.05 | 28300 | 2.8417
205349636 |  | TEMPSTAR | WBWHP | Water-to-Water and Brine-to-Water | HW036W**D/G***1**2 | [6 empty] | 37200 | 21.3 | 3.7 | 35800 | 3.1 | 34100 | 16.1 | 3.05 | 28300 | 2.8417
205349637 |  | COMFORTMAKER | WBWHP | Water-to-Water and Brine-to-Water | HW036W**D/G***1**2 | [6 empty] | 37200 | 21.3 | 3.7 | 35800 | 3.1 | 34100 | 16.1 | 3.05 | 28300 | 2.8417
205349638 |  | DAY & NIGHT | WBWHP | Water-to-Water and Brine-to-Water | HW036W**D/G***1**2 | [6 empty] | 37200 | 21.3 | 3.7 | 35800 | 3.1 | 34100 | 16.1 | 3.05 | 28300 | 2.8417
205349639 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | GW060W**D/G***1**2 | [6 empty] | 58500 | 21 | 3.6 | 55900 | 4.875 | 54400 | 16.2 | 3.05 | 45400 | 4.5333
205349640 |  | BRYANT | WBWHP | Water-to-Water and Brine-to-Water | GW060W**D/G***1**2 | [6 empty] | 58500 | 21 | 3.6 | 55900 | 4.875 | 54400 | 16.2 | 3.05 | 45400 | 4.5333
205349641 |  | HEIL | WBWHP | Water-to-Water and Brine-to-Water | HW060W**D/G***1**2 | [6 empty] | 58500 | 21 | 3.6 | 55900 | 4.875 | 54400 | 16.2 | 3.05 | 45400 | 4.5333
205349642 |  | ARCOAIRE | WBWHP | Water-to-Water and Brine-to-Water | HW060W**D/G***1**2 | [6 empty] | 58500 | 21 | 3.6 | 55900 | 4.875 | 54400 | 16.2 | 3.05 | 45400 | 4.5333
205349643 |  | KEEPRITE | WBWHP | Water-to-Water and Brine-to-Water | HW060W**D/G***1**2 | [6 empty] | 58500 | 21 | 3.6 | 55900 | 4.875 | 54400 | 16.2 | 3.05 | 45400 | 4.5333
205349644 |  | TEMPSTAR | WBWHP | Water-to-Water and Brine-to-Water | HW060W**D/G***1**2 | [6 empty] | 58500 | 21 | 3.6 | 55900 | 4.875 | 54400 | 16.2 | 3.05 | 45400 | 4.5333
205349645 |  | COMFORTMAKER | WBWHP | Water-to-Water and Brine-to-Water | HW060W**D/G***1**2 | [6 empty] | 58500 | 21 | 3.6 | 55900 | 4.875 | 54400 | 16.2 | 3.05 | 45400 | 4.5333
205349647 |  | DAY & NIGHT | WBWHP | Water-to-Water and Brine-to-Water | HW060W**D/G***1**2 | [6 empty] | 58500 | 21 | 3.6 | 55900 | 4.875 | 54400 | 16.2 | 3.05 | 45400 | 4.5333
4219426 |  | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | R65HACW-P-1T-*-SDE** | [6 empty] | 62600 | 21.5 | 4.5 | 58700 | 5.2167 | 57600 | 16.8 | 3.7 | 44000 | 4.8
4219429 |  | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | RH45HACW-P-1T-*-SDE** | [6 empty] | 37800 | 19.7 | 4.2 | 35000 | 3.15 | 35000 | 16.3 | 3.6 | 26600 | 2.9167
4219430 |  | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | RH55HACW-P-1T-*-SDE** | [6 empty] | 49200 | 20 | 4.4 | 46200 | 4.1 | 44400 | 17 | 3.6 | 34700 | 3.7
4219431 |  | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | RH65HACW-P-1T-*-SDE** | [6 empty] | 61400 | 19.4 | 4.3 | 57500 | 5.1167 | 56400 | 15 | 3.5 | 42800 | 4.7
4219433 |  | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | TF45HACW-P-1T-*-SDE** | [6 empty] | 39200 | 20.8 | 4.2 | 34300 | 3.2667 | 36200 | 16.2 | 3.6 | 25200 | 3.0167
4219434 |  | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | TF55HACW-P-1T-*-SDE** | [6 empty] | 51100 | 22.5 | 4.4 | 47100 | 4.2583 | 45400 | 17.1 | 3.8 | 35400 | 3.7833
4219435 |  | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | TF65HACW-P-1T-*-SDE** | [6 empty] | 62500 | 20.9 | 4.3 | 58400 | 5.2083 | 57400 | 16.6 | 3.6 | 43800 | 4.7833
4219443 |  | NORDIC | WBAHP-CB | Water-to-Air and Brine-to-Air | RS45HACW-P-1T-* | AH-45-P-1-***** | [5 empty] | 38500 | 21.3 | 4.3 | 35700 | 3.2083 | 35100 | 16.3 | 3.6 | 27200 | 2.925
4219444 |  | NORDIC | WBAHP-CB | Water-to-Air and Brine-to-Air | RS55HACW-P-1T-* | AH-55-P-1-***** | [5 empty] | 50200 | 22.5 | 4.5 | 47200 | 4.1833 | 45400 | 17 | 3.8 | 35600 | 3.7833
4219445 |  | NORDIC | WBAHP-CB | Water-to-Air and Brine-to-Air | RS65HACW-P-1T-* | AH-65-P-1-***** | [5 empty] | 62600 | 21.5 | 4.5 | 58700 | 5.2167 | 57600 | 16.8 | 3.7 | 44000 | 4.8
4230301 |  | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W-25-HACW-P-1T-** | [6 empty] | 23200 | 21 | 3.8 | 22600 | 1.9333 | 21000 | 14.5 | 3.1 | 17300 | 1.75
4230302 |  | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W-45-HACW-P-1T-** | [6 empty] | 34000 | 20.4 | 3.9 | 32700 | 2.8333 | 30500 | 14.6 | 3.1 | 24400 | 2.5417
4230303 |  | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W-75-HACW-P-1T-** | [6 empty] | 62400 | 20.1 | 3.9 | 64500 | 5.2 | 55900 | 14.9 | 3.1 | 49000 | 4.6583
4230458 |  | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W55-HACW-P-1T-** | [6 empty] | 44700 | 20.5 | 3.7 | 45000 | 3.725 | 40300 | 15 | 3.1 | 34600 | 3.3583
4230459 |  | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W65-HACW-P-1T-** | [6 empty] | 54800 | 20.2 | 3.7 | 54900 | 4.5667 | 49600 | 15 | 3.1 | 42600 | 4.1333
4230749 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCW4024*E*01* | [6 empty] | 29600 | 22.8 | 4.2 | 23500 | 2.4667
4230751 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCW4024*F*01* | [6 empty] | 0 | 22.8 | 4.2 | 23500 | 0
4230753 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCW4024*J*01* | [6 empty] | 29600 | 22.8 | 4.2 | 23500 | 2.4667
4230922 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCW4024*K*01* | [6 empty] | 29600 | 22.8 | 4.2 | 23500 | 2.4667
215837698 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030F3*C/S*T |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
215837701 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030K3*C/S*T |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
215837707 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030F3*C/S*C |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
215837709 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMH030K3*C/S*C |  | 28300 | 17.25 | 5.59 | 35300 | 2.3583
218157959 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S2**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157960 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S3**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157961 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S3**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157962 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S3**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157963 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S4**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157964 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S4**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157965 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S4**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157966 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D0**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157967 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D0**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157968 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D0**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157969 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D2**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157970 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D3**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157971 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D3**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157972 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D3**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157973 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D4**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157974 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D4**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157975 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*D4**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157976 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S0**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157977 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S0**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157978 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S0**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157979 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S2**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157980 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S3**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157981 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S3**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157982 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S3**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157983 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S4**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157984 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S4**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157985 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042*S4**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
218157986 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)048*D0**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
215224478 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF007-1VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224479 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF009-1VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224480 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF009-1VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224481 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF012-1VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224482 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF012-1VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224483 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF015-1VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224484 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF015-1VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224485 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF018-1VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224486 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF018-1VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224487 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF007-2VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224488 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF007-2VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224489 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF009-2VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224490 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF009-2VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224491 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF012-2VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224492 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF012-2VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224493 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF015-2VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224494 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF015-2VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224495 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF018-2VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
8738074 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS048*3 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738075 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS048*3 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738076 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS048*4 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738077 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS048*4 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738078 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS048*4 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8740368 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS048*****1 |  | 49900 | 17.3 | 5.5 | 58400 | 4.1583 | 54900 | 26.4 | 4.8 | 47500 | 4.575 | 51600 | 20.1 | 3.9 | 38700 | 4.3
216419879 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
216419880 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
216419882 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)018A | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
216419883 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)018A*V | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
216419898 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
216419899 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
216419902 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
216419904 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
216419907 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
216419908 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
216419909 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
216419920 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
216419921 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
216419922 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)018A | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
216419924 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)018A*V | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
216419941 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WZ(L/R/B/P/T/K)024A | [6 empty] | 27000 | 24.1 | 4.7 | 23500 | 2.25 | 25000 | 18 | 3.9 | 18400 | 2.0833
216419942 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WZ(L/R/B/P/T/K)030A | [6 empty] | 32900 | 21.7 | 4.1 | 28700 | 2.7417 | 30200 | 15.45 | 3.6 | 23200 | 2.5167
216419944 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WZ(L/R/B/P/T/K)036A | [6 empty] | 39300 | 20.2 | 4.2 | 36300 | 3.275 | 36400 | 16.4 | 3.6 | 28600 | 3.0333
216419945 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WZ(L/R/B/P/T/K)042A | [6 empty] | 47500 | 22.8 | 4.2 | 41000 | 3.9583 | 44500 | 17.3 | 3.5 | 32500 | 3.7083
216419946 |  | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WZ(L/R/B/P/T/K)048A | [6 empty] | 52000 | 22.9 | 4.3 | 45000 | 4.3333 | 49000 | 17.7 | 3.7 | 36000 | 4.0833
216439574 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5TV036BD1**2 |  | 36000 | 17.9 | 5.6 | 42300 | 3 | 41400 | 26.9 | 5.1 | 35700 | 3.45 | 38000 | 20.1 | 4.3 | 29300 | 3.1667
216439575 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5TV048BD1**2 | [6 empty] | 52500 | 24.5 | 4.7 | 47400 | 4.375 | 49100 | 18.5 | 4.1 | 38400 | 4.0917
216727177 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024*******1**1 | FE*****36*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
216727178 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE*****36*** | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
216727179 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE*****48*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
216687118 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SZ024BD1 | W5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216687119 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SZ036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216687120 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SZ048BD1 | W5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216687121 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | W5SZ060BD1 | W5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216687731 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SS024BD1 | G5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216687732 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SS036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216687733 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SS048BD1 | G5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216687734 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SS060BD1 | G5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216687736 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SZ024BD1 | G5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216687737 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SZ036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216687738 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SZ048BD1 | G5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216687739 |  | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | G5SZ060BD1 | G5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216714606 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)006*R0**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
216714607 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)006*R2**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
216714612 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)015*R0**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
216714613 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)015*R0**4 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
216714614 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)015*R2**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
216714615 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)015*R2**4 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
216714620 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S0**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714621 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S0**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714622 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S2**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714623 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S2**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714624 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S3**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714625 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S3**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714626 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S4**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714627 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024*S4**4 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
216714636 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036*S0**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
216714637 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036*S0**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
216714638 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036*S2**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
216714639 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036*S2**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
216714640 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036*S3**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
216714641 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036*S3**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
3863923 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW025*0 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3863932 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW025*2 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3863933 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW025*4 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3863934 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW040*0 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3864041 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW040*3 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3864042 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW040*4 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3864043 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW040*5 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3864044 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW050*0 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3864046 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW050*2 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3864047 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW050*3 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3864048 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW050*4 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3864049 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW050*5 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3864050 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW060*0 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3864052 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW060*3 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3864053 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW060*4 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3864054 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | GSW060*5 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3864071 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS018*0 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
3864072 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS018*1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
3864073 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS025*0 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3864083 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS025*2 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3864084 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS025*4 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3864085 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS025*1 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3864086 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS040*0 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3864087 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS040*1 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3864088 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS040*4 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3864089 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS040*3 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3864090 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS040*5 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3870360 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS050*1 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3870361 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS050*2 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3870362 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS050*0 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3870363 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS050*3 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3870364 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS050*4 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3870365 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS050*5 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3870366 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS060*0 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3870367 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS060*1 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3870368 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS060*3 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3870369 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS060*4 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3870370 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HS060*5 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
215224827 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR24V/H**C******1 | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224828 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR24V/H**N******1 | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224829 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR24V/H**N******1 | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224830 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR24V/H**N******1 | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224831 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR24V/H**N******1 | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224832 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR24V/H**N******1 | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224833 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR24V/H**N******1 | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224834 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**C******1 | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224835 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**C******1 | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224836 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**C******1 | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224837 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**C******1 | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224838 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**C******1 | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224839 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**C******1 | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224840 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**N******1 | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224841 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**N******1 | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224842 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**N******1 | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224843 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**N******1 | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224844 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**N******1 | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224845 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR30V/H**N******1 | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224846 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**C******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224847 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**C******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224848 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**C******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224849 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**C******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224850 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**C******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224851 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**C******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224852 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**N******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224853 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**N******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224854 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**N******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224855 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HBR36V/H**N******1 | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
216569713 |  | GeoCool | WBAHP | Water-to-Air and Brine-to-Air | GCHPV/H/D024BT**A*** | [6 empty] | 28500 | 27.4 | 4.8 | 24500 | 2.375 | 26400 | 17.95 | 4.2 | 19000 | 2.2
216569714 |  | GeoCool | WBAHP | Water-to-Air and Brine-to-Air | GCHPV/H/D036BT**A*** | [6 empty] | 41500 | 27.2 | 4.9 | 36600 | 3.4583 | 39000 | 17.86 | 4.2 | 28500 | 3.25
216569715 |  | GeoCool | WBAHP | Water-to-Air and Brine-to-Air | GCHPV/H/D048BT**A*** | [6 empty] | 54800 | 26 | 4.9 | 48200 | 4.5667 | 51500 | 16.65 | 4.2 | 37000 | 4.2917
216621309 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)009*R0**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
216621310 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)012*R0**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
216621311 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)015*R0**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216621312 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*R0**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216621313 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S0**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216621314 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*S0**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216621315 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S0**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216621316 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S0**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216621317 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S0**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216621323 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*D0**1 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
216621324 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*D0**4 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
216621325 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D0**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621326 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D2**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621327 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D3**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621328 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D4**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621329 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D0**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621330 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D2**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621331 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D3**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621332 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D4**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621333 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D0**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621334 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D3**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621335 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D0**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621336 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D3**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621337 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D0**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621338 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D3**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621339 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D0**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621340 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D3**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621341 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D0**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621342 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D3**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621343 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D0**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621344 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D3**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621345 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D0**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621346 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D3**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621347 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D0**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621348 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D3**4 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216621349 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*D0**1 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
218353298 |  | SKYMARK | WBAHP-O | Water-to-Air and Brine-to-Air | PK009-1***-******E | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
218353299 |  | SKYMARK | WBAHP-O | Water-to-Air and Brine-to-Air | PK009-2***-******E | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
218353306 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-1HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353307 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-1HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353308 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-1VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353309 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-1VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353310 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-2HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353311 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-2HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353312 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-2VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353313 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-2VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353314 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ036-1VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218353315 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ036-1VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218353316 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ036-2VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218353317 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ036-2VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218353318 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ048-1VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
218353319 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ048-1VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218353320 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ060-1VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
218353321 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ060-1VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
215415870 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
215415871 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
215415872 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
215415873 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
215415874 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)018A | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
215415875 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)018A | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
215415876 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)018A*V | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
215415877 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)018A*V | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
215415878 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)024A | [6 empty] | 27000 | 24.1 | 4.7 | 23500 | 2.25 | 25000 | 18 | 3.9 | 18400 | 2.0833
215415879 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)024A | [6 empty] | 27000 | 24.1 | 4.7 | 23500 | 2.25 | 25000 | 18 | 3.9 | 18400 | 2.0833
215415880 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)030A | [6 empty] | 32900 | 21.7 | 4.1 | 28700 | 2.7417 | 30200 | 15.45 | 3.6 | 23200 | 2.5167
215415881 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)030A | [6 empty] | 32900 | 21.7 | 4.1 | 28700 | 2.7417 | 30200 | 15.45 | 3.6 | 23200 | 2.5167
215415882 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)036A | [6 empty] | 39300 | 20.2 | 4.2 | 36300 | 3.275 | 36400 | 16.4 | 3.6 | 28600 | 3.0333
215415883 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)036A | [6 empty] | 39300 | 20.2 | 4.2 | 36300 | 3.275 | 36400 | 16.4 | 3.6 | 28600 | 3.0333
215415884 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)042A | [6 empty] | 47500 | 22.8 | 4.2 | 41000 | 3.9583 | 44500 | 17.3 | 3.5 | 32500 | 3.7083
215415885 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)042A | [6 empty] | 47500 | 22.8 | 4.2 | 41000 | 3.9583 | 44500 | 17.3 | 3.5 | 32500 | 3.7083
215415886 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)048A | [6 empty] | 52000 | 22.9 | 4.3 | 45000 | 4.3333 | 49000 | 17.7 | 3.7 | 36000 | 4.0833
215415887 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MZ(L/R/B/P/T/K)048A | [6 empty] | 52000 | 22.9 | 4.3 | 45000 | 4.3333 | 49000 | 17.7 | 3.7 | 36000 | 4.0833
215415909 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | ME(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 5.7 | 29000 | 2.1083 | 28600 | 26.1 | 5 | 23700 | 2.3833 | 26300 | 19.9 | 4.1 | 17800 | 2.1917
215415910 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | ME(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 5.7 | 29000 | 2.1083 | 28600 | 26.1 | 5 | 23700 | 2.3833 | 26300 | 19.9 | 4.1 | 17800 | 2.1917
215415911 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | ME(L/R/B/P/D/N/T/K)036A |  | 38000 | 17.5 | 5.5 | 43100 | 3.1667 | 42000 | 25 | 4.9 | 36000 | 3.5 | 39200 | 19.5 | 4.2 | 28400 | 3.2667
215415912 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | ME(L/R/B/P/D/N/T/K)036A |  | 38000 | 17.5 | 5.5 | 43100 | 3.1667 | 42000 | 25 | 4.9 | 36000 | 3.5 | 39200 | 19.5 | 4.2 | 28400 | 3.2667
215415913 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | ME(L/R/B/P/D/N/T/K)048A |  | 51000 | 18 | 5.6 | 58700 | 4.25 | 56000 | 27 | 4.9 | 47300 | 4.6667 | 52000 | 20.2 | 4.1 | 37600 | 4.3333
215415914 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | ME(L/R/B/P/D/N/T/K)048A |  | 51000 | 18 | 5.6 | 58700 | 4.25 | 56000 | 27 | 4.9 | 47300 | 4.6667 | 52000 | 20.2 | 4.1 | 37600 | 4.3333
215415915 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | ME(L/R/B/P/D/N/T/K)060A |  | 61800 | 16.9 | 5.3 | 67300 | 5.15 | [5 empty] | 62600 | 18.7 | 3.9 | 44300 | 5.2167
215415916 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | ME(L/R/B/P/D/N/T/K)060A |  | 61800 | 16.9 | 5.3 | 67300 | 5.15 | [5 empty] | 62600 | 18.7 | 3.9 | 44300 | 5.2167
215270421 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024*******1**1 | FE****003*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
215270422 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE****003*** | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
215270423 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE****005*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
215270424 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1**1 | FE****005*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
215270425 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060*******1**1 | FE****006*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
215270427 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024*******1**1 | FE****003*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
215270428 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE****003*** | [5 empty] | 40300 | 19.75 | 4.2 | 36700 | 3.3583 | 36800 | 15.4 | 3.4 | 26900 | 3.0667
215270429 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ036*******1**2 | FE****005*** | [5 empty] | 41400 | 22.75 | 4.4 | 36700 | 3.45 | 39200 | 17.6 | 3.4 | 27400 | 3.2667
215270430 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1**1 | FE****005*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
215270431 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060*******1**1 | FE****006*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
215278610 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W3A(V/H)024BD1**1 | [6 empty] | 25700 | 21.3 | 4.6 | 23000 | 2.1417 | 23200 | 15.7 | 4 | 19000 | 1.9333
215278611 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W3A(V/H)036BD1**1 | [6 empty] | 37500 | 20.5 | 4.3 | 35400 | 3.125 | 35600 | 15.8 | 3.7 | 26800 | 2.9667
215278612 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W3A(V/H)048BD1**1 | [6 empty] | 51200 | 19.6 | 4.2 | 46000 | 4.2667 | 49000 | 16 | 3.7 | 37300 | 4.0833
215278613 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W3A(V/H)060BD1**1 | [6 empty] | 63000 | 18.8 | 4 | 55800 | 5.25 | 59500 | 15.2 | 3.4 | 45800 | 4.9583
215285739 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 5.7 | 29000 | 2.1083 | 28600 | 26.1 | 5 | 23700 | 2.3833 | 26300 | 19.9 | 4.1 | 17800 | 2.1917
215285740 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)036A |  | 38000 | 17.5 | 5.5 | 43100 | 3.1667 | 42000 | 25 | 4.9 | 36000 | 3.5 | 39200 | 19.5 | 4.2 | 28400 | 3.2667
215285741 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)048A |  | 51000 | 18 | 5.6 | 58700 | 4.25 | 56000 | 27 | 4.9 | 47300 | 4.6667 | 52000 | 20.2 | 4.1 | 37600 | 4.3333
215285742 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)060A |  | 61800 | 16.9 | 5.3 | 67300 | 5.15 | [5 empty] | 62600 | 18.7 | 3.9 | 44300 | 5.2167
215287172 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)024BD1**1 | [6 empty] | 25700 | 21.3 | 4.6 | 23000 | 2.1417 | 23200 | 15.7 | 4 | 19000 | 1.9333
215287173 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)036BD1**1 | [6 empty] | 37500 | 20.5 | 4.3 | 35400 | 3.125 | 35600 | 15.8 | 3.7 | 26800 | 2.9667
215287174 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)048BD1**1 | [6 empty] | 51200 | 19.6 | 4.2 | 46000 | 4.2667 | 49000 | 16 | 3.7 | 37300 | 4.0833
215287175 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)060BD1**1 | [6 empty] | 63000 | 18.8 | 4 | 55800 | 5.25 | 59500 | 15.2 | 3.4 | 45800 | 4.9583
215287179 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)024BD1**1 | [6 empty] | 25700 | 21.3 | 4.6 | 23000 | 2.1417 | 23200 | 15.7 | 4 | 19000 | 1.9333
215287180 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)036BD1**1 | [6 empty] | 37500 | 20.5 | 4.3 | 35400 | 3.125 | 35600 | 15.8 | 3.7 | 26800 | 2.9667
215287181 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)048BD1**1 | [6 empty] | 51200 | 19.6 | 4.2 | 46000 | 4.2667 | 49000 | 16 | 3.7 | 37300 | 4.0833
215287182 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)060BD1**1 | [6 empty] | 63000 | 18.8 | 4 | 55800 | 5.25 | 59500 | 15.2 | 3.4 | 45800 | 4.9583
215310891 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G7A(V/H)024BV1**2 |  | 22200 | 16.9 | 6 | 39200 | 1.85 | 26300 | 37.8 | 5 | 32100 | 2.1917 | 24100 | 23.6 | 4.1 | 24800 | 2.0083
215310892 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G7A(V/H)036BV1**2 |  | 33500 | 15.3 | 5.4 | 51800 | 2.7917 | 38200 | 28.7 | 4.7 | 41900 | 3.1833 | 35800 | 18.1 | 3.8 | 32900 | 2.9833
215310893 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G7A(V/H)048BV1**2 |  | 41500 | 16 | 4.8 | 66000 | 3.4583 | 49000 | 27.4 | 4.2 | 54500 | 4.0833 | 45000 | 18.9 | 3.6 | 42000 | 3.75
215310895 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G7A(V/H)060BV1**2 |  | 50000 | 15.3 | 4.7 | 79800 | 4.1667 | 60700 | 23.4 | 4.3 | 66000 | 5.0583 | 56000 | 17.1 | 3.5 | 51700 | 4.6667
215310990 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S7A(V/H)024BV1**2 |  | 22200 | 16.9 | 6 | 39200 | 1.85 | 26300 | 37.8 | 5 | 32100 | 2.1917 | 24100 | 23.6 | 4.1 | 24800 | 2.0083
215310991 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S7A(V/H)036BV1**2 |  | 33500 | 15.3 | 5.4 | 51800 | 2.7917 | 38200 | 28.7 | 4.7 | 41900 | 3.1833 | 35800 | 18.1 | 3.8 | 32900 | 2.9833
215310992 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S7A(V/H)048BV1**2 |  | 41500 | 16 | 4.8 | 66000 | 3.4583 | 49000 | 27.4 | 4.2 | 54500 | 4.0833 | 45000 | 18.9 | 3.6 | 42000 | 3.75
215310994 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S7A(V/H)060BV1**2 |  | 50000 | 15.3 | 4.7 | 79800 | 4.1667 | 60700 | 23.4 | 4.3 | 66000 | 5.0583 | 56000 | 17.1 | 3.5 | 51700 | 4.6667
217465611 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KB2CWRB | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
217465612 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KB2CWBB | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
217465613 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KB2BWRB | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
217465614 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KB2BWBB | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
217531660 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)006A | [6 empty] | 7600 | 30 | 4.8 | 6200 | 0.63333 | 6700 | 20 | 3.6 | 4600 | 0.55833
217531661 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)009A | [6 empty] | 10500 | 28 | 4.6 | 9000 | 0.875 | 9700 | 19 | 3.7 | 7000 | 0.80833
217531662 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)012A | [6 empty] | 13600 | 26.2 | 4.3 | 12200 | 1.1333 | 12400 | 18.9 | 3.6 | 9200 | 1.0333
217531663 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)018A | [6 empty] | 22000 | 28.1 | 4.9 | 18900 | 1.8333 | 20100 | 19.5 | 4.1 | 14500 | 1.675
215399856 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV015A1*B*T |  | 16100 | 19.51 | 5.82 | 18600 | 1.3417
215399857 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV015J1*B*T |  | 16100 | 18.01 | 5.72 | 18600 | 1.3417
215399860 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV015A1*B*C |  | 16100 | 19.51 | 5.82 | 18600 | 1.3417
215399861 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV015J1*B*C |  | 16100 | 18.01 | 5.72 | 18600 | 1.3417
215399864 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV019J1*B*T |  | 19600 | 17.18 | 5.23 | 23500 | 1.6333
215399866 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV019J1*B*C |  | 19600 | 17.18 | 5.23 | 23500 | 1.6333
215399868 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042J1*B*T |  | 42570 | 18.17 | 5.38 | 47124 | 3.5475
215399869 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042K3*B*T |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
215399872 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042J1*B*C |  | 42570 | 18.17 | 5.38 | 47124 | 3.5475
215399873 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042K3*B*C |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
215399876 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048K3*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
217735651 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030(U/V/W/Y)**3*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217735652 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030(U/V/W/Y)**4*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
217735653 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030(U/V/W/Y)**4*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217735654 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030(U/V/W/Y)**5*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
217735655 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030(U/V/W/Y)**5*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217735656 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030(U/V/W/Y)**6*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
217735657 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030(U/V/W/Y)**6*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217735658 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036(U/V/W/Y)**3*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217735659 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036(U/V/W/Y)**3*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
217735660 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036(U/V/W/Y)**4*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217735661 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036(U/V/W/Y)**4*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
217735662 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036(U/V/W/Y)**5*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217735663 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036(U/V/W/Y)**5*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
217735664 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036(U/V/W/Y)**6*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217735665 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036(U/V/W/Y)**6*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
217735666 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042(U/V/W/Y)**3*(A-H)** | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
217735667 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042(U/V/W/Y)**3*(J-R)** | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
217735668 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042(U/V/W/Y)**5*(A-H)** | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
217735669 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042(U/V/W/Y)**5*(J-R)** | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
217735670 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042(U/V/W/Y)**6*(A-H)** | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
217735671 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042(U/V/W/Y)**6*(J-R)** | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
217735672 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048(U/V/W/Y)**3*(A-H)** | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
217735673 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048(U/V/W/Y)**3*(J-R)** | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
217735674 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048(U/V/W/Y)**5*(A-H)** | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
217735675 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048(U/V/W/Y)**5*(J-R)** | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
217735676 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048(U/V/W/Y)**6*(A-H)** | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
217735677 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048(U/V/W/Y)**6*(J-R)** | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
217735679 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*060(U/V/W/Y)**3*(J-R)** | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
217735681 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*060(U/V/W/Y)**5*(J-R)** | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
217735683 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*060(U/V/W/Y)**6*(J-R)** | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
217752676 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024K1*B*T |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
217752678 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024K1*B*C |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
207177436 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0157 | [6 empty] | 16600 | 23 | 4.3 | 15400 | 1.3833 | 15500 | 17.4 | 3.6 | 12300 | 1.2917
207177437 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG018A | [6 empty] | 19300 | 23.5 | 4.4 | 18400 | 1.6083 | 18100 | 17.7 | 3.6 | 14300 | 1.5083
207177438 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0187 | [6 empty] | 19300 | 23.5 | 4.4 | 18400 | 1.6083 | 18100 | 17.7 | 3.6 | 14300 | 1.5083
207177439 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG024A | [6 empty] | 26600 | 24.4 | 4.6 | 25300 | 2.2167 | 24800 | 18.5 | 3.8 | 19600 | 2.0667
207177440 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG024B | [6 empty] | 26600 | 24.4 | 4.6 | 25300 | 2.2167 | 24800 | 18.5 | 3.8 | 19600 | 2.0667
207177441 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0244 | [6 empty] | 26600 | 24.4 | 4.6 | 25300 | 2.2167 | 24800 | 18.5 | 3.8 | 19600 | 2.0667
207177442 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0247 | [6 empty] | 26600 | 24.4 | 4.6 | 25300 | 2.2167 | 24800 | 18.5 | 3.8 | 19600 | 2.0667
207177443 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG030A | [6 empty] | 32300 | 23 | 4.5 | 30800 | 2.6917 | 30200 | 17.7 | 3.7 | 23300 | 2.5167
207177444 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG030B | [6 empty] | 32300 | 23 | 4.5 | 30800 | 2.6917 | 30200 | 17.7 | 3.7 | 23300 | 2.5167
207177445 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0304 | [6 empty] | 32300 | 23 | 4.5 | 30800 | 2.6917 | 30200 | 17.7 | 3.7 | 23300 | 2.5167
207177446 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0307 | [6 empty] | 32300 | 23 | 4.5 | 30800 | 2.6917 | 30200 | 17.7 | 3.7 | 23300 | 2.5167
3059237 |  | WaterFurnace | WBAHP-O | Water-to-Air and Brine-to-Air | NCC/NCW/NCS/NCE15*0 | [6 empty] | 16200 | 22 | 4.1 | 14000 | 1.35
3627926 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH015**0*0 | [6 empty] | 16000 | 24 | 4.1 | 15000 | 1.3333
3627927 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH015**2*0 | [6 empty] | 16000 | 24 | 4.1 | 15000 | 1.3333
206438893 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***5/EA* | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
216743662 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP060-4VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216759673 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7SZ030BV1**F | W7BM030BN1**2 | 31600 | 15.1 | 5.1 | 48300 | 2.6333 | 35800 | 27.8 | 4.5 | 40700 | 2.9833 | 32400 | 18.1 | 3.4 | 31700 | 2.7
216759674 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7SZ042BV1**F | W7BM042BN1**2 | 38100 | 15.6 | 4.9 | 55900 | 3.175 | 44400 | 28.8 | 4.4 | 51300 | 3.7 | 41600 | 19.3 | 3.8 | 41400 | 3.4667
216759675 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7SZ048BV1**F | W7BM048BN1**2 | [5 empty] | 56600 | 21 | 3.8 | 69600 | 4.7167 | 48000 | 14 | 3.2 | 53500 | 4
216759816 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SS024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216759817 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216759818 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SS048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216759819 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SS060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216759821 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | G5SS024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216759822 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | G5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216759823 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | G5SS048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216759824 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | G5SS060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216759826 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SZ024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216759827 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216759828 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SZ048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216759829 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SZ060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216759831 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | G5SZ024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216759832 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | G5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
216759833 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | G5SZ048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
216759834 |  | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | G5SZ060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
216767321 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVT024* | [6 empty] | 27600 | 23.8 | 4.6 | 23900 | 2.3 | 25800 | 18.6 | 4 | 19400 | 2.15
216767322 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVT030* | [6 empty] | 34100 | 23.1 | 4.6 | 30300 | 2.8417 | 32200 | 18.4 | 3.8 | 24300 | 2.6833
216767323 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVT036* | [6 empty] | 40000 | 22.8 | 4.6 | 36900 | 3.3333 | 37400 | 17.7 | 3.9 | 29500 | 3.1167
216767324 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVT042* | [6 empty] | 49200 | 24 | 4.6 | 40100 | 4.1 | 45900 | 18.5 | 3.9 | 32400 | 3.825
216767325 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVT048* | [6 empty] | 53600 | 24.5 | 4.9 | 48500 | 4.4667 | 50300 | 18.8 | 4 | 38500 | 4.1917
216767326 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT024* | [6 empty] | 29200 | 25.7 | 5.3 | 23400 | 2.4333 | 27100 | 19.9 | 4.3 | 19000 | 2.2583
216767327 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT036* | [6 empty] | 42300 | 27.9 | 5.4 | 35500 | 3.525 | 39700 | 21 | 4.3 | 27900 | 3.3083
216767328 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TYT048* | [6 empty] | 55200 | 24.9 | 5 | 46500 | 4.6 | 51900 | 19.2 | 4.1 | 36700 | 4.325
216767329 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVT060* | [6 empty] | 64200 | 22 | 4.5 | 57500 | 5.35 | 60900 | 17.6 | 3.8 | 46300 | 5.075
214063739 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH012**2*0 | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
214063740 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH015**0*0 | [6 empty] | 16700 | 26 | 4.5 | 15500 | 1.3917 | 15000 | 18 | 3.8 | 12000 | 1.25
214063741 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH015**0*1 | [6 empty] | 16700 | 27 | 4.7 | 15500 | 1.3917 | 15000 | 18.8 | 4 | 12000 | 1.25
214063742 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH015**0*4 | [6 empty] | 16700 | 27 | 4.7 | 15500 | 1.3917 | 15000 | 18.8 | 4 | 12000 | 1.25
214063743 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH015**2*0 | [6 empty] | 16700 | 26 | 4.5 | 15500 | 1.3917 | 15000 | 18 | 3.8 | 12000 | 1.25
214063744 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH015**2*1 | [6 empty] | 16700 | 27 | 4.7 | 15500 | 1.3917 | 15000 | 18.8 | 4 | 12000 | 1.25
214063745 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH015**2*4 | [6 empty] | 16700 | 27 | 4.7 | 15500 | 1.3917 | 15000 | 18.8 | 4 | 12000 | 1.25
214063746 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH018**0*0 | [6 empty] | 20600 | 24.7 | 4.3 | 18700 | 1.7167
214063747 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH018**0*1 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
214063748 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH018**0*4 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
214063749 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH018**2*0 | [6 empty] | 20600 | 24.7 | 4.3 | 18700 | 1.7167
214063750 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH018**2*1 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
214063751 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH018**2*4 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
214063752 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**0*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
214063753 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**0*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214063754 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**0*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214063755 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**2*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
214063756 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**2*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214063757 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**2*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214063758 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**0*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214063759 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**0*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214063760 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**2*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214063761 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**2*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214063762 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**0*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
214063763 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**0*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214063764 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**0*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214063765 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**2*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
214063766 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**2*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214063767 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**2*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214063768 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**0*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
214063769 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**0*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214063770 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**0*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214063771 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**2*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
214063772 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**2*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214063773 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**2*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214063774 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**0*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214063775 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**0*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214063776 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**2*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214063777 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**2*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214063778 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**0*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214063779 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**0*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214063780 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**0*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
214063781 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**0*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
214063785 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
214063786 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
215837835 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH030F3*C/S*C |  | 29500 | 18.91 | 5.88 | 34500 | 2.4583
215837836 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH030J1*C/S*C |  | 29500 | 18.14 | 5.64 | 34500 | 2.4583
215837837 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH030K3*C/S*C |  | 29500 | 18.91 | 5.88 | 34500 | 2.4583
215837843 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036F3*C/S*T |  | 39000 | 18.66 | 5.06 | 44600 | 3.25
215837844 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036J1*C/S*T |  | 39000 | 18.2 | 5.07 | 44600 | 3.25
215837845 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036K3*C/S*T |  | 39000 | 18.59 | 5.06 | 44600 | 3.25
215837851 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036F3*C/S*C |  | 39000 | 18.66 | 5.06 | 44600 | 3.25
215837853 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036J1*C/S*C |  | 39000 | 18.2 | 5.07 | 44600 | 3.25
215837854 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH036K3*C/S*C |  | 39000 | 18.59 | 5.06 | 44600 | 3.25
215837859 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042F3*C/S*T |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
215837860 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042J1*C/S*T |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
215837862 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042K3*C/S*T |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
215837867 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042F3*C/S*C |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
215837869 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042J1*C/S*C |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
215837870 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH042K3*C/S*C |  | 42600 | 18.03 | 5.29 | 47000 | 3.55
218472100 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD007-1VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218472101 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD007-1VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218472102 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD009-1VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218472103 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD009-1VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218472104 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD012-1VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
218472105 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD012-1VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
218472106 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD015-1VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
218472107 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD015-1VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
218472108 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD018-1VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
218472109 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD018-1VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
218472110 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD007-2VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218472111 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD007-2VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
218472112 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD009-2VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218472113 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD009-2VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
218472114 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD012-2VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
218472115 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD012-2VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
218472116 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD015-2VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
218472117 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD015-2VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
218472118 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD018-2VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
218472119 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD018-2VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
218472120 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-2VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218472121 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-2VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218472122 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-2VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
218472123 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-2VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
218353651 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-1HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353652 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-1HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353653 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-1VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353654 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-1VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353655 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-2HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353656 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-2HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353657 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-2VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353658 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-2VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353659 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-3HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353660 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-3HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353661 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-3VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353662 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-3VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353663 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-4HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353664 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-4HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353665 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-4VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353666 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ024-4VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353667 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ036-1VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218353668 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ036-1VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218353669 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ036-2VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218353670 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ036-2VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218353671 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ036-3VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218353672 |  | JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | DQ036-3VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
217602189 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042C**5*(A-H)** | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
217602190 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042C**5*(J-R)** | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
217602191 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042C**6*(A-H)** | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
217602192 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042C**6*(J-R)** | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
217602193 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048C**5*(A-H)** | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
217602194 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048C**5*(J-R)** | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
217602195 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048C**6*(A-H)** | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
217602196 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048C**6*(J-R)** | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
217602198 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*060C**5*(J-R)** | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
217602200 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*060C**6*(J-R)** | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
217602219 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**3*(A-H)** | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
217602221 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**3*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
217602222 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**3*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
217602224 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**3*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217602225 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**3*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217602227 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**3*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
217602228 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042C**3*(A-H)** | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
217602230 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042C**3*(J-R)** | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
217602231 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048C**3*(A-H)** | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
217602233 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*048C**3*(J-R)** | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
217602236 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*060C**3*(J-R)** | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
217642876 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)006*R0**6 | [6 empty] | 9000 | 25 | 4.2 | 8000 | 0.75
217642879 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)015*R0**1 | [6 empty] | 16500 | 23 | 4.2 | 13500 | 1.375
217642881 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)024*S0**1 | [6 empty] | 26000 | 23 | 4.5 | 24000 | 2.1667 | 24800 | 17.8 | 3.7 | 18500 | 2.0667
217642883 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)036*S0**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
217642884 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S0**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
7409789 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH009**0*0 | [6 empty] | 10800 | 22.2 | 4.4 | 10600 | 0.9
7409859 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH009**2*0 | [6 empty] | 10800 | 22.2 | 4.4 | 10600 | 0.9
7409937 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH012**0*0 | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
7410008 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH012**2*0 | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
7410095 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH015**0*0 | [6 empty] | 16700 | 26 | 4.5 | 15500 | 1.3917 | 15000 | 18 | 3.8 | 12000 | 1.25
7410164 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH015**0*1 | [6 empty] | 16700 | 27 | 4.7 | 15500 | 1.3917 | 15000 | 18.8 | 4 | 12000 | 1.25
7410223 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH015**0*4 | [6 empty] | 16700 | 27 | 4.7 | 15500 | 1.3917 | 15000 | 18.8 | 4 | 12000 | 1.25
7410291 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH015**2*0 | [6 empty] | 16700 | 26 | 4.5 | 15500 | 1.3917 | 15000 | 18 | 3.8 | 12000 | 1.25
7410355 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH015**2*1 | [6 empty] | 16700 | 27 | 4.7 | 15500 | 1.3917 | 15000 | 18.8 | 4 | 12000 | 1.25
7410435 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH015**2*4 | [6 empty] | 16700 | 27 | 4.7 | 15500 | 1.3917 | 15000 | 18.8 | 4 | 12000 | 1.25
7410522 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH018**0*0 | [6 empty] | 20600 | 24.7 | 4.3 | 18700 | 1.7167
7410657 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH018**0*4 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
7410717 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH018**2*0 | [6 empty] | 20600 | 24.7 | 4.3 | 18700 | 1.7167
7410825 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH018**2*1 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
7410908 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH018**2*4 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
7411002 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**0*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
7411100 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH024**0*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
215224606 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*009***4*(J-R)** | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224607 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*012***3*(A-H)** | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224608 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*012***3*(J-R)** | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224609 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*012***4*(A-H)** | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224610 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*012***4*(J-R)** | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224611 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*015***3*(A-H)** | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224612 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*015***3*(J-R)** | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224613 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*015***4*(A-H)** | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224614 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*015***4*(J-R)** | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224615 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*018***3*(A-H)** | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224616 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*018***3*(J-R)** | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224617 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*018***4*(A-H)** | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224618 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*018***4*(J-R)** | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224619 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***3*(A-H)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224620 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***3*(J-R)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224621 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***4*(A-H)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224622 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***4*(J-R)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224623 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***5*(A-H)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224624 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***5*(J-R)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224625 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***6*(A-H)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224626 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024***6*(J-R)** | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224627 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***3*(A-H)** | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224628 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***3*(J-R)** | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224629 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***4*(A-H)** | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224630 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***4*(J-R)** | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224631 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***5*(A-H)** | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224632 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***5*(J-R)** | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224633 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***6*(A-H)** | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224634 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030***6*(J-R)** | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224635 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***3*(A-H)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224636 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***3*(J-R)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224637 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***4*(A-H)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224638 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***4*(J-R)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224639 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***5*(A-H)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224640 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***5*(J-R)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224641 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***6*(A-H)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224642 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036***6*(J-R)** | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224643 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042***3*(A-H)** | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224644 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042***3*(J-R)** | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224645 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*042***5*(A-H)** | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
218472124 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-2VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
218472125 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-2VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
218472126 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-2CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
218472127 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-2CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
218472128 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-2CFC-*****A | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
218472129 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-2CFN-*****A | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
218472130 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-2CFC-*****A | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
218472131 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-2CFN-*****A | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
218472132 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-1VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218472133 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-1VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218472134 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-1VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
218472135 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-1VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
218472136 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-1VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
218472137 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-1VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
218472138 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD042-1VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
218472139 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD042-1VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
218472140 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD048-1VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
218472141 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD048-1VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
218472148 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-1CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
218472149 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD024-1CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
218472150 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-1CFC-*****A | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
218472151 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD030-1CFN-*****A | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
218472152 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-1CFC-*****A | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
218472153 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD036-1CFN-*****A | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
218472154 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD042-1CFC-*****A | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
218472155 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD042-1CFN-*****A | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
218472156 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD048-1CFC-*****A | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
218472157 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AD048-1CFN-*****A | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
215224078 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-4CFC-*****A | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
215224079 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-2CFN-*****A | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
215224080 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-4CFN-*****A | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
215224081 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-4CFC-*****A | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
215224082 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-4CFN-*****A | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
215224083 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-4CFC-*****A | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
215224084 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-4CFN-*****A | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
215224086 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF060-4CFN-*****A | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
215224089 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-1VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224090 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-3VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224091 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-1VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224092 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-3VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224093 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-1VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224094 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-3VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224095 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-1VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224096 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-3VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224097 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-1VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224098 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-3VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224099 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-1VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224100 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-3VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224101 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-1VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224102 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-3VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224103 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-1VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224104 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-3VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224105 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-1VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224106 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-3VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224107 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-1VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224108 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-3VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224121 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-1CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
215224122 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-3CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
215224123 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-1CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
215224124 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-3CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
215224125 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-1CFC-*****A | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
215224126 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-3CFC-*****A | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
215224127 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-1CFN-*****A | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
215224128 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-3CFN-*****A | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
215224129 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-1CFC-*****A | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
215224130 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-3CFC-*****A | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
215224131 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-1CFN-*****A | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
215224132 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF036-3CFN-*****A | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
215224133 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-1CFC-*****A | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
216801935 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***6/FB |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
207348707 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348708 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348709 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348710 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*3*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348711 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*3*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348712 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*3*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348713 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348714 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348715 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348716 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*0*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348717 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*0*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348718 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*0*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348719 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348720 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348721 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348722 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348723 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348724 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348725 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348726 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348727 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348728 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348729 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348730 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348731 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348732 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348733 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
5646343 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT024D | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646344 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT024D | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646345 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT024D | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646346 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT024D2 | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646347 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT024D2 | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646348 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT024D2 | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646349 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT024D3 | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646350 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT024D3 | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646351 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT024D3 | [6 empty] | 29600 | 26.9 | 5.2 | 24700 | 2.4667 | 27200 | 20.3 | 4.3 | 19800 | 2.2667
5646371 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT036D | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646372 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT036D | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646373 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT036D | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646374 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT036D2 | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646375 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT036D2 | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646376 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT036D2 | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646377 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GXT036D3 | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646378 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HXT036D3 | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646379 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TXT036D3 | [6 empty] | 42200 | 24 | 5.1 | 37000 | 3.5167 | 38900 | 18.3 | 4.2 | 29200 | 3.2417
5646381 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GCT036D | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646382 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HCT036D | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
5646383 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TCT036D | [6 empty] | 41700 | 23.5 | 5 | 36700 | 3.475 | 38600 | 18.3 | 4.1 | 28600 | 3.2167
206438789 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP030-1HZ/VT*-*****B | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438801 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT025-2***-*****A | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
206438802 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT025-4***-*****A | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
206438803 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT025-3***-*****A | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
207318100 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | LD(V,H)060B | [6 empty] | 64100 | 20.7 | 4 | 56500 | 5.3417 | 59900 | 16.5 | 3.4 | 45300 | 4.9917
207318101 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | LD(V,H)024A | [6 empty] | 25100 | 20.6 | 4.4 | 23500 | 2.0917 | 23100 | 15.6 | 3.8 | 18900 | 1.925
207323881 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDZ026H1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207323882 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDZ026H1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207323883 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDS026H1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207323884 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDS026H1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207323885 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDZ038J1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207323886 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDZ038J1 | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207323887 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDS038J1 | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207323888 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDZ049J1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207323889 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDZ049J1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207323890 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDS049H1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207323891 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDS049H1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207323892 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDZ064J1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207323893 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDZ064J1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207323894 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDS064H1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207323895 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NDS064H1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207323900 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NDS038J1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207323901 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ022H1* | SAH022* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207323902 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ030H1* | SAH030* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207323903 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ036J1* | SAH036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207323904 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ042J1* | SAH042* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207323905 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ048J1* | SAH048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
207323906 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NSZ048J1* | SRAA048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
207323907 |  | WaterFurnace | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ060J1* | SAH060* | [5 empty] | 61700 | 23.6 | 4.3 | 54500 | 5.1417 | 56300 | 17.7 | 3.7 | 44000 | 4.6917
207323908 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NSZ060J1* | SRAA060* | [5 empty] | 61700 | 23.6 | 4.3 | 54500 | 5.1417 | 56300 | 17.7 | 3.7 | 44000 | 4.6917
207323910 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NSZ022H1* | SRAA026* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207323911 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NSZ030H1* | SRAA026* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207323912 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NSZ036J1* | SRAA036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207323913 |  | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | NSZ042J1* | SRAA048* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207324064 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NVV/NVH036C1*(1,2) |  | 32300 | 17.7 | 5.3 | 51000 | 2.6917 | 38000 | 31.2 | 4.5 | 41700 | 3.1667 | 35800 | 21.6 | 3.5 | 32900 | 2.9833
207324065 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NVV/NVH048C1*1 |  | 40700 | 16.9 | 4.9 | 67000 | 3.3917 | 49000 | 30 | 4 | 55200 | 4.0833 | 45000 | 20 | 3.4 | 43500 | 3.75
207324066 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NVV/NVH060C1*1 |  | 50000 | 15.9 | 4.9 | 79000 | 4.1667 | 60000 | 27.1 | 4.3 | 66000 | 5 | 56000 | 19.1 | 3.4 | 51700 | 4.6667
207335086 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW018*1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
207335087 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW025*1 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
207335088 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*1 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
207335089 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*1 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
207335090 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*1 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
207335091 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NEW040*1* | [6 empty] | 33000 | 20.1 | 4 | 40000 | 2.75 | 30600 | 16.1 | 3.3 | 34000 | 2.55
215415792 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)042A*VB | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
215415793 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)042A*VC | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
215415794 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*B | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215415795 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*C | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215415796 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*VB | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
215415797 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*VC | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
215415814 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)015A*B | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
215415815 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)015A*C | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
215415816 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)015A*VB | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
215415817 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)015A*VC | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
215415818 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)018A*B | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
215415819 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)018A*C | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
215415820 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)018A*VB | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
215415821 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)018A*VC | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
215415822 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)024A*B | [6 empty] | 27000 | 24.1 | 4.7 | 23500 | 2.25 | 25000 | 18 | 3.9 | 18400 | 2.0833
215415823 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)024A*C | [6 empty] | 27000 | 24.1 | 4.7 | 23500 | 2.25 | 25000 | 18 | 3.9 | 18400 | 2.0833
215415824 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)030A*B | [6 empty] | 32900 | 21.7 | 4.1 | 28700 | 2.7417 | 30200 | 15.45 | 3.6 | 23200 | 2.5167
215415825 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)030A*C | [6 empty] | 32900 | 21.7 | 4.1 | 28700 | 2.7417 | 30200 | 15.45 | 3.6 | 23200 | 2.5167
215415826 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)036A*B | [6 empty] | 39300 | 20.2 | 4.2 | 36300 | 3.275 | 36400 | 16.4 | 3.6 | 28600 | 3.0333
215415827 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)036A*C | [6 empty] | 39300 | 20.2 | 4.2 | 36300 | 3.275 | 36400 | 16.4 | 3.6 | 28600 | 3.0333
215415828 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)042A*B | [6 empty] | 47500 | 22.8 | 4.2 | 41000 | 3.9583 | 44500 | 17.3 | 3.5 | 32500 | 3.7083
215415829 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)042A*C | [6 empty] | 47500 | 22.8 | 4.2 | 41000 | 3.9583 | 44500 | 17.3 | 3.5 | 32500 | 3.7083
215415830 |  | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)048A*B | [6 empty] | 52000 | 22.9 | 4.3 | 45000 | 4.3333 | 49000 | 17.7 | 3.7 | 36000 | 4.0833
215415831 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BY(L/R/B/P/T/K)048A*C | [6 empty] | 52000 | 22.9 | 4.3 | 45000 | 4.3333 | 49000 | 17.7 | 3.7 | 36000 | 4.0833
215415834 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
215415835 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
215415836 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
215415837 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
215415840 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
215415841 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MC(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
218353063 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-3HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353064 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-3HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353065 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-3VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353066 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-3VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353067 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-4HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353068 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-4HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353069 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-4VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218353070 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ024-4VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218353071 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ036-3VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218353072 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ036-3VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218353073 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ036-4VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
218353074 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ036-4VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
218353075 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ048-3VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
218353076 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ048-3VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
218353077 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PQ048-4VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
211594262 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG0704 |  | 63800 | 17.3 | 5.4 | 82100 | 5.3167
211594263 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG024B |  | 24700 | 16.8 | 5.5 | 32100 | 2.0583 | 27500 | 24.4 | 4.9 | 25700 | 2.2917 | 25900 | 19.2 | 3.9 | 19400 | 2.1583
211594264 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG0244 |  | 24700 | 16.8 | 5.5 | 32100 | 2.0583 | 27500 | 24.4 | 4.9 | 25700 | 2.2917 | 25900 | 19.2 | 3.9 | 19400 | 2.1583
211594265 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG0247 |  | 24700 | 16.8 | 5.5 | 32100 | 2.0583 | 27500 | 24.4 | 4.9 | 25700 | 2.2917 | 25900 | 19.2 | 3.9 | 19400 | 2.1583
211594266 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG036B |  | 33000 | 17.3 | 5.9 | 40900 | 2.75 | 37100 | 25.1 | 5.1 | 32900 | 3.0917 | 34500 | 19.7 | 4.1 | 25500 | 2.875
211594267 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG0364 |  | 33000 | 17.3 | 5.9 | 40900 | 2.75 | 37100 | 25.1 | 5.1 | 32900 | 3.0917 | 34500 | 19.7 | 4.1 | 25500 | 2.875
211594268 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG0367 |  | 33000 | 17.3 | 5.9 | 40900 | 2.75 | 37100 | 25.1 | 5.1 | 32900 | 3.0917 | 34500 | 19.7 | 4.1 | 25500 | 2.875
211594269 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG048B |  | 45200 | 17.9 | 6.1 | 55200 | 3.7667 | 50400 | 26.4 | 5.3 | 44400 | 4.2 | 46600 | 20.6 | 4.3 | 34500 | 3.8833
211594270 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG0484 |  | 45200 | 17.9 | 6.1 | 55200 | 3.7667 | 50400 | 26.4 | 5.3 | 44400 | 4.2 | 46600 | 20.6 | 4.3 | 34500 | 3.8833
211594271 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG060B |  | 52100 | 17.6 | 6 | 63900 | 4.3417 | 56600 | 24.8 | 5.2 | 51700 | 4.7167 | 53900 | 19.9 | 4.2 | 39800 | 4.4917
211594272 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXHG0604 |  | 52100 | 17.6 | 6 | 63900 | 4.3417 | 56600 | 24.8 | 5.2 | 51700 | 4.7167 | 53900 | 19.9 | 4.2 | 39800 | 4.4917
215748031 |  | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | R-55-HACW-X-1T-*-*DE** | [6 empty] | 48000 | 22.2 | 4.5 | 47000 | 4 | 43900 | 16 | 3.8 | 35600 | 3.6583
215748227 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SMT(S,M)24A*Q |  | 25000 | 17.6 | 5.1 | 28000 | 2.0833 | [5 empty] | 25900 | 20.4 | 3.7 | 18000 | 2.1583
218157947 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D2**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
218157948 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D3**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
218157949 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D3**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
218157950 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D3**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
218157951 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D4**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
218157952 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D4**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
218157953 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*D4**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
218157954 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S0**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157955 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S0**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157956 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S0**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157957 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S2**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
218157958 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036*S2**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
9910584 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS030*****1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910585 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*****1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910586 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*****1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910587 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS030*2***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910588 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*2***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910589 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*2***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910590 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS030*3***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910591 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*3***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910592 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*3***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910593 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS030*A***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910594 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*A***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910595 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*A***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
205973166 |  | Enertech | WBAHP | Water-to-Air and Brine-to-Air | ERE036D | [6 empty] | 39800 | 21.7 | 4.4 | 35400 | 3.3167
205973167 |  | Enertech | WBAHP | Water-to-Air and Brine-to-Air | ERE048D | [6 empty] | 54800 | 21.1 | 4.1 | 48500 | 4.5667
205973771 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEV/H024D | [6 empty] | 26500 | 21.7 | 4.1 | 23000 | 2.2083 | 24600 | 16 | 3.6 | 17800 | 2.05
205973772 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEV/H024D | [6 empty] | 26500 | 21.7 | 4.1 | 23000 | 2.2083 | 24600 | 16 | 3.6 | 17800 | 2.05
205973773 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEV/H030D | [6 empty] | 32300 | 20.7 | 4.2 | 30000 | 2.6917 | 29900 | 15.7 | 3.6 | 23800 | 2.4917
205973774 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEV/H030D | [6 empty] | 32300 | 20.7 | 4.2 | 30000 | 2.6917 | 29900 | 15.7 | 3.6 | 23800 | 2.4917
205973775 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEV/H042D | [6 empty] | 46300 | 21.3 | 4.1 | 42300 | 3.8583 | 43100 | 16.1 | 3.4 | 33300 | 3.5917
205973776 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEV/H042D | [6 empty] | 46300 | 21.3 | 4.1 | 42300 | 3.8583 | 43100 | 16.1 | 3.4 | 33300 | 3.5917
205973777 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEV/H048D | [6 empty] | 51800 | 20.9 | 4.4 | 45000 | 4.3167 | 48100 | 15.5 | 3.7 | 35600 | 4.0083
205973778 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEV/H048D | [6 empty] | 51800 | 20.9 | 4.4 | 45000 | 4.3167 | 48100 | 15.5 | 3.7 | 35600 | 4.0083
5220675 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH030B*E |  | 30000 | 17.3 | 5.8 | 33600 | 2.5 | [5 empty] | 31300 | 20.1 | 4.1 | 21600 | 2.6083
5220676 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH030B*F |  | 30000 | 17.3 | 5.8 | 33600 | 2.5 | [5 empty] | 31300 | 20.1 | 4.1 | 21600 | 2.6083
5220677 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH030B*J |  | 30000 | 17.3 | 5.8 | 33600 | 2.5 | [5 empty] | 31300 | 20.1 | 4.1 | 21600 | 2.6083
5220678 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH030B*K |  | 30000 | 17.3 | 5.8 | 33600 | 2.5 | [5 empty] | 31300 | 20.1 | 4.1 | 21600 | 2.6083
5220681 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WGSV/WGSH036B*E |  | 37300 | 19.2 | 6 | 40800 | 3.1083 | [5 empty] | 38500 | 22 | 4.3 | 26200 | 3.2083
202449784 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH036**0*1 | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
202449785 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH036**2*1 | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
202449786 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH036**3*1 | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
202449787 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH036**4*1 | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
202449788 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH036**0*4 | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
202449789 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH036**2*4 | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
202449790 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH036**3*4 | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
202449791 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH036**4*4 | [6 empty] | 40000 | 23 | 4.4 | 35600 | 3.3333
202449795 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH042**0*1 | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
202449796 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH042**3*1 | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
202449797 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH042**4*1 | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
202449798 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH042**0*4 | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
202449799 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH042**3*4 | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
202449800 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH042**4*4 | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
201907621 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*0*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907622 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907623 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907624 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907625 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907626 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907627 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
201907628 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
201907629 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
201907630 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
201907631 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
201907632 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
201907633 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
201926779 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
201926783 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
201926787 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
201930362 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
206422417 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HBH/V015*W/K | [6 empty] | 16500 | 25 | 4.5 | 14100 | 1.375 | 14800 | 18 | 3.6 | 11000 | 1.2333
206422418 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HBH/V015*W/K | [6 empty] | 16500 | 25 | 4.5 | 14100 | 1.375 | 14800 | 18 | 3.6 | 11000 | 1.2333
206422419 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HBH/V018*W/K | [6 empty] | 21500 | 23.6 | 4.5 | 17800 | 1.7917 | 19500 | 17.1 | 3.7 | 14100 | 1.625
206422420 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HBH/V018*W/K | [6 empty] | 21500 | 23.6 | 4.5 | 17800 | 1.7917 | 19500 | 17.1 | 3.7 | 14100 | 1.625
206422421 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HBH/V024*W/K | [6 empty] | 27000 | 21.5 | 4.3 | 23500 | 2.25
206422422 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HBH/V024*W/K | [6 empty] | 27000 | 21.5 | 4.3 | 23500 | 2.25
206422423 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HBH/V030*W/K | [6 empty] | 32000 | 21.6 | 4.3 | 30500 | 2.6667
206422424 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HBH/V030*W/K | [6 empty] | 32000 | 21.6 | 4.3 | 30500 | 2.6667
206438717 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP007-1HZ/VT*-*****B | [6 empty] | 8400 | 25.1 | 4.7 | 6900 | 0.7
206438718 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP007-2HZ/VT*-*****B | [6 empty] | 8400 | 25.1 | 4.7 | 6900 | 0.7
206438719 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP009-1HZ/VT*-*****B | [6 empty] | 10500 | 24.35 | 4.5 | 9000 | 0.875
206438720 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP009-2HZ/VT*-*****B | [6 empty] | 10500 | 24.35 | 4.5 | 9000 | 0.875
206438721 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-0HZC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438722 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-0HZN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438723 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-0VTC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438724 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-0VTN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438725 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-1HZC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438726 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-1HZN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438727 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-1VTC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438728 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-1VTN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438729 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-2HZC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438730 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-2HZN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438731 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP012-2VTC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
215224134 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-3CFC-*****A | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
215224135 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-1CFN-*****A | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
215224136 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF042-3CFN-*****A | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
215224137 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-1CFC-*****A | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
215224138 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-3CFC-*****A | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
215224139 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-1CFN-*****A | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
215224140 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF048-3CFN-*****A | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
215224143 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF060-1CFN-*****A | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
215224144 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF060-3CFN-*****A | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
215224293 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF007-1VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224294 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF007-1VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224295 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF009-1VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224296 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF009-1VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224297 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF012-1VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224298 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF012-1VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224299 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF015-1VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224300 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF015-1VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224301 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF018-1VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224302 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF018-1VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224303 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF024-1CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
215224304 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF024-1CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
215224305 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF024-1VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224306 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF024-1VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224307 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF030-1CFC-*****A | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
215224308 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF030-1CFN-*****A | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
215224309 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF030-1VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224310 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF030-1VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224311 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF036-1CFC-*****A | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
215224312 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF036-1CFN-*****A | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
215224313 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF036-1VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224314 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF036-1VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224315 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF042-1CFC-*****A | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
215224316 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF042-1CFN-*****A | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
215224317 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF042-1VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224318 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF042-1VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224319 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF048-1CFC-*****A | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
215224320 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF048-1CFN-*****A | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
215224321 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF048-1VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224322 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF048-1VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224324 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RF060-1CFN-*****A | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
215224477 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF007-1VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
216979809 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979810 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979811 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979812 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979813 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979814 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979815 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979816 |  | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
211580597 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW040*5 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
211580598 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW050*0 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
211580599 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW050*2 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
211580600 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW050*3 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
211580601 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW050*4 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
211580602 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW050*5 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
211580603 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW060*0 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
211580604 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW060*3 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
211580605 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW060*4 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
211580606 |  | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YHSW060*5 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
211594118 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG006A | [6 empty] | 8100 | 21.3 | 4.1 | 7500 | 0.675
211594119 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG009A | [6 empty] | 9600 | 23.8 | 4.7 | 9100 | 0.8 | 8900 | 17.8 | 3.7 | 6700 | 0.74167
211594120 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG012A | [6 empty] | 13300 | 24.2 | 4.6 | 12400 | 1.1083 | 12100 | 17.6 | 3.7 | 9400 | 1.0083
211594121 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG015A | [6 empty] | 16600 | 23 | 4.3 | 15400 | 1.3833 | 15500 | 17.4 | 3.6 | 12300 | 1.2917
211594122 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG018A | [6 empty] | 19300 | 23.5 | 4.4 | 18400 | 1.6083 | 18100 | 17.7 | 3.6 | 14300 | 1.5083
211594123 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG024A | [6 empty] | 26600 | 24.4 | 4.6 | 25300 | 2.2167 | 24800 | 18.5 | 3.8 | 19600 | 2.0667
211594124 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG030A | [6 empty] | 32300 | 23 | 4.5 | 30800 | 2.6917 | 30200 | 17.7 | 3.7 | 23300 | 2.5167
211594125 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG036A | [6 empty] | 39900 | 22.6 | 4.4 | 36900 | 3.325 | 37300 | 17.6 | 3.6 | 28700 | 3.1083
211594126 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG042A | [6 empty] | 45500 | 22 | 4.2 | 45600 | 3.7917
211594127 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG048A | [6 empty] | 55700 | 22.8 | 4.2 | 50000 | 4.6417
211594128 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEHG060A | [6 empty] | 61700 | 21.3 | 4.1 | 61200 | 5.1417
211594129 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG009A | [6 empty] | 8800 | 25 | 4.8 | 8200 | 0.73333 | 8300 | 18.8 | 3.7 | 6100 | 0.69167
211594130 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG012A | [6 empty] | 13700 | 27.9 | 5 | 12300 | 1.1417 | 12300 | 19.5 | 4 | 9300 | 1.025
211594131 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG015A | [6 empty] | 17000 | 25.8 | 4.6 | 15300 | 1.4167 | 15800 | 19 | 3.8 | 12100 | 1.3167
211594132 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG018A |  | 18800 | 17.6 | 5.7 | 23600 | 1.5667 | 21100 | 28.7 | 4.9 | 18800 | 1.7583 | 19600 | 20.6 | 4.1 | 14600 | 1.6333
211594133 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG024A |  | 24600 | 17.4 | 5.7 | 32100 | 2.05 | 27400 | 27.2 | 5 | 25900 | 2.2833 | 25600 | 20.3 | 3.9 | 19500 | 2.1333
211594134 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG030A |  | 31400 | 17.8 | 5.8 | 38400 | 2.6167 | 35000 | 27.2 | 5 | 31000 | 2.9167 | 32800 | 20.7 | 4.1 | 23600 | 2.7333
211594135 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG036A |  | 35500 | 17.6 | 5.8 | 43100 | 2.9583 | 39400 | 26.5 | 5 | 35000 | 3.2833 | 37100 | 20.4 | 4.1 | 27200 | 3.0917
211594136 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG042A |  | 38400 | 18 | 6.4 | 48000 | 3.2 | 43300 | 27.5 | 5.5 | 38500 | 3.6083 | 40500 | 21.1 | 4.3 | 29400 | 3.375
211594137 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG048A |  | 45400 | 17.7 | 6.1 | 55600 | 3.7833 | 50400 | 26.4 | 5.3 | 44800 | 4.2 | 47100 | 20.3 | 4.3 | 34600 | 3.925
211594138 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG060A |  | 55700 | 17.5 | 5.9 | 69000 | 4.6417 | 60800 | 25.7 | 5.1 | 55900 | 5.0667 | 57700 | 20.1 | 4.1 | 42900 | 4.8083
211594139 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXHG070A |  | 63800 | 17.3 | 5.4 | 82100 | 5.3167
8993504 |  | YORK BY JOHNSON CONTROLS | WBAHP-O | Water-to-Air and Brine-to-Air | YCC/YCW/YCS/YCE15*0 | [6 empty] | 16200 | 22 | 4.1 | 14000 | 1.35
8993505 |  | YORK BY JOHNSON CONTROLS | WBAHP-O | Water-to-Air and Brine-to-Air | YCC/YCW/YCS/YCE15*2 | [6 empty] | 16200 | 22 | 4.1 | 14000 | 1.35
8993797 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | ES049-1CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
8993798 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | ES049-3CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
8993799 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | ES049-4CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
9008839 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | ES025-1CF/HZ/VT*-*****A | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
9008840 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | ES025-2CF/HZ/VT*-*****A | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
9008841 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | ES035-1CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
9008842 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | ES035-3CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
9008843 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | ES035-4CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
9009353 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES025-1CF/HZ/VT*-*****A | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
9009366 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES025-2CF/HZ/VT*-*****A | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
9009369 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES035-1CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
9009382 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES035-3CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
202921913 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-3HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921914 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-4HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921915 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921952 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921953 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-3HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921954 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-4HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921956 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921957 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-1VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921958 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-3VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921959 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-4VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921960 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP036-1VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922686 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***3/CA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922689 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***5/EA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922692 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***6/FA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922695 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
207349388 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH038**3*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207349389 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH038**2*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207349390 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH038**4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207349391 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH038**0*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207349392 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH038**3*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207349393 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH038**4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207349394 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH038**2*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207349395 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH049**0*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207349396 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH049**3*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207349397 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH049**4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207349398 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH049**0*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207349399 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH049**3*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207349400 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH049**4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207349401 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349402 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349403 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**4*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349404 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**4*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349405 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**3*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207349406 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH064**0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207530615 |  | BOSCH | WBAHP-O | Water-to-Air and Brine-to-Air | CA009-1*C-*****D | [6 empty] | 10000 | 22.1 | 4.25 | 8600 | 0.83333
207542447 |  | FHP | WBAHP-O | Water-to-Air and Brine-to-Air | CA009-1*C-*****D | [6 empty] | 10000 | 22.1 | 4.25 | 8600 | 0.83333
207549518 |  | CARRIER | WBAHP-O | Water-to-Air and Brine-to-Air | 50PEC09***E3/CF | [6 empty] | 10000 | 22.1 | 4.25 | 8600 | 0.83333
215400184 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024J1*B*C |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
215400185 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024K3*B*C |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
215400188 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030J1*B*T |  | 29200 | 18.02 | 5.67 | 34500 | 2.4333
215400189 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030K3*B*T |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
218471794 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD012-1VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
218471795 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD012-1VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
218471796 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD015-1VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
218471797 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD015-1VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
218471798 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD018-1VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
218471799 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD018-1VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
218471800 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD024-1CFC-*****A | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
218471801 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD024-1CFN-*****A | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
218471802 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD024-1VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218471803 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD024-1VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
218471804 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD030-1CFC-*****A | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
218471805 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD030-1CFN-*****A | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
218471806 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD030-1VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
218471807 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD030-1VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
218471808 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD036-1CFC-*****A | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
218471809 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD036-1CFN-*****A | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
218471810 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD036-1VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
218471811 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD036-1VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
218471812 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD042-1CFC-*****A | [6 empty] | 43500 | 20.4 | 4.1 | 39000 | 3.625 | 41500 | 16 | 3.6 | 31000 | 3.4583
218471813 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD042-1CFN-*****A | [6 empty] | 42500 | 20 | 4 | 38000 | 3.5417 | 40500 | 15.7 | 3.5 | 30500 | 3.375
218471814 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD042-1VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
218471815 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD042-1VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
218471816 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD048-1CFC-*****A | [6 empty] | 50500 | 20.4 | 4.1 | 46500 | 4.2083 | 47500 | 16 | 3.6 | 37000 | 3.9583
218471817 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD048-1CFN-*****A | [6 empty] | 49500 | 20 | 4 | 45500 | 4.125 | 46500 | 15.7 | 3.5 | 36000 | 3.875
218471818 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD048-1VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
218471819 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD048-1VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
218471821 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QD060-1CFN-*****A | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
218471830 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ024-1VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218471831 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ024-3VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218471832 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ024-4VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218471833 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ024-1VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218471834 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ024-3VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218471835 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ024-4VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
218471836 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QQ024-1HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
218471837 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AQ024-3HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216625485 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S2**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625486 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S3**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625487 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S4**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625488 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S0**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625489 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S2**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625490 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S3**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625491 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S4**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216625492 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D2**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625493 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D4**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625494 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D2**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625495 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D4**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625496 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D2**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625497 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D4**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216625498 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S3**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625499 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S0**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625500 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S3**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625501 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S4**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625502 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S0**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625503 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S3**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625504 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S4**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216625505 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D4**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625506 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D2**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216625507 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*D4**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
3706370 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS018**2*1 | [6 empty] | 20600 | 24 | 4.4 | 17500 | 1.7167 | 18500 | 17.5 | 3.7 | 13700 | 1.5417
3706371 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS023**0*1 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
3706373 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS023**2*1 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
3706374 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS023**3*1 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
3706375 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS023**4*1 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
3706376 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS024**0*1 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
3706377 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS024**2*1 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
3706378 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS024**3*1 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
3706379 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS024**4*1 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
3706380 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS030**0*1 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
3706381 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS030**2*1 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
3706382 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS030**3*1 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
3706383 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS030**4*1 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
3706384 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS036**0*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417
3706385 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS036**3*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417
3706387 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS036**4*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417
3706391 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS042**0*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
3706392 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS042**3*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
3706393 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS042**4*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
3706394 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS048**0*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
3706395 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS048**3*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
3706396 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZS048**4*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
3811671 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH024**2*1 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
3811673 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH024**3*1 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
3837472 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW018*0 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
3837729 |  | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NSW018*1 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
3837731 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW025*0 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3837732 |  | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NSW025*1 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3837733 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW025*2 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
3838431 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*0 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3838432 |  | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NSW040*1 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3838433 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*3 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3838434 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*4 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3838435 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*5 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
3838437 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*0 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3838438 |  | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NSW050*1 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3838439 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*2 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3838440 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*3 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3838441 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*4 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3838442 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*5 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
3838483 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*0 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3838484 |  | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NSW060*1 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3838485 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*3 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3838500 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*4 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
3838508 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*5 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
4504310 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP012-1HZ/VT | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
4509712 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP024-1HZ/VT | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
4510474 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP030-1HZ/VT | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
4651271 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USH023**0*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651272 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USH023**2*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651273 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USH023**3*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651274 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USH023**4*4 | [6 empty] | 25400 | 23 | 4.3 | 21900 | 2.1167
4651339 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH024**0*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651340 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH024**2*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651341 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH024**3*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651342 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH024**4*4 | [6 empty] | 26400 | 23.4 | 4.5 | 22300 | 2.2 | 24400 | 17.5 | 3.8 | 17500 | 2.0333
4651403 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH030**0*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
4651404 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH030**2*4 | [6 empty] | 32900 | 23.9 | 4.4 | 28300 | 2.7417 | 29000 | 18.3 | 3.8 | 22800 | 2.4167
8738042 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVT060*A | [6 empty] | 64200 | 21.1 | 4.4 | 57500 | 5.35 | 60900 | 16.9 | 3.7 | 46300 | 5.075
8738051 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS042 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738052 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS042 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738053 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS042 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738054 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS042*2 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738055 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS042*2 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738056 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS042*2 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738057 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS042*3 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738058 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS042*3 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738059 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS042*3 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738060 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS042*4 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738061 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS042*4 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738062 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS042*4 | [6 empty] | 46700 | 24.4 | 4.7 | 39200 | 3.8917 | 43600 | 18.6 | 3.8 | 32000 | 3.6333
8738067 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS048 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738068 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS048 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738069 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS048 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738070 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS048*2 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738071 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS048*2 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738072 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS048*2 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
8738073 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS048*3 | [6 empty] | 53400 | 22.6 | 4.4 | 48100 | 4.45 | 50500 | 17.6 | 3.6 | 39600 | 4.2083
214839122 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CL042-1HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839123 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CL042-1VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839124 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CL042-3HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839125 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CL042-3VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839126 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CL042-4HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839127 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | CL042-4VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
216714645 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)042*S0**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
216714646 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)042*S3**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
216714647 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)042*S3**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
216714648 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)042*S4**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
216714649 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G3A(V/H)042*S4**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
216719392 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | W5WZ024BS1* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
216719393 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | W5WZ048BS1* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
216719394 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | W5WZ060BS1* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
207335092 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NEW050*1* | [6 empty] | 47000 | 20.1 | 3.9 | 54900 | 3.9167 | 44500 | 16.1 | 3.3 | 45000 | 3.7083
207335134 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 101/102J012**1*0***** | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
207335135 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 101/102J018**1*(1,4)***** | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
207335136 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 101/102J030**1*(1,4)***** |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
207335137 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 101/102K036**1*(1,2,4)***** |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
207335138 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 101/102K042**1*(1,2,4)***** |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
207335139 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 101/102K048**1*(1,2,4) | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207335142 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | 101/102J026**1*(1,4)***** |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
215399772 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV015A1*C/S*T |  | 15500 | 17.51 | 5.09 | 17000 | 1.2917
215399776 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV015A1*C/S*C |  | 15500 | 17.51 | 5.09 | 17000 | 1.2917
215399790 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024J1*C/S*T |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215399791 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024K3*C/S*T |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215399794 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024J1*C/S*C |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215399795 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024K3*C/S*C |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
215268358 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V3A(V/H)042*S4**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
215268359 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V3A(V/H)042*S4**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
215268663 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)009*R0**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
215268664 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)012*R0**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
215268665 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)015*R0**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
215268666 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)018*R0**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
215268667 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S0**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268668 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S0**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268669 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S0**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268670 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S0**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268671 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S0**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268674 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)009*R2**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
215268675 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)012*R2**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
215268676 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)015*R2**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
215268677 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)015*R0**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
215268678 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)015*R2**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
215268679 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)018*R2**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
215268680 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)018*R0**4 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
215268681 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)018*R2**4 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
215268682 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S2**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268683 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S3**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268684 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S4**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268685 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S0**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268686 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S2**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268687 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S3**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268688 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S4**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268689 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S3**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268690 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S0**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268691 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S3**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268692 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S3**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268693 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S0**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268694 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S3**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268695 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S0**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268696 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S3**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268697 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S3**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268698 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S0**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268699 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S3**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268700 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S0**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268701 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S3**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
217351787 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*N******1 | F(C,T)MA5*36**** | [5 empty] | 39000 | 21.3 | 4.5 | 35800 | 3.25 | 36000 | 16.6 | 3.7 | 27600 | 3
217351788 |  | ARCOAIRE | WBAHP-CB | Water-to-Air and Brine-to-Air | HS036SR*C******1 | F(C,T)MA5*48**** | [5 empty] | 41000 | 22.8 | 4.8 | 34800 | 3.4167 | 39000 | 18.5 | 3.7 | 27400 | 3.25
202147015 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS036*2***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202147016 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS036*3***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202147017 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS036*A***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202147018 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS042 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147019 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS042*2 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147020 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS042*3 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147021 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS042*4 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147022 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS042*****1 | [6 empty] | 43700 | 25.6 | 4.5 | 37500 | 3.6417 | 40700 | 19.2 | 3.8 | 30200 | 3.3917
202147023 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS042*2***1 | [6 empty] | 43700 | 25.6 | 4.5 | 37500 | 3.6417 | 40700 | 19.2 | 3.8 | 30200 | 3.3917
202147024 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS042 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147025 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS042*2 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147026 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS042*3 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147027 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS042*4 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147028 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS042*****1 | [6 empty] | 43700 | 25.6 | 4.5 | 37500 | 3.6417 | 40700 | 19.2 | 3.8 | 30200 | 3.3917
202147029 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS042*2***1 | [6 empty] | 43700 | 25.6 | 4.5 | 37500 | 3.6417 | 40700 | 19.2 | 3.8 | 30200 | 3.3917
202147030 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS042 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147031 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS042*2 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147032 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS042*3 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147033 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS042*4 | [6 empty] | 44200 | 23.7 | 4.5 | 38900 | 3.6833 | 41100 | 17.9 | 3.7 | 31700 | 3.425
202147034 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS042*****1 | [6 empty] | 43700 | 25.6 | 4.5 | 37500 | 3.6417 | 40700 | 19.2 | 3.8 | 30200 | 3.3917
202147035 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS042*2***1 | [6 empty] | 43700 | 25.6 | 4.5 | 37500 | 3.6417 | 40700 | 19.2 | 3.8 | 30200 | 3.3917
202147036 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS048 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147037 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS048*2 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147038 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS048*3 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147039 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS048*4 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147040 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS048*****1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
202147041 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS048*2***1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
202147042 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS048*3***1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
202147043 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS048 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147044 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS048*2 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147045 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS048*3 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147046 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS048*4 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147047 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS048*****1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
202147048 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS048*2***1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
202147049 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS048*3***1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
202147050 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS048 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147051 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS048*2 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147052 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS048*3 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147053 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS048*4 | [6 empty] | 52100 | 22.4 | 4.2 | 46800 | 4.3417
202147054 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS048*****1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
202147055 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS048*2***1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
202147056 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS048*3***1 | [6 empty] | 52900 | 22.6 | 4.3 | 45600 | 4.4083 | 49300 | 17.4 | 3.6 | 36200 | 4.1083
206703396 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931140/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703397 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931141/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206703398 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931230/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703399 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931231/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703400 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931240/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703401 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931241/1 | [6 empty] | 32057 | 18.57 | 3.47 | 62244 | 2.6714 | 29297 | 13.72 | 2.87 | 48688 | 2.4414
206703402 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931330/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703403 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931331/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703404 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931340/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206703405 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 931341/1 | [6 empty] | 48967 | 18.75 | 3.22 | 86016 | 4.0806 | 44726 | 13.95 | 2.81 | 70898 | 3.7272
206710951 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921130/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206710952 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 921131/1 | [6 empty] | 23901 | 18.6 | 3.35 | 46261 | 1.9917 | 21781 | 13.65 | 2.83 | 36024 | 1.8151
206722530 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | TRH/V006A*W/K | [6 empty] | 7000 | 24 | 4.2 | 6300 | 0.58333
206726680 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UVV/UVH024**0*1 |  | 23500 | 18.7 | 5.9 | 29300 | 1.9583 | 27300 | 37.4 | 5 | 23400 | 2.275 | 25500 | 23.6 | 3.9 | 17800 | 2.125
206726691 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UVV/UVH024**3*1 |  | 23500 | 18.7 | 5.9 | 29300 | 1.9583 | 27300 | 37.4 | 5 | 23400 | 2.275 | 25500 | 23.6 | 3.9 | 17800 | 2.125
206726692 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UVV/UVH024**4*1 |  | 23500 | 18.7 | 5.9 | 29300 | 1.9583 | 27300 | 37.4 | 5 | 23400 | 2.275 | 25500 | 23.6 | 3.9 | 17800 | 2.125
206726812 |  | GEOCOMFORT | WBAHP-C | Water-to-Air and Brine-to-Air | GBS018 | EED018 | 20900 | 18 | 6 | 23400 | 1.7417 | 24200 | 30.5 | 5 | 18600 | 2.0167 | 22100 | 21.7 | 3.9 | 14500 | 1.8417
206726813 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBS018 | EAD018 | 20700 | 17.7 | 6 | 23300 | 1.725 | 23700 | 29.8 | 5 | 18500 | 1.975 | 21800 | 21.1 | 3.9 | 14400 | 1.8167
206726814 |  | HYDRON MODULE | WBAHP-C | Water-to-Air and Brine-to-Air | HBS018 | EED018 | 20900 | 18 | 6 | 23400 | 1.7417 | 24200 | 30.5 | 5 | 18600 | 2.0167 | 22100 | 21.7 | 3.9 | 14500 | 1.8417
206726815 |  | HYDRON MODULE | WBAHP-CB | Water-to-Air and Brine-to-Air | HBS018 | EAD018 | 20700 | 17.7 | 6 | 23300 | 1.725 | 23700 | 29.8 | 5 | 18500 | 1.975 | 21800 | 21.1 | 3.9 | 14400 | 1.8167
206726816 |  | TETCO | WBAHP-C | Water-to-Air and Brine-to-Air | TBS018 | EED018 | 20900 | 18 | 6 | 23400 | 1.7417 | 24200 | 30.5 | 5 | 18600 | 2.0167 | 22100 | 21.7 | 3.9 | 14500 | 1.8417
206726817 |  | TETCO | WBAHP-CB | Water-to-Air and Brine-to-Air | TBS018 | EAD018 | 20700 | 17.7 | 6 | 23300 | 1.725 | 23700 | 29.8 | 5 | 18500 | 1.975 | 21800 | 21.1 | 3.9 | 14400 | 1.8167
206726818 |  | GEOCOMFORT | WBAHP-C | Water-to-Air and Brine-to-Air | GBS018*2 | EED018 | 20900 | 18 | 6 | 23400 | 1.7417 | 24200 | 30.5 | 5 | 18600 | 2.0167 | 22100 | 21.7 | 3.9 | 14500 | 1.8417
206726819 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBS018*2 | EAD018 | 20700 | 17.7 | 6 | 23300 | 1.725 | 23700 | 29.8 | 5 | 18500 | 1.975 | 21800 | 21.1 | 3.9 | 14400 | 1.8167
206726820 |  | HYDRON MODULE | WBAHP-C | Water-to-Air and Brine-to-Air | HBS018*2 | EED018 | 20900 | 18 | 6 | 23400 | 1.7417 | 24200 | 30.5 | 5 | 18600 | 2.0167 | 22100 | 21.7 | 3.9 | 14500 | 1.8417
206726821 |  | HYDRON MODULE | WBAHP-CB | Water-to-Air and Brine-to-Air | HBS018*2 | EAD018 | 20700 | 17.7 | 6 | 23300 | 1.725 | 23700 | 29.8 | 5 | 18500 | 1.975 | 21800 | 21.1 | 3.9 | 14400 | 1.8167
206726822 |  | TETCO | WBAHP-C | Water-to-Air and Brine-to-Air | TBS018*2 | EED018 | 20900 | 18 | 6 | 23400 | 1.7417 | 24200 | 30.5 | 5 | 18600 | 2.0167 | 22100 | 21.7 | 3.9 | 14500 | 1.8417
206726823 |  | TETCO | WBAHP-CB | Water-to-Air and Brine-to-Air | TBS018*2 | EAD018 | 20700 | 17.7 | 6 | 23300 | 1.725 | 23700 | 29.8 | 5 | 18500 | 1.975 | 21800 | 21.1 | 3.9 | 14400 | 1.8167
206726824 |  | GEOCOMFORT | WBAHP-C | Water-to-Air and Brine-to-Air | GBT036 | EED036 | 35800 | 16.6 | 4.9 | 45200 | 2.9833 | 40500 | 24.6 | 4.7 | 36800 | 3.375 | 37600 | 19.2 | 3.8 | 28800 | 3.1333
206726825 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBT036 | EAD036 | 35200 | 16.6 | 5.3 | 46000 | 2.9333 | 39700 | 24.8 | 4.7 | 36700 | 3.3083 | 36900 | 19.2 | 3.8 | 27800 | 3.075
206726826 |  | HYDRON MODULE | WBAHP-C | Water-to-Air and Brine-to-Air | HBT036 | EED036 | 35800 | 16.6 | 4.9 | 45200 | 2.9833 | 40500 | 24.6 | 4.7 | 36800 | 3.375 | 37600 | 19.2 | 3.8 | 28800 | 3.1333
218029300 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S036SN13* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029301 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S036SN14* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029302 |  | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | T1(H/W)S036SN15* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029303 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G5WZ036BS1* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029304 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S036SN10* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029305 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S036SN13* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029306 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S036SN14* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029307 |  | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | G1(H/W)S036SN15* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029342 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S5WZ036BS1* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029343 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S036SN10* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029344 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S036SN13* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029345 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S036SN14* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218029346 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S036SN15* | [6 empty] | 37800 | 22.2 | 3.8 | 37800 | 3.15 | 36600 | 16.2 | 3.1 | 30500 | 3.05
218157883 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)018BD1**2 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
218157884 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)024BD1**2 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
218157885 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030BD1**2 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
218157886 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)036BD1**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
218157887 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)042BD1**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
218157888 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)048BD1**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
218157891 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)024BD1**1 | [6 empty] | 25700 | 21.3 | 4.6 | 23000 | 2.1417 | 23200 | 15.7 | 4 | 19000 | 1.9333
218157892 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)036BD1**1 | [6 empty] | 37500 | 20.5 | 4.3 | 35400 | 3.125 | 35600 | 15.8 | 3.7 | 26800 | 2.9667
218157893 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)048BD1**1 | [6 empty] | 51200 | 19.6 | 4.2 | 46000 | 4.2667 | 49000 | 16 | 3.7 | 37300 | 4.0833
218157894 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y3A(V/H)060BD1**1 | [6 empty] | 63000 | 18.8 | 4 | 55800 | 5.25 | 59500 | 15.2 | 3.4 | 45800 | 4.9583
218157896 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)009*R0**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
218157897 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)009*R2**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
218157898 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)012*R0**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
218157899 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)012*R2**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
218157900 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)015*R0**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
218157901 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)015*R0**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
218157902 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)015*R2**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
9114310 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT060*2****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114311 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT060*2****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114312 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT060*3****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114313 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT060*3****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114314 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT060*3****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114315 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT060*A****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114316 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT060*A****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9114317 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT060*A****B |  | 59400 | 16.3 | 5.1 | 74600 | 4.95 | [5 empty] | 61200 | 18.7 | 3.9 | 48100 | 5.1
9910449 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS018*****1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910450 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS018*****1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910451 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS018*****1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910452 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910453 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910454 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
201756612 |  | COMFORT-AIRE | WBWHP | Water-to-Water and Brine-to-Water | HNW060 | [6 empty] | 60900 | 20.8 | 3.5 | 58600 | 5.075
201756613 |  | CENTURY | WBWHP | Water-to-Water and Brine-to-Water | HNW060 | [6 empty] | 60900 | 20.8 | 3.5 | 58600 | 5.075
201756620 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | RA-VE-041-* | [6 empty] | 42000 | 22.89 | 4.28 | 42600 | 3.5 | 38100 | 17.47 | 3.66 | 32700 | 3.175
201756621 |  | NORTHSTAR SERIES | WBAHP | Water-to-Air and Brine-to-Air | RA-VE-041-* | [6 empty] | 42000 | 22.89 | 4.28 | 42600 | 3.5 | 38100 | 17.47 | 3.66 | 32700 | 3.175
201756622 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | RA-VE-053-* | [6 empty] | 55400 | 22.21 | 4.1 | 57300 | 4.6167 | 52600 | 17.1 | 3.6 | 45200 | 4.3833
201756623 |  | NORTHSTAR SERIES | WBAHP | Water-to-Air and Brine-to-Air | RA-VE-053-* | [6 empty] | 55400 | 22.21 | 4.1 | 57300 | 4.6167 | 52600 | 17.1 | 3.6 | 45200 | 4.3833
201756626 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | RT-VE-026-* | [6 empty] | 36500 | 19.74 | 4.01 | 30300 | 3.0417 | 32700 | 16.09 | 3.66 | 24100 | 2.725
201756627 |  | NORTHSTAR SERIES | WBAHP | Water-to-Air and Brine-to-Air | RT-VE-026-* | [6 empty] | 36500 | 19.7 | 4 | 30300 | 3.0417 | 32700 | 16 | 3.6 | 24100 | 2.725
201756650 |  | NORTHERN HEAT PUMP | WBWHP | Water-to-Water and Brine-to-Water | RA-WE-024-* | [6 empty] | 27000 | 21.1 | 3.6 | 24800 | 2.25 | 23000 | 16.2 | 3.1 | 21500 | 1.9167
201756651 |  | NORTHSTAR SERIES | WBWHP | Water-to-Water and Brine-to-Water | RA-WE-024-* | [6 empty] | 27000 | 21.1 | 3.6 | 24800 | 2.25 | 23000 | 16.2 | 3.1 | 21500 | 1.9167
201756654 |  | NORTHERN HEAT PUMP | WBWHP | Water-to-Water and Brine-to-Water | RA-WE-050-* | [6 empty] | 55100 | 20.1 | 3.6 | 60100 | 4.5917 | 54200 | 16.1 | 3.1 | 45200 | 4.5167
201756655 |  | NORTHSTAR SERIES | WBWHP | Water-to-Water and Brine-to-Water | RA-WE-050-* | [6 empty] | 55100 | 20.1 | 3.6 | 60100 | 4.5917 | 54200 | 16.1 | 3.1 | 45200 | 4.5167
201864513 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024*A | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
201864514 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024*A | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
201864515 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT024*A | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
201864519 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024*3 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
201864521 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024*3 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
201864523 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT024*3 | [6 empty] | 28200 | 23.7 | 4.6 | 22900 | 2.35 | 26400 | 18.3 | 3.9 | 18300 | 2.2
201907610 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*0*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
201907611 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*0*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
201907612 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*0*5 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
201907613 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS036*3*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
217642915 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)036*S3**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
217642916 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)036*S4**1 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
217642917 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)036*S4**4 | [6 empty] | 40000 | 23.5 | 4.4 | 35000 | 3.3333 | 36000 | 17.5 | 3.7 | 27000 | 3
217642918 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S0**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642919 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S3**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642920 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S3**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642921 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S4**1 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
217642922 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S3A(V/H)042*S4**4 | [6 empty] | 45000 | 23 | 4.6 | 41000 | 3.75 | 42000 | 17.5 | 3.7 | 32000 | 3.5
7414470 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**2*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
7414553 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**2*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
7414651 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**2*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
7414828 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**3*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
7414896 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**3*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
7415098 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**3*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
7415209 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**4*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
7415301 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**4*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
7415373 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH030**4*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
7415455 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**0*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
7415878 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**0*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
7416559 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**0*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
7416688 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**2*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
7416782 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**2*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
7416889 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**2*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
7416979 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**3*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
7417060 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**3*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
7417146 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**3*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
7417250 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**4*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
7417329 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**4*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
7417419 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH036**4*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
7417586 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH038**0*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
7417698 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH038**0*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
7417776 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH038**2*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
7417867 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH038**2*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
7417918 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH038**3*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
7417992 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH038**3*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
7418047 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH038**4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
7418154 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH038**4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
7418286 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**0*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
7418360 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**0*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
7418435 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**0*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
7418524 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**3*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
7418635 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**3*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
7418715 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**3*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
7418803 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**4*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
7418887 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**4*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
7418965 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**4*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
7419110 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**5*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
7419218 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**0*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
7419321 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**0*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419403 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**0*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419473 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**3*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
7419527 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**3*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419618 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**3*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419681 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**4*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
7419733 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**4*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419797 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**4*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7420917 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**5*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
7421327 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**0*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7421397 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**0*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7421438 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**3*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7421969 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7421970 |  | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
216014181 |  | RHEEM | WBAHP | Water-to-Air and Brine-to-Air | RPVV/H/D036D |  | 37700 | 17.9 | 5.8 | 45700 | 3.1417 | 42100 | 26.1 | 5.2 | 37900 | 3.5083 | 39000 | 20.3 | 4.4 | 29700 | 3.25
216054107 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5TV036BD1**2 |  | 36000 | 17.9 | 5.6 | 42300 | 3 | 41400 | 26.9 | 5.1 | 35700 | 3.45 | 38000 | 20.1 | 4.3 | 29300 | 3.1667
216054108 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5TV048BD1**2 | [6 empty] | 52500 | 24.5 | 4.7 | 47400 | 4.375 | 49100 | 18.5 | 4.1 | 38400 | 4.0917
216054475 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBS018* | EAD018 | [5 empty] | 23700 | 29.8 | 5 | 18500 | 1.975 | 21800 | 21.1 | 3.9 | 14400 | 1.8167
216054476 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBT024* | EAD024 | [5 empty] | 27800 | 24.5 | 4.7 | 23900 | 2.3167 | 26300 | 19.5 | 3.9 | 18800 | 2.1917
216054477 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBT036* | EAD036 | [5 empty] | 39700 | 24.8 | 4.7 | 36700 | 3.3083 | 36900 | 19.2 | 3.8 | 27800 | 3.075
216054478 |  | GEOCOMFORT | WBAHP-CB | Water-to-Air and Brine-to-Air | GBT048* | EAD048 | [5 empty] | 51500 | 22.5 | 4.5 | 51300 | 4.2917 | 47800 | 17.3 | 3.6 | 41000 | 3.9833
216054479 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS009* | [6 empty] | 11900 | 22.1 | 4.4 | 10600 | 0.99167 | 10900 | 17.4 | 3.6 | 8500 | 0.90833
216054480 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS012* | [6 empty] | 13400 | 24.1 | 4.3 | 12100 | 1.1167 | 11900 | 18.1 | 3.6 | 9400 | 0.99167
216054481 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS018* | [6 empty] | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
218353008 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PA042-3HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218353012 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PA042-3VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218353016 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PA042-4HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218353020 |  | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | PA042-4VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
215852846 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH024E1*C/S*C |  | 24500 | 17.53 | 5.29 | 26100 | 2.0417
215852847 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH024F3*C/S*C |  | 24500 | 17.18 | 5.19 | 26100 | 2.0417
215852850 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH030E1*C/S*C |  | 31400 | 17.12 | 5.36 | 34900 | 2.6167
215852851 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH030F3*C/S*C |  | 31400 | 16.78 | 5.26 | 34900 | 2.6167
215852854 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH036E1*C/S*C |  | 38000 | 18.43 | 5.36 | 42900 | 3.1667
215852855 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH036F3*C/S*C |  | 38000 | 18.06 | 5.25 | 42900 | 3.1667
215852858 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH042E1*C/S*C |  | 44000 | 17.59 | 5.12 | 50300 | 3.6667
215852859 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH042F3*C/S*C |  | 44000 | 17.24 | 5.02 | 50300 | 3.6667
215852862 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060E1*C/S*C |  | 60000 | 16.8 | 4.9 | 68600 | 5
215852863 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060F3*C/S*C |  | 60000 | 16.46 | 4.8 | 68600 | 5
215852868 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024E1*C/S*C |  | 24300 | 17.59 | 5.81 | 28000 | 2.025
215852869 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024F3*C/S*C |  | 24300 | 17.24 | 5.7 | 28000 | 2.025
215852870 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030E1*C/S*C |  | 31200 | 16.97 | 5.52 | 34700 | 2.6
215852871 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV030F3*C/S*C |  | 31200 | 16.63 | 5.41 | 34700 | 2.6
215852874 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036E1*C/S*C |  | 38100 | 18.45 | 5.18 | 41100 | 3.175
215852875 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036F3*C/S*C |  | 38100 | 18.08 | 5.08 | 41100 | 3.175
215852878 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042E1*C/S*C |  | 43500 | 17.3 | 5.06 | 50000 | 3.625
215852879 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042F3*C/S*C |  | 43500 | 16.95 | 4.96 | 50000 | 3.625
215852882 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048E1*C/S*C |  | 50800 | 17.62 | 5.52 | 58500 | 4.2333
215852883 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048F3*C/S*C |  | 50800 | 17.27 | 5.41 | 58500 | 4.2333
215852884 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060E1*C/S*C |  | 60500 | 17.3 | 5.5 | 74700 | 5.0417
215852885 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060F3*C/S*C |  | 60500 | 16.95 | 5.39 | 74700 | 5.0417
215866231 |  | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SMT24A*L |  | 25000 | 17.6 | 5.1 | 28000 | 2.0833 | [5 empty] | 25900 | 20.5 | 3.7 | 18000 | 2.1583
215866538 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH048E1*C/S*C |  | 48200 | 17.34 | 5.08 | 56900 | 4.0167
218338474 |  | GeoSmart Energy | WBAHP-O | Water-to-Air and Brine-to-Air | S5C(C/W/S)015**0**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
218338478 |  | GeoSmart Energy | WBAHP-O | Water-to-Air and Brine-to-Air | S5C(C/W/S)015**2**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
215268740 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*D4**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
215268741 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*D0**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
215268742 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*D2**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
215268743 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*D3**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
215268744 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*D4**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
215268745 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*D0**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
215268746 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*D3**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
215268747 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*D0**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
215268748 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*D3**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
215268749 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D0**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268750 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D3**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268751 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D0**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268752 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D3**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268753 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D0**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268754 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*D3**4 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
215268755 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D0**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268756 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D3**1 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
215268757 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*D0**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
216979888 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979889 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979890 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979891 |  | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979892 |  | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979893 |  | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979894 |  | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979895 |  | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979896 |  | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
215742630 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 31630/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742631 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 31640/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742632 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 21630/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742633 |  | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 21640/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215743134 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK006 | [6 empty] | 9300 | 21.7 | 4.5 | 8100 | 0.775
215743135 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK009 | [6 empty] | 9500 | 23 | 4.5 | 8400 | 0.79167
215743136 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK012 | [6 empty] | 13300 | 23.2 | 4.3 | 11600 | 1.1083
215743520 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0062 | [6 empty] | 9300 | 21.7 | 4.5 | 8100 | 0.775
215743521 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0067 | [6 empty] | 9300 | 21.7 | 4.5 | 8100 | 0.775
215743522 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0092 | [6 empty] | 9500 | 23 | 4.5 | 8400 | 0.79167
215743523 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0097 | [6 empty] | 9500 | 23 | 4.5 | 8400 | 0.79167
215743524 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0122 | [6 empty] | 13300 | 23.2 | 4.3 | 11600 | 1.1083
215743525 |  | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK0127 | [6 empty] | 13300 | 23.2 | 4.3 | 11600 | 1.1083
215744815 |  | TRANE | WBWHP | Water-to-Water and Brine-to-Water | EXWK060 | [6 empty] | 56000 | 22 | 3.65 | 58200 | 4.6667
215744817 |  | TRANE | WBWHP | Water-to-Water and Brine-to-Water | EXWK0602 | [6 empty] | 56000 | 22 | 3.65 | 58200 | 4.6667
215744818 |  | TRANE | WBWHP | Water-to-Water and Brine-to-Water | EXWK0603 | [6 empty] | 56000 | 22 | 3.65 | 58200 | 4.6667
215744819 |  | TRANE | WBWHP | Water-to-Water and Brine-to-Water | EXWK0608 | [6 empty] | 56000 | 22 | 3.65 | 58200 | 4.6667
215744820 |  | TRANE | WBWHP | Water-to-Water and Brine-to-Water | EXWK0604 | [6 empty] | 56000 | 22 | 3.65 | 58200 | 4.6667
215744821 |  | TRANE | WBWHP | Water-to-Water and Brine-to-Water | EXWK0605 | [6 empty] | 56000 | 22 | 3.65 | 58200 | 4.6667
215746915 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK036A3 |  | 40281 | 19.2 | 6.06 | 47492 | 3.3567 | 43925 | 29.6 | 5.26 | 39058 | 3.6604 | 41280 | 22.1 | 4.28 | 29804 | 3.44
215746916 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK048A3 |  | 53537 | 17.6 | 5.79 | 62760 | 4.4614 | 57887 | 27.2 | 5.05 | 51760 | 4.8239 | 55159 | 20.4 | 4.14 | 39719 | 4.5966
215746923 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK036A4 |  | 40281 | 19.2 | 6.06 | 47492 | 3.3567 | 43925 | 29.6 | 5.26 | 39058 | 3.6604 | 41280 | 22.1 | 4.28 | 29804 | 3.44
215746924 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK036AW |  | 40281 | 19.2 | 6.06 | 47492 | 3.3567 | 43925 | 29.6 | 5.26 | 39058 | 3.6604 | 41280 | 22.1 | 4.28 | 29804 | 3.44
215746925 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK048A4 |  | 53537 | 17.6 | 5.79 | 62760 | 4.4614 | 57887 | 27.2 | 5.05 | 51760 | 4.8239 | 55159 | 20.4 | 4.14 | 39719 | 4.5966
215746926 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GSK048AW |  | 53537 | 17.6 | 5.79 | 62760 | 4.4614 | 57887 | 27.2 | 5.05 | 51760 | 4.8239 | 55159 | 20.4 | 4.14 | 39719 | 4.5966
218471911 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | AZ060-1CSC-*****A | JDE60F5XX2DS1 | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
218471912 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | AZ060-1CSN-*****A | JDE60F5XX2DS1 | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
218471913 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | QZ060-1CSC-*****A | JDE60F5XX2DS1 | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
218471914 |  | YORK | WBAHP-CB | Water-to-Air and Brine-to-Air | QZ060-1CSN-*****A | JDE60F5XX2DS1 | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
217754428 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F1*B*C |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
217754431 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F1*B*T |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
217754434 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F1*B*C |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
217754437 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036F1*B*T |  | 39000 | 18.4 | 5.34 | 44100 | 3.25
217754440 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036F1*B*C |  | 39000 | 18.4 | 5.34 | 44100 | 3.25
217754443 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F1*B*T |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
217754446 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F1*B*C |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
217754449 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F1*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
217754453 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F1*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
217754457 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F1*B*T |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
217754461 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F1*B*C |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
207177429 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG006A | [6 empty] | 8100 | 21.3 | 4.1 | 7500 | 0.675
207177430 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0067 | [6 empty] | 8100 | 21.3 | 4.1 | 7500 | 0.675
207177431 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG009A | [6 empty] | 9600 | 23.8 | 4.7 | 9100 | 0.8 | 8900 | 17.8 | 3.7 | 6700 | 0.74167
207177432 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0097 | [6 empty] | 9600 | 23.8 | 4.7 | 9100 | 0.8 | 8900 | 17.8 | 3.7 | 6700 | 0.74167
207177433 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG012A | [6 empty] | 13300 | 24.2 | 4.6 | 12400 | 1.1083 | 12100 | 17.6 | 3.7 | 9400 | 1.0083
207177434 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0127 | [6 empty] | 13300 | 24.2 | 4.6 | 12400 | 1.1083 | 12100 | 17.6 | 3.7 | 9400 | 1.0083
207177435 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG015A | [6 empty] | 16600 | 23 | 4.3 | 15400 | 1.3833 | 15500 | 17.4 | 3.6 | 12300 | 1.2917
207177447 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG036A | [6 empty] | 39900 | 22.6 | 4.4 | 36900 | 3.325 | 37300 | 17.6 | 3.6 | 28700 | 3.1083
207177448 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG036B | [6 empty] | 39900 | 22.6 | 4.4 | 36900 | 3.325 | 37300 | 17.6 | 3.6 | 28700 | 3.1083
207177449 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0364 | [6 empty] | 39900 | 22.6 | 4.4 | 36900 | 3.325 | 37300 | 17.6 | 3.6 | 28700 | 3.1083
207177450 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0367 | [6 empty] | 39900 | 22.6 | 4.4 | 36900 | 3.325 | 37300 | 17.6 | 3.6 | 28700 | 3.1083
207177451 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG042A | [6 empty] | 45500 | 22 | 4.2 | 45600 | 3.7917
207177452 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG042B | [6 empty] | 45500 | 22 | 4.2 | 45600 | 3.7917
207177453 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0424 | [6 empty] | 45500 | 22 | 4.2 | 45600 | 3.7917
207177454 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG048A | [6 empty] | 55700 | 22.8 | 4.2 | 50000 | 4.6417
207177455 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG048B | [6 empty] | 55700 | 22.8 | 4.2 | 50000 | 4.6417
207177456 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0484 | [6 empty] | 55700 | 22.8 | 4.2 | 50000 | 4.6417
207177457 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG060A | [6 empty] | 61700 | 21.3 | 4.1 | 61200 | 5.1417
207177458 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG060B | [6 empty] | 61700 | 21.3 | 4.1 | 61200 | 5.1417
207177459 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GEVG0604 | [6 empty] | 61700 | 21.3 | 4.1 | 61200 | 5.1417
207177460 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG009A | [6 empty] | 8800 | 25 | 4.8 | 8200 | 0.73333 | 8300 | 18.8 | 3.7 | 6100 | 0.69167
207177461 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0097 | [6 empty] | 8800 | 25 | 4.8 | 8200 | 0.73333 | 8300 | 18.8 | 3.7 | 6100 | 0.69167
207177462 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG012A | [6 empty] | 13700 | 27.9 | 5 | 12300 | 1.1417 | 12300 | 19.5 | 4 | 9300 | 1.025
207177463 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0127 | [6 empty] | 13700 | 27.9 | 5 | 12300 | 1.1417 | 12300 | 19.5 | 4 | 9300 | 1.025
207177464 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG015A | [6 empty] | 17000 | 25.8 | 4.6 | 15300 | 1.4167 | 15800 | 19 | 3.8 | 12100 | 1.3167
207177465 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0157 | [6 empty] | 17000 | 25.8 | 4.6 | 15300 | 1.4167 | 15800 | 19 | 3.8 | 12100 | 1.3167
207177466 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG018A |  | 18800 | 17.6 | 5.7 | 23600 | 1.5667 | 21100 | 28.7 | 4.9 | 18800 | 1.7583 | 19600 | 20.6 | 4.1 | 14600 | 1.6333
207177467 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0187 |  | 18800 | 17.6 | 5.7 | 23600 | 1.5667 | 21100 | 28.7 | 4.9 | 18800 | 1.7583 | 19600 | 20.6 | 4.1 | 14600 | 1.6333
207177468 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG024A |  | 24600 | 17.4 | 5.7 | 32100 | 2.05 | 27400 | 27.2 | 5 | 25900 | 2.2833 | 25600 | 20.3 | 3.9 | 19500 | 2.1333
207177469 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG024B |  | 24600 | 17.4 | 5.7 | 32100 | 2.05 | 27400 | 27.2 | 5 | 25900 | 2.2833 | 25600 | 20.3 | 3.9 | 19500 | 2.1333
207177470 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0244 |  | 24600 | 17.4 | 5.7 | 32100 | 2.05 | 27400 | 27.2 | 5 | 25900 | 2.2833 | 25600 | 20.3 | 3.9 | 19500 | 2.1333
207177471 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0247 |  | 24600 | 17.4 | 5.7 | 32100 | 2.05 | 27400 | 27.2 | 5 | 25900 | 2.2833 | 25600 | 20.3 | 3.9 | 19500 | 2.1333
207177472 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG030A |  | 31400 | 17.8 | 5.8 | 38400 | 2.6167 | 35000 | 27.2 | 5 | 31000 | 2.9167 | 32800 | 20.7 | 4.1 | 23600 | 2.7333
207177473 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG030B |  | 31400 | 17.8 | 5.8 | 38400 | 2.6167 | 35000 | 27.2 | 5 | 31000 | 2.9167 | 32800 | 20.7 | 4.1 | 23600 | 2.7333
207177474 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0304 |  | 31400 | 17.8 | 5.8 | 38400 | 2.6167 | 35000 | 27.2 | 5 | 31000 | 2.9167 | 32800 | 20.7 | 4.1 | 23600 | 2.7333
207177475 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0307 |  | 31400 | 17.8 | 5.8 | 38400 | 2.6167 | 35000 | 27.2 | 5 | 31000 | 2.9167 | 32800 | 20.7 | 4.1 | 23600 | 2.7333
207177476 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG036A |  | 35500 | 17.6 | 5.8 | 43100 | 2.9583 | 39400 | 26.5 | 5 | 35000 | 3.2833 | 37100 | 20.4 | 4.1 | 27200 | 3.0917
207177477 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG036B |  | 35500 | 17.6 | 5.8 | 43100 | 2.9583 | 39400 | 26.5 | 5 | 35000 | 3.2833 | 37100 | 20.4 | 4.1 | 27200 | 3.0917
207177478 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0364 |  | 35500 | 17.6 | 5.8 | 43100 | 2.9583 | 39400 | 26.5 | 5 | 35000 | 3.2833 | 37100 | 20.4 | 4.1 | 27200 | 3.0917
207177479 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0367 |  | 35500 | 17.6 | 5.8 | 43100 | 2.9583 | 39400 | 26.5 | 5 | 35000 | 3.2833 | 37100 | 20.4 | 4.1 | 27200 | 3.0917
207177480 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG042A |  | 38400 | 18 | 6.4 | 48000 | 3.2 | 43300 | 27.5 | 5.5 | 38500 | 3.6083 | 40500 | 21.1 | 4.3 | 29400 | 3.375
207177481 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG042B |  | 38400 | 18 | 6.4 | 48000 | 3.2 | 43300 | 27.5 | 5.5 | 38500 | 3.6083 | 40500 | 21.1 | 4.3 | 29400 | 3.375
207177482 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0424 |  | 38400 | 18 | 6.4 | 48000 | 3.2 | 43300 | 27.5 | 5.5 | 38500 | 3.6083 | 40500 | 21.1 | 4.3 | 29400 | 3.375
207177483 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG048A |  | 45400 | 17.7 | 6.1 | 55600 | 3.7833 | 50400 | 26.4 | 5.3 | 44800 | 4.2 | 47100 | 20.3 | 4.3 | 34600 | 3.925
207177484 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG048B |  | 45400 | 17.7 | 6.1 | 55600 | 3.7833 | 50400 | 26.4 | 5.3 | 44800 | 4.2 | 47100 | 20.3 | 4.3 | 34600 | 3.925
207177485 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0484 |  | 45400 | 17.7 | 6.1 | 55600 | 3.7833 | 50400 | 26.4 | 5.3 | 44800 | 4.2 | 47100 | 20.3 | 4.3 | 34600 | 3.925
207177486 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG060A |  | 55700 | 17.5 | 5.9 | 69000 | 4.6417 | 60800 | 25.7 | 5.1 | 55900 | 5.0667 | 57700 | 20.1 | 4.1 | 42900 | 4.8083
207177487 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG060B |  | 55700 | 17.5 | 5.9 | 69000 | 4.6417 | 60800 | 25.7 | 5.1 | 55900 | 5.0667 | 57700 | 20.1 | 4.1 | 42900 | 4.8083
207177488 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0604 |  | 55700 | 17.5 | 5.9 | 69000 | 4.6417 | 60800 | 25.7 | 5.1 | 55900 | 5.0667 | 57700 | 20.1 | 4.1 | 42900 | 4.8083
207177489 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG070A |  | 63800 | 17.3 | 5.4 | 82100 | 5.3167
207177490 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG070B |  | 63800 | 17.3 | 5.4 | 82100 | 5.3167
207177491 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | EXVG0704 |  | 63800 | 17.3 | 5.4 | 82100 | 5.3167
207177492 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG024A |  | 24700 | 16.8 | 5.5 | 32100 | 2.0583 | 27500 | 24.4 | 4.9 | 25700 | 2.2917 | 25900 | 19.2 | 3.9 | 19400 | 2.1583
207177493 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG024B |  | 24700 | 16.8 | 5.5 | 32100 | 2.0583 | 27500 | 24.4 | 4.9 | 25700 | 2.2917 | 25900 | 19.2 | 3.9 | 19400 | 2.1583
207177494 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG0244 |  | 24700 | 16.8 | 5.5 | 32100 | 2.0583 | 27500 | 24.4 | 4.9 | 25700 | 2.2917 | 25900 | 19.2 | 3.9 | 19400 | 2.1583
207177495 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG0247 |  | 24700 | 16.8 | 5.5 | 32100 | 2.0583 | 27500 | 24.4 | 4.9 | 25700 | 2.2917 | 25900 | 19.2 | 3.9 | 19400 | 2.1583
207177496 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG036A |  | 33000 | 17.3 | 5.9 | 40900 | 2.75 | 37100 | 25.1 | 5.1 | 32900 | 3.0917 | 34500 | 19.7 | 4.1 | 25500 | 2.875
207177497 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG036B |  | 33000 | 17.3 | 5.9 | 40900 | 2.75 | 37100 | 25.1 | 5.1 | 32900 | 3.0917 | 34500 | 19.7 | 4.1 | 25500 | 2.875
207177498 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG0364 |  | 33000 | 17.3 | 5.9 | 40900 | 2.75 | 37100 | 25.1 | 5.1 | 32900 | 3.0917 | 34500 | 19.7 | 4.1 | 25500 | 2.875
207177499 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG0367 |  | 33000 | 17.3 | 5.9 | 40900 | 2.75 | 37100 | 25.1 | 5.1 | 32900 | 3.0917 | 34500 | 19.7 | 4.1 | 25500 | 2.875
207177500 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG048A |  | 45200 | 17.9 | 6.1 | 55200 | 3.7667 | 50400 | 26.4 | 5.3 | 44400 | 4.2 | 46600 | 20.6 | 4.3 | 34500 | 3.8833
207177501 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG048B |  | 45200 | 17.9 | 6.1 | 55200 | 3.7667 | 50400 | 26.4 | 5.3 | 44400 | 4.2 | 46600 | 20.6 | 4.3 | 34500 | 3.8833
207177502 |  | TRANE | WBAHP | Water-to-Air and Brine-to-Air | DXVG0484 |  | 45200 | 17.9 | 6.1 | 55200 | 3.7667 | 50400 | 26.4 | 5.3 | 44400 | 4.2 | 46600 | 20.6 | 4.3 | 34500 | 3.8833
202146914 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS015*A | [6 empty] | 16100 | 24.4 | 4.7 | 14300 | 1.3417 | 14500 | 17.1 | 3.9 | 11300 | 1.2083
202146915 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS015*****1 | [6 empty] | 15600 | 24.9 | 4.8 | 14300 | 1.3 | 14200 | 17.6 | 3.9 | 11200 | 1.1833
202146916 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS015 | [6 empty] | 16100 | 24.4 | 4.7 | 14300 | 1.3417 | 14500 | 17.1 | 3.9 | 11300 | 1.2083
202146917 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS015*A | [6 empty] | 16100 | 24.4 | 4.7 | 14300 | 1.3417 | 14500 | 17.1 | 3.9 | 11300 | 1.2083
202146918 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS015*****1 | [6 empty] | 15600 | 24.9 | 4.8 | 14300 | 1.3 | 14200 | 17.6 | 3.9 | 11200 | 1.1833
202146919 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS015 | [6 empty] | 16100 | 24.4 | 4.7 | 14300 | 1.3417 | 14500 | 17.1 | 3.9 | 11300 | 1.2083
202146920 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS015*A | [6 empty] | 16100 | 24.4 | 4.7 | 14300 | 1.3417 | 14500 | 17.1 | 3.9 | 11300 | 1.2083
202146921 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS015*****1 | [6 empty] | 15600 | 24.9 | 4.8 | 14300 | 1.3 | 14200 | 17.6 | 3.9 | 11200 | 1.1833
202146922 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS017 | [6 empty] | 19200 | 22.5 | 4.5 | 16900 | 1.6 | 17900 | 17.1 | 3.7 | 13700 | 1.4917
202146923 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS017*A | [6 empty] | 19200 | 22.5 | 4.5 | 16900 | 1.6 | 17900 | 17.1 | 3.7 | 13700 | 1.4917
202146924 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS017*****1 | [6 empty] | 19400 | 24.9 | 4.7 | 16700 | 1.6167 | 17800 | 18.2 | 3.9 | 13500 | 1.4833
202146925 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS017*A***1 | [6 empty] | 19400 | 24.9 | 4.7 | 16700 | 1.6167 | 17800 | 18.2 | 3.9 | 13500 | 1.4833
202146926 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS017 | [6 empty] | 19200 | 22.5 | 4.5 | 16900 | 1.6 | 17900 | 17.1 | 3.7 | 13700 | 1.4917
202146927 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS017*A | [6 empty] | 19200 | 22.5 | 4.5 | 16900 | 1.6 | 17900 | 17.1 | 3.7 | 13700 | 1.4917
202146928 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS017*****1 | [6 empty] | 19400 | 24.9 | 4.7 | 16700 | 1.6167 | 17800 | 18.2 | 3.9 | 13500 | 1.4833
202146929 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS017*A***1 | [6 empty] | 19400 | 24.9 | 4.7 | 16700 | 1.6167 | 17800 | 18.2 | 3.9 | 13500 | 1.4833
202146930 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS017 | [6 empty] | 19200 | 22.5 | 4.5 | 16900 | 1.6 | 17900 | 17.1 | 3.7 | 13700 | 1.4917
202146931 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS017*A | [6 empty] | 19200 | 22.5 | 4.5 | 16900 | 1.6 | 17900 | 17.1 | 3.7 | 13700 | 1.4917
202146932 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS017*****1 | [6 empty] | 19400 | 24.9 | 4.7 | 16700 | 1.6167 | 17800 | 18.2 | 3.9 | 13500 | 1.4833
202146933 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS017*A***1 | [6 empty] | 19400 | 24.9 | 4.7 | 16700 | 1.6167 | 17800 | 18.2 | 3.9 | 13500 | 1.4833
202146936 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS018*****1 | [6 empty] | 21400 | 26 | 4.7 | 17500 | 1.7833 | 20100 | 18.7 | 3.7 | 14100 | 1.675
202146939 |  | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS018*****1 | [6 empty] | 21400 | 26 | 4.7 | 17500 | 1.7833 | 20100 | 18.7 | 3.7 | 14100 | 1.675
202146942 |  | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS018*****1 | [6 empty] | 21400 | 26 | 4.7 | 17500 | 1.7833 | 20100 | 18.7 | 3.7 | 14100 | 1.675
202146943 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024 | [6 empty] | 27400 | 22.9 | 4.3 | 23700 | 2.2833 | 25700 | 17.4 | 3.6 | 18500 | 2.1417
202146944 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*2 | [6 empty] | 27400 | 22.9 | 4.3 | 23700 | 2.2833 | 25700 | 17.4 | 3.6 | 18500 | 2.1417
202146945 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*3 | [6 empty] | 27400 | 22.9 | 4.3 | 23700 | 2.2833 | 25700 | 17.4 | 3.6 | 18500 | 2.1417
202146946 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*4 | [6 empty] | 27400 | 22.9 | 4.3 | 23700 | 2.2833 | 25700 | 17.4 | 3.6 | 18500 | 2.1417
202146947 |  | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*A | [6 empty] | 27400 | 22.9 | 4.3 | 23700 | 2.2833 | 25700 | 17.4 | 3.6 | 18500 | 2.1417
206438813 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-1VTC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438814 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-1HZC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438815 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-1VTN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438816 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-1HZN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438817 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-0VTC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438818 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-2VTC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438819 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-0HZC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438820 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-2HZC-*****B | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438821 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-0VTN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438822 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-2VTN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438823 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-0HZN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438824 |  | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP012-2HZN-*****B | [6 empty] | 14200 | 22.7 | 4.1 | 12000 | 1.1833
206438864 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***3/CA* | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
206438869 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V007***4/DA* | [6 empty] | 8400 | 25.1 | 4.7 | 6900 | 0.7
206438870 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V007***3/CA* | [6 empty] | 8400 | 25.1 | 4.7 | 6900 | 0.7
206438871 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V009***3/CA* | [6 empty] | 10500 | 24.35 | 4.5 | 9000 | 0.875
206438872 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V009***4/DA* | [6 empty] | 10500 | 24.35 | 4.5 | 9000 | 0.875
206438873 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V012***3/CA* | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
206438874 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V015***3/CA* | [6 empty] | 17000 | 27.25 | 4.28 | 13000 | 1.4167 | 16200 | 19.8 | 3.63 | 11000 | 1.35
206438875 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V015***4/DA* | [6 empty] | 17000 | 27.25 | 4.28 | 13000 | 1.4167 | 16200 | 19.8 | 3.63 | 11000 | 1.35
206438876 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V030***4/DA* | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438877 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V030***6/FA* | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438878 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V030***5/EA* | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438879 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH/V030***3/CA* | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
206438891 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***4/DA* | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
206438892 |  | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | 50PSW025***6/FA* | [6 empty] | 24500 | 21.2 | 3.5 | 23600 | 2.0417
8714940 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024******1**1 | FE/V***F003*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
8714941 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024******1*X1 | FE/V***F003*** | [5 empty] | 28200 | 22 | 4.45 | 23500 | 2.35 | 26000 | 16.8 | 3.75 | 18900 | 2.1667
8714948 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1**1 | FE/V***F005*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
8714949 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ048******1*X1 | FE/V***F005*** | [5 empty] | 52300 | 20.45 | 4.2 | 47400 | 4.3583 | 48600 | 15.5 | 3.6 | 37900 | 4.05
8714952 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060******1**1 | FE/V***F006*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
8714953 |  | BRYANT | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ060******1*X1 | FE/V***F006*** | [5 empty] | 64300 | 20.7 | 4 | 57500 | 5.3583 | 60800 | 16.8 | 3.4 | 45000 | 5.0667
205230416 |  | COMFORTMAKER | WBWHP | Water-to-Water and Brine-to-Water | HW048W**D/G***1**2 | [6 empty] | 48500 | 22.1 | 3.6 | 46200 | 4.0417 | 44800 | 16.7 | 3.05 | 37300 | 3.7333
205230417 |  | DAY & NIGHT | WBWHP | Water-to-Water and Brine-to-Water | HW048W**D/G***1**2 | [6 empty] | 48500 | 22.1 | 3.6 | 46200 | 4.0417 | 44800 | 16.7 | 3.05 | 37300 | 3.7333
205230418 |  | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW049-1***-****CB | [6 empty] | 48500 | 22.1 | 3.6 | 46200 | 4.0417 | 44800 | 16.7 | 3.05 | 37300 | 3.7333
205311951 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH009**0*6 | [6 empty] | 10300 | 22 | 4.1 | 9600 | 0.85833
205311952 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH009**9*6 | [6 empty] | 10300 | 22 | 4.1 | 9600 | 0.85833
205311983 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH030**0*1 | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
205311984 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH030**2*1 | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
205311985 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH030**3*1 | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
205311986 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH030**4*1 | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
205311987 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH030**0*4 | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
205311988 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH030**2*4 | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
205311989 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH030**3*4 | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
205311990 |  | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH030**4*4 | [6 empty] | 33500 | 22.5 | 4.2 | 28000 | 2.7917
214063737 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH009**2*0 | [6 empty] | 10800 | 22.2 | 4.4 | 10600 | 0.9
214063738 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH012**0*0 | [6 empty] | 13200 | 23.1 | 4.2 | 12000 | 1.1
218396741 |  | SKYMARK | WBWHP | Water-to-Water and Brine-to-Water | PH061-1***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
218433695 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSC-*****A | BIVB-24RCB-M20X | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
218433696 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSN-*****A | BIVB-24RCB-M20X | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
218433697 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | CP036-1CSC-*****A | BIVB-36RCB-M20X | [5 empty] | 40200 | 23.4 | 4.7 | 36400 | 3.35 | 38200 | 17.6 | 4 | 29200 | 3.1833
218433698 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | CP036-1CSN-*****A | BIVB-36RCB-M20X | [5 empty] | 41400 | 24.1 | 4.8 | 37000 | 3.45 | 39200 | 18.6 | 4.1 | 29800 | 3.2667
218433699 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | CP048-1CSC-*****A | BIVB-48RCB-M20X | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
218433700 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | CP048-1CSN-*****A | BIVB-48RCB-M20X | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
218433701 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | CP060-1CSC-*****A | BIVB-60RCB-M20X | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
218433702 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | CP060-1CSN-*****A | BIVB-60RCB-M20X | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
218433703 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | RP024-1CSC-*****A | BIVB-24RCB-M20X | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
218433704 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | RP024-1CSN-*****A | BIVB-24RCB-M20X | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
218433705 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | RP036-1CSC-*****A | BIVB-36RCB-M20X | [5 empty] | 40200 | 23.4 | 4.7 | 36400 | 3.35 | 38200 | 17.6 | 4 | 29200 | 3.1833
218433706 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | RP036-1CSN-*****A | BIVB-36RCB-M20X | [5 empty] | 41400 | 24.1 | 4.8 | 37000 | 3.45 | 39200 | 18.6 | 4.1 | 29800 | 3.2667
218433707 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | RP048-1CSC-*****A | BIVB-48RCB-M20X | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
218433708 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | RP048-1CSN-*****A | BIVB-48RCB-M20X | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
218433709 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | RP060-1CSC-*****A | BIVB-60RCB-M20X | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
218433710 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | RP060-1CSN-*****A | BIVB-60RCB-M20X | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
218433932 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP024-1CSC-*****A | BIVB-24RCB-M20X | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
218433933 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP024-1CSN-*****A | BIVB-24RCB-M20X | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
218433934 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP036-1CSC-*****A | BIVB-36RCB-M20X | [5 empty] | 40200 | 23.4 | 4.7 | 36400 | 3.35 | 38200 | 17.6 | 4 | 29200 | 3.1833
218433935 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP036-1CSN-*****A | BIVB-36RCB-M20X | [5 empty] | 41400 | 24.1 | 4.8 | 37000 | 3.45 | 39200 | 18.6 | 4.1 | 29800 | 3.2667
218433936 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP048-1CSC-*****A | BIVB-48RCB-M20X | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
218433937 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP048-1CSN-*****A | BIVB-48RCB-M20X | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
218433938 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP060-1CSC-*****A | BIVB-60RCB-M20X | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
218433939 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP060-1CSN-*****A | BIVB-60RCB-M20X | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
218433940 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSC-*****A | BIVB-24RCB-M20X | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
218433941 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSN-*****A | BIVB-24RCB-M20X | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
218433942 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP036-1CSC-*****A | BIVB-36RCB-M20X | [5 empty] | 40200 | 23.4 | 4.7 | 36400 | 3.35 | 38200 | 17.6 | 4 | 29200 | 3.1833
218433943 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP036-1CSN-*****A | BIVB-36RCB-M20X | [5 empty] | 41400 | 24.1 | 4.8 | 37000 | 3.45 | 39200 | 18.6 | 4.1 | 29800 | 3.2667
218433944 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP048-1CSC-*****A | BIVB-48RCB-M20X | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
218433945 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP048-1CSN-*****A | BIVB-48RCB-M20X | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
218433946 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP060-1CSC-*****A | BIVB-60RCB-M20X | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
218433947 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | CP060-1CSN-*****A | BIVB-60RCB-M20X | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
217048799 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S024SN12* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048800 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S024SN14* | [6 empty] | 26000 | 22.2 | 3.8 | 27000 | 2.1667 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
217048801 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S048SN10* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048802 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S048SN13* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048803 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S048SN14* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048804 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S048SN15* | [6 empty] | 51500 | 20.9 | 3.6 | 52600 | 4.2917 | 49700 | 16.1 | 3.1 | 42700 | 4.1417
217048805 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | S1(H/W)S060SN10* | [6 empty] | 62800 | 20.4 | 3.8 | 63400 | 5.2333 | 58800 | 16.1 | 3.1 | 50200 | 4.9
218472068 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AA042-1HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218472069 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QA042-1HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218472070 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | AA042-1VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
218472071 |  | YORK | WBAHP | Water-to-Air and Brine-to-Air | QA042-1VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
207200602 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTZ049*1*J | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207200603 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS064*1*J | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207200604 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GTS064*1*J | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207200605 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GSZ036*1*J | SRAA036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207200606 |  | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | GSZ042*1*J | SRAA048* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207200607 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTZ038*1*J | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207200608 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS038*1*J | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207200609 |  | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | GTS038*1*J | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207200610 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HE040*1* | [6 empty] | 33000 | 20.1 | 4 | 40000 | 2.75 | 30600 | 16.1 | 3.3 | 34000 | 2.55
207200611 |  | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HE050*1* | [6 empty] | 47000 | 20.1 | 3.9 | 54900 | 3.9167 | 44500 | 16.1 | 3.3 | 45000 | 3.7083
207200613 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | QT038**1*(1,2)* | [6 empty] | 38200 | 23.8 | 4.5 | 33200 | 3.1833 | 36000 | 18.7 | 3.9 | 27400 | 3
207200614 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | VI036**1*(1,2)** |  | 32300 | 17.7 | 5.3 | 51000 | 2.6917 | 38000 | 31.2 | 4.5 | 41700 | 3.1667 | 35800 | 21.6 | 3.5 | 32900 | 2.9833
207200615 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | VI048**1*1* |  | 40700 | 16.9 | 4.9 | 67000 | 3.3917 | 49000 | 30 | 4 | 55200 | 4.0833 | 45000 | 20 | 3.4 | 43500 | 3.75
207200616 |  | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | VI060**1*1* |  | 50000 | 15.9 | 4.9 | 79000 | 4.1667 | 60000 | 27.1 | 4.3 | 66000 | 5 | 56000 | 19.1 | 3.4 | 51700 | 4.6667
217602175 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**6*(A-H)** | [6 empty] | 25200 | 22.3 | 3.9 | 22200 | 2.1 | 24200 | 16.5 | 3.6 | 17400 | 2.0167
217602176 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*024C**6*(J-R)** | [6 empty] | 24800 | 21.9 | 3.9 | 21800 | 2.0667 | 23800 | 16.2 | 3.5 | 17000 | 1.9833
217602177 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**4*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
217602178 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**4*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217602179 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**5*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
217602180 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**5*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217602181 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**6*(A-H)** | [6 empty] | 31000 | 21.3 | 3.9 | 27200 | 2.5833 | 30000 | 16 | 3.6 | 22600 | 2.5
217602182 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*030C**6*(J-R)** | [6 empty] | 30400 | 20.4 | 3.9 | 26600 | 2.5333 | 29400 | 15.7 | 3.5 | 22200 | 2.45
217602183 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**4*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217602184 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**4*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
217602185 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**5*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217602186 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**5*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
217602187 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**6*(A-H)** | [6 empty] | 38800 | 20.4 | 4.1 | 34400 | 3.2333 | 36800 | 16 | 3.6 | 27200 | 3.0667
217602188 |  | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WD*036C**6*(J-R)** | [6 empty] | 38000 | 20 | 4 | 33400 | 3.1667 | 36000 | 15.7 | 3.5 | 26600 | 3
206347035 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCH*015*J***14* |  | 15600 | 17.6 | 5.6 | 17200 | 1.3
206347037 |  | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCH*015*E***14* |  | 16000 | 17.6 | 5.6 | 18100 | 1.3333
206347324 |  | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | HEV/H036D | [6 empty] | 38200 | 22.3 | 4.3 | 35100 | 3.1833 | 35200 | 16.7 | 3.6 | 27300 | 2.9333
206347325 |  | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | HEV/H036D | [6 empty] | 38200 | 22.3 | 4.3 | 35100 | 3.1833 | 35200 | 16.7 | 3.6 | 27300 | 2.9333
206347960 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSS6006*6* | [6 empty] | 8600 | 26 | 4.5 | 7200 | 0.71667
206347961 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSS6009*6* | [6 empty] | 11200 | 26 | 4.5 | 8200 | 0.93333
206347962 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSS6012*6* | [6 empty] | 13800 | 26 | 4.5 | 10400 | 1.15
206347963 |  | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSS6015*6* | [6 empty] | 18100 | 23.1 | 4.3 | 15500 | 1.5083
214839280 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-1HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839281 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-1VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839282 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-3HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839283 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-3VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839284 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-4HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214839285 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | RL042-4VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
202262237 |  | 5 SERIES INDOOR SPLITS | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ036J1 | SAH036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
202262238 |  | 5 SERIES INDOOR SPLITS | WBAHP-CB | Water-to-Air and Brine-to-Air | NSZ042J1 | SAH042* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
202272873 |  | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP018-1VT*******C | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202319675 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | SM036-1AV*-*****B | [5 empty] | 40900 | 21.05 | 4.4 | 35200 | 3.4083 | 37900 | 16.25 | 3.65 | 27400 | 3.1583
202319679 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSN-*****B | SM036-1AV*-*****B | [5 empty] | 40900 | 21.05 | 4.4 | 35200 | 3.4083 | 37900 | 16.25 | 3.65 | 27400 | 3.1583
202319683 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM048-1CSC-*****A | SM048-1AV*-*****A | [5 empty] | 52800 | 21.25 | 4.6 | 46600 | 4.4 | 48900 | 16.2 | 3.9 | 37800 | 4.075
202319688 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM060-1CSC-*****A | SM060-1AV*-*****A | [5 empty] | 64500 | 20.5 | 4.4 | 60500 | 5.375 | 58900 | 16.1 | 3.8 | 49000 | 4.9083
202319692 |  | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM060-1CSN-*****A | SM060-1AV*-*****A | [5 empty] | 64500 | 20.5 | 4.4 | 60500 | 5.375 | 58900 | 16.1 | 3.8 | 49000 | 4.9083
202324846 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH009**0*6 | [6 empty] | 10300 | 22 | 4.1 | 9600 | 0.85833
202324847 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | UBV/UBH009**9*6 | [6 empty] | 10300 | 22 | 4.1 | 9600 | 0.85833
202326797 |  | 5 SERIES INDOOR SPLITS | WBAHP-CB | Water-to-Air and Brine-to-Air | NDZ038J1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
202326829 |  | 5 SERIES OUTDOOR SPLITS | WBAHP-CB | Water-to-Air and Brine-to-Air | NDS038J1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
202328431 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | SM036-1AV*-*****B | [5 empty] | 40900 | 21.05 | 4.4 | 35200 | 3.4083 | 37900 | 16.25 | 3.65 | 27400 | 3.1583
202328432 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSN-*****B | SM036-1AV*-*****B | [5 empty] | 40900 | 21.05 | 4.4 | 35200 | 3.4083 | 37900 | 16.25 | 3.65 | 27400 | 3.1583
202328433 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM048-1CSC-*****A | SM048-1AV*-*****A | [5 empty] | 52800 | 21.25 | 4.6 | 46600 | 4.4 | 48900 | 16.2 | 3.9 | 37800 | 4.075
202328434 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM060-1CSC-*****A | SM060-1AV*-*****A | [5 empty] | 64500 | 20.5 | 4.4 | 60500 | 5.375 | 58900 | 16.1 | 3.8 | 49000 | 4.9083
202328435 |  | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM060-1CSN-*****A | SM060-1AV*-*****A | [5 empty] | 64500 | 20.5 | 4.4 | 60500 | 5.375 | 58900 | 16.1 | 3.8 | 49000 | 4.9083
202328436 |  | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP018-1VT*******C | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202330436 |  | AAON, Inc. | WBAHP | Water-to-Air and Brine-to-Air | RQ-003-1-0-BCAY-V0-10-000-A | [6 empty] | 42600 | 23.1 | 4.3 | 37100 | 3.55
217351720 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT025-3***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351721 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT025-4***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351722 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT035-3***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351723 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT035-4***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351726 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT061-3***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
217351727 |  | FHP | WBWHP | Water-to-Water and Brine-to-Water | WT061-4***-*****C | [6 empty] | 59000 | 20.1 | 3.66 | 60000 | 4.9167 | 55500 | 15.3 | 3.06 | 49500 | 4.625
217351730 |  | CARRIER | WBAHP-CB | Water-to-Air and Brine-to-Air | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | [5 empty] | 28200 | 24.2 | 4.9 | 23400 | 2.35 | 26000 | 18.5 | 4.1 | 18800 | 2.1667
207348666 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348667 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348668 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*3*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348669 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348670 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
207348671 |  | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URS048*4*5 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
202132024 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | N-D/H/V-A-038-* | [6 empty] | 42000 | 22.89 | 4.28 | 42600 | 3.5 | 38100 | 17.47 | 3.66 | 32700 | 3.175
202132025 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | N-D/H/V-A-050-* | [6 empty] | 55400 | 22.21 | 4.1 | 57300 | 4.6167 | 52600 | 17.1 | 3.6 | 45200 | 4.3833
202132027 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | N-D/H/V-T-032-* | [6 empty] | 36500 | 20.8 | 4 | 30300 | 3.0417 | 32700 | 16.1 | 3.6 | 24100 | 2.725
202132029 |  | NORTHERN HEAT PUMP | WBAHP | Water-to-Air and Brine-to-Air | N-D/H/V-T-048-* | [6 empty] | 49300 | 19.3 | 4 | 44600 | 4.1083 | 47600 | 14.9 | 3.5 | 35600 | 3.9667